## test results
CRE test for: |  | MURRY P8 to PAIP4B [1371 - 6169] | [5 empty] | PASS
Line Rating: |  | 155
Direcction |  | West | → | North |  | W-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | MURRY P8 to PAIP4B [1371 - 6169]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.0054568
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.0010518
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.051813
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0024105
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | MURRY P8 to PAIP4B [1371 - 6169]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.0060267
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.00097227
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.048997
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.0024334
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | MURRY P8 to PAIP4B [1371 - 6169]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.0044846
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.054454
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.0030234
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.050049
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.0013587
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.054247
PTDF tests
West | → | North | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | -0.05784 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.05784 | 0.0044846
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.06175
[6 empty] | Concentration |  | -1.0676 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.062916
[6 empty] | Concentration |  | -1.0878 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 36.1702
| Percent of line rating => | [6 empty] | 23.34% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -14.0514
[7 empty] | B1(N-S) | 0.022888 | -0.040127 | -0.063014 | 0.022888
[7 empty] | B2 (N-W) | -0.049618 | -0.81477 | -0.76515 | -0.049618
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.023508 | -0.018975 | -0.042483 | 0.023508
[7 empty] | B4 (S-W) | -0.072516 | -0.77577 | -0.70325 | -0.072516
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.000932 | 0.020024 | 0.019092 | 0.000932
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.030695 | 0.79294 | 0.76224 | 0.030695
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | 2.816%
Deployment Error Percent | [6 empty] | B2 | -6.105%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 2.893%
[7 empty] | B4 | -8.923%
[7 empty] | B5 | 0.1147%
[7 empty] | B6 | 3.777%
[7 empty] | Max Abs Error | 8.923% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: MURRY P8 to PAIP4B [1371 - 6169] C: cookfield - long creek - graham [1430 - 1435] and [1430 - 1442] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: MURRY P8 to PAIP4B [1371 - 6169] C: cookfield - long creek - graham [1430 - 1435] and [1430 - 1442]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.003337 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 0.85093
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.003337 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 0.49721
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.003848 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.05772
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.003848 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.05772
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.003337 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 0.51056
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.003414 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 0.5121
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.003414 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.27312
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.012427 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 0.90717
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.012427 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 1.4788
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.012427 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 2.5475
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.012427 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 1.2676
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.012427 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 1.193
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.02288 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.27456
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.02288 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.27456
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.004225 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 0.7098
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.004225 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 0.38025
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.012641 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.22754
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.012641 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.22754
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.012641 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.48036
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.01006 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 2.8973
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.01006 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 1.4788
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.01006 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 1.4788
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.007983 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 0.89809
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.004738 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.18952
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004756 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 0.37572
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004756 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 0.50414
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004756 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 0.69438
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004756 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 0.36146
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.005768 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 0.34608
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.005768 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 0.36338
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.004739 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.09478
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.004739 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.11847
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.004739 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.1943
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.00316 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 1.4631
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -3.3292
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -3.2787
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -3.3796
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -3.3796
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -3.3796
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.050442 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -5.7504
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.050442 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -25.9776
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -3.7547
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -3.9253
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -3.9253
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -3.8116
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -3.8116
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -3.6978
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.049339 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -3.4537
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.049339 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -3.6215
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.049339 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -3.4735
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -7.3633
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -10.7996
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.073351 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -7.2617
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.073351 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -4.4744
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.072885 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -10.2768
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.073351 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -1.8338
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.073351 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -3.3521
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.073351 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -3.3521
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.072885 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -8.7462
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.05794 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -1.4949
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.053903 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -5.4173
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.059789 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -7.1747
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.053933 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -3.1281
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.054347 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -11.6411
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.071826 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -10.7739
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.056168 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -0.37071
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.056168 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -1.9266
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.071826 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -7.2544
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.061098 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -7.3318
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.010343 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 3.7855
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.069487 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 16.8159
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.052721 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -21.0884
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.052712 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -12.44
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.052712 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -8.6975
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.006714 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 1.3697
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.006714 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 1.3495
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.006714 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 1.6248
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.24394
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.24394
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.24394
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.20735
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.039372 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 4.7246
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.005866 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 0.35196
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.004876 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 0.3657
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.004876 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 0.38813
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.004876 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 0.43104
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 0.78032
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.76081
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 0.95589
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.76081
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 0.76569
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 0.96565
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.005003 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 0.85051
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.005003 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 2.6016
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004896 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 1.8115
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.004833 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 2.6968
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.004833 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 2.7983
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.004833 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 3.9051
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.006061 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 0.67883
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.006061 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 0.6061
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.006061 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 2.2911
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.00281 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 0.61061
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.00281 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 0.57605
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.00281 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 0.76544
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.003711 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 2.8575
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 0.31969
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.31512
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.31512
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.31056
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.002558 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 2.9596
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.002558 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 2.9622
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 0.91616
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 0.92434
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.004234 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 0.91624
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.004234 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 0.91497
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 0.86708
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 0.86299
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.004757 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 1.879
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.004766 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 2.0732
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.004757 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 2.0693
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.005061 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 0.69842
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.004551 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 0.53702
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.004551 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 0.52336
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.004551 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 2.5304
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.004654 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 1.8058
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.004654 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 2.3968
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004376 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 3.4352
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004376 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 3.4789
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004376 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 3.4133
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.004303 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 0.78315
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.004303 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 2.0827
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.004233 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 0.94819
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.004307 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.21535
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.004311 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.18106
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.003932 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 2.4182
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.003932 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 2.3081
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.003244 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 1.742
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.003244 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 2.553
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.003142 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.23565
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.003142 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 0.69752
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.002067 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 1.1761
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000778 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.1626
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000778 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.16805
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.000749 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 0.30484
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.035788
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.036566
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.035788
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.035788
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.000794 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 0.33666
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.000794 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 0.33745
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000664 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.038512
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000664 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.059096
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.029216
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.029216
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.028552
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.02988
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.000779 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 0.32095
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.000779 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 0.3116
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.000903 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 0.49304
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.000903 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 0.67725
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.000857 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.052277
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.000857 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.081415
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.000857 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.12941
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.000875 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.13562
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.000875 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.14875
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.000875 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.13562
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.001145 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.02519
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.001145 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.012595
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.001145 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.012595
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.056286
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.044014
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.05428
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.05664
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000493 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.005916
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000493 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.005423
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.000993 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.023832
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.000993 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.023832
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.000993 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.022839
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.000764 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 0.30254
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.001949 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 2.598
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.001949 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 2.5883
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000965 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.03667
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000965 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.018624
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000965 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.014475
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000965 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.045355
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.047327 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -3.5495
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.12405 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -18.6083
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.050845 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -8.6182
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.035508 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -5.3262
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.069302 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -4.366
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.02595 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -16.8597
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.005076 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.20304
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.005076 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.20304
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.000736 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -0.31059
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.001519 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.20051
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.001519 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.20355
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.001519 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 0.49064
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.001616 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.25533
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.001616 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.25856
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.001616 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 0.2828
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.001618 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 0.94491
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.001618 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 0.96271
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.001617 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 0.70016
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.25525
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.2565
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.25604
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.25844
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.001343 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.010744
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.001343 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.010744
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.00081 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.01458
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.00081 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.01458
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.00081 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.01215
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.001376 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.018851
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.000251 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.004518
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.000251 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.004518
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000849 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.029715
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000849 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.028866
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000849 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.029715
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.000613 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.017164
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.000613 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.017777
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.050997 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -1.7849
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.050997 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -1.5299
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.0789
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.0789
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.0789
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.0789
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.001027 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.006162
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.001089 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0026136
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.001089 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0026136
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.001089 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.0030492
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.001011 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.004044
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.001169 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0028056
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.001169 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0028056
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.15288
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.14352
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.1456
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.15288
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.18928
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.20592
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.001524 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.23241
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.001524 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.22784
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.001524 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 0.35448
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.15478
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.15805
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.16459
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 0.3161
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.012989 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.42864
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.012989 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.32472
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000493 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.005916
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.001214 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.088622
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.10594
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.10862
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.035168
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.008792
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.10594
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.10728
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.10513
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.033525
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.061686
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.001037 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 0.65227
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.001195 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.17208
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.001195 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.22466
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.001168 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.014016
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.009177 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.055062
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.001033 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 0.34709
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.001026 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 0.34268
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.001026 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 0.34884
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.001017 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.038646
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.001021 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.025525
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.001021 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.025525
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.001021 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.038798
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.000998 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.028942
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.001032 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.15305
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.001032 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.15336
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.001032 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.1579
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.1689
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.16356
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.1069
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.15501
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.15714
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.13576
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.000866 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.12687
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.000866 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.12808
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.000866 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.14982
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.1921
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.2011
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.22458
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.13363
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.13363
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.15869
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.001389 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 0.43059
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.001389 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 0.57366
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.060018
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.062876
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.062876
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.067163
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.067424
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.063296
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.063296
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.064672
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.001376 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.2119
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.001376 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.20365
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.066048
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.066048
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -3.4791
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -3.4791
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -4.6123
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -3.9761
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -3.9761
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -5.7156
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -10.3492
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -7.0635
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -6.5813
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -6.7603
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -7.3071
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -10.4387
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -8.6141
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -5.2138
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -10.2628
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -8.1196
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -9.8178
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -5.9839
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.052256 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -7.7861
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.065965 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -11.8737
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.065965 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -11.8737
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.065405 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -14.7161
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.049368 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -6.171
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.049368 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -6.171
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 0.68544
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 0.69034
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 1.5129
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 0.70013
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 0.70502
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 1.5178
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.004298 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 0.84241
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.004298 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 0.47708
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.004918 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.74623
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.76014
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.76014
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 1.9189
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 0.75087
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.74623
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 0.7555
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 1.8957
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.004626 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.004626 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 0.64247
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 0.56433
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 0.62945
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 1.7321
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.00399 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 0.60129
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.00399 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 0.60249
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.00399 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 0.70783
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.004005 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 0.60676
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.004005 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 0.60996
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.004005 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 0.71089
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.002067 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 1.2009
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 2.9703
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 2.9703
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.003161 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.10115
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.003156 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.15149
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.003156 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.14518
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.037956
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.16131
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.003163 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.053771
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.069586
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.079075
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.003156 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.33138
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.082765 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -6.9523
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.047282 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -3.7826
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.047254 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -7.0881
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.047254 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -7.0881
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.16928
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.15948
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.12672
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 0.3663
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 0.36702
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 0.36415
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 0.22954
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 0.5834
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.09564
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 0.23982
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 0.22212
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 0.24556
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 0.24388
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.076512
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.07173
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.24642
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.24642
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 0.26418
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 0.24309
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 0.52909
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 0.53152
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.002493 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 0.33905
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.002334 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.077022
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.10471
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.10471
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.094734
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.094734
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.002189 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.15542
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.002189 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.02189
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.00233 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 0.37979
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.00233 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 0.37979
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.00233 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 0.57085
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.15951
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.14724
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.15951
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.15951
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.002479 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 0.36937
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.002479 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.16138
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 0.22268
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.21436
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.21289
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.13336
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.029853
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.002523 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 1.8746
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.00251 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 1.8449
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.002526 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.43447
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.002526 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.43447
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.002526 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.43447
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 0.44893
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.002495 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 0.43163
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.002495 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 0.33682
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 0.4127
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 0.40915
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 0.40281
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 0.68242
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.15872
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.15674
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.20485
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.18253
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 0.40327
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 0.38819
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 0.38918
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 0.38795
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 0.6647
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.002522 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.01261
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.002522 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.052962
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 0.47247
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.47798
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.47798
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 1.1643
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.002539 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 1.0105
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.11348
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.11348
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.11348
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.13569
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.13569
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.13322
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.0036 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 2.9772
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.0036 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 2.9484
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.002319 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.10691
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.15033
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.15033
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 0.20769
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.14637
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.14637
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 0.20176
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.00248 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 0.4464
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.00248 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 0.39333
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.00248 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 0.38936
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.002475 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.086625
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.002428 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 1.1145
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.164
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.16652
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.17661
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.15895
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.15643
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 0.26239
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.14886
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 0.40482
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.39963
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.39963
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.002595 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 0.42039
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.002526 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 0.39658
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.17644
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.17892
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.096915
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.07455
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.002468 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.1925
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.002468 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.19744
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.040176
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.002479 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 0.40903
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.002479 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 0.41895
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.00248 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 0.52824
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.00248 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 0.56544
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.002478 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.029736
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.002478 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.044604
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.002415 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.12075
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.26083
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.26083
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.13543
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.13292
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.13543
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.14296
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.13543
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.13543
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.14546
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.14546
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.002519 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.030228
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.14252
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.15016
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.14252
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.14252
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.15016
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.14252
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.002 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.132
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.002349 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 0.37819
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.002349 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 0.38993
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.002349 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 0.58255
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.002349 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 1.2826
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.002349 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 1.5104
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.002329 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 1.5162
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.002329 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 1.3136
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.002329 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 1.3974
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.002349 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.030537
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.002523 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.030276
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.085476
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.087236
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.082208
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.11539
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.044498
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.051286
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.050029
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.08799
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.045252
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.2147
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 0.37207
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.13342
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.15365
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.09684
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.21735
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.18507
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.18938
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.1076
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.038736
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 0.20229
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.15064
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.13558
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.15494
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.13945
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.21735
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 0.20874
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 0.22166
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.16355
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.17216
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.17216
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 0.36799
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01139
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.045939 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -3.5143
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.047327 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -3.7862
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.047327 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -1.8931
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.047523 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -3.8018
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.047289 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -3.7831
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.046224 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -3.6979
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.045877 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -3.8537
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.047523 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -3.8018
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.068856
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.05351 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -6.4212
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.05351 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -12.4678
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.05351 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -9.1074
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.13409
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.11114
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.1353
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.06946
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.0604
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.13826 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -8.2957
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.013819 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.040416 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.048407 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.23235
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -1.922
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -5.5096
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -6.919
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -6.099
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -5.3815
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -4.1258
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.046572 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -6.9858
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -5.1877
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -6.8939
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -8.577
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -9.8912
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.000965 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.00829 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.000274 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.037548
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.058468
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.099234
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.09212
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.04018
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.03724
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.01862
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.09212
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.03528
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.04214
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.02156
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.048984
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.01884
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.008792
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.01884
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.048984
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.048984
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.14504
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.049
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.0539
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.049
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001069 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.012828
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.001238 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.01857
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.001238 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.028474
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.001323 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.063504
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.001243 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.009944
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.001032 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.18576
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.001033 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.18594
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.001026 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.18468
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.001026 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.18468
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000273 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.0273
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000273 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.0273
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.02635
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.02635
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.02635
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.016864
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.02635
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.02635
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.02635
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.01581
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -0.1365
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -0.1365
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.000823 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.012989 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.000136 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.000788 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: MURRY P8 to PAIP4B [1371 - 6169] C: cookfield - long creek - graham [1430 - 1435] and [1430 - 1442] | [7 empty] | 36.1702
Number of Bus | Name of Bus | ID | Max MW | L: MURRY P8 to PAIP4B [1371 - 6169] C: cookfield - long creek - graham [1430 - 1435] and [1430 - 1442] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.003337 | north | -0.0021198 | 0.0022852 | 0.05515 | 0.00092647 | 0.00092647 | houston | Y | 0.0021198 | 0.30431
239 | BOSQUESW | 1 | 149 | 0.003337 | north | -0.0021198 | 0.0022852 | 0.05515 | 0.00092647 | 0.00092647 | houston | Y | 0.0021198 | 0.17781
244 | WHITNYDM | 1 | 15 | 0.003848 | north | -0.0016088 | 0.0027962 | 0.055661 | 0.0014375 | 0.0014375 | houston | Y | 0.0016088 | 0.0025706
245 | WHITNYDM | 2 | 15 | 0.003848 | north | -0.0016088 | 0.0027962 | 0.055661 | 0.0014375 | 0.0014375 | houston | Y | 0.0016088 | 0.0025706
247 | BOSQUESW | 2 | 153 | 0.003337 | north | -0.0021198 | 0.0022852 | 0.05515 | 0.00092647 | 0.00092647 | houston | Y | 0.0021198 | 0.18259
251 | BOSQUESW | 2 | 150 | 0.003414 | north | -0.0020428 | 0.0023622 | 0.055227 | 0.0010035 | 0.0010035 | houston | Y | 0.0020428 | 0.15591
253 | BOSQUESW | 2 | 80 | 0.003414 | north | -0.0020428 | 0.0023622 | 0.055227 | 0.0010035 | 0.0010035 | houston | Y | 0.0020428 | 0.08315
332 | RWMILLER | 1 | 73 | 0.012427 | north | 0.0069702 | 0.011375 | 0.06424 | 0.010016 | 0.0069702 | North | N | 0.0069702 | 0
333 | RWMILLER | 2 | 119 | 0.012427 | north | 0.0069702 | 0.011375 | 0.06424 | 0.010016 | 0.0069702 | North | N | 0.0069702 | 0
334 | RWMILLER | 3 | 205 | 0.012427 | north | 0.0069702 | 0.011375 | 0.06424 | 0.010016 | 0.0069702 | North | N | 0.0069702 | 0
335 | RWMILLER | 4 | 102 | 0.012427 | north | 0.0069702 | 0.011375 | 0.06424 | 0.010016 | 0.0069702 | North | N | 0.0069702 | 0
336 | RWMILLER | 5 | 96 | 0.012427 | north | 0.0069702 | 0.011375 | 0.06424 | 0.010016 | 0.0069702 | North | N | 0.0069702 | 0
344 | MRSSHPRD | 1 | 12 | 0.02288 | north | 0.017423 | 0.021828 | 0.074693 | 0.020469 | 0.017423 | North | N | 0.017423 | 0
345 | MRSSHPRD | 2 | 12 | 0.02288 | north | 0.017423 | 0.021828 | 0.074693 | 0.020469 | 0.017423 | North | N | 0.017423 | 0
366 | JNSNCNTY | 1 | 168 | 0.004225 | north | -0.0012318 | 0.0031732 | 0.056038 | 0.0018145 | 0.0012318 | North | N | 0.0012318 | 0
367 | JNSNCNTY | 2 | 90 | 0.004225 | north | -0.0012318 | 0.0031732 | 0.056038 | 0.0018145 | 0.0012318 | North | N | 0.0012318 | 0
503 | NTHTEXAS | 1 | 18 | 0.012641 | north | 0.0071842 | 0.011589 | 0.064454 | 0.01023 | 0.0071842 | North | N | 0.0071842 | 0
504 | NTHTEXAS | 2 | 18 | 0.012641 | north | 0.0071842 | 0.011589 | 0.064454 | 0.01023 | 0.0071842 | North | N | 0.0071842 | 0
505 | NTHTEXAS | 3 | 38 | 0.012641 | north | 0.0071842 | 0.011589 | 0.064454 | 0.01023 | 0.0071842 | North | N | 0.0071842 | 0
580 | JCKCNTY8 | 1 | 288 | 0.01006 | north | 0.0046032 | 0.0090082 | 0.061873 | 0.0076495 | 0.0046032 | North | N | 0.0046032 | 0
581 | JCKCNTY8 | 2 | 147 | 0.01006 | north | 0.0046032 | 0.0090082 | 0.061873 | 0.0076495 | 0.0046032 | North | N | 0.0046032 | 0
582 | JCKCNTY8 | 3 | 147 | 0.01006 | north | 0.0046032 | 0.0090082 | 0.061873 | 0.0076495 | 0.0046032 | North | N | 0.0046032 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.007983 | north | 0.0025262 | 0.0069312 | 0.059796 | 0.0055725 | 0.0025262 | North | N | 0.0025262 | 0
837 | NEWMAN_G | 1 | 40 | 0.004738 | north | -0.00071884 | 0.0036862 | 0.056551 | 0.0023275 | 0.00071884 | North | N | 0.00071884 | 0
842 | OLINGER_ | 1 | 79 | 0.004756 | north | -0.00070084 | 0.0037042 | 0.056569 | 0.0023455 | 0.00070084 | North | N | 0.00070084 | 0
843 | OLINGER_ | 1 | 106 | 0.004756 | north | -0.00070084 | 0.0037042 | 0.056569 | 0.0023455 | 0.00070084 | North | N | 0.00070084 | 0
844 | OLINGER_ | 1 | 146 | 0.004756 | north | -0.00070084 | 0.0037042 | 0.056569 | 0.0023455 | 0.00070084 | North | N | 0.00070084 | 0
845 | OLINGER_ | 1 | 76 | 0.004756 | north | -0.00070084 | 0.0037042 | 0.056569 | 0.0023455 | 0.00070084 | North | N | 0.00070084 | 0
923 | SPENCER_ | 1 | 60 | 0.005768 | north | 0.00031116 | 0.0047162 | 0.057581 | 0.0033575 | 0.00031116 | North | N | 0.00031116 | 0
924 | SPENCER_ | 1 | 63 | 0.005768 | north | 0.00031116 | 0.0047162 | 0.057581 | 0.0033575 | 0.00031116 | North | N | 0.00031116 | 0
948 | STEAM1 | 1 | 20 | 0.004739 | north | -0.00071784 | 0.0036872 | 0.056552 | 0.0023285 | 0.00071784 | North | N | 0.00071784 | 0
949 | STEAM2 | 1 | 25 | 0.004739 | north | -0.00071784 | 0.0036872 | 0.056552 | 0.0023285 | 0.00071784 | North | N | 0.00071784 | 0
950 | STEAM3 | 1 | 41 | 0.004739 | north | -0.00071784 | 0.0036872 | 0.056552 | 0.0023285 | 0.00071784 | North | N | 0.00071784 | 0
990 | GIBN_CRE | 1 | 463 | 0.00316 | north | -0.0022968 | 0.0021082 | 0.054973 | 0.00074947 | 0.00074947 | houston | Y | 0.0022968 | 0.71643
1002 | PBCTAGE_ | A | 66 | -0.050442 | west | -0.055899 | -0.051494 | 0.0013713 | -0.052853 | 0.0013713 | west | N | 0.0013713 | 0
1003 | PBCTBGE_ | B | 65 | -0.050442 | west | -0.055899 | -0.051494 | 0.0013713 | -0.052853 | 0.0013713 | west | N | 0.0013713 | 0
1004 | PBCTCGE_ | C | 67 | -0.050442 | west | -0.055899 | -0.051494 | 0.0013713 | -0.052853 | 0.0013713 | west | N | 0.0013713 | 0
1005 | PBCTDGE_ | D | 67 | -0.050442 | west | -0.055899 | -0.051494 | 0.0013713 | -0.052853 | 0.0013713 | west | N | 0.0013713 | 0
1006 | PBCTEGE_ | E | 67 | -0.050442 | west | -0.055899 | -0.051494 | 0.0013713 | -0.052853 | 0.0013713 | west | N | 0.0013713 | 0
1007 | PB5GEN_6 | MB | 114 | -0.050442 | west | -0.055899 | -0.051494 | 0.0013713 | -0.052853 | 0.0013713 | west | N | 0.0013713 | 0
1008 | PB6GEN_7 | MB | 515 | -0.050442 | west | -0.055899 | -0.051494 | 0.0013713 | -0.052853 | 0.0013713 | west | N | 0.0013713 | 0
1039 | MRGNAG_1 | A | 66 | -0.056889 | west | -0.062346 | -0.057941 | -0.0050757 | -0.0593 | 0.0050757 | west | N | 0.0050757 | 0
1040 | MRGNBG_2 | B | 69 | -0.056889 | west | -0.062346 | -0.057941 | -0.0050757 | -0.0593 | 0.0050757 | west | N | 0.0050757 | 0
1041 | MRGNCG_3 | C | 69 | -0.056889 | west | -0.062346 | -0.057941 | -0.0050757 | -0.0593 | 0.0050757 | west | N | 0.0050757 | 0
1042 | MRGNDG_4 | D | 67 | -0.056889 | west | -0.062346 | -0.057941 | -0.0050757 | -0.0593 | 0.0050757 | west | N | 0.0050757 | 0
1043 | MRGNEG_5 | E | 67 | -0.056889 | west | -0.062346 | -0.057941 | -0.0050757 | -0.0593 | 0.0050757 | west | N | 0.0050757 | 0
1044 | MRGNFG_6 | F | 65 | -0.056889 | west | -0.062346 | -0.057941 | -0.0050757 | -0.0593 | 0.0050757 | west | N | 0.0050757 | 0
1045 | CALENG1G | 1 | 70 | -0.049339 | west | -0.054796 | -0.050391 | 0.0024743 | -0.05175 | 0.0024743 | west | N | 0.0024743 | 0
1046 | CALENG2G | 2 | 73.4 | -0.049339 | west | -0.054796 | -0.050391 | 0.0024743 | -0.05175 | 0.0024743 | west | N | 0.0024743 | 0
1047 | CALENG3G | 3 | 70.4 | -0.049339 | west | -0.054796 | -0.050391 | 0.0024743 | -0.05175 | 0.0024743 | west | N | 0.0024743 | 0
1058 | LONGSHOR | 1 | 150 | -0.049089 | west | -0.054546 | -0.050141 | 0.0027243 | -0.0515 | 0.0027243 | west | N | 0.0027243 | 0
1058 | LONGSHOR | 2 | 220 | -0.049089 | west | -0.054546 | -0.050141 | 0.0027243 | -0.0515 | 0.0027243 | west | N | 0.0027243 | 0
1061 | CIELOGEN | 1 | 99 | -0.073351 | west | -0.078808 | -0.074403 | -0.021538 | -0.075762 | 0.021538 | west | N | 0.021538 | 0
1062 | CIELOGEN | 1 | 61 | -0.073351 | west | -0.078808 | -0.074403 | -0.021538 | -0.075762 | 0.021538 | west | N | 0.021538 | 0
1068 | SCURRYCW | 1 | 141 | -0.072885 | west | -0.078342 | -0.073937 | -0.021072 | -0.075296 | 0.021072 | west | N | 0.021072 | 0
1069 | KINDERMG | 1 | 25 | -0.073351 | west | -0.078808 | -0.074403 | -0.021538 | -0.075762 | 0.021538 | west | N | 0.021538 | 0
1070 | KINDERMG | 1 | 45.7 | -0.073351 | west | -0.078808 | -0.074403 | -0.021538 | -0.075762 | 0.021538 | west | N | 0.021538 | 0
1071 | KINDERMG | 1 | 45.7 | -0.073351 | west | -0.078808 | -0.074403 | -0.021538 | -0.075762 | 0.021538 | west | N | 0.021538 | 0
1073 | SCURRYCW | 2 | 120 | -0.072885 | west | -0.078342 | -0.073937 | -0.021072 | -0.075296 | 0.021072 | west | N | 0.021072 | 0
1320 | BSP 1 | 1 | 25.8 | -0.05794 | west | -0.063397 | -0.058992 | -0.0061267 | -0.060351 | 0.0061267 | west | N | 0.0061267 | 0
1326 | STANTONW | 1 | 100.5 | -0.053903 | west | -0.05936 | -0.054955 | -0.0020897 | -0.056314 | 0.0020897 | west | N | 0.0020897 | 0
1327 | WILDHRSE | 1 | 120 | -0.059789 | west | -0.065246 | -0.060841 | -0.0079757 | -0.0622 | 0.0079757 | west | N | 0.0079757 | 0
1328 | OCOTILLO | 1 | 58 | -0.053933 | west | -0.05939 | -0.054985 | -0.0021197 | -0.056344 | 0.0021197 | west | N | 0.0021197 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.054347 | west | -0.059804 | -0.055399 | -0.0025337 | -0.056758 | 0.0025337 | west | N | 0.0025337 | 0
1343 | TRENTIPP | 1 | 150 | -0.071826 | west | -0.077283 | -0.072878 | -0.020013 | -0.074237 | 0.020013 | west | N | 0.020013 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.056168 | west | -0.061625 | -0.05722 | -0.0043547 | -0.058579 | 0.0043547 | west | N | 0.0043547 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.056168 | west | -0.061625 | -0.05722 | -0.0043547 | -0.058579 | 0.0043547 | west | N | 0.0043547 | 0
1354 | AEPWIND_ | 1 | 101 | -0.071826 | west | -0.077283 | -0.072878 | -0.020013 | -0.074237 | 0.020013 | west | N | 0.020013 | 0
1360 | GUNSIGHT | 1 | 120 | -0.061098 | west | -0.066555 | -0.06215 | -0.0092847 | -0.063509 | 0.0092847 | west | N | 0.0092847 | 0
1432 | GRHAMSES | 2 | 366 | 0.010343 | north | 0.0048862 | 0.0092912 | 0.062156 | 0.0079325 | 0.0048862 | North | N | 0.0048862 | 0
1433 | GRHAMSES | 1 | 242 | 0.069487 | north | 0.06403 | 0.068435 | 0.1213 | 0.067076 | 0.06403 | North | N | 0.06403 | 0
1437 | MESQUITW | 1 | 400 | -0.052721 | west | -0.058178 | -0.053773 | -0.00090774 | -0.055132 | 0.00090774 | west | N | 0.00090774 | 0
1438 | MESQUITW | 1 | 236 | -0.052712 | west | -0.058169 | -0.053764 | -0.00089874 | -0.055123 | 0.00089874 | west | N | 0.00089874 | 0
1442 | COKFIELD | 1 | 165 | -0.052712 | west | -0.058169 | -0.053764 | -0.00089874 | -0.055123 | 0.00089874 | west | N | 0.00089874 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.006714 | north | 0.0012572 | 0.0056622 | 0.058527 | 0.0043035 | 0.0012572 | North | N | 0.0012572 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.006714 | north | 0.0012572 | 0.0056622 | 0.058527 | 0.0043035 | 0.0012572 | North | N | 0.0012572 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.006714 | north | 0.0012572 | 0.0056622 | 0.058527 | 0.0043035 | 0.0012572 | North | N | 0.0012572 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.012197 | west | 0.0067402 | 0.011145 | 0.06401 | 0.0097865 | 0.0067402 | North | Y | 0.06401 | 1.1454
1479 | WFCOGEN_ | 2 | 20 | 0.012197 | west | 0.0067402 | 0.011145 | 0.06401 | 0.0097865 | 0.0067402 | North | Y | 0.06401 | 1.1454
1482 | WFCOGEN_ | 1 | 20 | 0.012197 | west | 0.0067402 | 0.011145 | 0.06401 | 0.0097865 | 0.0067402 | North | Y | 0.06401 | 1.1454
1482 | WFCOGEN_ | 2 | 17 | 0.012197 | west | 0.0067402 | 0.011145 | 0.06401 | 0.0097865 | 0.0067402 | North | Y | 0.06401 | 0.97359
1600 | BARTNWND | 1 | 120 | 0.039372 | north | 0.033915 | 0.03832 | 0.091185 | 0.036961 | 0.033915 | North | N | 0.033915 | 0
1643 | SLSTR1PP | 1 | 60 | 0.005866 | north | 0.00040916 | 0.0048142 | 0.057679 | 0.0034555 | 0.00040916 | North | N | 0.00040916 | 0
1675 | PEC_1G | 1 | 75 | 0.004876 | north | -0.00058084 | 0.0038242 | 0.056689 | 0.0024655 | 0.00058084 | North | N | 0.00058084 | 0
1676 | PEC_2G | 2 | 79.6 | 0.004876 | north | -0.00058084 | 0.0038242 | 0.056689 | 0.0024655 | 0.00058084 | North | N | 0.00058084 | 0
1677 | PEC_3G | 3 | 88.4 | 0.004876 | north | -0.00058084 | 0.0038242 | 0.056689 | 0.0024655 | 0.00058084 | North | N | 0.00058084 | 0
1678 | LAMARPWR | 1 | 160 | 0.004877 | north | -0.00057984 | 0.0038252 | 0.05669 | 0.0024665 | 0.00057984 | North | N | 0.00057984 | 0
1679 | LAMARPWR | 2 | 156 | 0.004877 | north | -0.00057984 | 0.0038252 | 0.05669 | 0.0024665 | 0.00057984 | North | N | 0.00057984 | 0
1680 | LAMARPWR | 3 | 196 | 0.004877 | north | -0.00057984 | 0.0038252 | 0.05669 | 0.0024665 | 0.00057984 | North | N | 0.00057984 | 0
1681 | LAMARPWR | 4 | 156 | 0.004877 | north | -0.00057984 | 0.0038252 | 0.05669 | 0.0024665 | 0.00057984 | North | N | 0.00057984 | 0
1682 | LAMARPWR | 5 | 157 | 0.004877 | north | -0.00057984 | 0.0038252 | 0.05669 | 0.0024665 | 0.00057984 | North | N | 0.00057984 | 0
1683 | LAMARPWR | 6 | 198 | 0.004877 | north | -0.00057984 | 0.0038252 | 0.05669 | 0.0024665 | 0.00057984 | North | N | 0.00057984 | 0
1687 | VALLEY_1 | 1 | 170 | 0.005003 | north | -0.00045384 | 0.0039512 | 0.056816 | 0.0025925 | 0.00045384 | North | N | 0.00045384 | 0
1688 | VALLEY_2 | 2 | 520 | 0.005003 | north | -0.00045384 | 0.0039512 | 0.056816 | 0.0025925 | 0.00045384 | North | N | 0.00045384 | 0
1689 | VALLEY_3 | 3 | 370 | 0.004896 | north | -0.00056084 | 0.0038442 | 0.056709 | 0.0024855 | 0.00056084 | North | N | 0.00056084 | 0
1701 | MOSES_1G | 1 | 558 | 0.004833 | north | -0.00062384 | 0.0037812 | 0.056646 | 0.0024225 | 0.00062384 | North | N | 0.00062384 | 0
1702 | MOSES_2G | 2 | 579 | 0.004833 | north | -0.00062384 | 0.0037812 | 0.056646 | 0.0024225 | 0.00062384 | North | N | 0.00062384 | 0
1703 | MOSES_3G | 3 | 808 | 0.004833 | north | -0.00062384 | 0.0037812 | 0.056646 | 0.0024225 | 0.00062384 | North | N | 0.00062384 | 0
1861 | EAGLEMNT | MB | 112 | 0.006061 | north | 0.00060416 | 0.0050092 | 0.057874 | 0.0036505 | 0.00060416 | North | N | 0.00060416 | 0
1862 | EAGLEMNT | MB | 100 | 0.006061 | north | 0.00060416 | 0.0050092 | 0.057874 | 0.0036505 | 0.00060416 | North | N | 0.00060416 | 0
1863 | EAGLEMNT | MB | 378 | 0.006061 | north | 0.00060416 | 0.0050092 | 0.057874 | 0.0036505 | 0.00060416 | North | N | 0.00060416 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.00281 | north | -0.0026468 | 0.0017582 | 0.054623 | 0.00039947 | 0.00039947 | houston | Y | 0.0026468 | 0.48835
1878 | WLFHOLW_ | 2 | 205 | 0.00281 | north | -0.0026468 | 0.0017582 | 0.054623 | 0.00039947 | 0.00039947 | houston | Y | 0.0026468 | 0.46071
1879 | WLFHOLW_ | 3 | 272.4 | 0.00281 | north | -0.0026468 | 0.0017582 | 0.054623 | 0.00039947 | 0.00039947 | houston | Y | 0.0026468 | 0.61218
1889 | DECRDOVA | MB | 770 | 0.003711 | north | -0.0017458 | 0.0026592 | 0.055524 | 0.0013005 | 0.0013005 | houston | Y | 0.0017458 | 0.34294
1892 | DECRDOVA | A | 70 | 0.004567 | north | -0.00088984 | 0.0035152 | 0.05638 | 0.0021565 | 0.00088984 | North | N | 0.00088984 | 0
1893 | DECRDOVA | B | 69 | 0.004567 | north | -0.00088984 | 0.0035152 | 0.05638 | 0.0021565 | 0.00088984 | North | N | 0.00088984 | 0
1894 | DECRDOVA | C | 69 | 0.004567 | north | -0.00088984 | 0.0035152 | 0.05638 | 0.0021565 | 0.00088984 | North | N | 0.00088984 | 0
1895 | DECRDOVA | D | 68 | 0.004567 | north | -0.00088984 | 0.0035152 | 0.05638 | 0.0021565 | 0.00088984 | North | N | 0.00088984 | 0
1898 | COMCHEPK | 1 | 1157 | 0.002558 | north | -0.0028988 | 0.0015062 | 0.054371 | 0.00014747 | 0.00014747 | houston | Y | 0.0028988 | 3.1833
1899 | COMCHEPK | 2 | 1158 | 0.002558 | north | -0.0028988 | 0.0015062 | 0.054371 | 0.00014747 | 0.00014747 | houston | Y | 0.0028988 | 3.1861
1937 | MDLTHELP | 5 | 224 | 0.00409 | north | -0.0013668 | 0.0030382 | 0.055903 | 0.0016795 | 0.0013668 | North | N | 0.0013668 | 0
1938 | MDLTHELP | 6 | 226 | 0.00409 | north | -0.0013668 | 0.0030382 | 0.055903 | 0.0016795 | 0.0013668 | North | N | 0.0013668 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.004234 | north | -0.0012228 | 0.0031822 | 0.056047 | 0.0018235 | 0.0012228 | North | N | 0.0012228 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.004234 | north | -0.0012228 | 0.0031822 | 0.056047 | 0.0018235 | 0.0012228 | North | N | 0.0012228 | 0
1943 | MDLTHELP | 3 | 212 | 0.00409 | north | -0.0013668 | 0.0030382 | 0.055903 | 0.0016795 | 0.0013668 | North | N | 0.0013668 | 0
1944 | MDLTHELP | 4 | 211 | 0.00409 | north | -0.0013668 | 0.0030382 | 0.055903 | 0.0016795 | 0.0013668 | North | N | 0.0013668 | 0
1947 | HANDLEY_ | 3 | 395 | 0.004757 | north | -0.00069984 | 0.0037052 | 0.05657 | 0.0023465 | 0.00069984 | North | N | 0.00069984 | 0
1948 | HANDLEY_ | 4 | 435 | 0.004766 | north | -0.00069084 | 0.0037142 | 0.056579 | 0.0023555 | 0.00069084 | North | N | 0.00069084 | 0
1949 | HANDLEY_ | 5 | 435 | 0.004757 | north | -0.00069984 | 0.0037052 | 0.05657 | 0.0023465 | 0.00069984 | North | N | 0.00069984 | 0
2371 | COLLIN_1 | MB | 138 | 0.005061 | north | -0.00039584 | 0.0040092 | 0.056874 | 0.0026505 | 0.00039584 | North | N | 0.00039584 | 0
2413 | MTCK6_G | 6 | 118 | 0.004551 | north | -0.00090584 | 0.0034992 | 0.056364 | 0.0021405 | 0.00090584 | North | N | 0.00090584 | 0
2414 | MTCK7_G | 7 | 115 | 0.004551 | north | -0.00090584 | 0.0034992 | 0.056364 | 0.0021405 | 0.00090584 | North | N | 0.00090584 | 0
2417 | MTCK8_G | 8 | 556 | 0.004551 | north | -0.00090584 | 0.0034992 | 0.056364 | 0.0021405 | 0.00090584 | North | N | 0.00090584 | 0
2451 | LKHB1_G | 1 | 388 | 0.004654 | north | -0.00080284 | 0.0036022 | 0.056467 | 0.0022435 | 0.00080284 | North | N | 0.00080284 | 0
2452 | LKHB2_G | 2 | 515 | 0.004654 | north | -0.00080284 | 0.0036022 | 0.056467 | 0.0022435 | 0.00080284 | North | N | 0.00080284 | 0
3097 | MARTLAKE | 1 | 785 | 0.004376 | north | -0.0010808 | 0.0033242 | 0.056189 | 0.0019655 | 0.0010808 | North | N | 0.0010808 | 0
3098 | MARTLAKE | 2 | 795 | 0.004376 | north | -0.0010808 | 0.0033242 | 0.056189 | 0.0019655 | 0.0010808 | North | N | 0.0010808 | 0
3099 | MARTLAKE | 3 | 780 | 0.004376 | north | -0.0010808 | 0.0033242 | 0.056189 | 0.0019655 | 0.0010808 | North | N | 0.0010808 | 0
3107 | STRYKER_ | 1 | 182 | 0.004303 | north | -0.0011538 | 0.0032512 | 0.056116 | 0.0018925 | 0.0011538 | North | N | 0.0011538 | 0
3108 | STRYKER_ | 2 | 484 | 0.004303 | north | -0.0011538 | 0.0032512 | 0.056116 | 0.0018925 | 0.0011538 | North | N | 0.0011538 | 0
3126 | TRINIDAD | 1 | 224 | 0.004233 | north | -0.0012238 | 0.0031812 | 0.056046 | 0.0018225 | 0.0012238 | North | N | 0.0012238 | 0
3309 | ASPN_G | 1 | 50 | 0.004307 | north | -0.0011498 | 0.0032552 | 0.05612 | 0.0018965 | 0.0011498 | North | N | 0.0011498 | 0
3348 | CHAMPION | MB | 42 | 0.004311 | north | -0.0011458 | 0.0032592 | 0.056124 | 0.0019005 | 0.0011458 | North | N | 0.0011458 | 0
3381 | BBRN_1G | 1 | 615 | 0.003932 | north | -0.0015248 | 0.0028802 | 0.055745 | 0.0015215 | 0.0015215 | houston | Y | 0.0015248 | 0.0020748
3382 | BBRN_2G | 2 | 587 | 0.003932 | north | -0.0015248 | 0.0028802 | 0.055745 | 0.0015215 | 0.0015215 | houston | Y | 0.0015248 | 0.0019803
3403 | THOUSE_1 | MB | 537 | 0.003244 | north | -0.0022128 | 0.0021922 | 0.055057 | 0.00083347 | 0.00083347 | houston | Y | 0.0022128 | 0.74072
3404 | THOUSE_2 | 2 | 787 | 0.003244 | north | -0.0022128 | 0.0021922 | 0.055057 | 0.00083347 | 0.00083347 | houston | Y | 0.0022128 | 1.0856
3416 | LAKE_CRK | MB | 75 | 0.003142 | north | -0.0023148 | 0.0020902 | 0.054955 | 0.00073147 | 0.00073147 | houston | Y | 0.0023148 | 0.11875
3417 | LAKE_CRK | MB | 222 | 0.003142 | north | -0.0023148 | 0.0020902 | 0.054955 | 0.00073147 | 0.00073147 | houston | Y | 0.0023148 | 0.35151
3432 | SANDOW_4 | 4 | 569 | 0.002067 | south | -0.0033898 | 0.0010152 | 0.05388 | -0.00034353 | 0.00034353 | houston | Y | 0.0010152 | 0.38218
5026 | BRAUNIG_ | 1 | 209 | 0.000778 | south | -0.0046788 | -0.0002738 | 0.052591 | -0.0016325 | 0.0002738 | south | N | 0.0002738 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.000778 | south | -0.0046788 | -0.0002738 | 0.052591 | -0.0016325 | 0.0002738 | south | N | 0.0002738 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.000749 | south | -0.0047078 | -0.0003028 | 0.052562 | -0.0016615 | 0.0003028 | south | N | 0.0003028 | 0
5031 | BRA_VHBC | 1 | 46 | 0.000778 | south | -0.0046788 | -0.0002738 | 0.052591 | -0.0016325 | 0.0002738 | south | N | 0.0002738 | 0
5032 | BRA_VHBC | 2 | 47 | 0.000778 | south | -0.0046788 | -0.0002738 | 0.052591 | -0.0016325 | 0.0002738 | south | N | 0.0002738 | 0
5033 | BRA_VHBC | 3 | 46 | 0.000778 | south | -0.0046788 | -0.0002738 | 0.052591 | -0.0016325 | 0.0002738 | south | N | 0.0002738 | 0
5034 | BRA_VHBC | 4 | 46 | 0.000778 | south | -0.0046788 | -0.0002738 | 0.052591 | -0.0016325 | 0.0002738 | south | N | 0.0002738 | 0
5111 | CALAVER_ | 1 | 424 | 0.000794 | south | -0.0046628 | -0.0002578 | 0.052607 | -0.0016165 | 0.0002578 | south | N | 0.0002578 | 0
5112 | CALAVER_ | 2 | 425 | 0.000794 | south | -0.0046628 | -0.0002578 | 0.052607 | -0.0016165 | 0.0002578 | south | N | 0.0002578 | 0
5264 | LEON_LCP | 3 | 58 | 0.000664 | south | -0.0047928 | -0.0003878 | 0.052477 | -0.0017465 | 0.0003878 | south | N | 0.0003878 | 0
5265 | LEON_LCP | 4 | 89 | 0.000664 | south | -0.0047928 | -0.0003878 | 0.052477 | -0.0017465 | 0.0003878 | south | N | 0.0003878 | 0
5266 | LEON_LCP | 1 | 44 | 0.000664 | south | -0.0047928 | -0.0003878 | 0.052477 | -0.0017465 | 0.0003878 | south | N | 0.0003878 | 0
5267 | LEON_LCP | 2 | 44 | 0.000664 | south | -0.0047928 | -0.0003878 | 0.052477 | -0.0017465 | 0.0003878 | south | N | 0.0003878 | 0
5268 | LEON_LCP | 3 | 43 | 0.000664 | south | -0.0047928 | -0.0003878 | 0.052477 | -0.0017465 | 0.0003878 | south | N | 0.0003878 | 0
5269 | LEON_LCP | 4 | 45 | 0.000664 | south | -0.0047928 | -0.0003878 | 0.052477 | -0.0017465 | 0.0003878 | south | N | 0.0003878 | 0
5396 | CALAVER_ | 1 | 412 | 0.000779 | south | -0.0046778 | -0.0002728 | 0.052592 | -0.0016315 | 0.0002728 | south | N | 0.0002728 | 0
5397 | CALAVER_ | 2 | 400 | 0.000779 | south | -0.0046778 | -0.0002728 | 0.052592 | -0.0016315 | 0.0002728 | south | N | 0.0002728 | 0
5401 | CALAVER_ | 1 | 546 | 0.000903 | south | -0.0045538 | -0.0001488 | 0.052716 | -0.0015075 | 0.0001488 | south | N | 0.0001488 | 0
5402 | CALAVER_ | 2 | 750 | 0.000903 | south | -0.0045538 | -0.0001488 | 0.052716 | -0.0015075 | 0.0001488 | south | N | 0.0001488 | 0
5436 | TUTTL_WB | MB | 61 | 0.000857 | south | -0.0045998 | -0.0001948 | 0.05267 | -0.0015535 | 0.0001948 | south | N | 0.0001948 | 0
5438 | TUTTL_WB | MB | 95 | 0.000857 | south | -0.0045998 | -0.0001948 | 0.05267 | -0.0015535 | 0.0001948 | south | N | 0.0001948 | 0
5439 | TUTTL_WB | MB | 151 | 0.000857 | south | -0.0045998 | -0.0001948 | 0.05267 | -0.0015535 | 0.0001948 | south | N | 0.0001948 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.000875 | south | -0.0045818 | -0.0001768 | 0.052688 | -0.0015355 | 0.0001768 | south | N | 0.0001768 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.000875 | south | -0.0045818 | -0.0001768 | 0.052688 | -0.0015355 | 0.0001768 | south | N | 0.0001768 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.000875 | south | -0.0045818 | -0.0001768 | 0.052688 | -0.0015355 | 0.0001768 | south | N | 0.0001768 | 0
5503 | RAYBURNG | 1 | 22 | 0.001145 | south | -0.0043118 | 9.3199e-05 | 0.052958 | -0.0012655 | 9.3199e-05 | south | N | 9.3199e-05 | 0
5505 | RAYBURNG | 1 | 11 | 0.001145 | south | -0.0043118 | 9.3199e-05 | 0.052958 | -0.0012655 | 9.3199e-05 | south | N | 9.3199e-05 | 0
5506 | RAYBURNG | 1 | 11 | 0.001145 | south | -0.0043118 | 9.3199e-05 | 0.052958 | -0.0012655 | 9.3199e-05 | south | N | 9.3199e-05 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.00118 | south | -0.0042768 | 0.0001282 | 0.052993 | -0.0012305 | 0.0001282 | south | N | 0.0001282 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.00118 | south | -0.0042768 | 0.0001282 | 0.052993 | -0.0012305 | 0.0001282 | south | N | 0.0001282 | 0
5511 | RAYBURNC | 1 | 46 | 0.00118 | south | -0.0042768 | 0.0001282 | 0.052993 | -0.0012305 | 0.0001282 | south | N | 0.0001282 | 0
5512 | RAYBURNC | 1 | 48 | 0.00118 | south | -0.0042768 | 0.0001282 | 0.052993 | -0.0012305 | 0.0001282 | south | N | 0.0001282 | 0
5728 | FALCONHY | 2 | 12 | 0.000493 | south | -0.0049638 | -0.0005588 | 0.052306 | -0.0019175 | 0.0005588 | south | N | 0.0005588 | 0
5729 | FALCONHY | 3 | 11 | 0.000493 | south | -0.0049638 | -0.0005588 | 0.052306 | -0.0019175 | 0.0005588 | south | N | 0.0005588 | 0
5890 | PEARSALL | 1 | 24 | -0.000993 | south | -0.0064498 | -0.0020448 | 0.05082 | -0.0034035 | 0.0020448 | south | N | 0.0020448 | 0
5891 | PEARSALL | 1 | 24 | -0.000993 | south | -0.0064498 | -0.0020448 | 0.05082 | -0.0034035 | 0.0020448 | south | N | 0.0020448 | 0
5892 | PEARSALL | 1 | 23 | -0.000993 | south | -0.0064498 | -0.0020448 | 0.05082 | -0.0034035 | 0.0020448 | south | N | 0.0020448 | 0
5903 | SANMIGUE | 1 | 396 | 0.000764 | south | -0.0046928 | -0.0002878 | 0.052577 | -0.0016465 | 0.0002878 | south | N | 0.0002878 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.001949 | houston | -0.0035078 | 0.0008972 | 0.053762 | -0.00046153 | 0.00046153 | houston | N | 0.00046153 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.001949 | houston | -0.0035078 | 0.0008972 | 0.053762 | -0.00046153 | 0.00046153 | houston | N | 0.00046153 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | Y | 0.0054568 | 2.643
5932 | SI_RAY9 | 9 | 38 | 0.000965 | south | -0.0044918 | -8.6801e-05 | 0.052778 | -0.0014455 | 8.6801e-05 | south | N | 8.6801e-05 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.000965 | south | -0.0044918 | -8.6801e-05 | 0.052778 | -0.0014455 | 8.6801e-05 | south | N | 8.6801e-05 | 0
5934 | SI_RAY5 | 5 | 15 | 0.000965 | south | -0.0044918 | -8.6801e-05 | 0.052778 | -0.0014455 | 8.6801e-05 | south | N | 8.6801e-05 | 0
5935 | SI_RAY10 | 10 | 47 | 0.000965 | south | -0.0044918 | -8.6801e-05 | 0.052778 | -0.0014455 | 8.6801e-05 | south | N | 8.6801e-05 | 0
6016 | SWMESA | 1 | 75 | -0.047327 | west | -0.052784 | -0.048379 | 0.0044863 | -0.049738 | 0.0044863 | west | N | 0.0044863 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | Y | 0.051813 | 11.1675
6144 | MCADOO1A | 1 | 150 | -0.12405 | west | -0.12951 | -0.12511 | -0.072242 | -0.12647 | 0.072242 | west | N | 0.072242 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.050845 | west | -0.056302 | -0.051897 | 0.00096826 | -0.053256 | 0.00096826 | west | N | 0.00096826 | 0
6476 | LANGFORD | 1 | 150 | -0.035508 | west | -0.040965 | -0.03656 | 0.016305 | -0.037919 | 0.016305 | west | N | 0.016305 | 0
6637 | SNYDERW1 | 1 | 63 | -0.069302 | west | -0.074759 | -0.070354 | -0.017489 | -0.071713 | 0.017489 | west | N | 0.017489 | 0
6752 | OKLA0A | 1 | 649.7 | -0.02595 | west | -0.031407 | -0.027002 | 0.025863 | -0.028361 | 0.025863 | west | N | 0.025863 | 0
6948 | DENISNDM | 1 | 40 | 0.005076 | north | -0.00038084 | 0.0040242 | 0.056889 | 0.0026655 | 0.00038084 | North | N | 0.00038084 | 0
6948 | DENISNDM | 2 | 40 | 0.005076 | north | -0.00038084 | 0.0040242 | 0.056889 | 0.0026655 | 0.00038084 | North | N | 0.00038084 | 0
7000 | L_FERGUS | 1 | 422 | -0.000736 | south | -0.0061928 | -0.0017878 | 0.051077 | -0.0031465 | 0.0017878 | south | N | 0.0017878 | 0
7004 | L_SIMGID | 1 | 132 | 0.001519 | south | -0.0039378 | 0.0004672 | 0.053332 | -0.00089153 | 0.0004672 | south | N | 0.0004672 | 0
7005 | L_SIMGID | 2 | 134 | 0.001519 | south | -0.0039378 | 0.0004672 | 0.053332 | -0.00089153 | 0.0004672 | south | N | 0.0004672 | 0
7006 | L_SIMGID | 3 | 323 | 0.001519 | south | -0.0039378 | 0.0004672 | 0.053332 | -0.00089153 | 0.0004672 | south | N | 0.0004672 | 0
7007 | L_LOSTPI | 1 | 158 | 0.001616 | south | -0.0038408 | 0.0005642 | 0.053429 | -0.00079453 | 0.0005642 | south | N | 0.0005642 | 0
7008 | L_LOSTPI | 2 | 160 | 0.001616 | south | -0.0038408 | 0.0005642 | 0.053429 | -0.00079453 | 0.0005642 | south | N | 0.0005642 | 0
7009 | L_LOSTPI | 3 | 175 | 0.001616 | south | -0.0038408 | 0.0005642 | 0.053429 | -0.00079453 | 0.0005642 | south | N | 0.0005642 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.001618 | south | -0.0038388 | 0.0005662 | 0.053431 | -0.00079253 | 0.0005662 | south | N | 0.0005662 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.001618 | south | -0.0038388 | 0.0005662 | 0.053431 | -0.00079253 | 0.0005662 | south | N | 0.0005662 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.001617 | south | -0.0038398 | 0.0005652 | 0.05343 | -0.00079353 | 0.0005652 | south | N | 0.0005652 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.00114 | south | -0.0043168 | 8.8199e-05 | 0.052953 | -0.0012705 | 8.8199e-05 | south | N | 8.8199e-05 | 0
7015 | L_HAYSEN | 2 | 225 | 0.00114 | south | -0.0043168 | 8.8199e-05 | 0.052953 | -0.0012705 | 8.8199e-05 | south | N | 8.8199e-05 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.00114 | south | -0.0043168 | 8.8199e-05 | 0.052953 | -0.0012705 | 8.8199e-05 | south | N | 8.8199e-05 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.00114 | south | -0.0043168 | 8.8199e-05 | 0.052953 | -0.0012705 | 8.8199e-05 | south | N | 8.8199e-05 | 0
7020 | L_AUSTPL | 1 | 8 | 0.001343 | south | -0.0041138 | 0.0002912 | 0.053156 | -0.0010675 | 0.0002912 | south | N | 0.0002912 | 0
7020 | L_AUSTPL | 2 | 8 | 0.001343 | south | -0.0041138 | 0.0002912 | 0.053156 | -0.0010675 | 0.0002912 | south | N | 0.0002912 | 0
7022 | L_BUCHAN | 1 | 18 | -0.00081 | south | -0.0062668 | -0.0018618 | 0.051003 | -0.0032205 | 0.0018618 | south | N | 0.0018618 | 0
7023 | L_BUCHAN | 2 | 18 | -0.00081 | south | -0.0062668 | -0.0018618 | 0.051003 | -0.0032205 | 0.0018618 | south | N | 0.0018618 | 0
7024 | L_BUCHAN | 3 | 15 | -0.00081 | south | -0.0062668 | -0.0018618 | 0.051003 | -0.0032205 | 0.0018618 | south | N | 0.0018618 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.001376 | south | -0.0068328 | -0.0024278 | 0.050437 | -0.0037865 | 0.0024278 | south | N | 0.0024278 | 0
7028 | L_MARBFA | 1 | 18 | -0.000251 | south | -0.0057078 | -0.0013028 | 0.051562 | -0.0026615 | 0.0013028 | south | N | 0.0013028 | 0
7029 | L_MARBFA | 2 | 18 | -0.000251 | south | -0.0057078 | -0.0013028 | 0.051562 | -0.0026615 | 0.0013028 | south | N | 0.0013028 | 0
7031 | L_MARSFO | 1 | 35 | 0.000849 | south | -0.0046078 | -0.0002028 | 0.052662 | -0.0015615 | 0.0002028 | south | N | 0.0002028 | 0
7032 | L_MARSFO | 2 | 34 | 0.000849 | south | -0.0046078 | -0.0002028 | 0.052662 | -0.0015615 | 0.0002028 | south | N | 0.0002028 | 0
7033 | L_MARSFO | 3 | 35 | 0.000849 | south | -0.0046078 | -0.0002028 | 0.052662 | -0.0015615 | 0.0002028 | south | N | 0.0002028 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.000613 | south | -0.0060698 | -0.0016648 | 0.0512 | -0.0030235 | 0.0016648 | south | N | 0.0016648 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.000613 | south | -0.0060698 | -0.0016648 | 0.0512 | -0.0030235 | 0.0016648 | south | N | 0.0016648 | 0
7038 | L_DELAWA | 1 | 35 | -0.050997 | west | -0.056454 | -0.052049 | 0.00081626 | -0.053408 | 0.00081626 | west | N | 0.00081626 | 0
7038 | L_DELAWA | 2 | 30 | -0.050997 | west | -0.056454 | -0.052049 | 0.00081626 | -0.053408 | 0.00081626 | west | N | 0.00081626 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.001578 | south | -0.0038788 | 0.0005262 | 0.053391 | -0.00083253 | 0.0005262 | south | N | 0.0005262 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.001578 | south | -0.0038788 | 0.0005262 | 0.053391 | -0.00083253 | 0.0005262 | south | N | 0.0005262 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.001578 | south | -0.0038788 | 0.0005262 | 0.053391 | -0.00083253 | 0.0005262 | south | N | 0.0005262 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.001578 | south | -0.0038788 | 0.0005262 | 0.053391 | -0.00083253 | 0.0005262 | south | N | 0.0005262 | 0
7487 | L_CANYHY | 1 | 6 | 0.001027 | south | -0.0044298 | -2.4801e-05 | 0.05284 | -0.0013835 | 2.4801e-05 | south | N | 2.4801e-05 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.001089 | south | -0.0043678 | 3.7199e-05 | 0.052902 | -0.0013215 | 3.7199e-05 | south | N | 3.7199e-05 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.001089 | south | -0.0043678 | 3.7199e-05 | 0.052902 | -0.0013215 | 3.7199e-05 | south | N | 3.7199e-05 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.001089 | south | -0.0043678 | 3.7199e-05 | 0.052902 | -0.0013215 | 3.7199e-05 | south | N | 3.7199e-05 | 0
7609 | L_SCHUMA | 1 | 4 | 0.001011 | south | -0.0044458 | -4.0801e-05 | 0.052824 | -0.0013995 | 4.0801e-05 | south | N | 4.0801e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.001169 | south | -0.0042878 | 0.0001172 | 0.052982 | -0.0012415 | 0.0001172 | south | N | 0.0001172 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.001169 | south | -0.0042878 | 0.0001172 | 0.052982 | -0.0012415 | 0.0001172 | south | N | 0.0001172 | 0
7800 | L_GUADGE | 1 | 147 | 0.00104 | south | -0.0044168 | -1.1801e-05 | 0.052853 | -0.0013705 | 1.1801e-05 | south | N | 1.1801e-05 | 0
7801 | L_GUADGE | 2 | 138 | 0.00104 | south | -0.0044168 | -1.1801e-05 | 0.052853 | -0.0013705 | 1.1801e-05 | south | N | 1.1801e-05 | 0
7802 | L_GUADGE | 3 | 140 | 0.00104 | south | -0.0044168 | -1.1801e-05 | 0.052853 | -0.0013705 | 1.1801e-05 | south | N | 1.1801e-05 | 0
7803 | L_GUADGE | 4 | 147 | 0.00104 | south | -0.0044168 | -1.1801e-05 | 0.052853 | -0.0013705 | 1.1801e-05 | south | N | 1.1801e-05 | 0
7804 | L_GUADGE | 5 | 182 | 0.00104 | south | -0.0044168 | -1.1801e-05 | 0.052853 | -0.0013705 | 1.1801e-05 | south | N | 1.1801e-05 | 0
7805 | L_GUADGE | 6 | 198 | 0.00104 | south | -0.0044168 | -1.1801e-05 | 0.052853 | -0.0013705 | 1.1801e-05 | south | N | 1.1801e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.001524 | south | -0.0039328 | 0.0004722 | 0.053337 | -0.00088653 | 0.0004722 | south | N | 0.0004722 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.001524 | south | -0.0039328 | 0.0004722 | 0.053337 | -0.00088653 | 0.0004722 | south | N | 0.0004722 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.001524 | south | -0.0039328 | 0.0004722 | 0.053337 | -0.00088653 | 0.0004722 | south | N | 0.0004722 | 0
7810 | L_RIONOG | 1 | 142 | 0.00109 | south | -0.0043668 | 3.8199e-05 | 0.052903 | -0.0013205 | 3.8199e-05 | south | N | 3.8199e-05 | 0
7811 | L_RIONOG | 2 | 145 | 0.00109 | south | -0.0043668 | 3.8199e-05 | 0.052903 | -0.0013205 | 3.8199e-05 | south | N | 3.8199e-05 | 0
7812 | L_RIONOG | 3 | 151 | 0.00109 | south | -0.0043668 | 3.8199e-05 | 0.052903 | -0.0013205 | 3.8199e-05 | south | N | 3.8199e-05 | 0
7813 | L_RIONOG | 4 | 290 | 0.00109 | south | -0.0043668 | 3.8199e-05 | 0.052903 | -0.0013205 | 3.8199e-05 | south | N | 3.8199e-05 | 0
8032 | AMISTADH | 1 | 33 | -0.012989 | south | -0.018446 | -0.014041 | 0.038824 | -0.0154 | 0.014041 | south | N | 0.014041 | 0
8033 | AMISTADH | 2 | 25 | -0.012989 | south | -0.018446 | -0.014041 | 0.038824 | -0.0154 | 0.014041 | south | N | 0.014041 | 0
8048 | FALCONHY | 1 | 12 | 0.000493 | south | -0.0049638 | -0.0005588 | 0.052306 | -0.0019175 | 0.0005588 | south | N | 0.0005588 | 0
8066 | DUP1V#1 | 1 | 73 | 0.001214 | south | -0.0042428 | 0.0001622 | 0.053027 | -0.0011965 | 0.0001622 | south | N | 0.0001622 | 0
8134 | FOR69CG0 | 1 | 79 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
8138 | FOR69CG0 | 2 | 81 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
8139 | JOS #1 | MB | 255 | 0 | south | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | N | 0.0010518 | 0
8147 | UCAR #2 | 10 | 28 | 0.001256 | south | -0.0042008 | 0.0002042 | 0.053069 | -0.0011545 | 0.0002042 | south | N | 0.0002042 | 0
8148 | UCAR #1 | 2 | 7 | 0.001256 | south | -0.0042008 | 0.0002042 | 0.053069 | -0.0011545 | 0.0002042 | south | N | 0.0002042 | 0
8153 | FOR69CG0 | 3 | 79 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
8154 | FOR69CG0 | 4 | 80 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
8156 | FOR69CG0 | 6 | 25 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
8157 | FOR69CG0 | 7 | 46 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
8161 | COLETOU1 | 1 | 629 | 0.001037 | south | -0.0044198 | -1.4801e-05 | 0.05285 | -0.0013735 | 1.4801e-05 | south | N | 1.4801e-05 | 0
8173 | VICEC51A | 5 | 144 | 0.001195 | south | -0.0042618 | 0.0001432 | 0.053008 | -0.0012155 | 0.0001432 | south | N | 0.0001432 | 0
8174 | VICEC61A | 6 | 188 | 0.001195 | south | -0.0042618 | 0.0001432 | 0.053008 | -0.0012155 | 0.0001432 | south | N | 0.0001432 | 0
8189 | CUERO 2 | 1 | 12 | 0.001168 | south | -0.0042888 | 0.0001162 | 0.052981 | -0.0012425 | 0.0001162 | south | N | 0.0001162 | 0
8262 | ELPS | 1 | 6 | -0.009177 | south | -0.014634 | -0.010229 | 0.042636 | -0.011588 | 0.010229 | south | N | 0.010229 | 0
8285 | LAR #1 | MB | 32 | 0 | south | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | N | 0.0010518 | 0
8287 | LAR #2 | MB | 32 | 0 | south | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | N | 0.0010518 | 0
8288 | LAR #3 | MB | 105 | 0 | south | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | N | 0.0010518 | 0
8388 | BATES0A | MB | 70 | 0 | south | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | N | 0.0010518 | 0
8393 | BATES0B | MB | 110 | 0 | south | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | N | 0.0010518 | 0
8442 | NBEC71A | 1 | 336 | 0.001033 | south | -0.0044238 | -1.8801e-05 | 0.052846 | -0.0013775 | 1.8801e-05 | south | N | 1.8801e-05 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | N | 0.0010518 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | -0.0054568 | -0.0010518 | 0.051813 | -0.0024105 | 0.0010518 | south | N | 0.0010518 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.001026 | south | -0.0044308 | -2.5801e-05 | 0.052839 | -0.0013845 | 2.5801e-05 | south | N | 2.5801e-05 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.001026 | south | -0.0044308 | -2.5801e-05 | 0.052839 | -0.0013845 | 2.5801e-05 | south | N | 2.5801e-05 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.001017 | south | -0.0044398 | -3.4801e-05 | 0.05283 | -0.0013935 | 3.4801e-05 | south | N | 3.4801e-05 | 0
8506 | VAL #1 | 1 | 25 | 0.001021 | south | -0.0044358 | -3.0801e-05 | 0.052834 | -0.0013895 | 3.0801e-05 | south | N | 3.0801e-05 | 0
8507 | VAL #2 | 2 | 25 | 0.001021 | south | -0.0044358 | -3.0801e-05 | 0.052834 | -0.0013895 | 3.0801e-05 | south | N | 3.0801e-05 | 0
8511 | OXY_CC0A | 1 | 38 | 0.001021 | south | -0.0044358 | -3.0801e-05 | 0.052834 | -0.0013895 | 3.0801e-05 | south | N | 3.0801e-05 | 0
8517 | CELANEBI | 1 | 29 | 0.000998 | south | -0.0044588 | -5.3801e-05 | 0.052811 | -0.0014125 | 5.3801e-05 | south | N | 5.3801e-05 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.001032 | south | -0.0044248 | -1.9801e-05 | 0.052845 | -0.0013785 | 1.9801e-05 | south | N | 1.9801e-05 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.001032 | south | -0.0044248 | -1.9801e-05 | 0.052845 | -0.0013785 | 1.9801e-05 | south | N | 1.9801e-05 | 0
8562 | CNOPST1 | 3 | 153 | 0.001032 | south | -0.0044248 | -1.9801e-05 | 0.052845 | -0.0013785 | 1.9801e-05 | south | N | 1.9801e-05 | 0
8926 | LGE_GT10 | 1 | 158 | 0.001069 | south | -0.0043878 | 1.7199e-05 | 0.052882 | -0.0013415 | 1.7199e-05 | south | N | 1.7199e-05 | 0
8927 | LGE_GT20 | 2 | 153 | 0.001069 | south | -0.0043878 | 1.7199e-05 | 0.052882 | -0.0013415 | 1.7199e-05 | south | N | 1.7199e-05 | 0
8928 | LGE_STG0 | 3 | 100 | 0.001069 | south | -0.0043878 | 1.7199e-05 | 0.052882 | -0.0013415 | 1.7199e-05 | south | N | 1.7199e-05 | 0
8930 | ICPGN10A | 1 | 145 | 0.001069 | south | -0.0043878 | 1.7199e-05 | 0.052882 | -0.0013415 | 1.7199e-05 | south | N | 1.7199e-05 | 0
8931 | ICPGN20A | 2 | 147 | 0.001069 | south | -0.0043878 | 1.7199e-05 | 0.052882 | -0.0013415 | 1.7199e-05 | south | N | 1.7199e-05 | 0
8932 | ICPGN30A | 3 | 127 | 0.001069 | south | -0.0043878 | 1.7199e-05 | 0.052882 | -0.0013415 | 1.7199e-05 | south | N | 1.7199e-05 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.000866 | south | -0.0045908 | -0.0001858 | 0.052679 | -0.0015445 | 0.0001858 | south | N | 0.0001858 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.000866 | south | -0.0045908 | -0.0001858 | 0.052679 | -0.0015445 | 0.0001858 | south | N | 0.0001858 | 0
8935 | FGNTS201 | 3 | 173 | 0.000866 | south | -0.0045908 | -0.0001858 | 0.052679 | -0.0015445 | 0.0001858 | south | N | 0.0001858 | 0
8936 | MVGN#1 | 1 | 207 | 0.000928 | south | -0.0045288 | -0.0001238 | 0.052741 | -0.0014825 | 0.0001238 | south | N | 0.0001238 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.000928 | south | -0.0045288 | -0.0001238 | 0.052741 | -0.0014825 | 0.0001238 | south | N | 0.0001238 | 0
8938 | MVGN#3 | 3 | 242 | 0.000928 | south | -0.0045288 | -0.0001238 | 0.052741 | -0.0014825 | 0.0001238 | south | N | 0.0001238 | 0
8981 | HECN1 | 1 | 144 | 0.000928 | south | -0.0045288 | -0.0001238 | 0.052741 | -0.0014825 | 0.0001238 | south | N | 0.0001238 | 0
8982 | HECN2 | 2 | 144 | 0.000928 | south | -0.0045288 | -0.0001238 | 0.052741 | -0.0014825 | 0.0001238 | south | N | 0.0001238 | 0
8983 | HECN3 | 3 | 171 | 0.000928 | south | -0.0045288 | -0.0001238 | 0.052741 | -0.0014825 | 0.0001238 | south | N | 0.0001238 | 0
9000 | DECKR_G1 | 1 | 310 | 0.001389 | south | -0.0040678 | 0.0003372 | 0.053202 | -0.0010215 | 0.0003372 | south | N | 0.0003372 | 0
9001 | DECKR_G2 | 2 | 413 | 0.001389 | south | -0.0040678 | 0.0003372 | 0.053202 | -0.0010215 | 0.0003372 | south | N | 0.0003372 | 0
9002 | DECKR_G3 | 3 | 42 | 0.001429 | south | -0.0040278 | 0.0003772 | 0.053242 | -0.00098153 | 0.0003772 | south | N | 0.0003772 | 0
9003 | DECKR_G4 | 4 | 44 | 0.001429 | south | -0.0040278 | 0.0003772 | 0.053242 | -0.00098153 | 0.0003772 | south | N | 0.0003772 | 0
9004 | DECKR_G5 | 5 | 44 | 0.001429 | south | -0.0040278 | 0.0003772 | 0.053242 | -0.00098153 | 0.0003772 | south | N | 0.0003772 | 0
9005 | DECKR_G6 | 6 | 47 | 0.001429 | south | -0.0040278 | 0.0003772 | 0.053242 | -0.00098153 | 0.0003772 | south | N | 0.0003772 | 0
9016 | SANDH_G1 | 1 | 49 | 0.001376 | south | -0.0040808 | 0.0003242 | 0.053189 | -0.0010345 | 0.0003242 | south | N | 0.0003242 | 0
9017 | SANDH_G2 | 2 | 46 | 0.001376 | south | -0.0040808 | 0.0003242 | 0.053189 | -0.0010345 | 0.0003242 | south | N | 0.0003242 | 0
9018 | SANDH_G3 | 3 | 46 | 0.001376 | south | -0.0040808 | 0.0003242 | 0.053189 | -0.0010345 | 0.0003242 | south | N | 0.0003242 | 0
9019 | SANDH_G4 | 4 | 47 | 0.001376 | south | -0.0040808 | 0.0003242 | 0.053189 | -0.0010345 | 0.0003242 | south | N | 0.0003242 | 0
9020 | SANDHG5A | 5A | 154 | 0.001376 | south | -0.0040808 | 0.0003242 | 0.053189 | -0.0010345 | 0.0003242 | south | N | 0.0003242 | 0
9021 | SANDHG5C | 5C | 148 | 0.001376 | south | -0.0040808 | 0.0003242 | 0.053189 | -0.0010345 | 0.0003242 | south | N | 0.0003242 | 0
9022 | SANDH_G6 | 6 | 48 | 0.001376 | south | -0.0040808 | 0.0003242 | 0.053189 | -0.0010345 | 0.0003242 | south | N | 0.0003242 | 0
9023 | SANDH_G7 | 7 | 48 | 0.001376 | south | -0.0040808 | 0.0003242 | 0.053189 | -0.0010345 | 0.0003242 | south | N | 0.0003242 | 0
11001 | NAV1CT | 1 | 70 | -0.049701 | west | -0.055158 | -0.050753 | 0.0021123 | -0.052112 | 0.0021123 | west | N | 0.0021123 | 0
11009 | NAV2CT | 1 | 70 | -0.049701 | west | -0.055158 | -0.050753 | 0.0021123 | -0.052112 | 0.0021123 | west | N | 0.0021123 | 0
11011 | NAV3ST | 1 | 92.8 | -0.049701 | west | -0.055158 | -0.050753 | 0.0021123 | -0.052112 | 0.0021123 | west | N | 0.0021123 | 0
11012 | NAV4CT | 1 | 80 | -0.049701 | west | -0.055158 | -0.050753 | 0.0021123 | -0.052112 | 0.0021123 | west | N | 0.0021123 | 0
11013 | NAV5CT | 1 | 80 | -0.049701 | west | -0.055158 | -0.050753 | 0.0021123 | -0.052112 | 0.0021123 | west | N | 0.0021123 | 0
11014 | NAV6ST | 1 | 115 | -0.049701 | west | -0.055158 | -0.050753 | 0.0021123 | -0.052112 | 0.0021123 | west | N | 0.0021123 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.049708 | west | -0.055165 | -0.05076 | 0.0021053 | -0.052119 | 0.0021053 | west | N | 0.0021053 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.049708 | west | -0.055165 | -0.05076 | 0.0021053 | -0.052119 | 0.0021053 | west | N | 0.0021053 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.049708 | west | -0.055165 | -0.05076 | 0.0021053 | -0.052119 | 0.0021053 | west | N | 0.0021053 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.049708 | west | -0.055165 | -0.05076 | 0.0021053 | -0.052119 | 0.0021053 | west | N | 0.0021053 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.049708 | west | -0.055165 | -0.05076 | 0.0021053 | -0.052119 | 0.0021053 | west | N | 0.0021053 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.049708 | west | -0.055165 | -0.05076 | 0.0021053 | -0.052119 | 0.0021053 | west | N | 0.0021053 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.041216 | west | -0.046673 | -0.042268 | 0.010597 | -0.043627 | 0.010597 | west | N | 0.010597 | 0
11057 | CHAMPION | 1 | 126.5 | -0.041216 | west | -0.046673 | -0.042268 | 0.010597 | -0.043627 | 0.010597 | west | N | 0.010597 | 0
11058 | PYRON_1G | 1 | 249 | -0.041216 | west | -0.046673 | -0.042268 | 0.010597 | -0.043627 | 0.010597 | west | N | 0.010597 | 0
11059 | INADALE_ | 1 | 197 | -0.041216 | west | -0.046673 | -0.042268 | 0.010597 | -0.043627 | 0.010597 | west | N | 0.010597 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.049089 | west | -0.054546 | -0.050141 | 0.0027243 | -0.0515 | 0.0027243 | west | N | 0.0027243 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.049089 | west | -0.054546 | -0.050141 | 0.0027243 | -0.0515 | 0.0027243 | west | N | 0.0027243 | 0
11147 | NOTREES_ | 1 | 149 | -0.052256 | west | -0.057713 | -0.053308 | -0.00044274 | -0.054667 | 0.00044274 | west | N | 0.00044274 | 0
11309 | BULLCREK | 1 | 180 | -0.065965 | west | -0.071422 | -0.067017 | -0.014152 | -0.068376 | 0.014152 | west | N | 0.014152 | 0
11310 | BULLCREK | 1 | 180 | -0.065965 | west | -0.071422 | -0.067017 | -0.014152 | -0.068376 | 0.014152 | west | N | 0.014152 | 0
11320 | COYOTE_1 | 1 | 225 | -0.065405 | west | -0.070862 | -0.066457 | -0.013592 | -0.067816 | 0.013592 | west | N | 0.013592 | 0
11415 | LORAINE_ | 1 | 125 | -0.049368 | west | -0.054825 | -0.05042 | 0.0024453 | -0.051779 | 0.0024453 | west | N | 0.0024453 | 0
11416 | LORAINE_ | 1 | 125 | -0.049368 | west | -0.054825 | -0.05042 | 0.0024453 | -0.051779 | 0.0024453 | west | N | 0.0024453 | 0
11691 | KMICHICT | 1 | 140 | 0.004896 | north | -0.00056084 | 0.0038442 | 0.056709 | 0.0024855 | 0.00056084 | North | N | 0.00056084 | 0
11692 | KMICHICT | 2 | 141 | 0.004896 | north | -0.00056084 | 0.0038442 | 0.056709 | 0.0024855 | 0.00056084 | North | N | 0.00056084 | 0
11693 | KMICHIST | 3 | 309 | 0.004896 | north | -0.00056084 | 0.0038442 | 0.056709 | 0.0024855 | 0.00056084 | North | N | 0.00056084 | 0
11694 | KMICHICT | 4 | 143 | 0.004896 | north | -0.00056084 | 0.0038442 | 0.056709 | 0.0024855 | 0.00056084 | North | N | 0.00056084 | 0
11695 | KMICHICT | 5 | 144 | 0.004896 | north | -0.00056084 | 0.0038442 | 0.056709 | 0.0024855 | 0.00056084 | North | N | 0.00056084 | 0
11696 | KMICHIST | 6 | 310 | 0.004896 | north | -0.00056084 | 0.0038442 | 0.056709 | 0.0024855 | 0.00056084 | North | N | 0.00056084 | 0
12322 | ENNSTRAC | 1 | 196 | 0.004298 | north | -0.0011588 | 0.0032462 | 0.056111 | 0.0018875 | 0.0011588 | North | N | 0.0011588 | 0
12323 | ENNSTRAC | 2 | 111 | 0.004298 | north | -0.0011588 | 0.0032462 | 0.056111 | 0.0018875 | 0.0011588 | North | N | 0.0011588 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.004918 | north | -0.00053884 | 0.0038662 | 0.056731 | 0.0025075 | 0.00053884 | North | N | 0.00053884 | 0
12411 | FPLEFR1A | 1 | 161 | 0.004635 | north | -0.00082184 | 0.0035832 | 0.056448 | 0.0022245 | 0.00082184 | North | N | 0.00082184 | 0
12412 | FPLEFR1B | 2 | 164 | 0.004635 | north | -0.00082184 | 0.0035832 | 0.056448 | 0.0022245 | 0.00082184 | North | N | 0.00082184 | 0
12413 | FPLEFR1C | 3 | 164 | 0.004635 | north | -0.00082184 | 0.0035832 | 0.056448 | 0.0022245 | 0.00082184 | North | N | 0.00082184 | 0
12414 | FPLEFR1S | 4 | 414 | 0.004635 | north | -0.00082184 | 0.0035832 | 0.056448 | 0.0022245 | 0.00082184 | North | N | 0.00082184 | 0
12421 | FPLEFR2A | 1 | 162 | 0.004635 | north | -0.00082184 | 0.0035832 | 0.056448 | 0.0022245 | 0.00082184 | North | N | 0.00082184 | 0
12422 | FPLEFR2B | 2 | 161 | 0.004635 | north | -0.00082184 | 0.0035832 | 0.056448 | 0.0022245 | 0.00082184 | North | N | 0.00082184 | 0
12423 | FPLEFR2C | 3 | 163 | 0.004635 | north | -0.00082184 | 0.0035832 | 0.056448 | 0.0022245 | 0.00082184 | North | N | 0.00082184 | 0
12424 | FPLEFR2S | 4 | 409 | 0.004635 | north | -0.00082184 | 0.0035832 | 0.056448 | 0.0022245 | 0.00082184 | North | N | 0.00082184 | 0
12440 | PARKD_1S | 1 | 0 | 0.004626 | north | -0.00083084 | 0.0035742 | 0.056439 | 0.0022155 | 0.00083084 | North | N | 0.00083084 | 0
12449 | PARKD_2S | 1 | 0 | 0.004626 | north | -0.00083084 | 0.0035742 | 0.056439 | 0.0022155 | 0.00083084 | North | N | 0.00083084 | 0
13116 | TGATEWAY | 1 | 148 | 0.004341 | north | -0.0011158 | 0.0032892 | 0.056154 | 0.0019305 | 0.0011158 | North | N | 0.0011158 | 0
13117 | TGATEWAY | 2 | 130 | 0.004341 | north | -0.0011158 | 0.0032892 | 0.056154 | 0.0019305 | 0.0011158 | North | N | 0.0011158 | 0
13118 | TGATEWAY | 3 | 145 | 0.004341 | north | -0.0011158 | 0.0032892 | 0.056154 | 0.0019305 | 0.0011158 | North | N | 0.0011158 | 0
13119 | TGATEWAY | 4 | 399 | 0.004341 | north | -0.0011158 | 0.0032892 | 0.056154 | 0.0019305 | 0.0011158 | North | N | 0.0011158 | 0
13131 | CALFREST | 1 | 150.7 | 0.00399 | north | -0.0014668 | 0.0029382 | 0.055803 | 0.0015795 | 0.0014668 | North | N | 0.0014668 | 0
13132 | CALFREST | 2 | 151 | 0.00399 | north | -0.0014668 | 0.0029382 | 0.055803 | 0.0015795 | 0.0014668 | North | N | 0.0014668 | 0
13133 | CALFREST | 3 | 177.4 | 0.00399 | north | -0.0014668 | 0.0029382 | 0.055803 | 0.0015795 | 0.0014668 | North | N | 0.0014668 | 0
13134 | CALFREST | 4 | 151.5 | 0.004005 | north | -0.0014518 | 0.0029532 | 0.055818 | 0.0015945 | 0.0014518 | North | N | 0.0014518 | 0
13135 | CALFREST | 5 | 152.3 | 0.004005 | north | -0.0014518 | 0.0029532 | 0.055818 | 0.0015945 | 0.0014518 | North | N | 0.0014518 | 0
13136 | CALFREST | 6 | 177.5 | 0.004005 | north | -0.0014518 | 0.0029532 | 0.055818 | 0.0015945 | 0.0014518 | North | N | 0.0014518 | 0
13432 | SANDOW_5 | 5 | 581 | 0.002067 | south | -0.0033898 | 0.0010152 | 0.05388 | -0.00034353 | 0.00034353 | houston | Y | 0.0010152 | 0.39024
13691 | OAKGROVE | 1 | 855 | 0.003474 | north | -0.0019828 | 0.0024222 | 0.055287 | 0.0010635 | 0.0010635 | houston | Y | 0.0019828 | 0.78606
13692 | OAKGROVE | 2 | 855 | 0.003474 | north | -0.0019828 | 0.0024222 | 0.055287 | 0.0010635 | 0.0010635 | houston | Y | 0.0019828 | 0.78606
32798 | BRYN_TAM | 1 | 32 | 0.003161 | north | -0.0022958 | 0.0021092 | 0.054974 | 0.00075047 | 0.00075047 | houston | Y | 0.0022958 | 0.049452
32883 | BRYN_DNS | 1 | 48 | 0.003156 | north | -0.0023008 | 0.0021042 | 0.054969 | 0.00074547 | 0.00074547 | houston | Y | 0.0023008 | 0.074658
32884 | BRYN_DNS | 1 | 46 | 0.003156 | north | -0.0023008 | 0.0021042 | 0.054969 | 0.00074547 | 0.00074547 | houston | Y | 0.0023008 | 0.071547
32886 | BRYN_ATK | MB | 12 | 0.003163 | north | -0.0022938 | 0.0021112 | 0.054976 | 0.00075247 | 0.00075247 | houston | Y | 0.0022938 | 0.018496
32887 | BRYN_ATK | MB | 51 | 0.003163 | north | -0.0022938 | 0.0021112 | 0.054976 | 0.00075247 | 0.00075247 | houston | Y | 0.0022938 | 0.07861
32888 | BRYN_ATK | 1 | 17 | 0.003163 | north | -0.0022938 | 0.0021112 | 0.054976 | 0.00075247 | 0.00075247 | houston | Y | 0.0022938 | 0.026203
32890 | BRYN_ATK | MB | 22 | 0.003163 | north | -0.0022938 | 0.0021112 | 0.054976 | 0.00075247 | 0.00075247 | houston | Y | 0.0022938 | 0.03391
32891 | BRYN_ATK | MB | 25 | 0.003163 | north | -0.0022938 | 0.0021112 | 0.054976 | 0.00075247 | 0.00075247 | houston | Y | 0.0022938 | 0.038534
32892 | BRYN_DNS | 1 | 105 | 0.003156 | north | -0.0023008 | 0.0021042 | 0.054969 | 0.00074547 | 0.00074547 | houston | Y | 0.0023008 | 0.16331
36998 | RDCNYNG1 | 1 | 84 | -0.082765 | west | -0.088222 | -0.083817 | -0.030952 | -0.085176 | 0.030952 | west | N | 0.030952 | 0
38332 | WDWRDU2 | 1 | 80 | -0.047282 | west | -0.052739 | -0.048334 | 0.0045313 | -0.049693 | 0.0045313 | west | N | 0.0045313 | 0
38437 | TNSRBNMS | 1 | 150 | -0.047254 | west | -0.052711 | -0.048306 | 0.0045593 | -0.049665 | 0.0045593 | west | N | 0.0045593 | 0
38438 | TNSRBNMS | 1 | 150 | -0.047254 | west | -0.052711 | -0.048306 | 0.0045593 | -0.049665 | 0.0045593 | west | N | 0.0045593 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38600 | TNBP_CGN | 5 | 53 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38614 | TNBPAMCG | 4 | 96 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38615 | TNBPAMCG | 1 | 244 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38690 | TNBP_CGN | 3 | 40 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
39470 | TNDOWCGN | 1 | 32 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
39480 | TNDOWCGN | 1 | 30 | 0.002391 | houston | -0.0030658 | 0.0013392 | 0.054204 | -1.9534e-05 | 1.9534e-05 | houston | N | 1.9534e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.00222 | houston | -0.0032368 | 0.0011682 | 0.054033 | -0.00019053 | 0.00019053 | houston | N | 0.00019053 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.00222 | houston | -0.0032368 | 0.0011682 | 0.054033 | -0.00019053 | 0.00019053 | houston | N | 0.00019053 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.00222 | houston | -0.0032368 | 0.0011682 | 0.054033 | -0.00019053 | 0.00019053 | houston | N | 0.00019053 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.00222 | houston | -0.0032368 | 0.0011682 | 0.054033 | -0.00019053 | 0.00019053 | houston | N | 0.00019053 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.003474 | north | -0.0019828 | 0.0024222 | 0.055287 | 0.0010635 | 0.0010635 | houston | Y | 0.0019828 | 0.14002
39970 | TNTNPONE | 1 | 153 | 0.003474 | north | -0.0019828 | 0.0024222 | 0.055287 | 0.0010635 | 0.0010635 | houston | Y | 0.0019828 | 0.14066
48500 | APD_GT1_ | 1 | 136 | 0.002493 | houston | -0.0029638 | 0.0014412 | 0.054306 | 8.2466e-05 | 8.2466e-05 | houston | N | 8.2466e-05 | 0
48510 | AK_GT1__ | 1 | 33 | 0.002334 | houston | -0.0031228 | 0.0012822 | 0.054147 | -7.6534e-05 | 7.6534e-05 | houston | N | 7.6534e-05 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.002493 | houston | -0.0029638 | 0.0014412 | 0.054306 | 8.2466e-05 | 8.2466e-05 | houston | N | 8.2466e-05 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.002493 | houston | -0.0029638 | 0.0014412 | 0.054306 | 8.2466e-05 | 8.2466e-05 | houston | N | 8.2466e-05 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.002493 | houston | -0.0029638 | 0.0014412 | 0.054306 | 8.2466e-05 | 8.2466e-05 | houston | N | 8.2466e-05 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.002493 | houston | -0.0029638 | 0.0014412 | 0.054306 | 8.2466e-05 | 8.2466e-05 | houston | N | 8.2466e-05 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.002189 | houston | -0.0032678 | 0.0011372 | 0.054002 | -0.00022153 | 0.00022153 | houston | N | 0.00022153 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.002189 | houston | -0.0032678 | 0.0011372 | 0.054002 | -0.00022153 | 0.00022153 | houston | N | 0.00022153 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.00233 | houston | -0.0031268 | 0.0012782 | 0.054143 | -8.0534e-05 | 8.0534e-05 | houston | N | 8.0534e-05 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.00233 | houston | -0.0031268 | 0.0012782 | 0.054143 | -8.0534e-05 | 8.0534e-05 | houston | N | 8.0534e-05 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.00233 | houston | -0.0031268 | 0.0012782 | 0.054143 | -8.0534e-05 | 8.0534e-05 | houston | N | 8.0534e-05 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.002454 | houston | -0.0030028 | 0.0014022 | 0.054267 | 4.3466e-05 | 4.3466e-05 | houston | N | 4.3466e-05 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.002454 | houston | -0.0030028 | 0.0014022 | 0.054267 | 4.3466e-05 | 4.3466e-05 | houston | N | 4.3466e-05 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.002454 | houston | -0.0030028 | 0.0014022 | 0.054267 | 4.3466e-05 | 4.3466e-05 | houston | N | 4.3466e-05 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.002454 | houston | -0.0030028 | 0.0014022 | 0.054267 | 4.3466e-05 | 4.3466e-05 | houston | N | 4.3466e-05 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.002479 | houston | -0.0029778 | 0.0014272 | 0.054292 | 6.8466e-05 | 6.8466e-05 | houston | N | 6.8466e-05 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.002479 | houston | -0.0029778 | 0.0014272 | 0.054292 | 6.8466e-05 | 6.8466e-05 | houston | N | 6.8466e-05 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.002447 | houston | -0.0030098 | 0.0013952 | 0.05426 | 3.6466e-05 | 3.6466e-05 | houston | N | 3.6466e-05 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.002447 | houston | -0.0030098 | 0.0013952 | 0.05426 | 3.6466e-05 | 3.6466e-05 | houston | N | 3.6466e-05 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.002447 | houston | -0.0030098 | 0.0013952 | 0.05426 | 3.6466e-05 | 3.6466e-05 | houston | N | 3.6466e-05 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.002447 | houston | -0.0030098 | 0.0013952 | 0.05426 | 3.6466e-05 | 3.6466e-05 | houston | N | 3.6466e-05 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.002447 | houston | -0.0030098 | 0.0013952 | 0.05426 | 3.6466e-05 | 3.6466e-05 | houston | N | 3.6466e-05 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.002523 | houston | -0.0029338 | 0.0014712 | 0.054336 | 0.00011247 | 0.00011247 | houston | N | 0.00011247 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.00251 | houston | -0.0029468 | 0.0014582 | 0.054323 | 9.9466e-05 | 9.9466e-05 | houston | N | 9.9466e-05 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.002526 | houston | -0.0029308 | 0.0014742 | 0.054339 | 0.00011547 | 0.00011547 | houston | N | 0.00011547 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.002526 | houston | -0.0029308 | 0.0014742 | 0.054339 | 0.00011547 | 0.00011547 | houston | N | 0.00011547 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.002526 | houston | -0.0029308 | 0.0014742 | 0.054339 | 0.00011547 | 0.00011547 | houston | N | 0.00011547 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.002595 | houston | -0.0028618 | 0.0015432 | 0.054408 | 0.00018447 | 0.00018447 | houston | N | 0.00018447 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.002495 | houston | -0.0029618 | 0.0014432 | 0.054308 | 8.4466e-05 | 8.4466e-05 | houston | N | 8.4466e-05 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.002495 | houston | -0.0029618 | 0.0014432 | 0.054308 | 8.4466e-05 | 8.4466e-05 | houston | N | 8.4466e-05 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.002535 | houston | -0.0029218 | 0.0014832 | 0.054348 | 0.00012447 | 0.00012447 | houston | N | 0.00012447 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.002535 | houston | -0.0029218 | 0.0014832 | 0.054348 | 0.00012447 | 0.00012447 | houston | N | 0.00012447 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.002535 | houston | -0.0029218 | 0.0014832 | 0.054348 | 0.00012447 | 0.00012447 | houston | N | 0.00012447 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.002535 | houston | -0.0029218 | 0.0014832 | 0.054348 | 0.00012447 | 0.00012447 | houston | N | 0.00012447 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.002471 | houston | -0.0029858 | 0.0014192 | 0.054284 | 6.0466e-05 | 6.0466e-05 | houston | N | 6.0466e-05 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.002471 | houston | -0.0029858 | 0.0014192 | 0.054284 | 6.0466e-05 | 6.0466e-05 | houston | N | 6.0466e-05 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.002471 | houston | -0.0029858 | 0.0014192 | 0.054284 | 6.0466e-05 | 6.0466e-05 | houston | N | 6.0466e-05 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.002471 | houston | -0.0029858 | 0.0014192 | 0.054284 | 6.0466e-05 | 6.0466e-05 | houston | N | 6.0466e-05 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.002471 | houston | -0.0029858 | 0.0014192 | 0.054284 | 6.0466e-05 | 6.0466e-05 | houston | N | 6.0466e-05 | 0
48651 | EP_1_2 | 1 | 5 | 0.002522 | houston | -0.0029348 | 0.0014702 | 0.054335 | 0.00011147 | 0.00011147 | houston | N | 0.00011147 | 0
48651 | EP_1_2 | 2 | 21 | 0.002522 | houston | -0.0029348 | 0.0014702 | 0.054335 | 0.00011147 | 0.00011147 | houston | N | 0.00011147 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.003064 | north | -0.0023928 | 0.0020122 | 0.054877 | 0.00065347 | 0.00065347 | houston | Y | 0.0023928 | 0.26821
48672 | FTR_GT2_ | 2 | 156 | 0.003064 | north | -0.0023928 | 0.0020122 | 0.054877 | 0.00065347 | 0.00065347 | houston | Y | 0.0023928 | 0.27134
48673 | FTR_GT3_ | 3 | 156 | 0.003064 | north | -0.0023928 | 0.0020122 | 0.054877 | 0.00065347 | 0.00065347 | houston | Y | 0.0023928 | 0.27134
48674 | FTR_CN4_ | 4 | 380 | 0.003064 | north | -0.0023928 | 0.0020122 | 0.054877 | 0.00065347 | 0.00065347 | houston | Y | 0.0023928 | 0.66096
48690 | GBY_GN5_ | 5 | 398 | 0.002539 | houston | -0.0029178 | 0.0014872 | 0.054352 | 0.00012847 | 0.00012847 | houston | N | 0.00012847 | 0
48691 | GBY_7374 | A | 46 | 0.002467 | houston | -0.0029898 | 0.0014152 | 0.05428 | 5.6466e-05 | 5.6466e-05 | houston | N | 5.6466e-05 | 0
48691 | GBY_7374 | B | 46 | 0.002467 | houston | -0.0029898 | 0.0014152 | 0.05428 | 5.6466e-05 | 5.6466e-05 | houston | N | 5.6466e-05 | 0
48692 | GBY_8182 | C | 46 | 0.002467 | houston | -0.0029898 | 0.0014152 | 0.05428 | 5.6466e-05 | 5.6466e-05 | houston | N | 5.6466e-05 | 0
48692 | GBY_8182 | D | 55 | 0.002467 | houston | -0.0029898 | 0.0014152 | 0.05428 | 5.6466e-05 | 5.6466e-05 | houston | N | 5.6466e-05 | 0
48693 | GBY_8384 | E | 55 | 0.002467 | houston | -0.0029898 | 0.0014152 | 0.05428 | 5.6466e-05 | 5.6466e-05 | houston | N | 5.6466e-05 | 0
48693 | GBY_8384 | F | 54 | 0.002467 | houston | -0.0029898 | 0.0014152 | 0.05428 | 5.6466e-05 | 5.6466e-05 | houston | N | 5.6466e-05 | 0
48721 | LEG_1___ | 1 | 827 | 0.0036 | north | -0.0018568 | 0.0025482 | 0.055413 | 0.0011895 | 0.0011895 | houston | Y | 0.0018568 | 0.55192
48722 | LEG_2___ | 2 | 819 | 0.0036 | north | -0.0018568 | 0.0025482 | 0.055413 | 0.0011895 | 0.0011895 | houston | Y | 0.0018568 | 0.54658
48730 | MNS_GT | 1 | 46.1 | 0.002319 | houston | -0.0031378 | 0.0012672 | 0.054132 | -9.1534e-05 | 9.1534e-05 | houston | N | 9.1534e-05 | 0
48731 | CBE_GT1 | 1 | 76 | 0.001978 | houston | -0.0034788 | 0.0009262 | 0.053791 | -0.00043253 | 0.00043253 | houston | N | 0.00043253 | 0
48732 | CBE_GT2 | 1 | 76 | 0.001978 | houston | -0.0034788 | 0.0009262 | 0.053791 | -0.00043253 | 0.00043253 | houston | N | 0.00043253 | 0
48733 | CBE_ST12 | 1 | 105 | 0.001978 | houston | -0.0034788 | 0.0009262 | 0.053791 | -0.00043253 | 0.00043253 | houston | N | 0.00043253 | 0
48734 | CBE_GT3 | 1 | 74 | 0.001978 | houston | -0.0034788 | 0.0009262 | 0.053791 | -0.00043253 | 0.00043253 | houston | N | 0.00043253 | 0
48735 | CBE_GT4 | 1 | 74 | 0.001978 | houston | -0.0034788 | 0.0009262 | 0.053791 | -0.00043253 | 0.00043253 | houston | N | 0.00043253 | 0
48736 | CBE_ST34 | 1 | 102 | 0.001978 | houston | -0.0034788 | 0.0009262 | 0.053791 | -0.00043253 | 0.00043253 | houston | N | 0.00043253 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48761 | PR_GT1__ | 1 | 35 | 0.002475 | houston | -0.0029818 | 0.0014232 | 0.054288 | 6.4466e-05 | 6.4466e-05 | houston | N | 6.4466e-05 | 0
48772 | PHR_GN2_ | MB | 459 | 0.002428 | houston | -0.0030288 | 0.0013762 | 0.054241 | 1.7466e-05 | 1.7466e-05 | houston | N | 1.7466e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.002523 | houston | -0.0029338 | 0.0014712 | 0.054336 | 0.00011247 | 0.00011247 | houston | N | 0.00011247 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.002523 | houston | -0.0029338 | 0.0014712 | 0.054336 | 0.00011247 | 0.00011247 | houston | N | 0.00011247 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.002523 | houston | -0.0029338 | 0.0014712 | 0.054336 | 0.00011247 | 0.00011247 | houston | N | 0.00011247 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.002523 | houston | -0.0029338 | 0.0014712 | 0.054336 | 0.00011247 | 0.00011247 | houston | N | 0.00011247 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.002523 | houston | -0.0029338 | 0.0014712 | 0.054336 | 0.00011247 | 0.00011247 | houston | N | 0.00011247 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.002523 | houston | -0.0029338 | 0.0014712 | 0.054336 | 0.00011247 | 0.00011247 | houston | N | 0.00011247 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.002523 | houston | -0.0029338 | 0.0014712 | 0.054336 | 0.00011247 | 0.00011247 | houston | N | 0.00011247 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.002595 | houston | -0.0028618 | 0.0015432 | 0.054408 | 0.00018447 | 0.00018447 | houston | N | 0.00018447 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.002595 | houston | -0.0028618 | 0.0015432 | 0.054408 | 0.00018447 | 0.00018447 | houston | N | 0.00018447 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.002595 | houston | -0.0028618 | 0.0015432 | 0.054408 | 0.00018447 | 0.00018447 | houston | N | 0.00018447 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.002595 | houston | -0.0028618 | 0.0015432 | 0.054408 | 0.00018447 | 0.00018447 | houston | N | 0.00018447 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.002526 | houston | -0.0029308 | 0.0014742 | 0.054339 | 0.00011547 | 0.00011547 | houston | N | 0.00011547 | 0
48820 | SHELLG1_ | 1 | 71 | 0.002485 | houston | -0.0029718 | 0.0014332 | 0.054298 | 7.4466e-05 | 7.4466e-05 | houston | N | 7.4466e-05 | 0
48821 | SHELLG2 | 2 | 72 | 0.002485 | houston | -0.0029718 | 0.0014332 | 0.054298 | 7.4466e-05 | 7.4466e-05 | houston | N | 7.4466e-05 | 0
48822 | SHELLG3_ | 1 | 39 | 0.002485 | houston | -0.0029718 | 0.0014332 | 0.054298 | 7.4466e-05 | 7.4466e-05 | houston | N | 7.4466e-05 | 0
48822 | SHELLG3_ | 2 | 30 | 0.002485 | houston | -0.0029718 | 0.0014332 | 0.054298 | 7.4466e-05 | 7.4466e-05 | houston | N | 7.4466e-05 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.002468 | houston | -0.0029888 | 0.0014162 | 0.054281 | 5.7466e-05 | 5.7466e-05 | houston | N | 5.7466e-05 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.002468 | houston | -0.0029888 | 0.0014162 | 0.054281 | 5.7466e-05 | 5.7466e-05 | houston | N | 5.7466e-05 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.002479 | houston | -0.0029778 | 0.0014272 | 0.054292 | 6.8466e-05 | 6.8466e-05 | houston | N | 6.8466e-05 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.002479 | houston | -0.0029778 | 0.0014272 | 0.054292 | 6.8466e-05 | 6.8466e-05 | houston | N | 6.8466e-05 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.00248 | houston | -0.0029768 | 0.0014282 | 0.054293 | 6.9466e-05 | 6.9466e-05 | houston | N | 6.9466e-05 | 0
48855 | SRB_GT21 | B2 | 12 | 0.002478 | houston | -0.0029788 | 0.0014262 | 0.054291 | 6.7466e-05 | 6.7466e-05 | houston | N | 6.7466e-05 | 0
48855 | SRB_GT21 | MB | 18 | 0.002478 | houston | -0.0029788 | 0.0014262 | 0.054291 | 6.7466e-05 | 6.7466e-05 | houston | N | 6.7466e-05 | 0
48865 | TECO_GT1 | 1 | 50 | 0.002415 | houston | -0.0030418 | 0.0013632 | 0.054228 | 4.466e-06 | 4.466e-06 | houston | N | 4.466e-06 | 0
48873 | THW_ST3_ | 3 | 104 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48874 | THW_ST4_ | 4 | 104 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48875 | THW_3132 | A | 54 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48875 | THW_3132 | B | 53 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48877 | THW_3334 | C | 54 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48877 | THW_3334 | D | 57 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48879 | THW_4142 | E | 54 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48879 | THW_4142 | F | 54 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48881 | THW_4344 | G | 58 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48881 | THW_4344 | H | 58 | 0.002508 | houston | -0.0029488 | 0.0014562 | 0.054321 | 9.7466e-05 | 9.7466e-05 | houston | N | 9.7466e-05 | 0
48883 | THW_GT1_ | B2 | 12 | 0.002519 | houston | -0.0029378 | 0.0014672 | 0.054332 | 0.00010847 | 0.00010847 | houston | N | 0.00010847 | 0
48885 | THW_5152 | A | 56 | 0.002545 | houston | -0.0029118 | 0.0014932 | 0.054358 | 0.00013447 | 0.00013447 | houston | N | 0.00013447 | 0
48885 | THW_5152 | B | 59 | 0.002545 | houston | -0.0029118 | 0.0014932 | 0.054358 | 0.00013447 | 0.00013447 | houston | N | 0.00013447 | 0
48886 | THW_5354 | C | 56 | 0.002545 | houston | -0.0029118 | 0.0014932 | 0.054358 | 0.00013447 | 0.00013447 | houston | N | 0.00013447 | 0
48886 | THW_5354 | D | 56 | 0.002545 | houston | -0.0029118 | 0.0014932 | 0.054358 | 0.00013447 | 0.00013447 | houston | N | 0.00013447 | 0
48887 | THW_5556 | E | 59 | 0.002545 | houston | -0.0029118 | 0.0014932 | 0.054358 | 0.00013447 | 0.00013447 | houston | N | 0.00013447 | 0
48887 | THW_5556 | F | 56 | 0.002545 | houston | -0.0029118 | 0.0014932 | 0.054358 | 0.00013447 | 0.00013447 | houston | N | 0.00013447 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.002 | houston | -0.0034568 | 0.0009482 | 0.053813 | -0.00041053 | 0.00041053 | houston | N | 0.00041053 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.002349 | houston | -0.0031078 | 0.0012972 | 0.054162 | -6.1534e-05 | 6.1534e-05 | houston | N | 6.1534e-05 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.002349 | houston | -0.0031078 | 0.0012972 | 0.054162 | -6.1534e-05 | 6.1534e-05 | houston | N | 6.1534e-05 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.002349 | houston | -0.0031078 | 0.0012972 | 0.054162 | -6.1534e-05 | 6.1534e-05 | houston | N | 6.1534e-05 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.002349 | houston | -0.0031078 | 0.0012972 | 0.054162 | -6.1534e-05 | 6.1534e-05 | houston | N | 6.1534e-05 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.002349 | houston | -0.0031078 | 0.0012972 | 0.054162 | -6.1534e-05 | 6.1534e-05 | houston | N | 6.1534e-05 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.002329 | houston | -0.0031278 | 0.0012772 | 0.054142 | -8.1534e-05 | 8.1534e-05 | houston | N | 8.1534e-05 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.002329 | houston | -0.0031278 | 0.0012772 | 0.054142 | -8.1534e-05 | 8.1534e-05 | houston | N | 8.1534e-05 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.002329 | houston | -0.0031278 | 0.0012772 | 0.054142 | -8.1534e-05 | 8.1534e-05 | houston | N | 8.1534e-05 | 0
48929 | WAPGT21_ | B1 | 13 | 0.002349 | houston | -0.0031078 | 0.0012972 | 0.054162 | -6.1534e-05 | 6.1534e-05 | houston | N | 6.1534e-05 | 0
48940 | WARVUE_G | G1 | 12 | 0.002523 | houston | -0.0029338 | 0.0014712 | 0.054336 | 0.00011247 | 0.00011247 | houston | N | 0.00011247 | 0
49803 | EXN_15GT | 1 | 34 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49826 | EXN938GT | 5 | 45.9 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49828 | EXN941GT | 10 | 17.7 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49829 | EXN942GT | 11 | 20.4 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49830 | EXN943GT | 12 | 19.9 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49831 | EXN944GT | 13 | 35 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49832 | EXN945GT | 9 | 18 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49837 | EXN_GT | 4 | 85.4 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49838 | EXN_14GT | 14 | 148 | 0.002514 | houston | -0.0029428 | 0.0014622 | 0.054327 | 0.00010347 | 0.00010347 | houston | N | 0.00010347 | 0
49851 | DOW17000 | 37 | 62 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49858 | DOW38100 | 31 | 71.4 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49859 | DOW38200 | 33 | 45 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49860 | DOW38300 | 32 | 101 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49862 | DOW39100 | 36 | 86 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49863 | DOW39200 | 35 | 88 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49865 | DOW41000 | 41 | 50 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49866 | DOW42000 | 42 | 18 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49869 | DOW49000 | 45 | 94 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49870 | DOW61000 | 61 | 70 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49871 | DOW62000 | 62 | 63 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49872 | DOW63000 | 63 | 72 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49873 | DOW64000 | 64 | 64.8 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49876 | DOW65000 | 65 | 101 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49877 | DOW66000 | 66 | 97 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49878 | DOW67000 | 67 | 103 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49882 | DOW81000 | 81 | 76 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49884 | DOW82000 | 82 | 80 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49885 | DOW83000 | 83 | 80 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
49886 | DOW84000 | 84 | 171 | 0.002152 | houston | -0.0033048 | 0.0011002 | 0.053965 | -0.00025853 | 0.00025853 | houston | N | 0.00025853 | 0
58909 | PEARSALL | 1 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58909 | PEARSALL | 2 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58909 | PEARSALL | 3 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58909 | PEARSALL | 4 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58909 | PEARSALL | 5 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58909 | PEARSALL | 6 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58919 | PEARSALL | 1 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58919 | PEARSALL | 2 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58919 | PEARSALL | 3 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58919 | PEARSALL | 4 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58919 | PEARSALL | 5 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58919 | PEARSALL | 6 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58929 | PEARSALL | 1 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58929 | PEARSALL | 2 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58929 | PEARSALL | 3 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58929 | PEARSALL | 4 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58929 | PEARSALL | 5 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58929 | PEARSALL | 6 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58949 | PEARSALL | 1 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58949 | PEARSALL | 2 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58949 | PEARSALL | 3 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58949 | PEARSALL | 4 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58949 | PEARSALL | 5 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
58949 | PEARSALL | 6 | 8.4 | -0.001356 | south | -0.0068128 | -0.0024078 | 0.050457 | -0.0037665 | 0.0024078 | south | N | 0.0024078 | 0
60000 | DSKY2 | 1 | 76.5 | -0.045939 | west | -0.051396 | -0.046991 | 0.0058743 | -0.04835 | 0.0058743 | west | N | 0.0058743 | 0
60003 | KING_NE1 | 1 | 80 | -0.047327 | west | -0.052784 | -0.048379 | 0.0044863 | -0.049738 | 0.0044863 | west | N | 0.0044863 | 0
60005 | KING_SE1 | 1 | 40 | -0.047327 | west | -0.052784 | -0.048379 | 0.0044863 | -0.049738 | 0.0044863 | west | N | 0.0044863 | 0
60007 | KING_SW1 | 1 | 80 | -0.047523 | west | -0.05298 | -0.048575 | 0.0042903 | -0.049934 | 0.0042903 | west | N | 0.0042903 | 0
60016 | WOODWRD1 | 1 | 80 | -0.047289 | west | -0.052746 | -0.048341 | 0.0045243 | -0.0497 | 0.0045243 | west | N | 0.0045243 | 0
60017 | ORNNWP1 | 1 | 80 | -0.046224 | west | -0.051681 | -0.047276 | 0.0055893 | -0.048635 | 0.0055893 | west | N | 0.0055893 | 0
60018 | DSKY1 | 1 | 84 | -0.045877 | west | -0.051334 | -0.046929 | 0.0059363 | -0.048288 | 0.0059363 | west | N | 0.0059363 | 0
60019 | KING_NW1 | 1 | 80 | -0.047523 | west | -0.05298 | -0.048575 | 0.0042903 | -0.049934 | 0.0042903 | west | N | 0.0042903 | 0
60057 | CALLAHAN | 1 | 114 | 0.000604 | south | -0.0048528 | -0.0004478 | 0.052417 | -0.0018065 | 0.0004478 | south | N | 0.0004478 | 0
60058 | BUFF_GAP | 1 | 120 | -0.05351 | west | -0.058967 | -0.054562 | -0.0016967 | -0.055921 | 0.0016967 | west | N | 0.0016967 | 0
60060 | CIRELLO | 1 | 233 | -0.05351 | west | -0.058967 | -0.054562 | -0.0016967 | -0.055921 | 0.0016967 | west | N | 0.0016967 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.05351 | west | -0.058967 | -0.054562 | -0.0016967 | -0.055921 | 0.0016967 | west | N | 0.0016967 | 0
60066 | H_HOLLOW | 1 | 222 | 0.000604 | south | -0.0048528 | -0.0004478 | 0.052417 | -0.0018065 | 0.0004478 | south | N | 0.0004478 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.000604 | south | -0.0048528 | -0.0004478 | 0.052417 | -0.0018065 | 0.0004478 | south | N | 0.0004478 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.000604 | south | -0.0048528 | -0.0004478 | 0.052417 | -0.0018065 | 0.0004478 | south | N | 0.0004478 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.000604 | south | -0.0048528 | -0.0004478 | 0.052417 | -0.0018065 | 0.0004478 | south | N | 0.0004478 | 0
60074 | HORSH5 | 1 | 100 | 0.000604 | south | -0.0048528 | -0.0004478 | 0.052417 | -0.0018065 | 0.0004478 | south | N | 0.0004478 | 0
60081 | WHRLWIND | 1 | 60 | -0.13826 | west | -0.14372 | -0.13931 | -0.086449 | -0.14067 | 0.086449 | west | N | 0.086449 | 0
60201 | RIO DRCS | F | 0 | -0.013819 | south | -0.019276 | -0.014871 | 0.037994 | -0.01623 | 0.014871 | south | N | 0.014871 | 0
60202 | FRIEND_R | F | 0 | -0.040416 | west | -0.045873 | -0.041468 | 0.011397 | -0.042827 | 0.011397 | west | N | 0.011397 | 0
60203 | PRES0A | BT | 4.8 | -0.048407 | west | -0.053864 | -0.049459 | 0.0034063 | -0.050818 | 0.0034063 | west | N | 0.0034063 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.051252 | west | -0.056709 | -0.052304 | 0.00056126 | -0.053663 | 0.00056126 | west | N | 0.00056126 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.051252 | west | -0.056709 | -0.052304 | 0.00056126 | -0.053663 | 0.00056126 | west | N | 0.00056126 | 0
71057 | L_SWEETW | W1 | 135 | -0.051252 | west | -0.056709 | -0.052304 | 0.00056126 | -0.053663 | 0.00056126 | west | N | 0.00056126 | 0
71059 | L_SWEETW | W1 | 119 | -0.051252 | west | -0.056709 | -0.052304 | 0.00056126 | -0.053663 | 0.00056126 | west | N | 0.00056126 | 0
71060 | L_SWEETW | W1 | 105 | -0.051252 | west | -0.056709 | -0.052304 | 0.00056126 | -0.053663 | 0.00056126 | west | N | 0.00056126 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.051252 | west | -0.056709 | -0.052304 | 0.00056126 | -0.053663 | 0.00056126 | west | N | 0.00056126 | 0
76031 | L_GASCCR | W1 | 150 | -0.046572 | west | -0.052029 | -0.047624 | 0.0052413 | -0.048983 | 0.0052413 | west | N | 0.0052413 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.046113 | west | -0.05157 | -0.047165 | 0.0057003 | -0.048524 | 0.0057003 | west | N | 0.0057003 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.046113 | west | -0.05157 | -0.047165 | 0.0057003 | -0.048524 | 0.0057003 | west | N | 0.0057003 | 0
76096 | L_CAPRSI | W1 | 186 | -0.046113 | west | -0.05157 | -0.047165 | 0.0057003 | -0.048524 | 0.0057003 | west | N | 0.0057003 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.046113 | west | -0.05157 | -0.047165 | 0.0057003 | -0.048524 | 0.0057003 | west | N | 0.0057003 | 0
80003 | MILHWYS | F | 0 | 0.000965 | south | -0.0044918 | -8.6801e-05 | 0.052778 | -0.0014455 | 8.6801e-05 | south | N | 8.6801e-05 | 0
80010 | EPLVT1 | F | 0 | -0.00829 | south | -0.013747 | -0.0093418 | 0.043523 | -0.010701 | 0.0093418 | south | N | 0.0093418 | 0
80012 | LAR | F | 0 | -0.000274 | south | -0.0057308 | -0.0013258 | 0.051539 | -0.0026845 | 0.0013258 | south | N | 0.0013258 | 0
80051 | FORPVCM0 | 8 | 28 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
80053 | FOR69CG0 | 10 | 74 | 0.001341 | south | -0.0041158 | 0.0002892 | 0.053154 | -0.0010695 | 0.0002892 | south | N | 0.0002892 | 0
80080 | GWINDT11 | 1 | 94 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80080 | GWINDT11 | 2 | 41 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80080 | GWINDT11 | 3 | 38 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80080 | GWINDT11 | 4 | 19 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80081 | GWINDT21 | 1 | 94 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80081 | GWINDT21 | 2 | 36 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80081 | GWINDT21 | 3 | 43 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80081 | GWINDT21 | 4 | 22 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80137 | CSDR89 | 8 | 39 | 0.001256 | south | -0.0042008 | 0.0002042 | 0.053069 | -0.0011545 | 0.0002042 | south | N | 0.0002042 | 0
80137 | CSDR89 | 9 | 15 | 0.001256 | south | -0.0042008 | 0.0002042 | 0.053069 | -0.0011545 | 0.0002042 | south | N | 0.0002042 | 0
80138 | CSDR7 | 7 | 7 | 0.001256 | south | -0.0042008 | 0.0002042 | 0.053069 | -0.0011545 | 0.0002042 | south | N | 0.0002042 | 0
80139 | CSDR56 | 5 | 15 | 0.001256 | south | -0.0042008 | 0.0002042 | 0.053069 | -0.0011545 | 0.0002042 | south | N | 0.0002042 | 0
80139 | CSDR56 | 6 | 39 | 0.001256 | south | -0.0042008 | 0.0002042 | 0.053069 | -0.0011545 | 0.0002042 | south | N | 0.0002042 | 0
80140 | CSDR11 | 11 | 39 | 0.001256 | south | -0.0042008 | 0.0002042 | 0.053069 | -0.0011545 | 0.0002042 | south | N | 0.0002042 | 0
80180 | PNSCALT1 | 1 | 148 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80180 | PNSCALT1 | 2 | 50 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80181 | PNSCALT2 | 1 | 55 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80181 | PNSCALT2 | 2 | 50 | 0.00098 | south | -0.0044768 | -7.1801e-05 | 0.052793 | -0.0014305 | 7.1801e-05 | south | N | 7.1801e-05 | 0
80223 | REYSHR G | 1 | 12 | 0.001069 | south | -0.0043878 | 1.7199e-05 | 0.052882 | -0.0013415 | 1.7199e-05 | south | N | 1.7199e-05 | 0
80224 | VISTRONG | 1 | 15 | 0.001238 | south | -0.0042188 | 0.0001862 | 0.053051 | -0.0011725 | 0.0001862 | south | N | 0.0001862 | 0
80225 | VISTRONG | 2 | 23 | 0.001238 | south | -0.0042188 | 0.0001862 | 0.053051 | -0.0011725 | 0.0001862 | south | N | 0.0001862 | 0
80226 | ALCOA G | 1 | 48 | 0.001323 | south | -0.0041338 | 0.0002712 | 0.053136 | -0.0010875 | 0.0002712 | south | N | 0.0002712 | 0
80227 | AIRCO G | 1 | 8 | 0.001243 | south | -0.0042138 | 0.0001912 | 0.053056 | -0.0011675 | 0.0001912 | south | N | 0.0001912 | 0
80261 | NBEC81A | 1 | 180 | 0.001032 | south | -0.0044248 | -1.9801e-05 | 0.052845 | -0.0013785 | 1.9801e-05 | south | N | 1.9801e-05 | 0
80262 | NBEC91A | 1 | 180 | 0.001033 | south | -0.0044238 | -1.8801e-05 | 0.052846 | -0.0013775 | 1.8801e-05 | south | N | 1.8801e-05 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.001026 | south | -0.0044308 | -2.5801e-05 | 0.052839 | -0.0013845 | 2.5801e-05 | south | N | 2.5801e-05 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.001026 | south | -0.0044308 | -2.5801e-05 | 0.052839 | -0.0013845 | 2.5801e-05 | south | N | 2.5801e-05 | 0
80265 | LARECU40 | 4 | 100 | -0.000273 | south | -0.0057298 | -0.0013248 | 0.05154 | -0.0026835 | 0.0013248 | south | N | 0.0013248 | 0
80266 | LARECU50 | 5 | 100 | -0.000273 | south | -0.0057298 | -0.0013248 | 0.05154 | -0.0026835 | 0.0013248 | south | N | 0.0013248 | 0
80291 | PAPALOTE | 1 | 25 | 0.001054 | south | -0.0044028 | 2.199e-06 | 0.052867 | -0.0013565 | 2.199e-06 | south | N | 2.199e-06 | 0
80291 | PAPALOTE | 2 | 25 | 0.001054 | south | -0.0044028 | 2.199e-06 | 0.052867 | -0.0013565 | 2.199e-06 | south | N | 2.199e-06 | 0
80291 | PAPALOTE | 3 | 25 | 0.001054 | south | -0.0044028 | 2.199e-06 | 0.052867 | -0.0013565 | 2.199e-06 | south | N | 2.199e-06 | 0
80291 | PAPALOTE | 4 | 16 | 0.001054 | south | -0.0044028 | 2.199e-06 | 0.052867 | -0.0013565 | 2.199e-06 | south | N | 2.199e-06 | 0
80294 | PAPALOTE | 5 | 25 | 0.001054 | south | -0.0044028 | 2.199e-06 | 0.052867 | -0.0013565 | 2.199e-06 | south | N | 2.199e-06 | 0
80294 | PAPALOTE | 6 | 25 | 0.001054 | south | -0.0044028 | 2.199e-06 | 0.052867 | -0.0013565 | 2.199e-06 | south | N | 2.199e-06 | 0
80294 | PAPALOTE | 7 | 25 | 0.001054 | south | -0.0044028 | 2.199e-06 | 0.052867 | -0.0013565 | 2.199e-06 | south | N | 2.199e-06 | 0
80294 | PAPALOTE | 8 | 15 | 0.001054 | south | -0.0044028 | 2.199e-06 | 0.052867 | -0.0013565 | 2.199e-06 | south | N | 2.199e-06 | 0
86104 | CID-138 | EQ | 0 | -0.000273 | south | -0.0057298 | -0.0013248 | 0.05154 | -0.0026835 | 0.0013248 | south | N | 0.0013248 | 0
86105 | CID-230 | EQ | 500 | -0.000273 | south | -0.0057298 | -0.0013248 | 0.05154 | -0.0026835 | 0.0013248 | south | N | 0.0013248 | 0
86106 | CUF-230 | EQ | 500 | -0.000273 | south | -0.0057298 | -0.0013248 | 0.05154 | -0.0026835 | 0.0013248 | south | N | 0.0013248 | 0
86107 | CUF-138 | EQ | 0 | -0.000273 | south | -0.0057298 | -0.0013248 | 0.05154 | -0.0026835 | 0.0013248 | south | N | 0.0013248 | 0
88198 | BEEVILLE | F | 0 | 0.000823 | south | -0.0046338 | -0.0002288 | 0.052636 | -0.0015875 | 0.0002288 | south | N | 0.0002288 | 0
88253 | HAMILTON | F | 0 | -0.012989 | south | -0.018446 | -0.014041 | 0.038824 | -0.0154 | 0.014041 | south | N | 0.014041 | 0
88299 | ZAPATA | F | 0 | 0.000136 | south | -0.0053208 | -0.0009158 | 0.051949 | -0.0022745 | 0.0009158 | south | N | 0.0009158 | 0
88508 | FALFURRI | F | 0 | 0.000788 | south | -0.0046688 | -0.0002638 | 0.052601 | -0.0016225 | 0.0002638 | south | N | 0.0002638 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: MURRY P8 to PAIP4B [1371 - 6169] C: cookfield - long creek - graham [1430 - 1435] and [1430 - 1442] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.069487 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.8159 | 242 | 0.06346 | 15.3574 | 242 | 15.3574
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.44893 | 0 | 0.054408 | 0 | 242 | 15.3574
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.40482 | 0 | 0.054408 | 0 | 242 | 15.3574
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39963 | 0 | 0.054408 | 0 | 242 | 15.3574 | Weighted Shift Factors
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39963 | 0 | 0.054408 | 0 | 242 | 15.3574 | West | -0.051813
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.002595 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42039 | 0 | 0.054408 | 0 | 242 | 15.3574 | North | 0.0060267
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14252 | 56 | 0.054358 | 3.0441 | 298 | 18.4015 |  | -0.05784
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15016 | 59 | 0.054358 | 3.2071
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14252 | 56 | 0.054358 | 3.0441 |  |  | Line Rating | 155
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14252 | 56 | 0.054358 | 3.0441 |  |  | Conc Gen | 298
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15016 | 59 | 0.054358 | 3.2071 |  |  | Weighted Imp. | 18.4015
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14252 | 56 | 0.054358 | 3.0441 |  |  | PTDF | 0.06175
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.002539 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.0105 | 398 | 0.054352 | 21.6322
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4127 | 0 | 0.054348 | 0 |  |  | Concentration | -1.0676
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40915 | 0 | 0.054348 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40281 | 0 | 0.054348 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68242 | 0 | 0.054348 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.002526 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39658 | 0 | 0.054339 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.002526 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.43447 | 172 | 0.054339 | 9.3464
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.002526 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.43447 | 172 | 0.054339 | 9.3464
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.002526 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.43447 | 172 | 0.054339 | 9.3464
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.164 | 0 | 0.054336 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16652 | 0 | 0.054336 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17661 | 0 | 0.054336 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15895 | 0 | 0.054336 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15643 | 0 | 0.054336 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.26239 | 0 | 0.054336 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14886 | 0 | 0.054336 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.002523 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.030276 | 12 | 0.054336 | 0.65204
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.002523 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 1.8746 | 743 | 0.054336 | 40.3718
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.002522 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01261 | 0 | 0.054335 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.002522 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.052962 | 0 | 0.054335 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.002519 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.030228 | 12 | 0.054332 | 0.65199
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.085476 | 0 | 0.054327 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.087236 | 0 | 0.054327 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.082208 | 0 | 0.054327 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11539 | 0 | 0.054327 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.044498 | 0 | 0.054327 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.051286 | 0 | 0.054327 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.050029 | 0 | 0.054327 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.08799 | 0 | 0.054327 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.045252 | 0 | 0.054327 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2147 | 0 | 0.054327 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37207 | 0 | 0.054327 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.00251 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 1.8449 | 735 | 0.054323 | 39.9276
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.26083 | 104 | 0.054321 | 5.6494
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.26083 | 104 | 0.054321 | 5.6494
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13543 | 54 | 0.054321 | 2.9333
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13292 | 53 | 0.054321 | 2.879
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13543 | 54 | 0.054321 | 2.9333
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14296 | 57 | 0.054321 | 3.0963
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13543 | 54 | 0.054321 | 2.9333
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13543 | 54 | 0.054321 | 2.9333
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14546 | 58 | 0.054321 | 3.1506
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14546 | 58 | 0.054321 | 3.1506
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.002495 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43163 | 0 | 0.054308 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.002495 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.33682 | 0 | 0.054308 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.002493 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.33905 | 0 | 0.054306 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10471 | 42 | 0.054306 | 2.2809
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10471 | 42 | 0.054306 | 2.2809
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.094734 | 38 | 0.054306 | 2.0636
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.094734 | 38 | 0.054306 | 2.0636
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17644 | 0 | 0.054298 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17892 | 0 | 0.054298 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.096915 | 0 | 0.054298 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.07455 | 0 | 0.054298 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.00248 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.52824 | 213 | 0.054293 | 11.5645
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.040176 | 0 | 0.054293 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15872 | 0 | 0.054293 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15674 | 0 | 0.054293 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20485 | 0 | 0.054293 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18253 | 0 | 0.054293 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.00248 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.56544 | 228 | 0.054293 | 12.3789
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.00248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.4464 | 0 | 0.054293 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.00248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39333 | 0 | 0.054293 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.00248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38936 | 0 | 0.054293 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.002479 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.41895 | 169 | 0.054292 | 9.1754
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.002479 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.40903 | 165 | 0.054292 | 8.9582
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.002479 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36937 | 0 | 0.054292 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.002479 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16138 | 0 | 0.054292 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.002478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.029736 | 12 | 0.054291 | 0.6515
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.002478 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054291 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.002475 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.086625 | 0 | 0.054288 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.40327 | 0 | 0.054284 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38819 | 0 | 0.054284 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38918 | 0 | 0.054284 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38795 | 0 | 0.054284 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.6647 | 0 | 0.054284 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.002468 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.1925 | 0 | 0.054281 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.002468 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.19744 | 0 | 0.054281 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11348 | 46 | 0.05428 | 2.4969
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11348 | 46 | 0.05428 | 2.4969
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11348 | 46 | 0.05428 | 2.4969
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13569 | 55 | 0.05428 | 2.9854
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13569 | 55 | 0.05428 | 2.9854
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13322 | 54 | 0.05428 | 2.9311
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.15951 | 0 | 0.054267 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.14724 | 0 | 0.054267 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.15951 | 0 | 0.054267 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.15951 | 0 | 0.054267 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22268 | 0 | 0.05426 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21436 | 0 | 0.05426 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21289 | 0 | 0.05426 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13336 | 0 | 0.05426 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.029853 | 0 | 0.05426 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.002428 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054241 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.002415 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.12075 | 50 | 0.054228 | 2.7114
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.23982 | 0 | 0.054204 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.22212 | 0 | 0.054204 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24556 | 0 | 0.054204 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24388 | 0 | 0.054204 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.076512 | 0 | 0.054204 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.07173 | 0 | 0.054204 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16928 | 0 | 0.054204 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15948 | 0 | 0.054204 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.12672 | 0 | 0.054204 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.3663 | 0 | 0.054204 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.36702 | 0 | 0.054204 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.36415 | 0 | 0.054204 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.22954 | 0 | 0.054204 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5834 | 0 | 0.054204 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09564 | 0 | 0.054204 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.002349 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.37819 | 161 | 0.054162 | 8.7201
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.002349 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.38993 | 166 | 0.054162 | 8.9909
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.002349 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.58255 | 248 | 0.054162 | 13.4322
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.002349 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 1.2826 | 546 | 0.054162 | 29.5726
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.002349 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 1.5104 | 0 | 0.054162 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.002349 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.030537 | 13 | 0.054162 | 0.70411
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.002334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.077022 | 0 | 0.054147 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.00233 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37979 | 0 | 0.054143 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.00233 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37979 | 0 | 0.054143 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.00233 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.57085 | 0 | 0.054143 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.002329 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 1.5162 | 651 | 0.054142 | 35.2466
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.002329 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 1.3136 | 564 | 0.054142 | 30.5362
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.002329 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 1.3974 | 600 | 0.054142 | 32.4854
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.002319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10691 | 0 | 0.054132 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24642 | 0 | 0.054033 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24642 | 0 | 0.054033 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.26418 | 0 | 0.054033 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24309 | 0 | 0.054033 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.002189 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15542 | 0 | 0.054002 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.002189 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02189 | 0 | 0.054002 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13342 | 0 | 0.053965 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15365 | 0 | 0.053965 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09684 | 0 | 0.053965 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21735 | 0 | 0.053965 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18507 | 0 | 0.053965 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18938 | 0 | 0.053965 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1076 | 0 | 0.053965 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.038736 | 0 | 0.053965 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20229 | 0 | 0.053965 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15064 | 0 | 0.053965 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13558 | 0 | 0.053965 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15494 | 0 | 0.053965 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13945 | 0 | 0.053965 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21735 | 0 | 0.053965 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20874 | 0 | 0.053965 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22166 | 0 | 0.053965 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16355 | 0 | 0.053965 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17216 | 0 | 0.053965 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17216 | 0 | 0.053965 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36799 | 0 | 0.053965 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.002067 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1761 | 569 | 0.05388 | 30.6579
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.002067 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2009 | 581 | 0.05388 | 31.3044
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.002 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.132 | 66 | 0.053813 | 3.5517
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.15033 | 76 | 0.053791 | 4.0881
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.15033 | 76 | 0.053791 | 4.0881
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20769 | 105 | 0.053791 | 5.6481
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14637 | 74 | 0.053791 | 3.9806
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14637 | 74 | 0.053791 | 3.9806
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20176 | 102 | 0.053791 | 5.4867
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.001949 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 2.598 | 0 | 0.053762 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.001949 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 2.5883 | 0 | 0.053762 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.001618 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.94491 | 584 | 0.053431 | 31.2039
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.001618 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.96271 | 595 | 0.053431 | 31.7916
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.001617 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.70016 | 433 | 0.05343 | 23.1353
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.001616 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25533 | 158 | 0.053429 | 8.4418
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.001616 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25856 | 160 | 0.053429 | 8.5487
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.001616 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2828 | 175 | 0.053429 | 9.3501
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0789 | 50 | 0.053391 | 2.6696
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0789 | 50 | 0.053391 | 2.6696
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0789 | 50 | 0.053391 | 2.6696
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0789 | 50 | 0.053391 | 2.6696
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.001524 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.23241 | 152.5 | 0.053337 | 8.1339
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.001524 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22784 | 149.5 | 0.053337 | 7.9739
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.001524 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.35448 | 232.6 | 0.053337 | 12.4062
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.001519 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.20051 | 132 | 0.053332 | 7.0399
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.001519 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.20355 | 134 | 0.053332 | 7.1465
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.001519 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.49064 | 323 | 0.053332 | 17.2263
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.060018 | 42 | 0.053242 | 2.2362
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.062876 | 44 | 0.053242 | 2.3427
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.062876 | 44 | 0.053242 | 2.3427
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.067163 | 47 | 0.053242 | 2.5024
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.001389 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.43059 | 310 | 0.053202 | 16.4927
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.001389 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.57366 | 413 | 0.053202 | 21.9725
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.067424 | 49 | 0.053189 | 2.6063
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.063296 | 46 | 0.053189 | 2.4467
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.063296 | 46 | 0.053189 | 2.4467
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.064672 | 47 | 0.053189 | 2.4999
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.001376 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2119 | 154 | 0.053189 | 8.1911
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.001376 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.20365 | 148 | 0.053189 | 7.872
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.066048 | 48 | 0.053189 | 2.5531
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.066048 | 48 | 0.053189 | 2.5531
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.001343 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010744 | 0 | 0.053156 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.001343 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010744 | 0 | 0.053156 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10594 | 0 | 0.053154 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10862 | 0 | 0.053154 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10594 | 0 | 0.053154 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10728 | 0 | 0.053154 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10513 | 0 | 0.053154 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.033525 | 0 | 0.053154 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.061686 | 0 | 0.053154 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.037548 | 0 | 0.053154 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.058468 | 0 | 0.053154 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.099234 | 0 | 0.053154 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.001323 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.063504 | 0 | 0.053136 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.035168 | 0 | 0.053069 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.008792 | 0 | 0.053069 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.048984 | 0 | 0.053069 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01884 | 0 | 0.053069 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.008792 | 0 | 0.053069 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01884 | 0 | 0.053069 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.048984 | 0 | 0.053069 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.048984 | 0 | 0.053069 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.001243 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.009944 | 0 | 0.053056 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.001238 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01857 | 0 | 0.053051 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.001238 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.028474 | 0 | 0.053051 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.001214 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.088622 | 0 | 0.053027 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.001195 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17208 | 144 | 0.053008 | 7.6332
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.001195 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22466 | 188 | 0.053008 | 9.9656
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.056286 | 47.7 | 0.052993 | 2.5278
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.044014 | 37.3 | 0.052993 | 1.9766
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.05428 | 46 | 0.052993 | 2.4377
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.05664 | 48 | 0.052993 | 2.5437
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.001169 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0028056 | 0 | 0.052982 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.001169 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0028056 | 0 | 0.052982 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.001168 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.014016 | 0 | 0.052981 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.001145 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.02519 | 22 | 0.052958 | 1.1651
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.001145 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012595 | 11 | 0.052958 | 0.58254
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.001145 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012595 | 11 | 0.052958 | 0.58254
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25525 | 223.9 | 0.052953 | 11.8562
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2565 | 225 | 0.052953 | 11.9145
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25604 | 224.6 | 0.052953 | 11.8933
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25844 | 226.7 | 0.052953 | 12.0045
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15478 | 142 | 0.052903 | 7.5123
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15805 | 145 | 0.052903 | 7.671
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.16459 | 151 | 0.052903 | 7.9884
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.3161 | 290 | 0.052903 | 15.3419
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.001089 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0026136 | 0 | 0.052902 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.001089 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0026136 | 0 | 0.052902 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.001089 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0030492 | 0 | 0.052902 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1689 | 0 | 0.052882 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.16356 | 0 | 0.052882 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1069 | 0 | 0.052882 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.15501 | 0 | 0.052882 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.15714 | 0 | 0.052882 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.13576 | 0 | 0.052882 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.001069 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.012828 | 0 | 0.052882 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 25 | 0.052867 | 1.3217
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 25 | 0.052867 | 1.3217
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 25 | 0.052867 | 1.3217
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.016864 | 16 | 0.052867 | 0.84588
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 25 | 0.052867 | 1.3217
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 25 | 0.052867 | 1.3217
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 25 | 0.052867 | 1.3217
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01581 | 15 | 0.052867 | 0.79301
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15288 | 147 | 0.052853 | 7.7694
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14352 | 138 | 0.052853 | 7.2938
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1456 | 140 | 0.052853 | 7.3995
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15288 | 147 | 0.052853 | 7.7694
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18928 | 182 | 0.052853 | 9.6193
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.20592 | 198 | 0.052853 | 10.4649
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.001037 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.65227 | 629 | 0.05285 | 33.2428
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.001033 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.34709 | 336 | 0.052846 | 17.7563
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.001033 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18594 | 180 | 0.052846 | 9.5123
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.001032 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18576 | 180 | 0.052845 | 9.5121
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.001032 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.15305 | 0 | 0.052845 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.001032 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.15336 | 0 | 0.052845 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.001032 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1579 | 0 | 0.052845 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.001027 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.006162 | 0 | 0.05284 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.001026 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34268 | 334 | 0.052839 | 17.6483
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.001026 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34884 | 340 | 0.052839 | 17.9653
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.001026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18468 | 180 | 0.052839 | 9.5111
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.001026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18468 | 180 | 0.052839 | 9.5111
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.001021 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.038798 | 0 | 0.052834 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.001021 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.025525 | 0 | 0.052834 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.001021 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.025525 | 0 | 0.052834 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.001017 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.038646 | 0 | 0.05283 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.001011 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.004044 | 0 | 0.052824 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.000998 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.028942 | 0 | 0.052811 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09212 | 94 | 0.052793 | 4.9626
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04018 | 41 | 0.052793 | 2.1645
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.03724 | 38 | 0.052793 | 2.0061
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01862 | 19 | 0.052793 | 1.0031
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09212 | 94 | 0.052793 | 4.9626
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.03528 | 36 | 0.052793 | 1.9006
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04214 | 43 | 0.052793 | 2.2701
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02156 | 22 | 0.052793 | 1.1615
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.14504 | 148 | 0.052793 | 7.8134
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.049 | 50 | 0.052793 | 2.6397
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0539 | 55 | 0.052793 | 2.9036
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.049 | 50 | 0.052793 | 2.6397
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.000965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.052778 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.000965 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.03667 | 38 | 0.052778 | 2.0056
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.000965 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.018624 | 19.3 | 0.052778 | 1.0186
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.000965 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.014475 | 15 | 0.052778 | 0.79167
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.000965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.045355 | 47 | 0.052778 | 2.4806
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1921 | 207 | 0.052741 | 10.9174
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2011 | 216.7 | 0.052741 | 11.429
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22458 | 242 | 0.052741 | 12.7634
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13363 | 144 | 0.052741 | 7.5947
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13363 | 144 | 0.052741 | 7.5947
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15869 | 171 | 0.052741 | 9.0188
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.000903 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.49304 | 546 | 0.052716 | 28.7831
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.000903 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.67725 | 750 | 0.052716 | 39.5372
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000875 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13562 | 155 | 0.052688 | 8.1667
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.000875 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14875 | 170 | 0.052688 | 8.957
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000875 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13562 | 155 | 0.052688 | 8.1667
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.000866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12687 | 146.5 | 0.052679 | 7.7175
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.000866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12808 | 147.9 | 0.052679 | 7.7913
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.000866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14982 | 173 | 0.052679 | 9.1135
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.000857 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.05267 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.000857 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.05267 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.000857 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.05267 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.029715 | 0 | 0.052662 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.028866 | 0 | 0.052662 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.029715 | 0 | 0.052662 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.000823 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.052636 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.000794 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.33666 | 424 | 0.052607 | 22.3055
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.000794 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.33745 | 425 | 0.052607 | 22.3581
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.000788 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.052601 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.000779 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.32095 | 412 | 0.052592 | 21.668
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.000779 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.3116 | 400 | 0.052592 | 21.0369
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.000778 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.1626 | 209 | 0.052591 | 10.9916
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.000778 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.16805 | 216 | 0.052591 | 11.3597
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035788 | 46 | 0.052591 | 2.4192
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.036566 | 47 | 0.052591 | 2.4718
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035788 | 46 | 0.052591 | 2.4192
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035788 | 46 | 0.052591 | 2.4192
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.000764 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.30254 | 396 | 0.052577 | 20.8206
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.000749 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.30484 | 407 | 0.052562 | 21.3928
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000664 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.038512 | 58 | 0.052477 | 3.0437
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000664 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.059096 | 89 | 0.052477 | 4.6705
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029216 | 44 | 0.052477 | 2.309
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029216 | 44 | 0.052477 | 2.309
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.028552 | 43 | 0.052477 | 2.2565
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02988 | 45 | 0.052477 | 2.3615
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.068856 | 114 | 0.052417 | 5.9756
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13409 | 222 | 0.052417 | 11.6366
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11114 | 184 | 0.052417 | 9.6448
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1353 | 224 | 0.052417 | 11.7415
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.06946 | 115 | 0.052417 | 6.028
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000493 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.005916 | 0 | 0.052306 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000493 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.005423 | 0 | 0.052306 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000493 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.005916 | 0 | 0.052306 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.000136 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051949 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051813 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051813 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.000251 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004518 | 0 | 0.051562 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.000251 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004518 | 0 | 0.051562 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.000273 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0273 | 100 | 0.05154 | 5.154
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.000273 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0273 | 100 | 0.05154 | 5.154
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.05154 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.05154 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.05154 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.05154 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.000274 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051539 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000613 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.017164 | 0 | 0.0512 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000613 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.017777 | 0 | 0.0512 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.000736 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31059 | 422 | 0.051077 | 21.5546
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.00081 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01458 | 0 | 0.051003 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.00081 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01458 | 0 | 0.051003 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.00081 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01215 | 0 | 0.051003 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.000993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.023832 | 24 | 0.05082 | 1.2197
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.000993 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.023832 | 24 | 0.05082 | 1.2197
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.000993 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.022839 | 23 | 0.05082 | 1.1689
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.001376 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.018851 | 0 | 0.050437 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.00829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.043523 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.009177 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.055062 | 0 | 0.042636 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.012989 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.42864 | 0 | 0.038824 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.012989 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32472 | 0 | 0.038824 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.012989 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.038824 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.039372 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.7246 | 120 | 0.033345 | 4.0014
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.02288 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.27456 | 0 | 0.016853 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.02288 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.27456 | 0 | 0.016853 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.012641 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.22754 | 18 | 0.0066143 | 0.11906
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.012641 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.22754 | 18 | 0.0066143 | 0.11906
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.012641 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.48036 | 38 | 0.0066143 | 0.25134
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.012427 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.90717 | 73 | 0.0064003 | 0.46722
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.012427 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.4788 | 119 | 0.0064003 | 0.76164
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.012427 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.5475 | 205 | 0.0064003 | 1.3121
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.012427 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.2676 | 102 | 0.0064003 | 0.65283
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.012427 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.193 | 96 | 0.0064003 | 0.61443
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.24394 | 20 | 0.0061703 | 0.12341
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.24394 | 20 | 0.0061703 | 0.12341
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.24394 | 20 | 0.0061703 | 0.12341
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.20735 | 17 | 0.0061703 | 0.1049
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.010343 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.7855 | 366 | 0.0043163 | 1.5798
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.01006 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8973 | 288 | 0.0040333 | 1.1616
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.01006 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4788 | 147 | 0.0040333 | 0.5929
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.01006 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4788 | 147 | 0.0040333 | 0.5929
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.007983 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.89809 | 112.5 | 0.0019563 | 0.22009
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.006714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3697 | 204 | 0.00068733 | 0.14021
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.006714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3495 | 201 | 0.00068733 | 0.13815
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.006714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.6248 | 242 | 0.00068733 | 0.16633
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.006061 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 3.4328e-05 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.006061 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 3.4328e-05 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.006061 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 3.4328e-05 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.005866 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.35196 | 60 | -0.00016067 | -0.0096403
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.005768 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.34608 | 60 | -0.00025867 | -0.01552
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.005768 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.36338 | 63 | -0.00025867 | -0.016296
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.005076 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20304 | 0 | -0.00095067 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.005076 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20304 | 0 | -0.00095067 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.005061 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00096567 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.005003 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.85051 | 170 | -0.0010237 | -0.17402
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.005003 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.6016 | 520 | -0.0010237 | -0.53231
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.004918 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0011087 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.004896 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.8115 | 370 | -0.0011307 | -0.41835
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.68544 | 0 | -0.0011307 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.69034 | 0 | -0.0011307 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5129 | 0 | -0.0011307 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.70013 | 0 | -0.0011307 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.70502 | 0 | -0.0011307 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5178 | 0 | -0.0011307 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.78032 | 160 | -0.0011497 | -0.18395
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76081 | 156 | -0.0011497 | -0.17935
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.95589 | 196 | -0.0011497 | -0.22534
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76081 | 156 | -0.0011497 | -0.17935
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76569 | 157 | -0.0011497 | -0.1805
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.96565 | 198 | -0.0011497 | -0.22764
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.004876 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.3657 | 0 | -0.0011507 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.004876 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.38813 | 0 | -0.0011507 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.004876 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.43104 | 0 | -0.0011507 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.004833 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6968 | 558 | -0.0011937 | -0.66607
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.004833 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.7983 | 579 | -0.0011937 | -0.69114
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.004833 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.9051 | 808 | -0.0011937 | -0.96449
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.004766 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0732 | 435 | -0.0012607 | -0.54839
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.004757 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.879 | 395 | -0.0012697 | -0.50152
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.004757 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0693 | 435 | -0.0012697 | -0.55231
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.004756 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.37572 | 79 | -0.0012707 | -0.10038
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.004756 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.50414 | 106 | -0.0012707 | -0.13469
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.004756 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.69438 | 146 | -0.0012707 | -0.18552
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.004756 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36146 | 76 | -0.0012707 | -0.096571
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.004739 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.09478 | 20 | -0.0012877 | -0.025753
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.004739 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.11847 | 25 | -0.0012877 | -0.032192
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.004739 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1943 | 41 | -0.0012877 | -0.052795
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.004738 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.18952 | 40 | -0.0012887 | -0.051547
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.004654 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.8058 | 388 | -0.0013727 | -0.5326
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.004654 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.3968 | 515 | -0.0013727 | -0.70693
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74623 | 161 | -0.0013917 | -0.22406
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76014 | 164 | -0.0013917 | -0.22823
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76014 | 164 | -0.0013917 | -0.22823
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9189 | 414 | -0.0013917 | -0.57615
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75087 | 162 | -0.0013917 | -0.22545
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74623 | 161 | -0.0013917 | -0.22406
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7555 | 163 | -0.0013917 | -0.22684
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8957 | 409 | -0.0013917 | -0.56919
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004626 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0014007 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004626 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0014007 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.31969 | 70 | -0.0014597 | -0.10218
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.31512 | 69 | -0.0014597 | -0.10072
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.31512 | 69 | -0.0014597 | -0.10072
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.31056 | 68 | -0.0014597 | -0.099258
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.004551 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.53702 | 118 | -0.0014757 | -0.17413
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.004551 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.52336 | 115 | -0.0014757 | -0.1697
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.004551 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.5304 | 556 | -0.0014757 | -0.82047
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.004376 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4352 | 785 | -0.0016507 | -1.2958
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.004376 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4789 | 795 | -0.0016507 | -1.3123
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.004376 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4133 | 780 | -0.0016507 | -1.2875
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.64247 | 0 | -0.0016857 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.56433 | 0 | -0.0016857 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.62945 | 0 | -0.0016857 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7321 | 0 | -0.0016857 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.004311 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0017157 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.004307 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.21535 | 50 | -0.0017197 | -0.085984
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.004303 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.78315 | 182 | -0.0017237 | -0.31371
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.004303 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0827 | 484 | -0.0017237 | -0.83426
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.004298 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.84241 | 196 | -0.0017287 | -0.33882
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.004298 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.47708 | 111 | -0.0017287 | -0.19188
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.004234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.91624 | 216.4 | -0.0017927 | -0.38793
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.004234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.91497 | 216.1 | -0.0017927 | -0.3874
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.004233 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.94819 | 224 | -0.0017937 | -0.40178
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.004225 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7098 | 168 | -0.0018017 | -0.30268
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.004225 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.38025 | 90 | -0.0018017 | -0.16215
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.91616 | 224 | -0.0019367 | -0.43381
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.92434 | 226 | -0.0019367 | -0.43769
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.86708 | 212 | -0.0019367 | -0.41057
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.86299 | 211 | -0.0019367 | -0.40864
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.004005 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60676 | 151.5 | -0.0020217 | -0.30628
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.004005 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60996 | 152.3 | -0.0020217 | -0.3079
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.004005 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.71089 | 177.5 | -0.0020217 | -0.35885
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.00399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60129 | 150.7 | -0.0020367 | -0.30693
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.00399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60249 | 151 | -0.0020367 | -0.30754
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.00399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.70783 | 177.4 | -0.0020367 | -0.36131
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.003932 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4182 | 615 | -0.0020947 | -1.2882
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.003932 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.3081 | 587 | -0.0020947 | -1.2296
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.003848 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.05772 | 0 | -0.0021787 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.003848 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.05772 | 0 | -0.0021787 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.003711 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0023157 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.0036 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9772 | 827 | -0.0024267 | -2.0069
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.0036 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9484 | 819 | -0.0024267 | -1.9874
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9703 | 855 | -0.0025527 | -2.1825
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9703 | 855 | -0.0025527 | -2.1825
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.52909 | 152.3 | -0.0025527 | -0.38877
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.53152 | 153 | -0.0025527 | -0.39056
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.003414 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.5121 | 150 | -0.0026127 | -0.3919
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.003414 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.27312 | 80 | -0.0026127 | -0.20901
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.003337 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.85093 | 255 | -0.0026897 | -0.68587
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.003337 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.49721 | 149 | -0.0026897 | -0.40076
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.003337 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.51056 | 153 | -0.0026897 | -0.41152
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.003244 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0027827 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.003244 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.553 | 787 | -0.0027827 | -2.19
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028637 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028637 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.003163 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.053771 | 17 | -0.0028637 | -0.048682
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028637 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028637 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.003161 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.10115 | 0 | -0.0028657 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.00316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.4631 | 463 | -0.0028667 | -1.3273
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.003156 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.15149 | 48 | -0.0028707 | -0.13779
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.003156 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.14518 | 46 | -0.0028707 | -0.13205
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.003156 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.33138 | 105 | -0.0028707 | -0.30142
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.003142 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028847 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.003142 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028847 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.47247 | 0 | -0.0029627 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.47798 | 0 | -0.0029627 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.47798 | 0 | -0.0029627 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.1643 | 0 | -0.0029627 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.00281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61061 | 217.3 | -0.0032167 | -0.69898
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.00281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.57605 | 205 | -0.0032167 | -0.65942
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.00281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76544 | 272.4 | -0.0032167 | -0.87622
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.002558 | north | 3 | N | N | Nnorth | Nnorth | 1 | 2.9596 | 0 | -0.0034687 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.002558 | north | 3 | N | N | Nnorth | Nnorth | 1 | 2.9622 | 0 | -0.0034687 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0604 | 100 | -0.0054227 | -0.54227
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0060267 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0060267 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.013819 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.019846 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.02595 | west | 4 | Y | N | Ywest | Nwest | 1 | -16.8597 | 649.7 | -0.031977 | -20.7752
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.035508 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3262 | 150 | -0.041535 | -6.2302
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.040416 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.046443 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6141 | 209 | -0.047243 | -9.8737
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2138 | 126.5 | -0.047243 | -5.9762
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.2628 | 249 | -0.047243 | -11.7634
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1196 | 197 | -0.047243 | -9.3068
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.045877 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8537 | 84 | -0.051904 | -4.3599
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.045939 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5143 | 76.5 | -0.051966 | -3.9754
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1877 | 112.5 | -0.05214 | -5.8657
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.8939 | 149.5 | -0.05214 | -7.7949
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.577 | 186 | -0.05214 | -9.698
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.8912 | 214.5 | -0.05214 | -11.184
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.046224 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6979 | 80 | -0.052251 | -4.1801
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.046572 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9858 | 150 | -0.052599 | -7.8898
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.047254 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0881 | 150 | -0.053281 | -7.9921
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.047254 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0881 | 150 | -0.053281 | -7.9921
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.047282 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7826 | 80 | -0.053309 | -4.2647
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.047289 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7831 | 80 | -0.053316 | -4.2653
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.047327 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5495 | 75 | -0.053354 | -4.0015
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.047327 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7862 | 80 | -0.053354 | -4.2683
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.047327 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8931 | 40 | -0.053354 | -2.1341
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.047523 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8018 | 80 | -0.05355 | -4.284
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.047523 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8018 | 80 | -0.05355 | -4.284
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.048407 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.23235 | 0 | -0.054434 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3633 | 150 | -0.055116 | -8.2674
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.7996 | 220 | -0.055116 | -12.1254
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.8178 | 200 | -0.055116 | -11.0231
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.9839 | 121.9 | -0.055116 | -6.7186
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.049339 | west | 8 | N | N | Nwest | Nwest | 1 | -3.4537 | 0 | -0.055366 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.049339 | west | 8 | N | N | Nwest | Nwest | 1 | -3.6215 | 0 | -0.055366 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.049339 | west | 8 | N | N | Nwest | Nwest | 1 | -3.4735 | 0 | -0.055366 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.049368 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.171 | 125 | -0.055395 | -6.9243
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.049368 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.171 | 125 | -0.055395 | -6.9243
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.4791 | 70 | -0.055728 | -3.9009
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.4791 | 70 | -0.055728 | -3.9009
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6123 | 92.8 | -0.055728 | -5.1715
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.9761 | 80 | -0.055728 | -4.4582
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.9761 | 80 | -0.055728 | -4.4582
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.7156 | 115 | -0.055728 | -6.4087
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.3492 | 208.2 | -0.055735 | -11.604
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.0635 | 142.1 | -0.055735 | -7.9199
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -6.5813 | 132.4 | -0.055735 | -7.3793
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -6.7603 | 136 | -0.055735 | -7.5799
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.3071 | 147 | -0.055735 | -8.193
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.4387 | 210 | -0.055735 | -11.7043
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.3292 | 66 | -0.056469 | -3.7269
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.2787 | 65 | -0.056469 | -3.6705
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.3796 | 67 | -0.056469 | -3.7834
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.3796 | 67 | -0.056469 | -3.7834
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.3796 | 67 | -0.056469 | -3.7834
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.050442 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056469 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.050442 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056469 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.050845 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6182 | 169.5 | -0.056872 | -9.6397
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.050997 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7849 | 35 | -0.057024 | -1.9958
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.050997 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5299 | 30 | -0.057024 | -1.7107
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.922 | 37.5 | -0.057279 | -2.148
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5096 | 107.5 | -0.057279 | -6.1575
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.919 | 135 | -0.057279 | -7.7326
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.099 | 119 | -0.057279 | -6.8162
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3815 | 105 | -0.057279 | -6.0143
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1258 | 80.5 | -0.057279 | -4.6109
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.052256 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.7861 | 149 | -0.058283 | -8.6841
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.052712 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.44 | 236 | -0.058739 | -13.8623
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.052712 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6975 | 165 | -0.058739 | -9.6919
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.052721 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.0884 | 400 | -0.058748 | -23.4991
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.05351 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.4212 | 120 | -0.059537 | -7.1444
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.05351 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4678 | 233 | -0.059537 | -13.872
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.05351 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.1074 | 170.2 | -0.059537 | -10.1331
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.053903 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.4173 | 100.5 | -0.05993 | -6.0229
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.053933 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.1281 | 58 | -0.05996 | -3.4777
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.054347 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.6411 | 214.2 | -0.060374 | -12.932
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.056168 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.37071 | 6.6 | -0.062195 | -0.41048
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.056168 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9266 | 34.3 | -0.062195 | -2.1333
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.7547 | 66 | -0.062916 | -4.1524
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.9253 | 69 | -0.062916 | -4.3412
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.9253 | 69 | -0.062916 | -4.3412
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.8116 | 67 | -0.062916 | -4.2154
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.8116 | 67 | -0.062916 | -4.2154
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.6978 | 65 | -0.062916 | -4.0895
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.05794 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4949 | 0 | -0.063967 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.059789 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.1747 | 120 | -0.065816 | -7.8979
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.061098 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3318 | 120 | -0.067125 | -8.055
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.065405 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.7161 | 225 | -0.071432 | -16.0721
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.065965 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8737 | 180 | -0.071992 | -12.9585
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.065965 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8737 | 180 | -0.071992 | -12.9585
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.069302 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.366 | 63 | -0.075329 | -4.7457
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.071826 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.7739 | 150 | -0.077853 | -11.6779
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.071826 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2544 | 101 | -0.077853 | -7.8631
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.072885 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.2768 | 141 | -0.078912 | -11.1265
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.072885 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.7462 | 120 | -0.078912 | -9.4694
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.073351 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2617 | 99 | -0.079378 | -7.8584
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.073351 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4744 | 61 | -0.079378 | -4.842
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.073351 | west | 7 | N | N | Nwest | Nwest | 1 | -1.8338 | 0 | -0.079378 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.073351 | west | 7 | N | N | Nwest | Nwest | 1 | -3.3521 | 0 | -0.079378 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.073351 | west | 7 | N | N | Nwest | Nwest | 1 | -3.3521 | 0 | -0.079378 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.082765 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9523 | 84 | -0.088792 | -7.4585
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.12405 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.6083 | 150 | -0.13008 | -19.5123
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.13826 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2957 | 60 | -0.14429 | -8.6573

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: MURRY P8 to PAIP4B [1371 - 6169] C: cookfield - long creek - graham [1430 - 1435] and [1430 - 1442] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.13826 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2957 | 0 | -0.14429 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.12405 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.6083 | 0 | -0.13008 | 0 | 0 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.082765 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9523 | 0 | -0.088792 | 0 | 0 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.073351 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2617 | 0 | -0.079378 | 0 | 0 | 0 | Weighted Shift Factors
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.073351 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4744 | 0 | -0.079378 | 0 | 0 | 0 | West | -0.051813
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.073351 | west | 7 | N | N | Nwest | Nwest | 1 | -1.8338 | 0 | -0.079378 | 0 | 0 | 0 | North | 0.0060267
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.073351 | west | 7 | N | N | Nwest | Nwest | 1 | -3.3521 | 0 | -0.079378 | 0 | 0 | 0 |  | -0.05784
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.073351 | west | 7 | N | N | Nwest | Nwest | 1 | -3.3521 | 0 | -0.079378 | 0 | 0 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.072885 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.2768 | 0 | -0.078912 | 0 | 0 | 0 | Line Rating | 155
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.072885 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.7462 | 0 | -0.078912 | 0 | 0 | 0 | Conc Gen | 271
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.071826 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.7739 | 0 | -0.077853 | 0 | 0 | 0 | Weighted Imp. | 17.0501
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.071826 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2544 | 0 | -0.077853 | 0 | 0 | 0 | PTDF | 0.062916
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.069302 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.366 | 0 | -0.075329 | 0 | 0 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.065965 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8737 | 0 | -0.071992 | 0 | 0 | 0 | Concentration | -1.0878
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.065965 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8737 | 0 | -0.071992 | 0 | 0 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.065405 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.7161 | 0 | -0.071432 | 0 | 0 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.061098 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3318 | 0 | -0.067125 | 0 | 0 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.059789 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.1747 | 0 | -0.065816 | 0 | 0 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.05794 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4949 | 0 | -0.063967 | 0 | 0 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.7547 | 66 | -0.062916 | -4.1524 | 66 | 4.1524
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.9253 | 69 | -0.062916 | -4.3412 | 135 | 8.4936
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.9253 | 69 | -0.062916 | -4.3412 | 204 | 12.8348
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.8116 | 67 | -0.062916 | -4.2154 | 271 | 17.0501
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.8116 | 67 | -0.062916 | -4.2154
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.056889 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.6978 | 65 | -0.062916 | -4.0895
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.056168 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.37071 | 0 | -0.062195 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.056168 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9266 | 0 | -0.062195 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.054347 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.6411 | 0 | -0.060374 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.053933 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.1281 | 0 | -0.05996 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.053903 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.4173 | 0 | -0.05993 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.05351 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.4212 | 0 | -0.059537 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.05351 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4678 | 0 | -0.059537 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.05351 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.1074 | 0 | -0.059537 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.052721 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.0884 | 0 | -0.058748 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.052712 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6975 | 0 | -0.058739 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.052712 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.44 | 0 | -0.058739 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.052256 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.7861 | 0 | -0.058283 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.922 | 0 | -0.057279 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5096 | 0 | -0.057279 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.919 | 0 | -0.057279 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.099 | 0 | -0.057279 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3815 | 0 | -0.057279 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.051252 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1258 | 0 | -0.057279 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.050997 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7849 | 0 | -0.057024 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.050997 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5299 | 0 | -0.057024 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.050845 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6182 | 0 | -0.056872 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.3292 | 66 | -0.056469 | -3.7269
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.2787 | 65 | -0.056469 | -3.6705
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.3796 | 67 | -0.056469 | -3.7834
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.3796 | 67 | -0.056469 | -3.7834
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.050442 | west | 13 | Y | Y | Ywest | Ywest | 1 | -3.3796 | 67 | -0.056469 | -3.7834
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.050442 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056469 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.050442 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056469 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.3492 | 208.2 | -0.055735 | -11.604
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.0635 | 142.1 | -0.055735 | -7.9199
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -6.5813 | 132.4 | -0.055735 | -7.3793
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -6.7603 | 136 | -0.055735 | -7.5799
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.3071 | 147 | -0.055735 | -8.193
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.049708 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.4387 | 210 | -0.055735 | -11.7043
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.4791 | 70 | -0.055728 | -3.9009
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.4791 | 70 | -0.055728 | -3.9009
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6123 | 92.8 | -0.055728 | -5.1715
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.9761 | 80 | -0.055728 | -4.4582
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.9761 | 80 | -0.055728 | -4.4582
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.049701 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.7156 | 115 | -0.055728 | -6.4087
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.049368 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.171 | 0 | -0.055395 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.049368 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.171 | 0 | -0.055395 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.049339 | west | 8 | N | N | Nwest | Nwest | 1 | -3.4537 | 0 | -0.055366 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.049339 | west | 8 | N | N | Nwest | Nwest | 1 | -3.6215 | 0 | -0.055366 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.049339 | west | 8 | N | N | Nwest | Nwest | 1 | -3.4735 | 0 | -0.055366 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3633 | 0 | -0.055116 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.7996 | 0 | -0.055116 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.8178 | 0 | -0.055116 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.049089 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.9839 | 0 | -0.055116 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.048407 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.23235 | 0 | -0.054434 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.047523 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8018 | 0 | -0.05355 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.047523 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8018 | 0 | -0.05355 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.047327 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5495 | 0 | -0.053354 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.047327 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7862 | 0 | -0.053354 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.047327 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8931 | 0 | -0.053354 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.047289 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7831 | 0 | -0.053316 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.047282 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7826 | 0 | -0.053309 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.047254 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0881 | 0 | -0.053281 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.047254 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0881 | 0 | -0.053281 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.046572 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9858 | 0 | -0.052599 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.046224 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6979 | 0 | -0.052251 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1877 | 0 | -0.05214 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.8939 | 0 | -0.05214 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.577 | 0 | -0.05214 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.046113 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.8912 | 0 | -0.05214 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.045939 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5143 | 0 | -0.051966 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.045877 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8537 | 0 | -0.051904 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6141 | 0 | -0.047243 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2138 | 0 | -0.047243 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.2628 | 0 | -0.047243 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.041216 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1196 | 0 | -0.047243 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.040416 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.046443 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.035508 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3262 | 0 | -0.041535 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.02595 | west | 4 | Y | N | Ywest | Nwest | 1 | -16.8597 | 0 | -0.031977 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.013819 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.019846 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0060267 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0060267 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0604 | 0 | -0.0054227 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.002558 | north | 3 | N | N | Nnorth | Nnorth | 1 | 2.9596 | 0 | -0.0034687 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.002558 | north | 3 | N | N | Nnorth | Nnorth | 1 | 2.9622 | 0 | -0.0034687 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.00281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61061 | 217.3 | -0.0032167 | -0.69898
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.00281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.57605 | 205 | -0.0032167 | -0.65942
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.00281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76544 | 272.4 | -0.0032167 | -0.87622
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.47247 | 0 | -0.0029627 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.47798 | 0 | -0.0029627 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.47798 | 0 | -0.0029627 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.003064 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.1643 | 0 | -0.0029627 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.003142 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028847 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.003142 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028847 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.003156 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.15149 | 48 | -0.0028707 | -0.13779
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.003156 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.14518 | 46 | -0.0028707 | -0.13205
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.003156 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.33138 | 105 | -0.0028707 | -0.30142
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.00316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.4631 | 0 | -0.0028667 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.003161 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.10115 | 0 | -0.0028657 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028637 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028637 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.003163 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.053771 | 17 | -0.0028637 | -0.048682
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028637 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.003163 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0028637 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.003244 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0027827 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.003244 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.553 | 787 | -0.0027827 | -2.19
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.003337 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.85093 | 255 | -0.0026897 | -0.68587
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.003337 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.49721 | 149 | -0.0026897 | -0.40076
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.003337 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.51056 | 153 | -0.0026897 | -0.41152
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.003414 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.5121 | 150 | -0.0026127 | -0.3919
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.003414 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.27312 | 80 | -0.0026127 | -0.20901
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9703 | 0 | -0.0025527 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9703 | 0 | -0.0025527 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.52909 | 0 | -0.0025527 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.003474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.53152 | 0 | -0.0025527 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.0036 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9772 | 0 | -0.0024267 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.0036 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9484 | 0 | -0.0024267 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.003711 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0023157 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.003848 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.05772 | 0 | -0.0021787 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.003848 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.05772 | 0 | -0.0021787 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.003932 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4182 | 0 | -0.0020947 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.003932 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.3081 | 0 | -0.0020947 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.00399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60129 | 150.7 | -0.0020367 | -0.30693
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.00399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60249 | 151 | -0.0020367 | -0.30754
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.00399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.70783 | 177.4 | -0.0020367 | -0.36131
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.004005 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60676 | 151.5 | -0.0020217 | -0.30628
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.004005 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60996 | 152.3 | -0.0020217 | -0.3079
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.004005 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.71089 | 177.5 | -0.0020217 | -0.35885
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.91616 | 224 | -0.0019367 | -0.43381
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.92434 | 226 | -0.0019367 | -0.43769
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.86708 | 212 | -0.0019367 | -0.41057
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.00409 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.86299 | 211 | -0.0019367 | -0.40864
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.004225 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7098 | 168 | -0.0018017 | -0.30268
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.004225 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.38025 | 90 | -0.0018017 | -0.16215
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.004233 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.94819 | 224 | -0.0017937 | -0.40178
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.004234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.91624 | 216.4 | -0.0017927 | -0.38793
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.004234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.91497 | 216.1 | -0.0017927 | -0.3874
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.004298 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.84241 | 196 | -0.0017287 | -0.33882
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.004298 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.47708 | 111 | -0.0017287 | -0.19188
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.004303 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.78315 | 182 | -0.0017237 | -0.31371
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.004303 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0827 | 484 | -0.0017237 | -0.83426
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.004307 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.21535 | 0 | -0.0017197 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.004311 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0017157 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.64247 | 0 | -0.0016857 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.56433 | 0 | -0.0016857 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.62945 | 0 | -0.0016857 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.004341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7321 | 0 | -0.0016857 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.004376 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4352 | 0 | -0.0016507 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.004376 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4789 | 0 | -0.0016507 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.004376 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4133 | 0 | -0.0016507 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.004551 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.53702 | 118 | -0.0014757 | -0.17413
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.004551 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.52336 | 115 | -0.0014757 | -0.1697
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.004551 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.5304 | 556 | -0.0014757 | -0.82047
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.31969 | 70 | -0.0014597 | -0.10218
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.31512 | 69 | -0.0014597 | -0.10072
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.31512 | 69 | -0.0014597 | -0.10072
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.004567 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.31056 | 68 | -0.0014597 | -0.099258
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004626 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0014007 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004626 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0014007 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74623 | 161 | -0.0013917 | -0.22406
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76014 | 164 | -0.0013917 | -0.22823
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76014 | 164 | -0.0013917 | -0.22823
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9189 | 414 | -0.0013917 | -0.57615
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75087 | 162 | -0.0013917 | -0.22545
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74623 | 161 | -0.0013917 | -0.22406
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7555 | 163 | -0.0013917 | -0.22684
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.004635 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8957 | 409 | -0.0013917 | -0.56919
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.004654 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.8058 | 388 | -0.0013727 | -0.5326
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.004654 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.3968 | 515 | -0.0013727 | -0.70693
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.004738 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.18952 | 40 | -0.0012887 | -0.051547
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.004739 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.09478 | 20 | -0.0012877 | -0.025753
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.004739 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.11847 | 25 | -0.0012877 | -0.032192
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.004739 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1943 | 41 | -0.0012877 | -0.052795
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.004756 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.37572 | 79 | -0.0012707 | -0.10038
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.004756 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.50414 | 106 | -0.0012707 | -0.13469
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.004756 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.69438 | 146 | -0.0012707 | -0.18552
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.004756 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36146 | 76 | -0.0012707 | -0.096571
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.004757 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.879 | 395 | -0.0012697 | -0.50152
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.004757 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0693 | 435 | -0.0012697 | -0.55231
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.004766 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0732 | 435 | -0.0012607 | -0.54839
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.004833 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6968 | 0 | -0.0011937 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.004833 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.7983 | 0 | -0.0011937 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.004833 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.9051 | 0 | -0.0011937 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.004876 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.3657 | 0 | -0.0011507 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.004876 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.38813 | 0 | -0.0011507 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.004876 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.43104 | 0 | -0.0011507 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.78032 | 160 | -0.0011497 | -0.18395
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76081 | 156 | -0.0011497 | -0.17935
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.95589 | 196 | -0.0011497 | -0.22534
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76081 | 156 | -0.0011497 | -0.17935
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76569 | 157 | -0.0011497 | -0.1805
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.004877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.96565 | 198 | -0.0011497 | -0.22764
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.004896 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.8115 | 370 | -0.0011307 | -0.41835
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.68544 | 0 | -0.0011307 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.69034 | 0 | -0.0011307 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5129 | 0 | -0.0011307 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.70013 | 0 | -0.0011307 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.70502 | 0 | -0.0011307 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.004896 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5178 | 0 | -0.0011307 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.004918 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0011087 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.005003 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.85051 | 170 | -0.0010237 | -0.17402
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.005003 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.6016 | 520 | -0.0010237 | -0.53231
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.005061 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00096567 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.005076 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20304 | 0 | -0.00095067 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.005076 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20304 | 0 | -0.00095067 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.005768 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.34608 | 60 | -0.00025867 | -0.01552
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.005768 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.36338 | 63 | -0.00025867 | -0.016296
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.005866 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.35196 | 0 | -0.00016067 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.006061 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 3.4328e-05 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.006061 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 3.4328e-05 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.006061 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 3.4328e-05 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.006714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3697 | 204 | 0.00068733 | 0.14021
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.006714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3495 | 201 | 0.00068733 | 0.13815
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.006714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.6248 | 242 | 0.00068733 | 0.16633
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.007983 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.89809 | 0 | 0.0019563 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.01006 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8973 | 288 | 0.0040333 | 1.1616
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.01006 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4788 | 147 | 0.0040333 | 0.5929
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.01006 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4788 | 147 | 0.0040333 | 0.5929
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.010343 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.7855 | 366 | 0.0043163 | 1.5798
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.24394 | 20 | 0.0061703 | 0.12341
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.24394 | 20 | 0.0061703 | 0.12341
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.24394 | 20 | 0.0061703 | 0.12341
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.012197 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.20735 | 17 | 0.0061703 | 0.1049
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.012427 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.90717 | 73 | 0.0064003 | 0.46722
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.012427 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.4788 | 119 | 0.0064003 | 0.76164
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.012427 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.5475 | 205 | 0.0064003 | 1.3121
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.012427 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.2676 | 102 | 0.0064003 | 0.65283
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.012427 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.193 | 96 | 0.0064003 | 0.61443
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.012641 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.22754 | 18 | 0.0066143 | 0.11906
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.012641 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.22754 | 18 | 0.0066143 | 0.11906
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.012641 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.48036 | 38 | 0.0066143 | 0.25134
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.02288 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.27456 | 0 | 0.016853 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.02288 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.27456 | 0 | 0.016853 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.039372 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.7246 | 0 | 0.033345 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.012989 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.42864 | 0 | 0.038824 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.012989 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32472 | 0 | 0.038824 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.012989 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.038824 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.009177 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.055062 | 0 | 0.042636 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.00829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.043523 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.001376 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.018851 | 0 | 0.050437 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001356 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01139 | 8.4 | 0.050457 | 0.42384
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.000993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.023832 | 24 | 0.05082 | 1.2197
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.000993 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.023832 | 24 | 0.05082 | 1.2197
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.000993 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.022839 | 23 | 0.05082 | 1.1689
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.00081 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01458 | 0 | 0.051003 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.00081 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01458 | 0 | 0.051003 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.00081 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01215 | 0 | 0.051003 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.000736 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31059 | 422 | 0.051077 | 21.5546
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000613 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.017164 | 0 | 0.0512 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000613 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.017777 | 0 | 0.0512 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.000274 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051539 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.000273 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0273 | 100 | 0.05154 | 5.154
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.000273 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0273 | 100 | 0.05154 | 5.154
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.05154 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.05154 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.05154 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000273 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.05154 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.000251 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004518 | 0 | 0.051562 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.000251 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004518 | 0 | 0.051562 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051813 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051813 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051813 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.000136 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051949 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000493 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.005916 | 0 | 0.052306 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000493 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.005423 | 0 | 0.052306 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000493 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.005916 | 0 | 0.052306 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.068856 | 0 | 0.052417 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13409 | 0 | 0.052417 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11114 | 0 | 0.052417 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1353 | 0 | 0.052417 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000604 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.06946 | 0 | 0.052417 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000664 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.038512 | 58 | 0.052477 | 3.0437
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000664 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.059096 | 89 | 0.052477 | 4.6705
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029216 | 44 | 0.052477 | 2.309
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029216 | 44 | 0.052477 | 2.309
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.028552 | 43 | 0.052477 | 2.2565
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02988 | 45 | 0.052477 | 2.3615
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.000749 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.30484 | 407 | 0.052562 | 21.3928
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.000764 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.30254 | 0 | 0.052577 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.000778 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.1626 | 209 | 0.052591 | 10.9916
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.000778 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.16805 | 216 | 0.052591 | 11.3597
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035788 | 46 | 0.052591 | 2.4192
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.036566 | 47 | 0.052591 | 2.4718
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035788 | 46 | 0.052591 | 2.4192
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.000778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035788 | 46 | 0.052591 | 2.4192
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.000779 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.32095 | 412 | 0.052592 | 21.668
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.000779 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.3116 | 400 | 0.052592 | 21.0369
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.000788 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.052601 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.000794 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.33666 | 0 | 0.052607 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.000794 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.33745 | 0 | 0.052607 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.000823 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.052636 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.029715 | 0 | 0.052662 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.028866 | 0 | 0.052662 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.029715 | 0 | 0.052662 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.000857 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.05267 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.000857 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.05267 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.000857 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.05267 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.000866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12687 | 146.5 | 0.052679 | 7.7175
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.000866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12808 | 147.9 | 0.052679 | 7.7913
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.000866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14982 | 173 | 0.052679 | 9.1135
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000875 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13562 | 155 | 0.052688 | 8.1667
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.000875 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14875 | 170 | 0.052688 | 8.957
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000875 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13562 | 155 | 0.052688 | 8.1667
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.000903 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.49304 | 0 | 0.052716 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.000903 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.67725 | 0 | 0.052716 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13363 | 144 | 0.052741 | 7.5947
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13363 | 144 | 0.052741 | 7.5947
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15869 | 171 | 0.052741 | 9.0188
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1921 | 207 | 0.052741 | 10.9174
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2011 | 216.7 | 0.052741 | 11.429
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.000928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22458 | 242 | 0.052741 | 12.7634
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.000965 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.03667 | 38 | 0.052778 | 2.0056
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.000965 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.018624 | 19.3 | 0.052778 | 1.0186
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.000965 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.014475 | 15 | 0.052778 | 0.79167
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.000965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.045355 | 47 | 0.052778 | 2.4806
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.000965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.052778 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09212 | 0 | 0.052793 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04018 | 0 | 0.052793 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.03724 | 0 | 0.052793 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01862 | 0 | 0.052793 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09212 | 0 | 0.052793 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.03528 | 0 | 0.052793 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04214 | 0 | 0.052793 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02156 | 0 | 0.052793 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.14504 | 0 | 0.052793 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.049 | 0 | 0.052793 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0539 | 0 | 0.052793 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.00098 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.049 | 0 | 0.052793 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.000998 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.028942 | 0 | 0.052811 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.001011 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.004044 | 0 | 0.052824 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.001017 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.038646 | 0 | 0.05283 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.001021 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.025525 | 0 | 0.052834 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.001021 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.025525 | 0 | 0.052834 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.001021 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.038798 | 0 | 0.052834 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.001026 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34268 | 334 | 0.052839 | 17.6483
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.001026 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34884 | 340 | 0.052839 | 17.9653
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.001026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18468 | 180 | 0.052839 | 9.5111
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.001026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18468 | 180 | 0.052839 | 9.5111
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.001027 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.006162 | 0 | 0.05284 | 0
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.001032 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.15305 | 0 | 0.052845 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.001032 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.15336 | 0 | 0.052845 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.001032 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1579 | 0 | 0.052845 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.001032 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18576 | 180 | 0.052845 | 9.5121
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.001033 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.34709 | 336 | 0.052846 | 17.7563
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.001033 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18594 | 180 | 0.052846 | 9.5123
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.001037 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.65227 | 0 | 0.05285 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15288 | 147 | 0.052853 | 7.7694
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14352 | 138 | 0.052853 | 7.2938
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1456 | 140 | 0.052853 | 7.3995
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15288 | 147 | 0.052853 | 7.7694
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18928 | 182 | 0.052853 | 9.6193
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.00104 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.20592 | 198 | 0.052853 | 10.4649
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 0 | 0.052867 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 0 | 0.052867 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 0 | 0.052867 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.016864 | 0 | 0.052867 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 0 | 0.052867 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 0 | 0.052867 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02635 | 0 | 0.052867 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.001054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01581 | 0 | 0.052867 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1689 | 0 | 0.052882 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.16356 | 0 | 0.052882 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1069 | 0 | 0.052882 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.15501 | 0 | 0.052882 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.15714 | 0 | 0.052882 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.001069 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.13576 | 0 | 0.052882 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.001069 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.012828 | 0 | 0.052882 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.001089 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0026136 | 0 | 0.052902 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.001089 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0026136 | 0 | 0.052902 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.001089 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0030492 | 0 | 0.052902 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15478 | 142 | 0.052903 | 7.5123
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15805 | 145 | 0.052903 | 7.671
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.16459 | 151 | 0.052903 | 7.9884
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.00109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.3161 | 290 | 0.052903 | 15.3419
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25525 | 223.9 | 0.052953 | 11.8562
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2565 | 225 | 0.052953 | 11.9145
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25604 | 224.6 | 0.052953 | 11.8933
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.00114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25844 | 226.7 | 0.052953 | 12.0045
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.001145 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.02519 | 22 | 0.052958 | 1.1651
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.001145 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012595 | 11 | 0.052958 | 0.58254
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.001145 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012595 | 11 | 0.052958 | 0.58254
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.001168 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.014016 | 0 | 0.052981 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.001169 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0028056 | 0 | 0.052982 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.001169 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0028056 | 0 | 0.052982 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.056286 | 47.7 | 0.052993 | 2.5278
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.044014 | 37.3 | 0.052993 | 1.9766
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.05428 | 46 | 0.052993 | 2.4377
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.00118 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.05664 | 48 | 0.052993 | 2.5437
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.001195 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17208 | 144 | 0.053008 | 7.6332
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.001195 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22466 | 188 | 0.053008 | 9.9656
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.001214 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.088622 | 0 | 0.053027 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.001238 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01857 | 0 | 0.053051 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.001238 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.028474 | 0 | 0.053051 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.001243 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.009944 | 0 | 0.053056 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.035168 | 0 | 0.053069 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.008792 | 0 | 0.053069 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.048984 | 0 | 0.053069 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01884 | 0 | 0.053069 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.008792 | 0 | 0.053069 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01884 | 0 | 0.053069 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.048984 | 0 | 0.053069 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.001256 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.048984 | 0 | 0.053069 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.001323 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.063504 | 0 | 0.053136 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10594 | 0 | 0.053154 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10862 | 0 | 0.053154 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10594 | 0 | 0.053154 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10728 | 0 | 0.053154 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10513 | 0 | 0.053154 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.033525 | 0 | 0.053154 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.061686 | 0 | 0.053154 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.037548 | 0 | 0.053154 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.058468 | 0 | 0.053154 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.001341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.099234 | 0 | 0.053154 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.001343 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010744 | 0 | 0.053156 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.001343 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010744 | 0 | 0.053156 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.067424 | 49 | 0.053189 | 2.6063
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.063296 | 46 | 0.053189 | 2.4467
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.063296 | 46 | 0.053189 | 2.4467
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.064672 | 47 | 0.053189 | 2.4999
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.001376 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2119 | 154 | 0.053189 | 8.1911
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.001376 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.20365 | 148 | 0.053189 | 7.872
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.066048 | 48 | 0.053189 | 2.5531
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.001376 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.066048 | 48 | 0.053189 | 2.5531
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.001389 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.43059 | 310 | 0.053202 | 16.4927
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.001389 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.57366 | 413 | 0.053202 | 21.9725
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.060018 | 42 | 0.053242 | 2.2362
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.062876 | 44 | 0.053242 | 2.3427
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.062876 | 44 | 0.053242 | 2.3427
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.001429 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.067163 | 47 | 0.053242 | 2.5024
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.001519 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.20051 | 132 | 0.053332 | 7.0399
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.001519 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.20355 | 134 | 0.053332 | 7.1465
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.001519 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.49064 | 323 | 0.053332 | 17.2263
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.001524 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.23241 | 152.5 | 0.053337 | 8.1339
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.001524 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22784 | 149.5 | 0.053337 | 7.9739
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.001524 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.35448 | 232.6 | 0.053337 | 12.4062
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0789 | 50 | 0.053391 | 2.6696
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0789 | 50 | 0.053391 | 2.6696
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0789 | 50 | 0.053391 | 2.6696
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.001578 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0789 | 50 | 0.053391 | 2.6696
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.001616 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25533 | 158 | 0.053429 | 8.4418
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.001616 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25856 | 160 | 0.053429 | 8.5487
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.001616 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2828 | 175 | 0.053429 | 9.3501
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.001617 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.70016 | 0 | 0.05343 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.001618 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.94491 | 0 | 0.053431 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.001618 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.96271 | 0 | 0.053431 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.001949 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 2.598 | 0 | 0.053762 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.001949 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 2.5883 | 0 | 0.053762 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.15033 | 76 | 0.053791 | 4.0881
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.15033 | 76 | 0.053791 | 4.0881
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20769 | 105 | 0.053791 | 5.6481
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14637 | 74 | 0.053791 | 3.9806
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14637 | 74 | 0.053791 | 3.9806
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.001978 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20176 | 102 | 0.053791 | 5.4867
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.002 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.132 | 66 | 0.053813 | 3.5517
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.002067 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1761 | 0 | 0.05388 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.002067 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2009 | 0 | 0.05388 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13342 | 0 | 0.053965 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15365 | 0 | 0.053965 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09684 | 0 | 0.053965 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21735 | 0 | 0.053965 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18507 | 0 | 0.053965 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18938 | 0 | 0.053965 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1076 | 0 | 0.053965 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.038736 | 0 | 0.053965 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20229 | 0 | 0.053965 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15064 | 0 | 0.053965 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13558 | 0 | 0.053965 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15494 | 0 | 0.053965 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13945 | 0 | 0.053965 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21735 | 0 | 0.053965 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20874 | 0 | 0.053965 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22166 | 0 | 0.053965 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16355 | 0 | 0.053965 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17216 | 0 | 0.053965 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17216 | 0 | 0.053965 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.002152 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36799 | 0 | 0.053965 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.002189 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15542 | 0 | 0.054002 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.002189 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02189 | 0 | 0.054002 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24642 | 0 | 0.054033 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24642 | 0 | 0.054033 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.26418 | 0 | 0.054033 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24309 | 0 | 0.054033 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.002319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10691 | 0 | 0.054132 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.002329 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 1.5162 | 0 | 0.054142 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.002329 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 1.3136 | 0 | 0.054142 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.002329 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 1.3974 | 0 | 0.054142 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.00233 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37979 | 0 | 0.054143 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.00233 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37979 | 0 | 0.054143 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.00233 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.57085 | 0 | 0.054143 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.002334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.077022 | 0 | 0.054147 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.002349 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.37819 | 161 | 0.054162 | 8.7201
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.002349 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.38993 | 166 | 0.054162 | 8.9909
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.002349 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.58255 | 248 | 0.054162 | 13.4322
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.002349 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 1.2826 | 546 | 0.054162 | 29.5726
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.002349 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 1.5104 | 0 | 0.054162 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.002349 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.030537 | 13 | 0.054162 | 0.70411
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16928 | 0 | 0.054204 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15948 | 0 | 0.054204 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.12672 | 0 | 0.054204 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.3663 | 0 | 0.054204 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.36702 | 0 | 0.054204 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.36415 | 0 | 0.054204 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.22954 | 0 | 0.054204 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5834 | 0 | 0.054204 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09564 | 0 | 0.054204 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.076512 | 0 | 0.054204 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.002391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.07173 | 0 | 0.054204 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.23982 | 0 | 0.054204 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.22212 | 0 | 0.054204 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24556 | 0 | 0.054204 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.002391 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24388 | 0 | 0.054204 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.002415 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.12075 | 50 | 0.054228 | 2.7114
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.002428 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054241 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22268 | 0 | 0.05426 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21436 | 0 | 0.05426 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21289 | 0 | 0.05426 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13336 | 0 | 0.05426 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.002447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.029853 | 0 | 0.05426 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.15951 | 0 | 0.054267 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.14724 | 0 | 0.054267 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.15951 | 0 | 0.054267 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.002454 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.15951 | 0 | 0.054267 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11348 | 46 | 0.05428 | 2.4969
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11348 | 46 | 0.05428 | 2.4969
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11348 | 46 | 0.05428 | 2.4969
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13569 | 55 | 0.05428 | 2.9854
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13569 | 55 | 0.05428 | 2.9854
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.002467 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13322 | 54 | 0.05428 | 2.9311
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.002468 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.1925 | 0 | 0.054281 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.002468 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.19744 | 0 | 0.054281 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.40327 | 0 | 0.054284 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38819 | 0 | 0.054284 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38918 | 0 | 0.054284 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38795 | 0 | 0.054284 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.002471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.6647 | 0 | 0.054284 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.002475 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.086625 | 0 | 0.054288 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.002478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.029736 | 12 | 0.054291 | 0.6515
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.002478 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054291 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.002479 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36937 | 0 | 0.054292 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.002479 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16138 | 0 | 0.054292 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.002479 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.40903 | 165 | 0.054292 | 8.9582
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.002479 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.41895 | 169 | 0.054292 | 9.1754
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.00248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.4464 | 0 | 0.054293 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.00248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39333 | 0 | 0.054293 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.00248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38936 | 0 | 0.054293 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.00248 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.56544 | 228 | 0.054293 | 12.3789
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15872 | 0 | 0.054293 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15674 | 0 | 0.054293 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20485 | 0 | 0.054293 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18253 | 0 | 0.054293 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.00248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.040176 | 0 | 0.054293 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.00248 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.52824 | 213 | 0.054293 | 11.5645
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17644 | 0 | 0.054298 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17892 | 0 | 0.054298 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.096915 | 0 | 0.054298 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.002485 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.07455 | 0 | 0.054298 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10471 | 42 | 0.054306 | 2.2809
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10471 | 42 | 0.054306 | 2.2809
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.094734 | 38 | 0.054306 | 2.0636
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.002493 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.094734 | 38 | 0.054306 | 2.0636
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.002493 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.33905 | 0 | 0.054306 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.002495 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43163 | 0 | 0.054308 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.002495 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.33682 | 0 | 0.054308 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.26083 | 104 | 0.054321 | 5.6494
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.26083 | 104 | 0.054321 | 5.6494
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13543 | 54 | 0.054321 | 2.9333
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13292 | 53 | 0.054321 | 2.879
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13543 | 54 | 0.054321 | 2.9333
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14296 | 57 | 0.054321 | 3.0963
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13543 | 54 | 0.054321 | 2.9333
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.13543 | 54 | 0.054321 | 2.9333
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14546 | 58 | 0.054321 | 3.1506
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.002508 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.14546 | 58 | 0.054321 | 3.1506
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.00251 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 1.8449 | 735 | 0.054323 | 39.9276
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.085476 | 0 | 0.054327 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.087236 | 0 | 0.054327 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.082208 | 0 | 0.054327 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11539 | 0 | 0.054327 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.044498 | 0 | 0.054327 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.051286 | 0 | 0.054327 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.050029 | 0 | 0.054327 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.08799 | 0 | 0.054327 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.045252 | 0 | 0.054327 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2147 | 0 | 0.054327 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.002514 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37207 | 0 | 0.054327 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.002519 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.030228 | 12 | 0.054332 | 0.65199
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.002522 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01261 | 0 | 0.054335 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.002522 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.052962 | 0 | 0.054335 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.002523 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 1.8746 | 743 | 0.054336 | 40.3718
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.002523 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.030276 | 0 | 0.054336 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.164 | 0 | 0.054336 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16652 | 0 | 0.054336 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17661 | 0 | 0.054336 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15895 | 0 | 0.054336 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15643 | 0 | 0.054336 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.26239 | 0 | 0.054336 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.002523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14886 | 0 | 0.054336 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.002526 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.43447 | 172 | 0.054339 | 9.3464
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.002526 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.43447 | 172 | 0.054339 | 9.3464
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.002526 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.43447 | 172 | 0.054339 | 9.3464
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.002526 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39658 | 0 | 0.054339 | 0
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4127 | 0 | 0.054348 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40915 | 0 | 0.054348 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40281 | 0 | 0.054348 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68242 | 0 | 0.054348 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.002539 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.0105 | 398 | 0.054352 | 21.6322
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14252 | 56 | 0.054358 | 3.0441
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15016 | 59 | 0.054358 | 3.2071
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14252 | 56 | 0.054358 | 3.0441
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14252 | 56 | 0.054358 | 3.0441
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15016 | 59 | 0.054358 | 3.2071
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.002545 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14252 | 56 | 0.054358 | 3.0441
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.44893 | 0 | 0.054408 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.40482 | 0 | 0.054408 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39963 | 0 | 0.054408 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.002595 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39963 | 0 | 0.054408 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.002595 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42039 | 0 | 0.054408 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.069487 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.8159 | 242 | 0.06346 | 15.3574

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating