## test results
CRE test for: |  | TONKAWA_ - GRHAMSES 345kV [1048 - 1430] | [5 empty] | FAIL
Line Rating: |  | 1100
Direcction |  | west | → | North |  | w-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | TONKAWA_ - GRHAMSES 345kV [1048 - 1430]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.017868
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.004884
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.24712
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.010172
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | TONKAWA_ - GRHAMSES 345kV [1048 - 1430]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.018718
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.0045735
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.30811
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.010261
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | TONKAWA_ - GRHAMSES 345kV [1048 - 1430]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.013295
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.32598
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.0076076
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.313
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.0052877
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.25738
PTDF tests
west | → | North | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | 0.26584 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.26584 | -0.013295
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.38237
[6 empty] | Concentration |  | 1.4384 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.13849
[6 empty] | Concentration |  | 0.52096 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 520.8645
| Percent of line rating => | [6 empty] | 47.35% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 3.0573
[7 empty] | B1(N-S) | 0.00051843 | -0.040127 | -0.040645 | 0.00051843
[7 empty] | B2 (N-W) | 0.18185 | -0.81477 | -0.99661 | 0.18185
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.004284 | -0.018975 | -0.023259 | 0.004284
[7 empty] | B4 (S-W) | 0.18115 | -0.77577 | -0.95692 | 0.18115
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.0038582 | 0.020024 | 0.016166 | 0.0038582
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.0060609 | 0.79294 | 0.78688 | 0.0060609
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | 0.06379%
Deployment Error Percent | [6 empty] | B2 | 22.37%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0.5271%
[7 empty] | B4 | 22.29%
[7 empty] | B5 | 0.4747%
[7 empty] | B6 | 0.7457%
[7 empty] | Max Abs Error | 22.37% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.012686 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -3.2349
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.012686 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -1.8902
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.012731 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.19096
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.012731 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.19096
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.012686 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -1.941
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.012318 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -1.8477
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.012318 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -0.98544
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.012486 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -0.91148
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.012486 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -1.4858
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.012486 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -2.5596
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.012486 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -1.2736
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.012486 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -1.1987
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.015622 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.18746
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.015622 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.18746
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.014225 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -2.3898
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.014225 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -1.2803
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.017185 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.30933
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.017185 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.30933
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.017185 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.65303
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.019861 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -5.72
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.019861 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -2.9196
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.019861 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -2.9196
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.021427 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -2.4105
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.019206 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.76824
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.019274 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -1.5226
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.019274 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -2.043
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.019274 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -2.814
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.019274 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -1.4648
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.022404 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -1.3442
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.022404 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -1.4115
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.019209 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.38418
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.019209 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.48023
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.019209 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.78757
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.013091 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -6.0611
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 20.7074
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 20.3937
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 21.0212
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 21.0212
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 21.0212
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.31375 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 35.7674
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.31375 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 161.5807
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 20.4388
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 21.3679
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 21.3679
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 20.7485
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 20.7485
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 20.1291
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.33109 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 23.1761
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.33109 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 24.3018
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.33109 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 23.3085
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 49.9918
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 73.3214
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.27846 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 27.567
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.27846 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 16.9858
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.27926 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 39.3757
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.27846 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 6.9614
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.27846 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 12.7254
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.27846 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 12.7254
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.27926 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 33.5112
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.29304 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 7.5605
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.31085 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 31.2407
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.29876 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 35.8512
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.31015 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 17.9886
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.31008 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 66.4196
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.17126 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 25.6892
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.2752 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 1.8163
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.2752 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 9.4394
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.17126 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 17.2974
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.29628 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 35.553
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.050862 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -18.6155
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.023504 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -5.688
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.001756 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -0.7024
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.001925 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -0.4543
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.013669 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -2.2554
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.032845 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -6.7004
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.032845 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -6.6018
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.032845 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -7.9485
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.5652
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.5652
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.5652
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.48042
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.019361 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -2.3233
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.002903 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 0.17418
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.019596 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -1.4697
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.019596 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -1.5598
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.019596 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -1.7323
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -3.1411
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.0626
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -3.8479
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.0626
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -3.0822
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -3.8871
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.019814 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -3.3684
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.019814 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -10.3033
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019687 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -7.2842
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.019532 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -10.8989
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.019532 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -11.309
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.019532 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -15.7819
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.022061 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -2.4708
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.022061 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -2.2061
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.022061 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -8.3391
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.013189 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -2.866
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.013189 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -2.7037
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.013189 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -3.5927
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.015925 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -12.2622
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -0.98343
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.96938
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.96938
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -0.95533
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.012357 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -14.297
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.012357 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -14.3094
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -3.784
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -3.8178
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.017507 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -3.7885
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.017507 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -3.7833
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -3.5813
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -3.5644
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.019295 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -7.6215
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.019277 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -8.3855
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.019295 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -8.3933
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.020288 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -2.7997
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.018544 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -2.1882
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.018544 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -2.1326
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.018544 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -10.3105
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.018905 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -7.3351
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.018905 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -9.7361
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.017835 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -14.0005
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.017835 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -14.1788
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.017835 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -13.9113
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.017549 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -3.1939
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.017549 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -8.4937
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.017073 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -3.8244
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.017572 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -0.8786
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.017585 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.73857
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.016145 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -9.9292
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.016145 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -9.4771
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.013167 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -7.0707
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.013167 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -10.3624
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.012708 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -0.9531
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.012708 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -2.8212
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.008868 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -5.0459
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003756 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -0.785
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003756 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -0.8113
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.003641 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -1.4819
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.17278
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -0.17653
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.17278
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.17278
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.003833 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -1.6252
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.003833 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -1.629
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003265 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -0.18937
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003265 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -0.29058
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.14366
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.14366
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.14039
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -0.14693
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.003763 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -1.5504
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.003763 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -1.5052
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.004285 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -2.3396
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.004285 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -3.2138
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.004096 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -0.24986
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.004096 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -0.38912
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.004096 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -0.6185
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.004186 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.64883
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.004186 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -0.71162
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.004186 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.64883
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.005104 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.11229
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.005104 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.056144
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.005104 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.056144
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.25105
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.19631
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.2421
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.25262
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.00229 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.02748
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.00229 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.02519
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.004199 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.10078
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.004199 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.10078
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.004199 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.096577
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.003576 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -1.4161
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.008368 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -11.1545
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.008368 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -11.1127
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.004359 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.16564
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.004359 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.084129
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.004359 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.065385
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.004359 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.20487
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.27709 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 20.782
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.18785 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 28.1774
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.090905 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 15.4084
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.13254 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 19.8808
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.28323 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 17.8437
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.002066 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -1.3423
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.019914 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.79656
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.019914 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.79656
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.000486 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 0.20509
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.006862 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -0.90578
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.006862 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -0.91951
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.006862 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -2.2164
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.007171 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -1.133
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.007171 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -1.1474
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.007171 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -1.2549
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.007175 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -4.1902
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.007175 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -4.2691
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.007174 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -3.1063
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -1.1867
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -1.1925
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -1.1904
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -1.2015
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.006286 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.050288
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.006286 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.050288
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.000391 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.007038
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.000391 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.007038
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.000391 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.005865
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.002484 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.034031
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.001098 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.019764
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.001098 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.019764
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.004689 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.16412
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.004689 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.15943
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.004689 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.16412
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 4.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.001344
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 4.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.001392
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.31277 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 10.9469
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.31277 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 9.3831
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.3523
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.3523
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.3523
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.3523
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.004979 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.029874
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.005087 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.012209
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.005087 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.012209
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.005087 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.014244
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.004762 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.019048
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.005375 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.0129
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.005375 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.0129
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.71295
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -0.6693
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -0.679
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.71295
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -0.8827
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -0.9603
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.006834 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -1.0422
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.006834 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -1.0217
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.006834 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -1.5896
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -0.72065
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -0.73587
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -0.76633
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -1.4717
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.057571 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 1.8998
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.057571 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 1.4393
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.00229 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.02748
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.00541 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -0.39493
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.4676
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -0.47944
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.1561
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.039025
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.4676
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -0.47352
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -0.46405
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.14797
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.27227
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.004698 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -2.955
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.005338 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -0.76867
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.005338 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -1.0035
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.005314 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.063768
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.040613 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.24368
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.004646 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -1.5611
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.004617 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -1.5421
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.004617 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -1.5698
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.004578 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.17396
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.004598 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.11495
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.004598 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.11495
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.004597 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.17469
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.0045 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.1305
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.004645 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -0.68885
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.004645 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -0.69025
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.004645 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -0.71069
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -0.75793
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -0.73394
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -0.4797
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -0.69556
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -0.70516
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -0.60922
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.003924 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -0.57487
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.003924 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -0.58036
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.003924 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -0.67885
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.004196 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -0.86857
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.004196 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -0.90927
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.004196 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -1.0154
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.004197 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.60437
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.004197 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.60437
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.004197 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -0.71769
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.006441 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -1.9967
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.006441 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -2.6601
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.27657
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.28974
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.28974
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.3095
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.31277
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.29362
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.29362
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.3
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006383 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.98298
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006383 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.94468
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.30638
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.30638
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 22.6768
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 22.6768
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 30.0629
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 25.9163
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 25.9163
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 37.2547
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 67.4258
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 46.0192
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 42.8779
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 44.0437
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 47.6061
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 68.0087
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 86.8512
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 52.5678
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 103.4734
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 81.8645
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 66.6558
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 40.6267
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.31102 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 46.3414
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.2905 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 52.2891
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.2905 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 52.2891
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.29129 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 65.5405
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 41.9733
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 41.9733
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -2.7562
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -2.7759
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -6.0833
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -2.8152
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -2.8349
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -6.103
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.017255 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -3.382
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.017255 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -1.9153
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.01989 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.031
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.0875
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.0875
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -7.794
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -3.0498
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.031
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -3.0686
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -7.6998
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.018811 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.018811 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -2.6196
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -2.301
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -2.5665
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -7.0623
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.016374 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -2.4676
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.016374 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -2.4725
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.016374 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -2.9047
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.016423 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -2.4881
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.016423 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -2.5012
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.016423 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -2.9151
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.008868 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -5.1523
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -12.2402
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -12.2402
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.013091 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.41891
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.013072 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.62746
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.013072 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.60131
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.15719
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.66805
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013099 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.22268
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.28818
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.32748
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.013072 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -1.3726
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.26163 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 21.9772
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.27661 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 22.1289
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.27627 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 41.4408
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.27627 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 41.4408
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.71473
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.67334
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.53504
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -1.5466
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -1.5496
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -1.5375
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.96912
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -2.4632
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.4038
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -1.0124
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.93773
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -1.0367
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -1.0296
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.010094 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.32301
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.010094 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.30282
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.0462
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.0462
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -1.1216
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -1.032
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -2.1803
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -2.1903
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.010493 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -1.427
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.009872 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.32578
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.44062
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.44062
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.39866
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.39866
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.009304 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.66058
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.009304 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.09304
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.009858 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.6069
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.009858 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.6069
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.009858 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -2.4152
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.67223
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.62052
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.67223
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.67223
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.010439 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -1.5554
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.010439 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.67958
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.93857
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.90351
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.89732
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.56211
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.12583
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.01061 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -7.8832
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.010562 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -7.7631
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.010624 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.8273
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.010624 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.8273
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.010624 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.8273
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -1.8841
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.010502 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -1.8168
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.010502 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -1.4178
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -1.7351
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -1.7202
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -1.6936
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -2.8691
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.66829
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.65993
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.86251
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.76853
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -1.6986
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -1.6351
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -1.6393
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -1.6341
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -2.7998
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.010608 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.05304
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.010608 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.22277
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -1.9608
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.9837
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.9837
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -4.8321
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.010673 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -4.2479
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.47812
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.47812
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.47812
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.57167
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.57167
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.56128
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.014808 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -12.2462
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.014808 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -12.1278
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.009814 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.45243
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.64418
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.64418
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.88998
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.62722
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.62722
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.86455
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.010443 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -1.8797
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.010443 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -1.6563
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.010443 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -1.6396
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.010424 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.36484
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.010239 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -4.6997
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.68965
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.70026
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.7427
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.66843
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.65782
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -1.1034
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.62599
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -1.699
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -1.6772
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -1.6772
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.010891 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -1.7643
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.010621 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -1.6675
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.74273
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.75319
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.40798
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.31383
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.010396 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.81089
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.010396 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.83168
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.16916
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.010438 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -1.7223
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.010437 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -1.7639
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.010441 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -2.2239
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.010442 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -2.3808
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.010436 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.12523
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.010436 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.18785
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.010189 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.50945
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -1.0976
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -1.0976
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.56992
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.55936
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.56992
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.60158
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.56992
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.56992
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.61213
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.61213
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.010596 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.12715
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.59892
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.63101
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.59892
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.59892
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.63101
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.59892
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.008561 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.56503
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.009931 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -1.5989
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.009931 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -1.6485
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.009931 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -2.4629
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.009931 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -5.4223
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.009931 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -6.3856
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.009855 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -6.4156
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.009855 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -5.5582
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.009855 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -5.913
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.009931 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.1291
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.010609 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.12731
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.35952
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.36692
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.34577
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.48535
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.18716
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.21571
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.21042
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.37009
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.19033
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.90302
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -1.565
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.56804
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.65417
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.41229
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.92536
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.78793
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.80626
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.4581
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.16492
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.86123
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.64134
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.57721
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.65966
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.5937
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.92536
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.88871
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.94369
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.69631
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.73296
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.73296
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -1.5667
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.048812
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.25979 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 19.8738
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.27709 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 22.1674
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.27709 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 11.0837
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.27929 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 22.3433
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.27669 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 22.135
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.26453 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 21.1623
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.26057 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 21.8876
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.27929 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 22.3433
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -0.3827
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.076813 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 9.2176
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.076813 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 17.8974
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.076813 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 13.0736
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -0.74525
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -0.61769
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -0.75197
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -0.38605
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -0.3357
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.11925 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.1553
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.045609 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.19886 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.28983 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 1.3912
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 12.592
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 36.097
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 45.3311
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 39.9585
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 35.2575
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 27.0308
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.26498 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 39.7475
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 28.2582
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 37.552
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 46.7202
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 53.879
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.004359 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.036668 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.001056 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.16573
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.25807
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -0.43801
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.41576
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.18134
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.16807
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.084037
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.41576
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.15923
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.19019
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.097306
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.21743
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.083625
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.039025
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.083625
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.21743
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.21743
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -0.6546
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.22115
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -0.24327
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.22115
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.004797 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.057564
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.005503 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.082545
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.005503 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.12657
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.005846 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.28061
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.005522 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.044176
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.004642 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -0.83556
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.004646 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -0.83628
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.004617 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.83106
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.004617 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.83106
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001053 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.1053
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001053 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.1053
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.11832
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.11832
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.11832
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.075728
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.11832
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.11832
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.11832
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.070995
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 0.5265
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 0.5265
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.003764 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.057571 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.000727 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.003589 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | [7 empty] | 520.8645
Number of Bus | Name of Bus | ID | Max MW | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.012686 | north | 0.0051822 | -0.007802 | -0.2598 | -0.0025144 | 0.0025144 | houston | Y | 0.0051822 | 0.6803
239 | BOSQUESW | 1 | 149 | -0.012686 | north | 0.0051822 | -0.007802 | -0.2598 | -0.0025144 | 0.0025144 | houston | Y | 0.0051822 | 0.39751
244 | WHITNYDM | 1 | 15 | -0.012731 | north | 0.0051372 | -0.007847 | -0.25985 | -0.0025594 | 0.0025594 | houston | Y | 0.0051372 | 0.038668
245 | WHITNYDM | 2 | 15 | -0.012731 | north | 0.0051372 | -0.007847 | -0.25985 | -0.0025594 | 0.0025594 | houston | Y | 0.0051372 | 0.038668
247 | BOSQUESW | 2 | 153 | -0.012686 | north | 0.0051822 | -0.007802 | -0.2598 | -0.0025144 | 0.0025144 | houston | Y | 0.0051822 | 0.40818
251 | BOSQUESW | 2 | 150 | -0.012318 | north | 0.0055502 | -0.007434 | -0.25944 | -0.0021464 | 0.0021464 | houston | Y | 0.0055502 | 0.51058
253 | BOSQUESW | 2 | 80 | -0.012318 | north | 0.0055502 | -0.007434 | -0.25944 | -0.0021464 | 0.0021464 | houston | Y | 0.0055502 | 0.27231
332 | RWMILLER | 1 | 73 | -0.012486 | north | 0.0053822 | -0.007602 | -0.2596 | -0.0023144 | 0.0023144 | houston | Y | 0.0053822 | 0.22395
333 | RWMILLER | 2 | 119 | -0.012486 | north | 0.0053822 | -0.007602 | -0.2596 | -0.0023144 | 0.0023144 | houston | Y | 0.0053822 | 0.36507
334 | RWMILLER | 3 | 205 | -0.012486 | north | 0.0053822 | -0.007602 | -0.2596 | -0.0023144 | 0.0023144 | houston | Y | 0.0053822 | 0.62891
335 | RWMILLER | 4 | 102 | -0.012486 | north | 0.0053822 | -0.007602 | -0.2596 | -0.0023144 | 0.0023144 | houston | Y | 0.0053822 | 0.31292
336 | RWMILLER | 5 | 96 | -0.012486 | north | 0.0053822 | -0.007602 | -0.2596 | -0.0023144 | 0.0023144 | houston | Y | 0.0053822 | 0.29451
344 | MRSSHPRD | 1 | 12 | -0.015622 | north | 0.0022462 | -0.010738 | -0.26274 | -0.0054504 | 0.0022462 | North | N | 0.0022462 | 0
345 | MRSSHPRD | 2 | 12 | -0.015622 | north | 0.0022462 | -0.010738 | -0.26274 | -0.0054504 | 0.0022462 | North | N | 0.0022462 | 0
366 | JNSNCNTY | 1 | 168 | -0.014225 | north | 0.0036432 | -0.009341 | -0.26134 | -0.0040534 | 0.0036432 | North | N | 0.0036432 | 0
367 | JNSNCNTY | 2 | 90 | -0.014225 | north | 0.0036432 | -0.009341 | -0.26134 | -0.0040534 | 0.0036432 | North | N | 0.0036432 | 0
503 | NTHTEXAS | 1 | 18 | -0.017185 | north | 0.0006832 | -0.012301 | -0.2643 | -0.0070134 | 0.0006832 | North | N | 0.0006832 | 0
504 | NTHTEXAS | 2 | 18 | -0.017185 | north | 0.0006832 | -0.012301 | -0.2643 | -0.0070134 | 0.0006832 | North | N | 0.0006832 | 0
505 | NTHTEXAS | 3 | 38 | -0.017185 | north | 0.0006832 | -0.012301 | -0.2643 | -0.0070134 | 0.0006832 | North | N | 0.0006832 | 0
580 | JCKCNTY8 | 1 | 288 | -0.019861 | north | -0.0019928 | -0.014977 | -0.26698 | -0.0096894 | 0.0019928 | North | N | 0.0019928 | 0
581 | JCKCNTY8 | 2 | 147 | -0.019861 | north | -0.0019928 | -0.014977 | -0.26698 | -0.0096894 | 0.0019928 | North | N | 0.0019928 | 0
582 | JCKCNTY8 | 3 | 147 | -0.019861 | north | -0.0019928 | -0.014977 | -0.26698 | -0.0096894 | 0.0019928 | North | N | 0.0019928 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.021427 | north | -0.0035588 | -0.016543 | -0.26855 | -0.011255 | 0.0035588 | North | N | 0.0035588 | 0
837 | NEWMAN_G | 1 | 40 | -0.019206 | north | -0.0013378 | -0.014322 | -0.26632 | -0.0090344 | 0.0013378 | North | N | 0.0013378 | 0
842 | OLINGER_ | 1 | 79 | -0.019274 | north | -0.0014058 | -0.01439 | -0.26639 | -0.0091024 | 0.0014058 | North | N | 0.0014058 | 0
843 | OLINGER_ | 1 | 106 | -0.019274 | north | -0.0014058 | -0.01439 | -0.26639 | -0.0091024 | 0.0014058 | North | N | 0.0014058 | 0
844 | OLINGER_ | 1 | 146 | -0.019274 | north | -0.0014058 | -0.01439 | -0.26639 | -0.0091024 | 0.0014058 | North | N | 0.0014058 | 0
845 | OLINGER_ | 1 | 76 | -0.019274 | north | -0.0014058 | -0.01439 | -0.26639 | -0.0091024 | 0.0014058 | North | N | 0.0014058 | 0
923 | SPENCER_ | 1 | 60 | -0.022404 | north | -0.0045358 | -0.01752 | -0.26952 | -0.012232 | 0.0045358 | North | N | 0.0045358 | 0
924 | SPENCER_ | 1 | 63 | -0.022404 | north | -0.0045358 | -0.01752 | -0.26952 | -0.012232 | 0.0045358 | North | N | 0.0045358 | 0
948 | STEAM1 | 1 | 20 | -0.019209 | north | -0.0013408 | -0.014325 | -0.26633 | -0.0090374 | 0.0013408 | North | N | 0.0013408 | 0
949 | STEAM2 | 1 | 25 | -0.019209 | north | -0.0013408 | -0.014325 | -0.26633 | -0.0090374 | 0.0013408 | North | N | 0.0013408 | 0
950 | STEAM3 | 1 | 41 | -0.019209 | north | -0.0013408 | -0.014325 | -0.26633 | -0.0090374 | 0.0013408 | North | N | 0.0013408 | 0
990 | GIBN_CRE | 1 | 463 | -0.013091 | north | 0.0047772 | -0.008207 | -0.26021 | -0.0029194 | 0.0029194 | houston | Y | 0.0047772 | 0.86018
1002 | PBCTAGE_ | A | 66 | 0.31375 | west | 0.33162 | 0.31863 | 0.066631 | 0.32392 | 0.066631 | west | N | 0.066631 | 0
1003 | PBCTBGE_ | B | 65 | 0.31375 | west | 0.33162 | 0.31863 | 0.066631 | 0.32392 | 0.066631 | west | N | 0.066631 | 0
1004 | PBCTCGE_ | C | 67 | 0.31375 | west | 0.33162 | 0.31863 | 0.066631 | 0.32392 | 0.066631 | west | N | 0.066631 | 0
1005 | PBCTDGE_ | D | 67 | 0.31375 | west | 0.33162 | 0.31863 | 0.066631 | 0.32392 | 0.066631 | west | N | 0.066631 | 0
1006 | PBCTEGE_ | E | 67 | 0.31375 | west | 0.33162 | 0.31863 | 0.066631 | 0.32392 | 0.066631 | west | N | 0.066631 | 0
1007 | PB5GEN_6 | MB | 114 | 0.31375 | west | 0.33162 | 0.31863 | 0.066631 | 0.32392 | 0.066631 | west | N | 0.066631 | 0
1008 | PB6GEN_7 | MB | 515 | 0.31375 | west | 0.33162 | 0.31863 | 0.066631 | 0.32392 | 0.066631 | west | N | 0.066631 | 0
1039 | MRGNAG_1 | A | 66 | 0.30968 | west | 0.32755 | 0.31456 | 0.062561 | 0.31985 | 0.062561 | west | N | 0.062561 | 0
1040 | MRGNBG_2 | B | 69 | 0.30968 | west | 0.32755 | 0.31456 | 0.062561 | 0.31985 | 0.062561 | west | N | 0.062561 | 0
1041 | MRGNCG_3 | C | 69 | 0.30968 | west | 0.32755 | 0.31456 | 0.062561 | 0.31985 | 0.062561 | west | N | 0.062561 | 0
1042 | MRGNDG_4 | D | 67 | 0.30968 | west | 0.32755 | 0.31456 | 0.062561 | 0.31985 | 0.062561 | west | N | 0.062561 | 0
1043 | MRGNEG_5 | E | 67 | 0.30968 | west | 0.32755 | 0.31456 | 0.062561 | 0.31985 | 0.062561 | west | N | 0.062561 | 0
1044 | MRGNFG_6 | F | 65 | 0.30968 | west | 0.32755 | 0.31456 | 0.062561 | 0.31985 | 0.062561 | west | N | 0.062561 | 0
1045 | CALENG1G | 1 | 70 | 0.33109 | west | 0.34896 | 0.33597 | 0.083969 | 0.34126 | 0.083969 | west | N | 0.083969 | 0
1046 | CALENG2G | 2 | 73.4 | 0.33109 | west | 0.34896 | 0.33597 | 0.083969 | 0.34126 | 0.083969 | west | N | 0.083969 | 0
1047 | CALENG3G | 3 | 70.4 | 0.33109 | west | 0.34896 | 0.33597 | 0.083969 | 0.34126 | 0.083969 | west | N | 0.083969 | 0
1058 | LONGSHOR | 1 | 150 | 0.33328 | west | 0.35115 | 0.33816 | 0.086161 | 0.34345 | 0.086161 | west | N | 0.086161 | 0
1058 | LONGSHOR | 2 | 220 | 0.33328 | west | 0.35115 | 0.33816 | 0.086161 | 0.34345 | 0.086161 | west | N | 0.086161 | 0
1061 | CIELOGEN | 1 | 99 | 0.27846 | west | 0.29632 | 0.28334 | 0.031337 | 0.28863 | 0.031337 | west | N | 0.031337 | 0
1062 | CIELOGEN | 1 | 61 | 0.27846 | west | 0.29632 | 0.28334 | 0.031337 | 0.28863 | 0.031337 | west | N | 0.031337 | 0
1068 | SCURRYCW | 1 | 141 | 0.27926 | west | 0.29713 | 0.28414 | 0.032142 | 0.28943 | 0.032142 | west | N | 0.032142 | 0
1069 | KINDERMG | 1 | 25 | 0.27846 | west | 0.29632 | 0.28334 | 0.031337 | 0.28863 | 0.031337 | west | N | 0.031337 | 0
1070 | KINDERMG | 1 | 45.7 | 0.27846 | west | 0.29632 | 0.28334 | 0.031337 | 0.28863 | 0.031337 | west | N | 0.031337 | 0
1071 | KINDERMG | 1 | 45.7 | 0.27846 | west | 0.29632 | 0.28334 | 0.031337 | 0.28863 | 0.031337 | west | N | 0.031337 | 0
1073 | SCURRYCW | 2 | 120 | 0.27926 | west | 0.29713 | 0.28414 | 0.032142 | 0.28943 | 0.032142 | west | N | 0.032142 | 0
1320 | BSP 1 | 1 | 25.8 | 0.29304 | west | 0.31091 | 0.29793 | 0.045926 | 0.30322 | 0.045926 | west | N | 0.045926 | 0
1326 | STANTONW | 1 | 100.5 | 0.31085 | west | 0.32872 | 0.31574 | 0.063735 | 0.32102 | 0.063735 | west | N | 0.063735 | 0
1327 | WILDHRSE | 1 | 120 | 0.29876 | west | 0.31663 | 0.30364 | 0.051642 | 0.30893 | 0.051642 | west | N | 0.051642 | 0
1328 | OCOTILLO | 1 | 58 | 0.31015 | west | 0.32802 | 0.31503 | 0.06303 | 0.32032 | 0.06303 | west | N | 0.06303 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.31008 | west | 0.32795 | 0.31497 | 0.062964 | 0.32025 | 0.062964 | west | N | 0.062964 | 0
1343 | TRENTIPP | 1 | 150 | 0.17126 | west | 0.18913 | 0.17614 | -0.075857 | 0.18143 | 0.075857 | west | N | 0.075857 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.2752 | west | 0.29307 | 0.28008 | 0.028083 | 0.28537 | 0.028083 | west | N | 0.028083 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.2752 | west | 0.29307 | 0.28008 | 0.028083 | 0.28537 | 0.028083 | west | N | 0.028083 | 0
1354 | AEPWIND_ | 1 | 101 | 0.17126 | west | 0.18913 | 0.17614 | -0.075857 | 0.18143 | 0.075857 | west | N | 0.075857 | 0
1360 | GUNSIGHT | 1 | 120 | 0.29628 | west | 0.31414 | 0.30116 | 0.049157 | 0.30645 | 0.049157 | west | N | 0.049157 | 0
1432 | GRHAMSES | 2 | 366 | -0.050862 | north | -0.032994 | -0.045978 | -0.29798 | -0.04069 | 0.032994 | North | N | 0.032994 | 0
1433 | GRHAMSES | 1 | 242 | -0.023504 | north | -0.0056358 | -0.01862 | -0.27062 | -0.013332 | 0.0056358 | North | N | 0.0056358 | 0
1437 | MESQUITW | 1 | 400 | -0.001756 | west | 0.016112 | 0.003128 | -0.24887 | 0.0084156 | 0.003128 | south | Y | 0.24887 | 98.2984
1438 | MESQUITW | 1 | 236 | -0.001925 | west | 0.015943 | 0.002959 | -0.24904 | 0.0082466 | 0.002959 | south | Y | 0.24904 | 58.0758
1442 | COKFIELD | 1 | 165 | -0.013669 | west | 0.0041992 | -0.008785 | -0.26079 | -0.0034974 | 0.0034974 | houston | Y | 0.26079 | 42.4528
1453 | WCPWRCO_ | 1 | 204 | -0.032845 | north | -0.014977 | -0.027961 | -0.27996 | -0.022673 | 0.014977 | North | N | 0.014977 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.032845 | north | -0.014977 | -0.027961 | -0.27996 | -0.022673 | 0.014977 | North | N | 0.014977 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.032845 | north | -0.014977 | -0.027961 | -0.27996 | -0.022673 | 0.014977 | North | N | 0.014977 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.02826 | west | -0.010392 | -0.023376 | -0.27538 | -0.018088 | 0.010392 | North | Y | 0.27538 | 5.2997
1479 | WFCOGEN_ | 2 | 20 | -0.02826 | west | -0.010392 | -0.023376 | -0.27538 | -0.018088 | 0.010392 | North | Y | 0.27538 | 5.2997
1482 | WFCOGEN_ | 1 | 20 | -0.02826 | west | -0.010392 | -0.023376 | -0.27538 | -0.018088 | 0.010392 | North | Y | 0.27538 | 5.2997
1482 | WFCOGEN_ | 2 | 17 | -0.02826 | west | -0.010392 | -0.023376 | -0.27538 | -0.018088 | 0.010392 | North | Y | 0.27538 | 4.5048
1600 | BARTNWND | 1 | 120 | -0.019361 | north | -0.0014928 | -0.014477 | -0.26648 | -0.0091894 | 0.0014928 | North | N | 0.0014928 | 0
1643 | SLSTR1PP | 1 | 60 | 0.002903 | north | 0.020771 | 0.007787 | -0.24422 | 0.013075 | 0.007787 | south | Y | 0.020771 | 0.77905
1675 | PEC_1G | 1 | 75 | -0.019596 | north | -0.0017278 | -0.014712 | -0.26671 | -0.0094244 | 0.0017278 | North | N | 0.0017278 | 0
1676 | PEC_2G | 2 | 79.6 | -0.019596 | north | -0.0017278 | -0.014712 | -0.26671 | -0.0094244 | 0.0017278 | North | N | 0.0017278 | 0
1677 | PEC_3G | 3 | 88.4 | -0.019596 | north | -0.0017278 | -0.014712 | -0.26671 | -0.0094244 | 0.0017278 | North | N | 0.0017278 | 0
1678 | LAMARPWR | 1 | 160 | -0.019632 | north | -0.0017638 | -0.014748 | -0.26675 | -0.0094604 | 0.0017638 | North | N | 0.0017638 | 0
1679 | LAMARPWR | 2 | 156 | -0.019632 | north | -0.0017638 | -0.014748 | -0.26675 | -0.0094604 | 0.0017638 | North | N | 0.0017638 | 0
1680 | LAMARPWR | 3 | 196 | -0.019632 | north | -0.0017638 | -0.014748 | -0.26675 | -0.0094604 | 0.0017638 | North | N | 0.0017638 | 0
1681 | LAMARPWR | 4 | 156 | -0.019632 | north | -0.0017638 | -0.014748 | -0.26675 | -0.0094604 | 0.0017638 | North | N | 0.0017638 | 0
1682 | LAMARPWR | 5 | 157 | -0.019632 | north | -0.0017638 | -0.014748 | -0.26675 | -0.0094604 | 0.0017638 | North | N | 0.0017638 | 0
1683 | LAMARPWR | 6 | 198 | -0.019632 | north | -0.0017638 | -0.014748 | -0.26675 | -0.0094604 | 0.0017638 | North | N | 0.0017638 | 0
1687 | VALLEY_1 | 1 | 170 | -0.019814 | north | -0.0019458 | -0.01493 | -0.26693 | -0.0096424 | 0.0019458 | North | N | 0.0019458 | 0
1688 | VALLEY_2 | 2 | 520 | -0.019814 | north | -0.0019458 | -0.01493 | -0.26693 | -0.0096424 | 0.0019458 | North | N | 0.0019458 | 0
1689 | VALLEY_3 | 3 | 370 | -0.019687 | north | -0.0018188 | -0.014803 | -0.26681 | -0.0095154 | 0.0018188 | North | N | 0.0018188 | 0
1701 | MOSES_1G | 1 | 558 | -0.019532 | north | -0.0016638 | -0.014648 | -0.26665 | -0.0093604 | 0.0016638 | North | N | 0.0016638 | 0
1702 | MOSES_2G | 2 | 579 | -0.019532 | north | -0.0016638 | -0.014648 | -0.26665 | -0.0093604 | 0.0016638 | North | N | 0.0016638 | 0
1703 | MOSES_3G | 3 | 808 | -0.019532 | north | -0.0016638 | -0.014648 | -0.26665 | -0.0093604 | 0.0016638 | North | N | 0.0016638 | 0
1861 | EAGLEMNT | MB | 112 | -0.022061 | north | -0.0041928 | -0.017177 | -0.26918 | -0.011889 | 0.0041928 | North | N | 0.0041928 | 0
1862 | EAGLEMNT | MB | 100 | -0.022061 | north | -0.0041928 | -0.017177 | -0.26918 | -0.011889 | 0.0041928 | North | N | 0.0041928 | 0
1863 | EAGLEMNT | MB | 378 | -0.022061 | north | -0.0041928 | -0.017177 | -0.26918 | -0.011889 | 0.0041928 | North | N | 0.0041928 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.013189 | north | 0.0046792 | -0.008305 | -0.26031 | -0.0030174 | 0.0030174 | houston | Y | 0.0046792 | 0.36112
1878 | WLFHOLW_ | 2 | 205 | -0.013189 | north | 0.0046792 | -0.008305 | -0.26031 | -0.0030174 | 0.0030174 | houston | Y | 0.0046792 | 0.34068
1879 | WLFHOLW_ | 3 | 272.4 | -0.013189 | north | 0.0046792 | -0.008305 | -0.26031 | -0.0030174 | 0.0030174 | houston | Y | 0.0046792 | 0.45268
1889 | DECRDOVA | MB | 770 | -0.015925 | north | 0.0019432 | -0.011041 | -0.26304 | -0.0057534 | 0.0019432 | North | N | 0.0019432 | 0
1892 | DECRDOVA | A | 70 | -0.014049 | north | 0.0038192 | -0.009165 | -0.26117 | -0.0038774 | 0.0038192 | North | N | 0.0038192 | 0
1893 | DECRDOVA | B | 69 | -0.014049 | north | 0.0038192 | -0.009165 | -0.26117 | -0.0038774 | 0.0038192 | North | N | 0.0038192 | 0
1894 | DECRDOVA | C | 69 | -0.014049 | north | 0.0038192 | -0.009165 | -0.26117 | -0.0038774 | 0.0038192 | North | N | 0.0038192 | 0
1895 | DECRDOVA | D | 68 | -0.014049 | north | 0.0038192 | -0.009165 | -0.26117 | -0.0038774 | 0.0038192 | North | N | 0.0038192 | 0
1898 | COMCHEPK | 1 | 1157 | -0.012357 | north | 0.0055112 | -0.007473 | -0.25948 | -0.0021854 | 0.0021854 | houston | Y | 0.0055112 | 3.848
1899 | COMCHEPK | 2 | 1158 | -0.012357 | north | 0.0055112 | -0.007473 | -0.25948 | -0.0021854 | 0.0021854 | houston | Y | 0.0055112 | 3.8513
1937 | MDLTHELP | 5 | 224 | -0.016893 | north | 0.0009752 | -0.012009 | -0.26401 | -0.0067214 | 0.0009752 | North | N | 0.0009752 | 0
1938 | MDLTHELP | 6 | 226 | -0.016893 | north | 0.0009752 | -0.012009 | -0.26401 | -0.0067214 | 0.0009752 | North | N | 0.0009752 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.017507 | north | 0.0003612 | -0.012623 | -0.26463 | -0.0073354 | 0.0003612 | North | N | 0.0003612 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.017507 | north | 0.0003612 | -0.012623 | -0.26463 | -0.0073354 | 0.0003612 | North | N | 0.0003612 | 0
1943 | MDLTHELP | 3 | 212 | -0.016893 | north | 0.0009752 | -0.012009 | -0.26401 | -0.0067214 | 0.0009752 | North | N | 0.0009752 | 0
1944 | MDLTHELP | 4 | 211 | -0.016893 | north | 0.0009752 | -0.012009 | -0.26401 | -0.0067214 | 0.0009752 | North | N | 0.0009752 | 0
1947 | HANDLEY_ | 3 | 395 | -0.019295 | north | -0.0014268 | -0.014411 | -0.26641 | -0.0091234 | 0.0014268 | North | N | 0.0014268 | 0
1948 | HANDLEY_ | 4 | 435 | -0.019277 | north | -0.0014088 | -0.014393 | -0.2664 | -0.0091054 | 0.0014088 | North | N | 0.0014088 | 0
1949 | HANDLEY_ | 5 | 435 | -0.019295 | north | -0.0014268 | -0.014411 | -0.26641 | -0.0091234 | 0.0014268 | North | N | 0.0014268 | 0
2371 | COLLIN_1 | MB | 138 | -0.020288 | north | -0.0024198 | -0.015404 | -0.26741 | -0.010116 | 0.0024198 | North | N | 0.0024198 | 0
2413 | MTCK6_G | 6 | 118 | -0.018544 | north | -0.0006758 | -0.01366 | -0.26566 | -0.0083724 | 0.0006758 | North | N | 0.0006758 | 0
2414 | MTCK7_G | 7 | 115 | -0.018544 | north | -0.0006758 | -0.01366 | -0.26566 | -0.0083724 | 0.0006758 | North | N | 0.0006758 | 0
2417 | MTCK8_G | 8 | 556 | -0.018544 | north | -0.0006758 | -0.01366 | -0.26566 | -0.0083724 | 0.0006758 | North | N | 0.0006758 | 0
2451 | LKHB1_G | 1 | 388 | -0.018905 | north | -0.0010368 | -0.014021 | -0.26602 | -0.0087334 | 0.0010368 | North | N | 0.0010368 | 0
2452 | LKHB2_G | 2 | 515 | -0.018905 | north | -0.0010368 | -0.014021 | -0.26602 | -0.0087334 | 0.0010368 | North | N | 0.0010368 | 0
3097 | MARTLAKE | 1 | 785 | -0.017835 | north | 3.32e-05 | -0.012951 | -0.26495 | -0.0076634 | 3.32e-05 | North | N | 3.32e-05 | 0
3098 | MARTLAKE | 2 | 795 | -0.017835 | north | 3.32e-05 | -0.012951 | -0.26495 | -0.0076634 | 3.32e-05 | North | N | 3.32e-05 | 0
3099 | MARTLAKE | 3 | 780 | -0.017835 | north | 3.32e-05 | -0.012951 | -0.26495 | -0.0076634 | 3.32e-05 | North | N | 3.32e-05 | 0
3107 | STRYKER_ | 1 | 182 | -0.017549 | north | 0.0003192 | -0.012665 | -0.26467 | -0.0073774 | 0.0003192 | North | N | 0.0003192 | 0
3108 | STRYKER_ | 2 | 484 | -0.017549 | north | 0.0003192 | -0.012665 | -0.26467 | -0.0073774 | 0.0003192 | North | N | 0.0003192 | 0
3126 | TRINIDAD | 1 | 224 | -0.017073 | north | 0.0007952 | -0.012189 | -0.26419 | -0.0069014 | 0.0007952 | North | N | 0.0007952 | 0
3309 | ASPN_G | 1 | 50 | -0.017572 | north | 0.0002962 | -0.012688 | -0.26469 | -0.0074004 | 0.0002962 | North | N | 0.0002962 | 0
3348 | CHAMPION | MB | 42 | -0.017585 | north | 0.0002832 | -0.012701 | -0.2647 | -0.0074134 | 0.0002832 | North | N | 0.0002832 | 0
3381 | BBRN_1G | 1 | 615 | -0.016145 | north | 0.0017232 | -0.011261 | -0.26326 | -0.0059734 | 0.0017232 | North | N | 0.0017232 | 0
3382 | BBRN_2G | 2 | 587 | -0.016145 | north | 0.0017232 | -0.011261 | -0.26326 | -0.0059734 | 0.0017232 | North | N | 0.0017232 | 0
3403 | THOUSE_1 | MB | 537 | -0.013167 | north | 0.0047012 | -0.008283 | -0.26029 | -0.0029954 | 0.0029954 | houston | Y | 0.0047012 | 0.91603
3404 | THOUSE_2 | 2 | 787 | -0.013167 | north | 0.0047012 | -0.008283 | -0.26029 | -0.0029954 | 0.0029954 | houston | Y | 0.0047012 | 1.3425
3416 | LAKE_CRK | MB | 75 | -0.012708 | north | 0.0051602 | -0.007824 | -0.25983 | -0.0025364 | 0.0025364 | houston | Y | 0.0051602 | 0.19679
3417 | LAKE_CRK | MB | 222 | -0.012708 | north | 0.0051602 | -0.007824 | -0.25983 | -0.0025364 | 0.0025364 | houston | Y | 0.0051602 | 0.58249
3432 | SANDOW_4 | 4 | 569 | -0.008868 | south | 0.0090002 | -0.003984 | -0.25599 | 0.0013036 | 0.0013036 | houston | Y | 0.003984 | 1.5252
5026 | BRAUNIG_ | 1 | 209 | -0.003756 | south | 0.014112 | 0.001128 | -0.25087 | 0.0064156 | 0.001128 | south | N | 0.001128 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.003756 | south | 0.014112 | 0.001128 | -0.25087 | 0.0064156 | 0.001128 | south | N | 0.001128 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.003641 | south | 0.014227 | 0.001243 | -0.25076 | 0.0065306 | 0.001243 | south | N | 0.001243 | 0
5031 | BRA_VHBC | 1 | 46 | -0.003756 | south | 0.014112 | 0.001128 | -0.25087 | 0.0064156 | 0.001128 | south | N | 0.001128 | 0
5032 | BRA_VHBC | 2 | 47 | -0.003756 | south | 0.014112 | 0.001128 | -0.25087 | 0.0064156 | 0.001128 | south | N | 0.001128 | 0
5033 | BRA_VHBC | 3 | 46 | -0.003756 | south | 0.014112 | 0.001128 | -0.25087 | 0.0064156 | 0.001128 | south | N | 0.001128 | 0
5034 | BRA_VHBC | 4 | 46 | -0.003756 | south | 0.014112 | 0.001128 | -0.25087 | 0.0064156 | 0.001128 | south | N | 0.001128 | 0
5111 | CALAVER_ | 1 | 424 | -0.003833 | south | 0.014035 | 0.001051 | -0.25095 | 0.0063386 | 0.001051 | south | N | 0.001051 | 0
5112 | CALAVER_ | 2 | 425 | -0.003833 | south | 0.014035 | 0.001051 | -0.25095 | 0.0063386 | 0.001051 | south | N | 0.001051 | 0
5264 | LEON_LCP | 3 | 58 | -0.003265 | south | 0.014603 | 0.001619 | -0.25038 | 0.0069066 | 0.001619 | south | N | 0.001619 | 0
5265 | LEON_LCP | 4 | 89 | -0.003265 | south | 0.014603 | 0.001619 | -0.25038 | 0.0069066 | 0.001619 | south | N | 0.001619 | 0
5266 | LEON_LCP | 1 | 44 | -0.003265 | south | 0.014603 | 0.001619 | -0.25038 | 0.0069066 | 0.001619 | south | N | 0.001619 | 0
5267 | LEON_LCP | 2 | 44 | -0.003265 | south | 0.014603 | 0.001619 | -0.25038 | 0.0069066 | 0.001619 | south | N | 0.001619 | 0
5268 | LEON_LCP | 3 | 43 | -0.003265 | south | 0.014603 | 0.001619 | -0.25038 | 0.0069066 | 0.001619 | south | N | 0.001619 | 0
5269 | LEON_LCP | 4 | 45 | -0.003265 | south | 0.014603 | 0.001619 | -0.25038 | 0.0069066 | 0.001619 | south | N | 0.001619 | 0
5396 | CALAVER_ | 1 | 412 | -0.003763 | south | 0.014105 | 0.001121 | -0.25088 | 0.0064086 | 0.001121 | south | N | 0.001121 | 0
5397 | CALAVER_ | 2 | 400 | -0.003763 | south | 0.014105 | 0.001121 | -0.25088 | 0.0064086 | 0.001121 | south | N | 0.001121 | 0
5401 | CALAVER_ | 1 | 546 | -0.004285 | south | 0.013583 | 0.00059895 | -0.2514 | 0.0058866 | 0.00059895 | south | N | 0.00059895 | 0
5402 | CALAVER_ | 2 | 750 | -0.004285 | south | 0.013583 | 0.00059895 | -0.2514 | 0.0058866 | 0.00059895 | south | N | 0.00059895 | 0
5436 | TUTTL_WB | MB | 61 | -0.004096 | south | 0.013772 | 0.00078795 | -0.25121 | 0.0060756 | 0.00078795 | south | N | 0.00078795 | 0
5438 | TUTTL_WB | MB | 95 | -0.004096 | south | 0.013772 | 0.00078795 | -0.25121 | 0.0060756 | 0.00078795 | south | N | 0.00078795 | 0
5439 | TUTTL_WB | MB | 151 | -0.004096 | south | 0.013772 | 0.00078795 | -0.25121 | 0.0060756 | 0.00078795 | south | N | 0.00078795 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.004186 | south | 0.013682 | 0.00069795 | -0.2513 | 0.0059856 | 0.00069795 | south | N | 0.00069795 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.004186 | south | 0.013682 | 0.00069795 | -0.2513 | 0.0059856 | 0.00069795 | south | N | 0.00069795 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.004186 | south | 0.013682 | 0.00069795 | -0.2513 | 0.0059856 | 0.00069795 | south | N | 0.00069795 | 0
5503 | RAYBURNG | 1 | 22 | -0.005104 | south | 0.012764 | -0.00022005 | -0.25222 | 0.0050676 | 0.00022005 | south | N | 0.00022005 | 0
5505 | RAYBURNG | 1 | 11 | -0.005104 | south | 0.012764 | -0.00022005 | -0.25222 | 0.0050676 | 0.00022005 | south | N | 0.00022005 | 0
5506 | RAYBURNG | 1 | 11 | -0.005104 | south | 0.012764 | -0.00022005 | -0.25222 | 0.0050676 | 0.00022005 | south | N | 0.00022005 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.005263 | south | 0.012605 | -0.00037905 | -0.25238 | 0.0049086 | 0.00037905 | south | N | 0.00037905 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.005263 | south | 0.012605 | -0.00037905 | -0.25238 | 0.0049086 | 0.00037905 | south | N | 0.00037905 | 0
5511 | RAYBURNC | 1 | 46 | -0.005263 | south | 0.012605 | -0.00037905 | -0.25238 | 0.0049086 | 0.00037905 | south | N | 0.00037905 | 0
5512 | RAYBURNC | 1 | 48 | -0.005263 | south | 0.012605 | -0.00037905 | -0.25238 | 0.0049086 | 0.00037905 | south | N | 0.00037905 | 0
5728 | FALCONHY | 2 | 12 | -0.00229 | south | 0.015578 | 0.002594 | -0.24941 | 0.0078816 | 0.002594 | south | N | 0.002594 | 0
5729 | FALCONHY | 3 | 11 | -0.00229 | south | 0.015578 | 0.002594 | -0.24941 | 0.0078816 | 0.002594 | south | N | 0.002594 | 0
5890 | PEARSALL | 1 | 24 | 0.004199 | south | 0.022067 | 0.009083 | -0.24292 | 0.014371 | 0.009083 | south | N | 0.009083 | 0
5891 | PEARSALL | 1 | 24 | 0.004199 | south | 0.022067 | 0.009083 | -0.24292 | 0.014371 | 0.009083 | south | N | 0.009083 | 0
5892 | PEARSALL | 1 | 23 | 0.004199 | south | 0.022067 | 0.009083 | -0.24292 | 0.014371 | 0.009083 | south | N | 0.009083 | 0
5903 | SANMIGUE | 1 | 396 | -0.003576 | south | 0.014292 | 0.001308 | -0.25069 | 0.0065956 | 0.001308 | south | N | 0.001308 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.008368 | houston | 0.0095002 | -0.003484 | -0.25549 | 0.0018036 | 0.0018036 | houston | N | 0.0018036 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.008368 | houston | 0.0095002 | -0.003484 | -0.25549 | 0.0018036 | 0.0018036 | houston | N | 0.0018036 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | Y | 0.017868 | 7.7905
5932 | SI_RAY9 | 9 | 38 | -0.004359 | south | 0.013509 | 0.00052495 | -0.25148 | 0.0058126 | 0.00052495 | south | N | 0.00052495 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.004359 | south | 0.013509 | 0.00052495 | -0.25148 | 0.0058126 | 0.00052495 | south | N | 0.00052495 | 0
5934 | SI_RAY5 | 5 | 15 | -0.004359 | south | 0.013509 | 0.00052495 | -0.25148 | 0.0058126 | 0.00052495 | south | N | 0.00052495 | 0
5935 | SI_RAY10 | 10 | 47 | -0.004359 | south | 0.013509 | 0.00052495 | -0.25148 | 0.0058126 | 0.00052495 | south | N | 0.00052495 | 0
6016 | SWMESA | 1 | 75 | 0.27709 | west | 0.29496 | 0.28198 | 0.029975 | 0.28726 | 0.029975 | west | N | 0.029975 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | Y | 0.24712 | 53.2915
6144 | MCADOO1A | 1 | 150 | 0.18785 | west | 0.20572 | 0.19273 | -0.059269 | 0.19802 | 0.059269 | west | N | 0.059269 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.090905 | west | 0.10877 | 0.095789 | -0.15621 | 0.10108 | 0.095789 | south | Y | 0.15621 | 10.2419
6476 | LANGFORD | 1 | 150 | 0.13254 | west | 0.15041 | 0.13742 | -0.11458 | 0.14271 | 0.11458 | west | N | 0.11458 | 0
6637 | SNYDERW1 | 1 | 63 | 0.28323 | west | 0.3011 | 0.28812 | 0.036115 | 0.2934 | 0.036115 | west | N | 0.036115 | 0
6752 | OKLA0A | 1 | 649.7 | -0.002066 | west | 0.015802 | 0.002818 | -0.24918 | 0.0081056 | 0.002818 | south | Y | 0.24918 | 160.0641
6948 | DENISNDM | 1 | 40 | -0.019914 | north | -0.0020458 | -0.01503 | -0.26703 | -0.0097424 | 0.0020458 | North | N | 0.0020458 | 0
6948 | DENISNDM | 2 | 40 | -0.019914 | north | -0.0020458 | -0.01503 | -0.26703 | -0.0097424 | 0.0020458 | North | N | 0.0020458 | 0
7000 | L_FERGUS | 1 | 422 | 0.000486 | south | 0.018354 | 0.00537 | -0.24663 | 0.010658 | 0.00537 | south | N | 0.00537 | 0
7004 | L_SIMGID | 1 | 132 | -0.006862 | south | 0.011006 | -0.001978 | -0.25398 | 0.0033096 | 0.001978 | south | N | 0.001978 | 0
7005 | L_SIMGID | 2 | 134 | -0.006862 | south | 0.011006 | -0.001978 | -0.25398 | 0.0033096 | 0.001978 | south | N | 0.001978 | 0
7006 | L_SIMGID | 3 | 323 | -0.006862 | south | 0.011006 | -0.001978 | -0.25398 | 0.0033096 | 0.001978 | south | N | 0.001978 | 0
7007 | L_LOSTPI | 1 | 158 | -0.007171 | south | 0.010697 | -0.002287 | -0.25429 | 0.0030006 | 0.002287 | south | N | 0.002287 | 0
7008 | L_LOSTPI | 2 | 160 | -0.007171 | south | 0.010697 | -0.002287 | -0.25429 | 0.0030006 | 0.002287 | south | N | 0.002287 | 0
7009 | L_LOSTPI | 3 | 175 | -0.007171 | south | 0.010697 | -0.002287 | -0.25429 | 0.0030006 | 0.002287 | south | N | 0.002287 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.007175 | south | 0.010693 | -0.002291 | -0.25429 | 0.0029966 | 0.002291 | south | N | 0.002291 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.007175 | south | 0.010693 | -0.002291 | -0.25429 | 0.0029966 | 0.002291 | south | N | 0.002291 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.007174 | south | 0.010694 | -0.00229 | -0.25429 | 0.0029976 | 0.00229 | south | N | 0.00229 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.0053 | south | 0.012568 | -0.00041605 | -0.25242 | 0.0048716 | 0.00041605 | south | N | 0.00041605 | 0
7015 | L_HAYSEN | 2 | 225 | -0.0053 | south | 0.012568 | -0.00041605 | -0.25242 | 0.0048716 | 0.00041605 | south | N | 0.00041605 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.0053 | south | 0.012568 | -0.00041605 | -0.25242 | 0.0048716 | 0.00041605 | south | N | 0.00041605 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.0053 | south | 0.012568 | -0.00041605 | -0.25242 | 0.0048716 | 0.00041605 | south | N | 0.00041605 | 0
7020 | L_AUSTPL | 1 | 8 | -0.006286 | south | 0.011582 | -0.001402 | -0.2534 | 0.0038856 | 0.001402 | south | N | 0.001402 | 0
7020 | L_AUSTPL | 2 | 8 | -0.006286 | south | 0.011582 | -0.001402 | -0.2534 | 0.0038856 | 0.001402 | south | N | 0.001402 | 0
7022 | L_BUCHAN | 1 | 18 | 0.000391 | south | 0.018259 | 0.005275 | -0.24673 | 0.010563 | 0.005275 | south | N | 0.005275 | 0
7023 | L_BUCHAN | 2 | 18 | 0.000391 | south | 0.018259 | 0.005275 | -0.24673 | 0.010563 | 0.005275 | south | N | 0.005275 | 0
7024 | L_BUCHAN | 3 | 15 | 0.000391 | south | 0.018259 | 0.005275 | -0.24673 | 0.010563 | 0.005275 | south | N | 0.005275 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.002484 | south | 0.020352 | 0.007368 | -0.24463 | 0.012656 | 0.007368 | south | N | 0.007368 | 0
7028 | L_MARBFA | 1 | 18 | -0.001098 | south | 0.01677 | 0.003786 | -0.24822 | 0.0090736 | 0.003786 | south | N | 0.003786 | 0
7029 | L_MARBFA | 2 | 18 | -0.001098 | south | 0.01677 | 0.003786 | -0.24822 | 0.0090736 | 0.003786 | south | N | 0.003786 | 0
7031 | L_MARSFO | 1 | 35 | -0.004689 | south | 0.013179 | 0.00019495 | -0.25181 | 0.0054826 | 0.00019495 | south | N | 0.00019495 | 0
7032 | L_MARSFO | 2 | 34 | -0.004689 | south | 0.013179 | 0.00019495 | -0.25181 | 0.0054826 | 0.00019495 | south | N | 0.00019495 | 0
7033 | L_MARSFO | 3 | 35 | -0.004689 | south | 0.013179 | 0.00019495 | -0.25181 | 0.0054826 | 0.00019495 | south | N | 0.00019495 | 0
7035 | L_WIRTZ_ | 1 | 28 | 4.8e-05 | south | 0.017916 | 0.004932 | -0.24707 | 0.01022 | 0.004932 | south | N | 0.004932 | 0
7036 | L_WIRTZ_ | 2 | 29 | 4.8e-05 | south | 0.017916 | 0.004932 | -0.24707 | 0.01022 | 0.004932 | south | N | 0.004932 | 0
7038 | L_DELAWA | 1 | 35 | 0.31277 | west | 0.33064 | 0.31765 | 0.065651 | 0.32294 | 0.065651 | west | N | 0.065651 | 0
7038 | L_DELAWA | 2 | 30 | 0.31277 | west | 0.33064 | 0.31765 | 0.065651 | 0.32294 | 0.065651 | west | N | 0.065651 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.007046 | south | 0.010822 | -0.002162 | -0.25416 | 0.0031256 | 0.002162 | south | N | 0.002162 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.007046 | south | 0.010822 | -0.002162 | -0.25416 | 0.0031256 | 0.002162 | south | N | 0.002162 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.007046 | south | 0.010822 | -0.002162 | -0.25416 | 0.0031256 | 0.002162 | south | N | 0.002162 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.007046 | south | 0.010822 | -0.002162 | -0.25416 | 0.0031256 | 0.002162 | south | N | 0.002162 | 0
7487 | L_CANYHY | 1 | 6 | -0.004979 | south | 0.012889 | -9.5046e-05 | -0.2521 | 0.0051926 | 9.5046e-05 | south | N | 9.5046e-05 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.005087 | south | 0.012781 | -0.00020305 | -0.25221 | 0.0050846 | 0.00020305 | south | N | 0.00020305 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.005087 | south | 0.012781 | -0.00020305 | -0.25221 | 0.0050846 | 0.00020305 | south | N | 0.00020305 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.005087 | south | 0.012781 | -0.00020305 | -0.25221 | 0.0050846 | 0.00020305 | south | N | 0.00020305 | 0
7609 | L_SCHUMA | 1 | 4 | -0.004762 | south | 0.013106 | 0.00012195 | -0.25188 | 0.0054096 | 0.00012195 | south | N | 0.00012195 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.005375 | south | 0.012493 | -0.00049105 | -0.25249 | 0.0047966 | 0.00049105 | south | N | 0.00049105 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.005375 | south | 0.012493 | -0.00049105 | -0.25249 | 0.0047966 | 0.00049105 | south | N | 0.00049105 | 0
7800 | L_GUADGE | 1 | 147 | -0.00485 | south | 0.013018 | 3.3954e-05 | -0.25197 | 0.0053216 | 3.3954e-05 | south | N | 3.3954e-05 | 0
7801 | L_GUADGE | 2 | 138 | -0.00485 | south | 0.013018 | 3.3954e-05 | -0.25197 | 0.0053216 | 3.3954e-05 | south | N | 3.3954e-05 | 0
7802 | L_GUADGE | 3 | 140 | -0.00485 | south | 0.013018 | 3.3954e-05 | -0.25197 | 0.0053216 | 3.3954e-05 | south | N | 3.3954e-05 | 0
7803 | L_GUADGE | 4 | 147 | -0.00485 | south | 0.013018 | 3.3954e-05 | -0.25197 | 0.0053216 | 3.3954e-05 | south | N | 3.3954e-05 | 0
7804 | L_GUADGE | 5 | 182 | -0.00485 | south | 0.013018 | 3.3954e-05 | -0.25197 | 0.0053216 | 3.3954e-05 | south | N | 3.3954e-05 | 0
7805 | L_GUADGE | 6 | 198 | -0.00485 | south | 0.013018 | 3.3954e-05 | -0.25197 | 0.0053216 | 3.3954e-05 | south | N | 3.3954e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.006834 | south | 0.011034 | -0.00195 | -0.25395 | 0.0033376 | 0.00195 | south | N | 0.00195 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.006834 | south | 0.011034 | -0.00195 | -0.25395 | 0.0033376 | 0.00195 | south | N | 0.00195 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.006834 | south | 0.011034 | -0.00195 | -0.25395 | 0.0033376 | 0.00195 | south | N | 0.00195 | 0
7810 | L_RIONOG | 1 | 142 | -0.005075 | south | 0.012793 | -0.00019105 | -0.25219 | 0.0050966 | 0.00019105 | south | N | 0.00019105 | 0
7811 | L_RIONOG | 2 | 145 | -0.005075 | south | 0.012793 | -0.00019105 | -0.25219 | 0.0050966 | 0.00019105 | south | N | 0.00019105 | 0
7812 | L_RIONOG | 3 | 151 | -0.005075 | south | 0.012793 | -0.00019105 | -0.25219 | 0.0050966 | 0.00019105 | south | N | 0.00019105 | 0
7813 | L_RIONOG | 4 | 290 | -0.005075 | south | 0.012793 | -0.00019105 | -0.25219 | 0.0050966 | 0.00019105 | south | N | 0.00019105 | 0
8032 | AMISTADH | 1 | 33 | 0.057571 | south | 0.075439 | 0.062455 | -0.18955 | 0.067743 | 0.062455 | south | N | 0.062455 | 0
8033 | AMISTADH | 2 | 25 | 0.057571 | south | 0.075439 | 0.062455 | -0.18955 | 0.067743 | 0.062455 | south | N | 0.062455 | 0
8048 | FALCONHY | 1 | 12 | -0.00229 | south | 0.015578 | 0.002594 | -0.24941 | 0.0078816 | 0.002594 | south | N | 0.002594 | 0
8066 | DUP1V#1 | 1 | 73 | -0.00541 | south | 0.012458 | -0.00052605 | -0.25253 | 0.0047616 | 0.00052605 | south | N | 0.00052605 | 0
8134 | FOR69CG0 | 1 | 79 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
8138 | FOR69CG0 | 2 | 81 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
8139 | JOS #1 | MB | 255 | 0 | south | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | N | 0.004884 | 0
8147 | UCAR #2 | 10 | 28 | -0.005575 | south | 0.012293 | -0.00069105 | -0.25269 | 0.0045966 | 0.00069105 | south | N | 0.00069105 | 0
8148 | UCAR #1 | 2 | 7 | -0.005575 | south | 0.012293 | -0.00069105 | -0.25269 | 0.0045966 | 0.00069105 | south | N | 0.00069105 | 0
8153 | FOR69CG0 | 3 | 79 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
8154 | FOR69CG0 | 4 | 80 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
8156 | FOR69CG0 | 6 | 25 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
8157 | FOR69CG0 | 7 | 46 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
8161 | COLETOU1 | 1 | 629 | -0.004698 | south | 0.01317 | 0.00018595 | -0.25182 | 0.0054736 | 0.00018595 | south | N | 0.00018595 | 0
8173 | VICEC51A | 5 | 144 | -0.005338 | south | 0.01253 | -0.00045405 | -0.25246 | 0.0048336 | 0.00045405 | south | N | 0.00045405 | 0
8174 | VICEC61A | 6 | 188 | -0.005338 | south | 0.01253 | -0.00045405 | -0.25246 | 0.0048336 | 0.00045405 | south | N | 0.00045405 | 0
8189 | CUERO 2 | 1 | 12 | -0.005314 | south | 0.012554 | -0.00043005 | -0.25243 | 0.0048576 | 0.00043005 | south | N | 0.00043005 | 0
8262 | ELPS | 1 | 6 | 0.040613 | south | 0.058481 | 0.045497 | -0.20651 | 0.050785 | 0.045497 | south | N | 0.045497 | 0
8285 | LAR #1 | MB | 32 | 0 | south | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | N | 0.004884 | 0
8287 | LAR #2 | MB | 32 | 0 | south | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | N | 0.004884 | 0
8288 | LAR #3 | MB | 105 | 0 | south | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | N | 0.004884 | 0
8388 | BATES0A | MB | 70 | 0 | south | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | N | 0.004884 | 0
8393 | BATES0B | MB | 110 | 0 | south | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | N | 0.004884 | 0
8442 | NBEC71A | 1 | 336 | -0.004646 | south | 0.013222 | 0.00023795 | -0.25176 | 0.0055256 | 0.00023795 | south | N | 0.00023795 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | N | 0.004884 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | 0.017868 | 0.004884 | -0.24712 | 0.010172 | 0.004884 | south | N | 0.004884 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.004617 | south | 0.013251 | 0.00026695 | -0.25174 | 0.0055546 | 0.00026695 | south | N | 0.00026695 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.004617 | south | 0.013251 | 0.00026695 | -0.25174 | 0.0055546 | 0.00026695 | south | N | 0.00026695 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.004578 | south | 0.01329 | 0.00030595 | -0.2517 | 0.0055936 | 0.00030595 | south | N | 0.00030595 | 0
8506 | VAL #1 | 1 | 25 | -0.004598 | south | 0.01327 | 0.00028595 | -0.25172 | 0.0055736 | 0.00028595 | south | N | 0.00028595 | 0
8507 | VAL #2 | 2 | 25 | -0.004598 | south | 0.01327 | 0.00028595 | -0.25172 | 0.0055736 | 0.00028595 | south | N | 0.00028595 | 0
8511 | OXY_CC0A | 1 | 38 | -0.004597 | south | 0.013271 | 0.00028695 | -0.25172 | 0.0055746 | 0.00028695 | south | N | 0.00028695 | 0
8517 | CELANEBI | 1 | 29 | -0.0045 | south | 0.013368 | 0.00038395 | -0.25162 | 0.0056716 | 0.00038395 | south | N | 0.00038395 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.004645 | south | 0.013223 | 0.00023895 | -0.25176 | 0.0055266 | 0.00023895 | south | N | 0.00023895 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.004645 | south | 0.013223 | 0.00023895 | -0.25176 | 0.0055266 | 0.00023895 | south | N | 0.00023895 | 0
8562 | CNOPST1 | 3 | 153 | -0.004645 | south | 0.013223 | 0.00023895 | -0.25176 | 0.0055266 | 0.00023895 | south | N | 0.00023895 | 0
8926 | LGE_GT10 | 1 | 158 | -0.004797 | south | 0.013071 | 8.6954e-05 | -0.25192 | 0.0053746 | 8.6954e-05 | south | N | 8.6954e-05 | 0
8927 | LGE_GT20 | 2 | 153 | -0.004797 | south | 0.013071 | 8.6954e-05 | -0.25192 | 0.0053746 | 8.6954e-05 | south | N | 8.6954e-05 | 0
8928 | LGE_STG0 | 3 | 100 | -0.004797 | south | 0.013071 | 8.6954e-05 | -0.25192 | 0.0053746 | 8.6954e-05 | south | N | 8.6954e-05 | 0
8930 | ICPGN10A | 1 | 145 | -0.004797 | south | 0.013071 | 8.6954e-05 | -0.25192 | 0.0053746 | 8.6954e-05 | south | N | 8.6954e-05 | 0
8931 | ICPGN20A | 2 | 147 | -0.004797 | south | 0.013071 | 8.6954e-05 | -0.25192 | 0.0053746 | 8.6954e-05 | south | N | 8.6954e-05 | 0
8932 | ICPGN30A | 3 | 127 | -0.004797 | south | 0.013071 | 8.6954e-05 | -0.25192 | 0.0053746 | 8.6954e-05 | south | N | 8.6954e-05 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.003924 | south | 0.013944 | 0.00095995 | -0.25104 | 0.0062476 | 0.00095995 | south | N | 0.00095995 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.003924 | south | 0.013944 | 0.00095995 | -0.25104 | 0.0062476 | 0.00095995 | south | N | 0.00095995 | 0
8935 | FGNTS201 | 3 | 173 | -0.003924 | south | 0.013944 | 0.00095995 | -0.25104 | 0.0062476 | 0.00095995 | south | N | 0.00095995 | 0
8936 | MVGN#1 | 1 | 207 | -0.004196 | south | 0.013672 | 0.00068795 | -0.25131 | 0.0059756 | 0.00068795 | south | N | 0.00068795 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.004196 | south | 0.013672 | 0.00068795 | -0.25131 | 0.0059756 | 0.00068795 | south | N | 0.00068795 | 0
8938 | MVGN#3 | 3 | 242 | -0.004196 | south | 0.013672 | 0.00068795 | -0.25131 | 0.0059756 | 0.00068795 | south | N | 0.00068795 | 0
8981 | HECN1 | 1 | 144 | -0.004197 | south | 0.013671 | 0.00068695 | -0.25132 | 0.0059746 | 0.00068695 | south | N | 0.00068695 | 0
8982 | HECN2 | 2 | 144 | -0.004197 | south | 0.013671 | 0.00068695 | -0.25132 | 0.0059746 | 0.00068695 | south | N | 0.00068695 | 0
8983 | HECN3 | 3 | 171 | -0.004197 | south | 0.013671 | 0.00068695 | -0.25132 | 0.0059746 | 0.00068695 | south | N | 0.00068695 | 0
9000 | DECKR_G1 | 1 | 310 | -0.006441 | south | 0.011427 | -0.001557 | -0.25356 | 0.0037306 | 0.001557 | south | N | 0.001557 | 0
9001 | DECKR_G2 | 2 | 413 | -0.006441 | south | 0.011427 | -0.001557 | -0.25356 | 0.0037306 | 0.001557 | south | N | 0.001557 | 0
9002 | DECKR_G3 | 3 | 42 | -0.006585 | south | 0.011283 | -0.001701 | -0.2537 | 0.0035866 | 0.001701 | south | N | 0.001701 | 0
9003 | DECKR_G4 | 4 | 44 | -0.006585 | south | 0.011283 | -0.001701 | -0.2537 | 0.0035866 | 0.001701 | south | N | 0.001701 | 0
9004 | DECKR_G5 | 5 | 44 | -0.006585 | south | 0.011283 | -0.001701 | -0.2537 | 0.0035866 | 0.001701 | south | N | 0.001701 | 0
9005 | DECKR_G6 | 6 | 47 | -0.006585 | south | 0.011283 | -0.001701 | -0.2537 | 0.0035866 | 0.001701 | south | N | 0.001701 | 0
9016 | SANDH_G1 | 1 | 49 | -0.006383 | south | 0.011485 | -0.001499 | -0.2535 | 0.0037886 | 0.001499 | south | N | 0.001499 | 0
9017 | SANDH_G2 | 2 | 46 | -0.006383 | south | 0.011485 | -0.001499 | -0.2535 | 0.0037886 | 0.001499 | south | N | 0.001499 | 0
9018 | SANDH_G3 | 3 | 46 | -0.006383 | south | 0.011485 | -0.001499 | -0.2535 | 0.0037886 | 0.001499 | south | N | 0.001499 | 0
9019 | SANDH_G4 | 4 | 47 | -0.006383 | south | 0.011485 | -0.001499 | -0.2535 | 0.0037886 | 0.001499 | south | N | 0.001499 | 0
9020 | SANDHG5A | 5A | 154 | -0.006383 | south | 0.011485 | -0.001499 | -0.2535 | 0.0037886 | 0.001499 | south | N | 0.001499 | 0
9021 | SANDHG5C | 5C | 148 | -0.006383 | south | 0.011485 | -0.001499 | -0.2535 | 0.0037886 | 0.001499 | south | N | 0.001499 | 0
9022 | SANDH_G6 | 6 | 48 | -0.006383 | south | 0.011485 | -0.001499 | -0.2535 | 0.0037886 | 0.001499 | south | N | 0.001499 | 0
9023 | SANDH_G7 | 7 | 48 | -0.006383 | south | 0.011485 | -0.001499 | -0.2535 | 0.0037886 | 0.001499 | south | N | 0.001499 | 0
11001 | NAV1CT | 1 | 70 | 0.32395 | west | 0.34182 | 0.32884 | 0.076836 | 0.33413 | 0.076836 | west | N | 0.076836 | 0
11009 | NAV2CT | 1 | 70 | 0.32395 | west | 0.34182 | 0.32884 | 0.076836 | 0.33413 | 0.076836 | west | N | 0.076836 | 0
11011 | NAV3ST | 1 | 92.8 | 0.32395 | west | 0.34182 | 0.32884 | 0.076836 | 0.33413 | 0.076836 | west | N | 0.076836 | 0
11012 | NAV4CT | 1 | 80 | 0.32395 | west | 0.34182 | 0.32884 | 0.076836 | 0.33413 | 0.076836 | west | N | 0.076836 | 0
11013 | NAV5CT | 1 | 80 | 0.32395 | west | 0.34182 | 0.32884 | 0.076836 | 0.33413 | 0.076836 | west | N | 0.076836 | 0
11014 | NAV6ST | 1 | 115 | 0.32395 | west | 0.34182 | 0.32884 | 0.076836 | 0.33413 | 0.076836 | west | N | 0.076836 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.32385 | west | 0.34172 | 0.32873 | 0.076733 | 0.33402 | 0.076733 | west | N | 0.076733 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.32385 | west | 0.34172 | 0.32873 | 0.076733 | 0.33402 | 0.076733 | west | N | 0.076733 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.32385 | west | 0.34172 | 0.32873 | 0.076733 | 0.33402 | 0.076733 | west | N | 0.076733 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.32385 | west | 0.34172 | 0.32873 | 0.076733 | 0.33402 | 0.076733 | west | N | 0.076733 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.32385 | west | 0.34172 | 0.32873 | 0.076733 | 0.33402 | 0.076733 | west | N | 0.076733 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.32385 | west | 0.34172 | 0.32873 | 0.076733 | 0.33402 | 0.076733 | west | N | 0.076733 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.41556 | west | 0.43342 | 0.42044 | 0.16844 | 0.42573 | 0.16844 | west | N | 0.16844 | 0
11057 | CHAMPION | 1 | 126.5 | 0.41556 | west | 0.43342 | 0.42044 | 0.16844 | 0.42573 | 0.16844 | west | N | 0.16844 | 0
11058 | PYRON_1G | 1 | 249 | 0.41556 | west | 0.43342 | 0.42044 | 0.16844 | 0.42573 | 0.16844 | west | N | 0.16844 | 0
11059 | INADALE_ | 1 | 197 | 0.41556 | west | 0.43342 | 0.42044 | 0.16844 | 0.42573 | 0.16844 | west | N | 0.16844 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.33328 | west | 0.35115 | 0.33816 | 0.086161 | 0.34345 | 0.086161 | west | N | 0.086161 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.33328 | west | 0.35115 | 0.33816 | 0.086161 | 0.34345 | 0.086161 | west | N | 0.086161 | 0
11147 | NOTREES_ | 1 | 149 | 0.31102 | west | 0.32888 | 0.3159 | 0.063898 | 0.32119 | 0.063898 | west | N | 0.063898 | 0
11309 | BULLCREK | 1 | 180 | 0.2905 | west | 0.30836 | 0.29538 | 0.043377 | 0.30067 | 0.043377 | west | N | 0.043377 | 0
11310 | BULLCREK | 1 | 180 | 0.2905 | west | 0.30836 | 0.29538 | 0.043377 | 0.30067 | 0.043377 | west | N | 0.043377 | 0
11320 | COYOTE_1 | 1 | 225 | 0.29129 | west | 0.30916 | 0.29617 | 0.044173 | 0.30146 | 0.044173 | west | N | 0.044173 | 0
11415 | LORAINE_ | 1 | 125 | 0.33579 | west | 0.35365 | 0.34067 | 0.088668 | 0.34596 | 0.088668 | west | N | 0.088668 | 0
11416 | LORAINE_ | 1 | 125 | 0.33579 | west | 0.35365 | 0.34067 | 0.088668 | 0.34596 | 0.088668 | west | N | 0.088668 | 0
11691 | KMICHICT | 1 | 140 | -0.019687 | north | -0.0018188 | -0.014803 | -0.26681 | -0.0095154 | 0.0018188 | North | N | 0.0018188 | 0
11692 | KMICHICT | 2 | 141 | -0.019687 | north | -0.0018188 | -0.014803 | -0.26681 | -0.0095154 | 0.0018188 | North | N | 0.0018188 | 0
11693 | KMICHIST | 3 | 309 | -0.019687 | north | -0.0018188 | -0.014803 | -0.26681 | -0.0095154 | 0.0018188 | North | N | 0.0018188 | 0
11694 | KMICHICT | 4 | 143 | -0.019687 | north | -0.0018188 | -0.014803 | -0.26681 | -0.0095154 | 0.0018188 | North | N | 0.0018188 | 0
11695 | KMICHICT | 5 | 144 | -0.019687 | north | -0.0018188 | -0.014803 | -0.26681 | -0.0095154 | 0.0018188 | North | N | 0.0018188 | 0
11696 | KMICHIST | 6 | 310 | -0.019687 | north | -0.0018188 | -0.014803 | -0.26681 | -0.0095154 | 0.0018188 | North | N | 0.0018188 | 0
12322 | ENNSTRAC | 1 | 196 | -0.017255 | north | 0.0006132 | -0.012371 | -0.26437 | -0.0070834 | 0.0006132 | North | N | 0.0006132 | 0
12323 | ENNSTRAC | 2 | 111 | -0.017255 | north | 0.0006132 | -0.012371 | -0.26437 | -0.0070834 | 0.0006132 | North | N | 0.0006132 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.01989 | north | -0.0020218 | -0.015006 | -0.26701 | -0.0097184 | 0.0020218 | North | N | 0.0020218 | 0
12411 | FPLEFR1A | 1 | 161 | -0.018826 | north | -0.0009578 | -0.013942 | -0.26594 | -0.0086544 | 0.0009578 | North | N | 0.0009578 | 0
12412 | FPLEFR1B | 2 | 164 | -0.018826 | north | -0.0009578 | -0.013942 | -0.26594 | -0.0086544 | 0.0009578 | North | N | 0.0009578 | 0
12413 | FPLEFR1C | 3 | 164 | -0.018826 | north | -0.0009578 | -0.013942 | -0.26594 | -0.0086544 | 0.0009578 | North | N | 0.0009578 | 0
12414 | FPLEFR1S | 4 | 414 | -0.018826 | north | -0.0009578 | -0.013942 | -0.26594 | -0.0086544 | 0.0009578 | North | N | 0.0009578 | 0
12421 | FPLEFR2A | 1 | 162 | -0.018826 | north | -0.0009578 | -0.013942 | -0.26594 | -0.0086544 | 0.0009578 | North | N | 0.0009578 | 0
12422 | FPLEFR2B | 2 | 161 | -0.018826 | north | -0.0009578 | -0.013942 | -0.26594 | -0.0086544 | 0.0009578 | North | N | 0.0009578 | 0
12423 | FPLEFR2C | 3 | 163 | -0.018826 | north | -0.0009578 | -0.013942 | -0.26594 | -0.0086544 | 0.0009578 | North | N | 0.0009578 | 0
12424 | FPLEFR2S | 4 | 409 | -0.018826 | north | -0.0009578 | -0.013942 | -0.26594 | -0.0086544 | 0.0009578 | North | N | 0.0009578 | 0
12440 | PARKD_1S | 1 | 0 | -0.018811 | north | -0.0009428 | -0.013927 | -0.26593 | -0.0086394 | 0.0009428 | North | N | 0.0009428 | 0
12449 | PARKD_2S | 1 | 0 | -0.018811 | north | -0.0009428 | -0.013927 | -0.26593 | -0.0086394 | 0.0009428 | North | N | 0.0009428 | 0
13116 | TGATEWAY | 1 | 148 | -0.0177 | north | 0.0001682 | -0.012816 | -0.26482 | -0.0075284 | 0.0001682 | North | N | 0.0001682 | 0
13117 | TGATEWAY | 2 | 130 | -0.0177 | north | 0.0001682 | -0.012816 | -0.26482 | -0.0075284 | 0.0001682 | North | N | 0.0001682 | 0
13118 | TGATEWAY | 3 | 145 | -0.0177 | north | 0.0001682 | -0.012816 | -0.26482 | -0.0075284 | 0.0001682 | North | N | 0.0001682 | 0
13119 | TGATEWAY | 4 | 399 | -0.0177 | north | 0.0001682 | -0.012816 | -0.26482 | -0.0075284 | 0.0001682 | North | N | 0.0001682 | 0
13131 | CALFREST | 1 | 150.7 | -0.016374 | north | 0.0014942 | -0.01149 | -0.26349 | -0.0062024 | 0.0014942 | North | N | 0.0014942 | 0
13132 | CALFREST | 2 | 151 | -0.016374 | north | 0.0014942 | -0.01149 | -0.26349 | -0.0062024 | 0.0014942 | North | N | 0.0014942 | 0
13133 | CALFREST | 3 | 177.4 | -0.016374 | north | 0.0014942 | -0.01149 | -0.26349 | -0.0062024 | 0.0014942 | North | N | 0.0014942 | 0
13134 | CALFREST | 4 | 151.5 | -0.016423 | north | 0.0014452 | -0.011539 | -0.26354 | -0.0062514 | 0.0014452 | North | N | 0.0014452 | 0
13135 | CALFREST | 5 | 152.3 | -0.016423 | north | 0.0014452 | -0.011539 | -0.26354 | -0.0062514 | 0.0014452 | North | N | 0.0014452 | 0
13136 | CALFREST | 6 | 177.5 | -0.016423 | north | 0.0014452 | -0.011539 | -0.26354 | -0.0062514 | 0.0014452 | North | N | 0.0014452 | 0
13432 | SANDOW_5 | 5 | 581 | -0.008868 | south | 0.0090002 | -0.003984 | -0.25599 | 0.0013036 | 0.0013036 | houston | Y | 0.003984 | 1.5573
13691 | OAKGROVE | 1 | 855 | -0.014316 | north | 0.0035522 | -0.009432 | -0.26143 | -0.0041444 | 0.0035522 | North | N | 0.0035522 | 0
13692 | OAKGROVE | 2 | 855 | -0.014316 | north | 0.0035522 | -0.009432 | -0.26143 | -0.0041444 | 0.0035522 | North | N | 0.0035522 | 0
32798 | BRYN_TAM | 1 | 32 | -0.013091 | north | 0.0047772 | -0.008207 | -0.26021 | -0.0029194 | 0.0029194 | houston | Y | 0.0047772 | 0.059451
32883 | BRYN_DNS | 1 | 48 | -0.013072 | north | 0.0047962 | -0.008188 | -0.26019 | -0.0029004 | 0.0029004 | houston | Y | 0.0047962 | 0.091
32884 | BRYN_DNS | 1 | 46 | -0.013072 | north | 0.0047962 | -0.008188 | -0.26019 | -0.0029004 | 0.0029004 | houston | Y | 0.0047962 | 0.087208
32886 | BRYN_ATK | MB | 12 | -0.013099 | north | 0.0047692 | -0.008215 | -0.26022 | -0.0029274 | 0.0029274 | houston | Y | 0.0047692 | 0.022102
32887 | BRYN_ATK | MB | 51 | -0.013099 | north | 0.0047692 | -0.008215 | -0.26022 | -0.0029274 | 0.0029274 | houston | Y | 0.0047692 | 0.093934
32888 | BRYN_ATK | 1 | 17 | -0.013099 | north | 0.0047692 | -0.008215 | -0.26022 | -0.0029274 | 0.0029274 | houston | Y | 0.0047692 | 0.031311
32890 | BRYN_ATK | MB | 22 | -0.013099 | north | 0.0047692 | -0.008215 | -0.26022 | -0.0029274 | 0.0029274 | houston | Y | 0.0047692 | 0.04052
32891 | BRYN_ATK | MB | 25 | -0.013099 | north | 0.0047692 | -0.008215 | -0.26022 | -0.0029274 | 0.0029274 | houston | Y | 0.0047692 | 0.046046
32892 | BRYN_DNS | 1 | 105 | -0.013072 | north | 0.0047962 | -0.008188 | -0.26019 | -0.0029004 | 0.0029004 | houston | Y | 0.0047962 | 0.19906
36998 | RDCNYNG1 | 1 | 84 | 0.26163 | west | 0.2795 | 0.26652 | 0.014515 | 0.2718 | 0.014515 | west | N | 0.014515 | 0
38332 | WDWRDU2 | 1 | 80 | 0.27661 | west | 0.29448 | 0.28149 | 0.029493 | 0.28678 | 0.029493 | west | N | 0.029493 | 0
38437 | TNSRBNMS | 1 | 150 | 0.27627 | west | 0.29414 | 0.28116 | 0.029154 | 0.28644 | 0.029154 | west | N | 0.029154 | 0
38438 | TNSRBNMS | 1 | 150 | 0.27627 | west | 0.29414 | 0.28116 | 0.029154 | 0.28644 | 0.029154 | west | N | 0.029154 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.010095 | houston | 0.0077732 | -0.005211 | -0.25721 | 7.6635e-05 | 7.6635e-05 | houston | N | 7.6635e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.010095 | houston | 0.0077732 | -0.005211 | -0.25721 | 7.6635e-05 | 7.6635e-05 | houston | N | 7.6635e-05 | 0
38600 | TNBP_CGN | 5 | 53 | -0.010095 | houston | 0.0077732 | -0.005211 | -0.25721 | 7.6635e-05 | 7.6635e-05 | houston | N | 7.6635e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.010095 | houston | 0.0077732 | -0.005211 | -0.25721 | 7.6635e-05 | 7.6635e-05 | houston | N | 7.6635e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.010095 | houston | 0.0077732 | -0.005211 | -0.25721 | 7.6635e-05 | 7.6635e-05 | houston | N | 7.6635e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.010095 | houston | 0.0077732 | -0.005211 | -0.25721 | 7.6635e-05 | 7.6635e-05 | houston | N | 7.6635e-05 | 0
38614 | TNBPAMCG | 4 | 96 | -0.010095 | houston | 0.0077732 | -0.005211 | -0.25721 | 7.6635e-05 | 7.6635e-05 | houston | N | 7.6635e-05 | 0
38615 | TNBPAMCG | 1 | 244 | -0.010095 | houston | 0.0077732 | -0.005211 | -0.25721 | 7.6635e-05 | 7.6635e-05 | houston | N | 7.6635e-05 | 0
38690 | TNBP_CGN | 3 | 40 | -0.010095 | houston | 0.0077732 | -0.005211 | -0.25721 | 7.6635e-05 | 7.6635e-05 | houston | N | 7.6635e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.010094 | houston | 0.0077742 | -0.00521 | -0.25721 | 7.7635e-05 | 7.7635e-05 | houston | N | 7.7635e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.010094 | houston | 0.0077742 | -0.00521 | -0.25721 | 7.7635e-05 | 7.7635e-05 | houston | N | 7.7635e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.010094 | houston | 0.0077742 | -0.00521 | -0.25721 | 7.7635e-05 | 7.7635e-05 | houston | N | 7.7635e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.010094 | houston | 0.0077742 | -0.00521 | -0.25721 | 7.7635e-05 | 7.7635e-05 | houston | N | 7.7635e-05 | 0
39470 | TNDOWCGN | 1 | 32 | -0.010094 | houston | 0.0077742 | -0.00521 | -0.25721 | 7.7635e-05 | 7.7635e-05 | houston | N | 7.7635e-05 | 0
39480 | TNDOWCGN | 1 | 30 | -0.010094 | houston | 0.0077742 | -0.00521 | -0.25721 | 7.7635e-05 | 7.7635e-05 | houston | N | 7.7635e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.009425 | houston | 0.0084432 | -0.004541 | -0.25654 | 0.00074664 | 0.00074664 | houston | N | 0.00074664 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.009425 | houston | 0.0084432 | -0.004541 | -0.25654 | 0.00074664 | 0.00074664 | houston | N | 0.00074664 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.009425 | houston | 0.0084432 | -0.004541 | -0.25654 | 0.00074664 | 0.00074664 | houston | N | 0.00074664 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.009425 | houston | 0.0084432 | -0.004541 | -0.25654 | 0.00074664 | 0.00074664 | houston | N | 0.00074664 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.014316 | north | 0.0035522 | -0.009432 | -0.26143 | -0.0041444 | 0.0035522 | North | N | 0.0035522 | 0
39970 | TNTNPONE | 1 | 153 | -0.014316 | north | 0.0035522 | -0.009432 | -0.26143 | -0.0041444 | 0.0035522 | North | N | 0.0035522 | 0
48500 | APD_GT1_ | 1 | 136 | -0.010493 | houston | 0.0073752 | -0.005609 | -0.25761 | -0.00032136 | 0.00032136 | houston | N | 0.00032136 | 0
48510 | AK_GT1__ | 1 | 33 | -0.009872 | houston | 0.0079962 | -0.004988 | -0.25699 | 0.00029964 | 0.00029964 | houston | N | 0.00029964 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.010491 | houston | 0.0073772 | -0.005607 | -0.25761 | -0.00031936 | 0.00031936 | houston | N | 0.00031936 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.010491 | houston | 0.0073772 | -0.005607 | -0.25761 | -0.00031936 | 0.00031936 | houston | N | 0.00031936 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.010491 | houston | 0.0073772 | -0.005607 | -0.25761 | -0.00031936 | 0.00031936 | houston | N | 0.00031936 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.010491 | houston | 0.0073772 | -0.005607 | -0.25761 | -0.00031936 | 0.00031936 | houston | N | 0.00031936 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.009304 | houston | 0.0085642 | -0.00442 | -0.25642 | 0.00086764 | 0.00086764 | houston | N | 0.00086764 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.009304 | houston | 0.0085642 | -0.00442 | -0.25642 | 0.00086764 | 0.00086764 | houston | N | 0.00086764 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.009858 | houston | 0.0080102 | -0.004974 | -0.25698 | 0.00031364 | 0.00031364 | houston | N | 0.00031364 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.009858 | houston | 0.0080102 | -0.004974 | -0.25698 | 0.00031364 | 0.00031364 | houston | N | 0.00031364 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.009858 | houston | 0.0080102 | -0.004974 | -0.25698 | 0.00031364 | 0.00031364 | houston | N | 0.00031364 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.010342 | houston | 0.0075262 | -0.005458 | -0.25746 | -0.00017036 | 0.00017036 | houston | N | 0.00017036 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.010342 | houston | 0.0075262 | -0.005458 | -0.25746 | -0.00017036 | 0.00017036 | houston | N | 0.00017036 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.010342 | houston | 0.0075262 | -0.005458 | -0.25746 | -0.00017036 | 0.00017036 | houston | N | 0.00017036 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.010342 | houston | 0.0075262 | -0.005458 | -0.25746 | -0.00017036 | 0.00017036 | houston | N | 0.00017036 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.010439 | houston | 0.0074292 | -0.005555 | -0.25756 | -0.00026736 | 0.00026736 | houston | N | 0.00026736 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.010439 | houston | 0.0074292 | -0.005555 | -0.25756 | -0.00026736 | 0.00026736 | houston | N | 0.00026736 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.010314 | houston | 0.0075542 | -0.00543 | -0.25743 | -0.00014236 | 0.00014236 | houston | N | 0.00014236 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.010314 | houston | 0.0075542 | -0.00543 | -0.25743 | -0.00014236 | 0.00014236 | houston | N | 0.00014236 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.010314 | houston | 0.0075542 | -0.00543 | -0.25743 | -0.00014236 | 0.00014236 | houston | N | 0.00014236 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.010314 | houston | 0.0075542 | -0.00543 | -0.25743 | -0.00014236 | 0.00014236 | houston | N | 0.00014236 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.010314 | houston | 0.0075542 | -0.00543 | -0.25743 | -0.00014236 | 0.00014236 | houston | N | 0.00014236 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.01061 | houston | 0.0072582 | -0.005726 | -0.25773 | -0.00043836 | 0.00043836 | houston | N | 0.00043836 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.010562 | houston | 0.0073062 | -0.005678 | -0.25768 | -0.00039036 | 0.00039036 | houston | N | 0.00039036 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.010624 | houston | 0.0072442 | -0.00574 | -0.25774 | -0.00045236 | 0.00045236 | houston | N | 0.00045236 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.010624 | houston | 0.0072442 | -0.00574 | -0.25774 | -0.00045236 | 0.00045236 | houston | N | 0.00045236 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.010624 | houston | 0.0072442 | -0.00574 | -0.25774 | -0.00045236 | 0.00045236 | houston | N | 0.00045236 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.010891 | houston | 0.0069772 | -0.006007 | -0.25801 | -0.00071936 | 0.00071936 | houston | N | 0.00071936 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.010502 | houston | 0.0073662 | -0.005618 | -0.25762 | -0.00033036 | 0.00033036 | houston | N | 0.00033036 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.010502 | houston | 0.0073662 | -0.005618 | -0.25762 | -0.00033036 | 0.00033036 | houston | N | 0.00033036 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.010658 | houston | 0.0072102 | -0.005774 | -0.25778 | -0.00048636 | 0.00048636 | houston | N | 0.00048636 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.010658 | houston | 0.0072102 | -0.005774 | -0.25778 | -0.00048636 | 0.00048636 | houston | N | 0.00048636 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.010658 | houston | 0.0072102 | -0.005774 | -0.25778 | -0.00048636 | 0.00048636 | houston | N | 0.00048636 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.010658 | houston | 0.0072102 | -0.005774 | -0.25778 | -0.00048636 | 0.00048636 | houston | N | 0.00048636 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.010442 | houston | 0.0074262 | -0.005558 | -0.25756 | -0.00027036 | 0.00027036 | houston | N | 0.00027036 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.010442 | houston | 0.0074262 | -0.005558 | -0.25756 | -0.00027036 | 0.00027036 | houston | N | 0.00027036 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.010442 | houston | 0.0074262 | -0.005558 | -0.25756 | -0.00027036 | 0.00027036 | houston | N | 0.00027036 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.010442 | houston | 0.0074262 | -0.005558 | -0.25756 | -0.00027036 | 0.00027036 | houston | N | 0.00027036 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.010408 | houston | 0.0074602 | -0.005524 | -0.25753 | -0.00023636 | 0.00023636 | houston | N | 0.00023636 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.010408 | houston | 0.0074602 | -0.005524 | -0.25753 | -0.00023636 | 0.00023636 | houston | N | 0.00023636 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.010408 | houston | 0.0074602 | -0.005524 | -0.25753 | -0.00023636 | 0.00023636 | houston | N | 0.00023636 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.010408 | houston | 0.0074602 | -0.005524 | -0.25753 | -0.00023636 | 0.00023636 | houston | N | 0.00023636 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.010408 | houston | 0.0074602 | -0.005524 | -0.25753 | -0.00023636 | 0.00023636 | houston | N | 0.00023636 | 0
48651 | EP_1_2 | 1 | 5 | -0.010608 | houston | 0.0072602 | -0.005724 | -0.25773 | -0.00043636 | 0.00043636 | houston | N | 0.00043636 | 0
48651 | EP_1_2 | 2 | 21 | -0.010608 | houston | 0.0072602 | -0.005724 | -0.25773 | -0.00043636 | 0.00043636 | houston | N | 0.00043636 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.012716 | north | 0.0051522 | -0.007832 | -0.25983 | -0.0025444 | 0.0025444 | houston | Y | 0.0051522 | 0.40213
48672 | FTR_GT2_ | 2 | 156 | -0.012716 | north | 0.0051522 | -0.007832 | -0.25983 | -0.0025444 | 0.0025444 | houston | Y | 0.0051522 | 0.40682
48673 | FTR_GT3_ | 3 | 156 | -0.012716 | north | 0.0051522 | -0.007832 | -0.25983 | -0.0025444 | 0.0025444 | houston | Y | 0.0051522 | 0.40682
48674 | FTR_CN4_ | 4 | 380 | -0.012716 | north | 0.0051522 | -0.007832 | -0.25983 | -0.0025444 | 0.0025444 | houston | Y | 0.0051522 | 0.99098
48690 | GBY_GN5_ | 5 | 398 | -0.010673 | houston | 0.0071952 | -0.005789 | -0.25779 | -0.00050136 | 0.00050136 | houston | N | 0.00050136 | 0
48691 | GBY_7374 | A | 46 | -0.010394 | houston | 0.0074742 | -0.00551 | -0.25751 | -0.00022236 | 0.00022236 | houston | N | 0.00022236 | 0
48691 | GBY_7374 | B | 46 | -0.010394 | houston | 0.0074742 | -0.00551 | -0.25751 | -0.00022236 | 0.00022236 | houston | N | 0.00022236 | 0
48692 | GBY_8182 | C | 46 | -0.010394 | houston | 0.0074742 | -0.00551 | -0.25751 | -0.00022236 | 0.00022236 | houston | N | 0.00022236 | 0
48692 | GBY_8182 | D | 55 | -0.010394 | houston | 0.0074742 | -0.00551 | -0.25751 | -0.00022236 | 0.00022236 | houston | N | 0.00022236 | 0
48693 | GBY_8384 | E | 55 | -0.010394 | houston | 0.0074742 | -0.00551 | -0.25751 | -0.00022236 | 0.00022236 | houston | N | 0.00022236 | 0
48693 | GBY_8384 | F | 54 | -0.010394 | houston | 0.0074742 | -0.00551 | -0.25751 | -0.00022236 | 0.00022236 | houston | N | 0.00022236 | 0
48721 | LEG_1___ | 1 | 827 | -0.014808 | north | 0.0030602 | -0.009924 | -0.26193 | -0.0046364 | 0.0030602 | North | N | 0.0030602 | 0
48722 | LEG_2___ | 2 | 819 | -0.014808 | north | 0.0030602 | -0.009924 | -0.26193 | -0.0046364 | 0.0030602 | North | N | 0.0030602 | 0
48730 | MNS_GT | 1 | 46.1 | -0.009814 | houston | 0.0080542 | -0.00493 | -0.25693 | 0.00035764 | 0.00035764 | houston | N | 0.00035764 | 0
48731 | CBE_GT1 | 1 | 76 | -0.008476 | houston | 0.0093922 | -0.003592 | -0.25559 | 0.0016956 | 0.0016956 | houston | N | 0.0016956 | 0
48732 | CBE_GT2 | 1 | 76 | -0.008476 | houston | 0.0093922 | -0.003592 | -0.25559 | 0.0016956 | 0.0016956 | houston | N | 0.0016956 | 0
48733 | CBE_ST12 | 1 | 105 | -0.008476 | houston | 0.0093922 | -0.003592 | -0.25559 | 0.0016956 | 0.0016956 | houston | N | 0.0016956 | 0
48734 | CBE_GT3 | 1 | 74 | -0.008476 | houston | 0.0093922 | -0.003592 | -0.25559 | 0.0016956 | 0.0016956 | houston | N | 0.0016956 | 0
48735 | CBE_GT4 | 1 | 74 | -0.008476 | houston | 0.0093922 | -0.003592 | -0.25559 | 0.0016956 | 0.0016956 | houston | N | 0.0016956 | 0
48736 | CBE_ST34 | 1 | 102 | -0.008476 | houston | 0.0093922 | -0.003592 | -0.25559 | 0.0016956 | 0.0016956 | houston | N | 0.0016956 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.010443 | houston | 0.0074252 | -0.005559 | -0.25756 | -0.00027136 | 0.00027136 | houston | N | 0.00027136 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.010443 | houston | 0.0074252 | -0.005559 | -0.25756 | -0.00027136 | 0.00027136 | houston | N | 0.00027136 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.010443 | houston | 0.0074252 | -0.005559 | -0.25756 | -0.00027136 | 0.00027136 | houston | N | 0.00027136 | 0
48761 | PR_GT1__ | 1 | 35 | -0.010424 | houston | 0.0074442 | -0.00554 | -0.25754 | -0.00025236 | 0.00025236 | houston | N | 0.00025236 | 0
48772 | PHR_GN2_ | MB | 459 | -0.010239 | houston | 0.0076292 | -0.005355 | -0.25736 | -6.7365e-05 | 6.7365e-05 | houston | N | 6.7365e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.01061 | houston | 0.0072582 | -0.005726 | -0.25773 | -0.00043836 | 0.00043836 | houston | N | 0.00043836 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.01061 | houston | 0.0072582 | -0.005726 | -0.25773 | -0.00043836 | 0.00043836 | houston | N | 0.00043836 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.01061 | houston | 0.0072582 | -0.005726 | -0.25773 | -0.00043836 | 0.00043836 | houston | N | 0.00043836 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.01061 | houston | 0.0072582 | -0.005726 | -0.25773 | -0.00043836 | 0.00043836 | houston | N | 0.00043836 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.01061 | houston | 0.0072582 | -0.005726 | -0.25773 | -0.00043836 | 0.00043836 | houston | N | 0.00043836 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.01061 | houston | 0.0072582 | -0.005726 | -0.25773 | -0.00043836 | 0.00043836 | houston | N | 0.00043836 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.01061 | houston | 0.0072582 | -0.005726 | -0.25773 | -0.00043836 | 0.00043836 | houston | N | 0.00043836 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.010891 | houston | 0.0069772 | -0.006007 | -0.25801 | -0.00071936 | 0.00071936 | houston | N | 0.00071936 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.010891 | houston | 0.0069772 | -0.006007 | -0.25801 | -0.00071936 | 0.00071936 | houston | N | 0.00071936 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.010891 | houston | 0.0069772 | -0.006007 | -0.25801 | -0.00071936 | 0.00071936 | houston | N | 0.00071936 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.010891 | houston | 0.0069772 | -0.006007 | -0.25801 | -0.00071936 | 0.00071936 | houston | N | 0.00071936 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.010621 | houston | 0.0072472 | -0.005737 | -0.25774 | -0.00044936 | 0.00044936 | houston | N | 0.00044936 | 0
48820 | SHELLG1_ | 1 | 71 | -0.010461 | houston | 0.0074072 | -0.005577 | -0.25758 | -0.00028936 | 0.00028936 | houston | N | 0.00028936 | 0
48821 | SHELLG2 | 2 | 72 | -0.010461 | houston | 0.0074072 | -0.005577 | -0.25758 | -0.00028936 | 0.00028936 | houston | N | 0.00028936 | 0
48822 | SHELLG3_ | 1 | 39 | -0.010461 | houston | 0.0074072 | -0.005577 | -0.25758 | -0.00028936 | 0.00028936 | houston | N | 0.00028936 | 0
48822 | SHELLG3_ | 2 | 30 | -0.010461 | houston | 0.0074072 | -0.005577 | -0.25758 | -0.00028936 | 0.00028936 | houston | N | 0.00028936 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.010396 | houston | 0.0074722 | -0.005512 | -0.25751 | -0.00022436 | 0.00022436 | houston | N | 0.00022436 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.010396 | houston | 0.0074722 | -0.005512 | -0.25751 | -0.00022436 | 0.00022436 | houston | N | 0.00022436 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.010442 | houston | 0.0074262 | -0.005558 | -0.25756 | -0.00027036 | 0.00027036 | houston | N | 0.00027036 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.010438 | houston | 0.0074302 | -0.005554 | -0.25756 | -0.00026636 | 0.00026636 | houston | N | 0.00026636 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.010437 | houston | 0.0074312 | -0.005553 | -0.25756 | -0.00026536 | 0.00026536 | houston | N | 0.00026536 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.010441 | houston | 0.0074272 | -0.005557 | -0.25756 | -0.00026936 | 0.00026936 | houston | N | 0.00026936 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.010442 | houston | 0.0074262 | -0.005558 | -0.25756 | -0.00027036 | 0.00027036 | houston | N | 0.00027036 | 0
48855 | SRB_GT21 | B2 | 12 | -0.010436 | houston | 0.0074322 | -0.005552 | -0.25755 | -0.00026436 | 0.00026436 | houston | N | 0.00026436 | 0
48855 | SRB_GT21 | MB | 18 | -0.010436 | houston | 0.0074322 | -0.005552 | -0.25755 | -0.00026436 | 0.00026436 | houston | N | 0.00026436 | 0
48865 | TECO_GT1 | 1 | 50 | -0.010189 | houston | 0.0076792 | -0.005305 | -0.25731 | -1.7365e-05 | 1.7365e-05 | houston | N | 1.7365e-05 | 0
48873 | THW_ST3_ | 3 | 104 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48874 | THW_ST4_ | 4 | 104 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48875 | THW_3132 | A | 54 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48875 | THW_3132 | B | 53 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48877 | THW_3334 | C | 54 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48877 | THW_3334 | D | 57 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48879 | THW_4142 | E | 54 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48879 | THW_4142 | F | 54 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48881 | THW_4344 | G | 58 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48881 | THW_4344 | H | 58 | -0.010554 | houston | 0.0073142 | -0.00567 | -0.25767 | -0.00038236 | 0.00038236 | houston | N | 0.00038236 | 0
48883 | THW_GT1_ | B2 | 12 | -0.010596 | houston | 0.0072722 | -0.005712 | -0.25771 | -0.00042436 | 0.00042436 | houston | N | 0.00042436 | 0
48885 | THW_5152 | A | 56 | -0.010695 | houston | 0.0071732 | -0.005811 | -0.25781 | -0.00052336 | 0.00052336 | houston | N | 0.00052336 | 0
48885 | THW_5152 | B | 59 | -0.010695 | houston | 0.0071732 | -0.005811 | -0.25781 | -0.00052336 | 0.00052336 | houston | N | 0.00052336 | 0
48886 | THW_5354 | C | 56 | -0.010695 | houston | 0.0071732 | -0.005811 | -0.25781 | -0.00052336 | 0.00052336 | houston | N | 0.00052336 | 0
48886 | THW_5354 | D | 56 | -0.010695 | houston | 0.0071732 | -0.005811 | -0.25781 | -0.00052336 | 0.00052336 | houston | N | 0.00052336 | 0
48887 | THW_5556 | E | 59 | -0.010695 | houston | 0.0071732 | -0.005811 | -0.25781 | -0.00052336 | 0.00052336 | houston | N | 0.00052336 | 0
48887 | THW_5556 | F | 56 | -0.010695 | houston | 0.0071732 | -0.005811 | -0.25781 | -0.00052336 | 0.00052336 | houston | N | 0.00052336 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.008561 | houston | 0.0093072 | -0.003677 | -0.25568 | 0.0016106 | 0.0016106 | houston | N | 0.0016106 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.009931 | houston | 0.0079372 | -0.005047 | -0.25705 | 0.00024064 | 0.00024064 | houston | N | 0.00024064 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.009931 | houston | 0.0079372 | -0.005047 | -0.25705 | 0.00024064 | 0.00024064 | houston | N | 0.00024064 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.009931 | houston | 0.0079372 | -0.005047 | -0.25705 | 0.00024064 | 0.00024064 | houston | N | 0.00024064 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.009931 | houston | 0.0079372 | -0.005047 | -0.25705 | 0.00024064 | 0.00024064 | houston | N | 0.00024064 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.009931 | houston | 0.0079372 | -0.005047 | -0.25705 | 0.00024064 | 0.00024064 | houston | N | 0.00024064 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.009855 | houston | 0.0080132 | -0.004971 | -0.25697 | 0.00031664 | 0.00031664 | houston | N | 0.00031664 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.009855 | houston | 0.0080132 | -0.004971 | -0.25697 | 0.00031664 | 0.00031664 | houston | N | 0.00031664 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.009855 | houston | 0.0080132 | -0.004971 | -0.25697 | 0.00031664 | 0.00031664 | houston | N | 0.00031664 | 0
48929 | WAPGT21_ | B1 | 13 | -0.009931 | houston | 0.0079372 | -0.005047 | -0.25705 | 0.00024064 | 0.00024064 | houston | N | 0.00024064 | 0
48940 | WARVUE_G | G1 | 12 | -0.010609 | houston | 0.0072592 | -0.005725 | -0.25773 | -0.00043736 | 0.00043736 | houston | N | 0.00043736 | 0
49803 | EXN_15GT | 1 | 34 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49826 | EXN938GT | 5 | 45.9 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49828 | EXN941GT | 10 | 17.7 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49829 | EXN942GT | 11 | 20.4 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49830 | EXN943GT | 12 | 19.9 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49831 | EXN944GT | 13 | 35 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49832 | EXN945GT | 9 | 18 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49837 | EXN_GT | 4 | 85.4 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49838 | EXN_14GT | 14 | 148 | -0.010574 | houston | 0.0072942 | -0.00569 | -0.25769 | -0.00040236 | 0.00040236 | houston | N | 0.00040236 | 0
49851 | DOW17000 | 37 | 62 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49858 | DOW38100 | 31 | 71.4 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49859 | DOW38200 | 33 | 45 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49860 | DOW38300 | 32 | 101 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49862 | DOW39100 | 36 | 86 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49863 | DOW39200 | 35 | 88 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49865 | DOW41000 | 41 | 50 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49866 | DOW42000 | 42 | 18 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49869 | DOW49000 | 45 | 94 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49870 | DOW61000 | 61 | 70 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49871 | DOW62000 | 62 | 63 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49872 | DOW63000 | 63 | 72 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49873 | DOW64000 | 64 | 64.8 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49876 | DOW65000 | 65 | 101 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49877 | DOW66000 | 66 | 97 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49878 | DOW67000 | 67 | 103 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49882 | DOW81000 | 81 | 76 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49884 | DOW82000 | 82 | 80 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49885 | DOW83000 | 83 | 80 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
49886 | DOW84000 | 84 | 171 | -0.009162 | houston | 0.0087062 | -0.004278 | -0.25628 | 0.0010096 | 0.0010096 | houston | N | 0.0010096 | 0
58909 | PEARSALL | 1 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58909 | PEARSALL | 2 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58909 | PEARSALL | 3 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58909 | PEARSALL | 4 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58909 | PEARSALL | 5 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58909 | PEARSALL | 6 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58919 | PEARSALL | 1 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58919 | PEARSALL | 2 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58919 | PEARSALL | 3 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58919 | PEARSALL | 4 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58919 | PEARSALL | 5 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58919 | PEARSALL | 6 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58929 | PEARSALL | 1 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58929 | PEARSALL | 2 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58929 | PEARSALL | 3 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58929 | PEARSALL | 4 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58929 | PEARSALL | 5 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58929 | PEARSALL | 6 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58949 | PEARSALL | 1 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58949 | PEARSALL | 2 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58949 | PEARSALL | 3 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58949 | PEARSALL | 4 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58949 | PEARSALL | 5 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
58949 | PEARSALL | 6 | 8.4 | 0.005811 | south | 0.023679 | 0.010695 | -0.24131 | 0.015983 | 0.010695 | south | N | 0.010695 | 0
60000 | DSKY2 | 1 | 76.5 | 0.25979 | west | 0.27766 | 0.26467 | 0.01267 | 0.26996 | 0.01267 | west | N | 0.01267 | 0
60003 | KING_NE1 | 1 | 80 | 0.27709 | west | 0.29496 | 0.28198 | 0.029975 | 0.28726 | 0.029975 | west | N | 0.029975 | 0
60005 | KING_SE1 | 1 | 40 | 0.27709 | west | 0.29496 | 0.28198 | 0.029975 | 0.28726 | 0.029975 | west | N | 0.029975 | 0
60007 | KING_SW1 | 1 | 80 | 0.27929 | west | 0.29716 | 0.28417 | 0.032173 | 0.28946 | 0.032173 | west | N | 0.032173 | 0
60016 | WOODWRD1 | 1 | 80 | 0.27669 | west | 0.29456 | 0.28157 | 0.02957 | 0.28686 | 0.02957 | west | N | 0.02957 | 0
60017 | ORNNWP1 | 1 | 80 | 0.26453 | west | 0.2824 | 0.26941 | 0.017411 | 0.2747 | 0.017411 | west | N | 0.017411 | 0
60018 | DSKY1 | 1 | 84 | 0.26057 | west | 0.27844 | 0.26545 | 0.013449 | 0.27074 | 0.013449 | west | N | 0.013449 | 0
60019 | KING_NW1 | 1 | 80 | 0.27929 | west | 0.29716 | 0.28417 | 0.032173 | 0.28946 | 0.032173 | west | N | 0.032173 | 0
60057 | CALLAHAN | 1 | 114 | -0.003357 | south | 0.014511 | 0.001527 | -0.25048 | 0.0068146 | 0.001527 | south | N | 0.001527 | 0
60058 | BUFF_GAP | 1 | 120 | 0.076813 | west | 0.094681 | 0.081697 | -0.17031 | 0.086985 | 0.081697 | south | Y | 0.17031 | 10.633
60060 | CIRELLO | 1 | 233 | 0.076813 | west | 0.094681 | 0.081697 | -0.17031 | 0.086985 | 0.081697 | south | Y | 0.17031 | 20.6457
60063 | BUFF_GAP | 1 | 170.2 | 0.076813 | west | 0.094681 | 0.081697 | -0.17031 | 0.086985 | 0.081697 | south | Y | 0.17031 | 15.0811
60066 | H_HOLLOW | 1 | 222 | -0.003357 | south | 0.014511 | 0.001527 | -0.25048 | 0.0068146 | 0.001527 | south | N | 0.001527 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.003357 | south | 0.014511 | 0.001527 | -0.25048 | 0.0068146 | 0.001527 | south | N | 0.001527 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.003357 | south | 0.014511 | 0.001527 | -0.25048 | 0.0068146 | 0.001527 | south | N | 0.001527 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.003357 | south | 0.014511 | 0.001527 | -0.25048 | 0.0068146 | 0.001527 | south | N | 0.001527 | 0
60074 | HORSH5 | 1 | 100 | -0.003357 | south | 0.014511 | 0.001527 | -0.25048 | 0.0068146 | 0.001527 | south | N | 0.001527 | 0
60081 | WHRLWIND | 1 | 60 | 0.11925 | west | 0.13712 | 0.12414 | -0.12786 | 0.12943 | 0.12414 | south | Y | 0.12786 | 0.22345
60201 | RIO DRCS | F | 0 | 0.045609 | south | 0.063477 | 0.050493 | -0.20151 | 0.055781 | 0.050493 | south | N | 0.050493 | 0
60202 | FRIEND_R | F | 0 | 0.19886 | west | 0.21673 | 0.20374 | -0.048257 | 0.20903 | 0.048257 | west | N | 0.048257 | 0
60203 | PRES0A | BT | 4.8 | 0.28983 | west | 0.3077 | 0.29472 | 0.042714 | 0.3 | 0.042714 | west | N | 0.042714 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.33579 | west | 0.35365 | 0.34067 | 0.088668 | 0.34596 | 0.088668 | west | N | 0.088668 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.33579 | west | 0.35365 | 0.34067 | 0.088668 | 0.34596 | 0.088668 | west | N | 0.088668 | 0
71057 | L_SWEETW | W1 | 135 | 0.33579 | west | 0.35365 | 0.34067 | 0.088668 | 0.34596 | 0.088668 | west | N | 0.088668 | 0
71059 | L_SWEETW | W1 | 119 | 0.33579 | west | 0.35365 | 0.34067 | 0.088668 | 0.34596 | 0.088668 | west | N | 0.088668 | 0
71060 | L_SWEETW | W1 | 105 | 0.33579 | west | 0.35365 | 0.34067 | 0.088668 | 0.34596 | 0.088668 | west | N | 0.088668 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.33579 | west | 0.35365 | 0.34067 | 0.088668 | 0.34596 | 0.088668 | west | N | 0.088668 | 0
76031 | L_GASCCR | W1 | 150 | 0.26498 | west | 0.28285 | 0.26987 | 0.017865 | 0.27515 | 0.017865 | west | N | 0.017865 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.25118 | west | 0.26905 | 0.25607 | 0.0040659 | 0.26136 | 0.0040659 | west | N | 0.0040659 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.25118 | west | 0.26905 | 0.25607 | 0.0040659 | 0.26136 | 0.0040659 | west | N | 0.0040659 | 0
76096 | L_CAPRSI | W1 | 186 | 0.25118 | west | 0.26905 | 0.25607 | 0.0040659 | 0.26136 | 0.0040659 | west | N | 0.0040659 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.25118 | west | 0.26905 | 0.25607 | 0.0040659 | 0.26136 | 0.0040659 | west | N | 0.0040659 | 0
80003 | MILHWYS | F | 0 | -0.004359 | south | 0.013509 | 0.00052495 | -0.25148 | 0.0058126 | 0.00052495 | south | N | 0.00052495 | 0
80010 | EPLVT1 | F | 0 | 0.036668 | south | 0.054536 | 0.041552 | -0.21045 | 0.04684 | 0.041552 | south | N | 0.041552 | 0
80012 | LAR | F | 0 | 0.001056 | south | 0.018924 | 0.00594 | -0.24606 | 0.011228 | 0.00594 | south | N | 0.00594 | 0
80051 | FORPVCM0 | 8 | 28 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
80053 | FOR69CG0 | 10 | 74 | -0.005919 | south | 0.011949 | -0.001035 | -0.25304 | 0.0042526 | 0.001035 | south | N | 0.001035 | 0
80080 | GWINDT11 | 1 | 94 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80080 | GWINDT11 | 2 | 41 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80080 | GWINDT11 | 3 | 38 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80080 | GWINDT11 | 4 | 19 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80081 | GWINDT21 | 1 | 94 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80081 | GWINDT21 | 2 | 36 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80081 | GWINDT21 | 3 | 43 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80081 | GWINDT21 | 4 | 22 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80137 | CSDR89 | 8 | 39 | -0.005575 | south | 0.012293 | -0.00069105 | -0.25269 | 0.0045966 | 0.00069105 | south | N | 0.00069105 | 0
80137 | CSDR89 | 9 | 15 | -0.005575 | south | 0.012293 | -0.00069105 | -0.25269 | 0.0045966 | 0.00069105 | south | N | 0.00069105 | 0
80138 | CSDR7 | 7 | 7 | -0.005575 | south | 0.012293 | -0.00069105 | -0.25269 | 0.0045966 | 0.00069105 | south | N | 0.00069105 | 0
80139 | CSDR56 | 5 | 15 | -0.005575 | south | 0.012293 | -0.00069105 | -0.25269 | 0.0045966 | 0.00069105 | south | N | 0.00069105 | 0
80139 | CSDR56 | 6 | 39 | -0.005575 | south | 0.012293 | -0.00069105 | -0.25269 | 0.0045966 | 0.00069105 | south | N | 0.00069105 | 0
80140 | CSDR11 | 11 | 39 | -0.005575 | south | 0.012293 | -0.00069105 | -0.25269 | 0.0045966 | 0.00069105 | south | N | 0.00069105 | 0
80180 | PNSCALT1 | 1 | 148 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80180 | PNSCALT1 | 2 | 50 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80181 | PNSCALT2 | 1 | 55 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80181 | PNSCALT2 | 2 | 50 | -0.004423 | south | 0.013445 | 0.00046095 | -0.25154 | 0.0057486 | 0.00046095 | south | N | 0.00046095 | 0
80223 | REYSHR G | 1 | 12 | -0.004797 | south | 0.013071 | 8.6954e-05 | -0.25192 | 0.0053746 | 8.6954e-05 | south | N | 8.6954e-05 | 0
80224 | VISTRONG | 1 | 15 | -0.005503 | south | 0.012365 | -0.00061905 | -0.25262 | 0.0046686 | 0.00061905 | south | N | 0.00061905 | 0
80225 | VISTRONG | 2 | 23 | -0.005503 | south | 0.012365 | -0.00061905 | -0.25262 | 0.0046686 | 0.00061905 | south | N | 0.00061905 | 0
80226 | ALCOA G | 1 | 48 | -0.005846 | south | 0.012022 | -0.00096205 | -0.25296 | 0.0043256 | 0.00096205 | south | N | 0.00096205 | 0
80227 | AIRCO G | 1 | 8 | -0.005522 | south | 0.012346 | -0.00063805 | -0.25264 | 0.0046496 | 0.00063805 | south | N | 0.00063805 | 0
80261 | NBEC81A | 1 | 180 | -0.004642 | south | 0.013226 | 0.00024195 | -0.25176 | 0.0055296 | 0.00024195 | south | N | 0.00024195 | 0
80262 | NBEC91A | 1 | 180 | -0.004646 | south | 0.013222 | 0.00023795 | -0.25176 | 0.0055256 | 0.00023795 | south | N | 0.00023795 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.004617 | south | 0.013251 | 0.00026695 | -0.25174 | 0.0055546 | 0.00026695 | south | N | 0.00026695 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.004617 | south | 0.013251 | 0.00026695 | -0.25174 | 0.0055546 | 0.00026695 | south | N | 0.00026695 | 0
80265 | LARECU40 | 4 | 100 | 0.001053 | south | 0.018921 | 0.005937 | -0.24607 | 0.011225 | 0.005937 | south | N | 0.005937 | 0
80266 | LARECU50 | 5 | 100 | 0.001053 | south | 0.018921 | 0.005937 | -0.24607 | 0.011225 | 0.005937 | south | N | 0.005937 | 0
80291 | PAPALOTE | 1 | 25 | -0.004733 | south | 0.013135 | 0.00015095 | -0.25185 | 0.0054386 | 0.00015095 | south | N | 0.00015095 | 0
80291 | PAPALOTE | 2 | 25 | -0.004733 | south | 0.013135 | 0.00015095 | -0.25185 | 0.0054386 | 0.00015095 | south | N | 0.00015095 | 0
80291 | PAPALOTE | 3 | 25 | -0.004733 | south | 0.013135 | 0.00015095 | -0.25185 | 0.0054386 | 0.00015095 | south | N | 0.00015095 | 0
80291 | PAPALOTE | 4 | 16 | -0.004733 | south | 0.013135 | 0.00015095 | -0.25185 | 0.0054386 | 0.00015095 | south | N | 0.00015095 | 0
80294 | PAPALOTE | 5 | 25 | -0.004733 | south | 0.013135 | 0.00015095 | -0.25185 | 0.0054386 | 0.00015095 | south | N | 0.00015095 | 0
80294 | PAPALOTE | 6 | 25 | -0.004733 | south | 0.013135 | 0.00015095 | -0.25185 | 0.0054386 | 0.00015095 | south | N | 0.00015095 | 0
80294 | PAPALOTE | 7 | 25 | -0.004733 | south | 0.013135 | 0.00015095 | -0.25185 | 0.0054386 | 0.00015095 | south | N | 0.00015095 | 0
80294 | PAPALOTE | 8 | 15 | -0.004733 | south | 0.013135 | 0.00015095 | -0.25185 | 0.0054386 | 0.00015095 | south | N | 0.00015095 | 0
86104 | CID-138 | EQ | 0 | 0.001053 | south | 0.018921 | 0.005937 | -0.24607 | 0.011225 | 0.005937 | south | N | 0.005937 | 0
86105 | CID-230 | EQ | 500 | 0.001053 | south | 0.018921 | 0.005937 | -0.24607 | 0.011225 | 0.005937 | south | N | 0.005937 | 0
86106 | CUF-230 | EQ | 500 | 0.001053 | south | 0.018921 | 0.005937 | -0.24607 | 0.011225 | 0.005937 | south | N | 0.005937 | 0
86107 | CUF-138 | EQ | 0 | 0.001053 | south | 0.018921 | 0.005937 | -0.24607 | 0.011225 | 0.005937 | south | N | 0.005937 | 0
88198 | BEEVILLE | F | 0 | -0.003764 | south | 0.014104 | 0.00112 | -0.25088 | 0.0064076 | 0.00112 | south | N | 0.00112 | 0
88253 | HAMILTON | F | 0 | 0.057571 | south | 0.075439 | 0.062455 | -0.18955 | 0.067743 | 0.062455 | south | N | 0.062455 | 0
88299 | ZAPATA | F | 0 | -0.000727 | south | 0.017141 | 0.004157 | -0.24785 | 0.0094446 | 0.004157 | south | N | 0.004157 | 0
88508 | FALFURRI | F | 0 | -0.003589 | south | 0.014279 | 0.001295 | -0.25071 | 0.0065826 | 0.001295 | south | N | 0.001295 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 1 | 86.8512 | 209 | 0.43427 | 90.7632 | 209 | 90.7632
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.5678 | 126.5 | 0.43427 | 54.9356 | 335.5 | 145.6989
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 1 | 103.4734 | 249 | 0.43427 | 108.1342 | 584.5 | 253.833
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 1 | 81.8645 | 197 | 0.43427 | 85.5519 | 781.5 | 339.385 | Weighted Shift Factors
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.9733 | 125 | 0.3545 | 44.313 | 906.5 | 383.698 | west | 0.24712
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.9733 | 125 | 0.3545 | 44.313 | 1031.5 | 428.0109 | North | -0.018718
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.592 | 37.5 | 0.3545 | 13.2939 | 1069 | 441.3048 |  | 0.26584
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.097 | 107.5 | 0.3545 | 38.1092 | 1176.5 | 479.414
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 45.3311 | 135 | 0.3545 | 47.858 | 1311.5 | 527.272 | Line Rating | 1100
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.9585 | 119 | 0.3545 | 42.186 | 1430.5 | 569.4579 | Conc Gen | 2186
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 35.2575 | 105 | 0.3545 | 37.2229 | 1535.5 | 606.6808 | Weighted Imp. | 835.8566
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.0308 | 80.5 | 0.3545 | 28.5376 | 1616 | 635.2184 | PTDF | 0.38237
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 1 | 49.9918 | 150 | 0.352 | 52.7995 | 1766 | 688.0179
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 1 | 73.3214 | 220 | 0.352 | 77.4393 | 1986 | 765.4572 | Concentration | 1.4384
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 1 | 66.6558 | 200 | 0.352 | 70.3994 | 2186 | 835.8566
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 1 | 40.6267 | 121.9 | 0.352 | 42.9084
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.33109 | west | 8 | N | N | Nwest | Nwest | 1 | 23.1761 | 0 | 0.3498 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.33109 | west | 8 | N | N | Nwest | Nwest | 1 | 24.3018 | 0 | 0.3498 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.33109 | west | 8 | N | N | Nwest | Nwest | 1 | 23.3085 | 0 | 0.3498 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 22.6768 | 70 | 0.34267 | 23.987
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 22.6768 | 70 | 0.34267 | 23.987
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 30.0629 | 92.8 | 0.34267 | 31.7999
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.9163 | 80 | 0.34267 | 27.4137
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.9163 | 80 | 0.34267 | 27.4137
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 37.2547 | 115 | 0.34267 | 39.4073
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 67.4258 | 208.2 | 0.34257 | 71.3228
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 46.0192 | 142.1 | 0.34257 | 48.679
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 42.8779 | 132.4 | 0.34257 | 45.3561
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 44.0437 | 136 | 0.34257 | 46.5894
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 47.6061 | 147 | 0.34257 | 50.3576
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 68.0087 | 210 | 0.34257 | 71.9394
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.7074 | 66 | 0.33247 | 21.9428
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.3937 | 65 | 0.33247 | 21.6103
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.0212 | 67 | 0.33247 | 22.2753
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.0212 | 67 | 0.33247 | 22.2753
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.0212 | 67 | 0.33247 | 22.2753
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.31375 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33247 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.31375 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33247 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.31277 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.9469 | 35 | 0.33149 | 11.602
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.31277 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3831 | 30 | 0.33149 | 9.9446
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.31102 | west | 6 | Y | N | Ywest | Nwest | 1 | 46.3414 | 149 | 0.32973 | 49.1303
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.31085 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.2407 | 100.5 | 0.32957 | 33.1219
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.31015 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.9886 | 58 | 0.32887 | 19.0742
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.31008 | west | 6 | Y | N | Ywest | Nwest | 1 | 66.4196 | 214.2 | 0.3288 | 70.4289
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.4388 | 66 | 0.3284 | 21.6742
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.3679 | 69 | 0.3284 | 22.6594
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.3679 | 69 | 0.3284 | 22.6594
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.7485 | 67 | 0.3284 | 22.0026
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.7485 | 67 | 0.3284 | 22.0026
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.1291 | 65 | 0.3284 | 21.3458
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.29876 | west | 6 | Y | N | Ywest | Nwest | 1 | 35.8512 | 120 | 0.31748 | 38.0973
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.29628 | west | 6 | Y | N | Ywest | Nwest | 1 | 35.553 | 120 | 0.31499 | 37.7991
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.29304 | west | 8 | N | N | Nwest | Nwest | 1 | 7.5605 | 0 | 0.31176 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.29129 | west | 6 | Y | N | Ywest | Nwest | 1 | 65.5405 | 225 | 0.31001 | 69.752
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.2905 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.2891 | 180 | 0.30921 | 55.6583
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.2905 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.2891 | 180 | 0.30921 | 55.6583
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.28983 | west | #N/A | N | N | Nwest | Nwest | 1 | 1.3912 | 0 | 0.30855 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.28323 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8437 | 63 | 0.30195 | 19.0229
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.27929 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.3433 | 80 | 0.29801 | 23.8407
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.27929 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.3433 | 80 | 0.29801 | 23.8407
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.27926 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.3757 | 141 | 0.29798 | 42.0149
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.27926 | west | 6 | Y | N | Ywest | Nwest | 1 | 33.5112 | 120 | 0.29798 | 35.7573
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.27846 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.567 | 99 | 0.29717 | 29.4201
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.27846 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.9858 | 61 | 0.29717 | 18.1275
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.27846 | west | 7 | N | N | Nwest | Nwest | 1 | 6.9614 | 0 | 0.29717 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.27846 | west | 7 | N | N | Nwest | Nwest | 1 | 12.7254 | 0 | 0.29717 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.27846 | west | 7 | N | N | Nwest | Nwest | 1 | 12.7254 | 0 | 0.29717 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.27709 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.782 | 75 | 0.29581 | 22.1858
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.27709 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.1674 | 80 | 0.29581 | 23.6649
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.27709 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.0837 | 40 | 0.29581 | 11.8324
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.27669 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.135 | 80 | 0.29541 | 23.6325
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.27661 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.1289 | 80 | 0.29533 | 23.6263
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.27627 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.4408 | 150 | 0.29499 | 44.2485
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.27627 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.4408 | 150 | 0.29499 | 44.2485
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.2752 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8163 | 6.6 | 0.29392 | 1.9399
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.2752 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4394 | 34.3 | 0.29392 | 10.0814
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.26498 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.7475 | 150 | 0.2837 | 42.5551
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.26453 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1623 | 80 | 0.28325 | 22.6597
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.26163 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.9772 | 84 | 0.28035 | 23.5495
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.26057 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.8876 | 84 | 0.27928 | 23.4599
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.25979 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.8738 | 76.5 | 0.27851 | 21.3057
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.2582 | 112.5 | 0.2699 | 30.364
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 1 | 37.552 | 149.5 | 0.2699 | 40.3503
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 1 | 46.7202 | 186 | 0.2699 | 50.2017
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 1 | 53.879 | 214.5 | 0.2699 | 57.8939
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.19886 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.21758 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.18785 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.1774 | 150 | 0.20657 | 30.985
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.17126 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.6892 | 150 | 0.18998 | 28.4968
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.17126 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2974 | 101 | 0.18998 | 19.1879
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.13254 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.8808 | 150 | 0.15126 | 22.6885
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.11925 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1553 | 60 | 0.13797 | 8.2784
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.090905 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4084 | 169.5 | 0.10962 | 18.5811
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.076813 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2176 | 120 | 0.095531 | 11.4637
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.076813 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8974 | 233 | 0.095531 | 22.2587
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.076813 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.0736 | 170.2 | 0.095531 | 16.2593
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.045609 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.064327 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.057571 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8998 | 0 | -0.18955 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.057571 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4393 | 0 | -0.18955 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.057571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18955 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.040613 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.24368 | 0 | -0.20651 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.036668 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21045 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.002903 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.17418 | 60 | 0.021621 | 1.2972
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.018718 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.018718 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.001756 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.7024 | 400 | 0.016962 | 6.7847
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.001925 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.4543 | 236 | 0.016793 | 3.9631
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.002066 | west | 4 | Y | N | Ywest | Nwest | 1 | -1.3423 | 649.7 | 0.016652 | 10.8187
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.3357 | 100 | 0.015361 | 1.5361
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.004199 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.10078 | 24 | -0.24292 | -5.8301
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.004199 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.10078 | 24 | -0.24292 | -5.8301
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.004199 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.096577 | 23 | -0.24292 | -5.5871
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.002484 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.034031 | 0 | -0.24463 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.012318 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.8477 | 150 | 0.0063998 | 0.95997
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.012318 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.98544 | 80 | 0.0063998 | 0.51198
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.012357 | north | 3 | N | N | Nnorth | Nnorth | 1 | -14.297 | 0 | 0.0063608 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.012357 | north | 3 | N | N | Nnorth | Nnorth | 1 | -14.3094 | 0 | 0.0063608 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.012486 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.91148 | 73 | 0.0062318 | 0.45492
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.012486 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.4858 | 119 | 0.0062318 | 0.74158
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.012486 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.5596 | 205 | 0.0062318 | 1.2775
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.012486 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.2736 | 102 | 0.0062318 | 0.63564
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.012486 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.1987 | 96 | 0.0062318 | 0.59825
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.012686 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2349 | 255 | 0.0060318 | 1.5381
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.012686 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.8902 | 149 | 0.0060318 | 0.89874
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.012686 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.941 | 153 | 0.0060318 | 0.92287
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.012708 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060098 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.012708 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060098 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.9608 | 0 | 0.0060018 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.9837 | 0 | 0.0060018 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.9837 | 0 | 0.0060018 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | 1 | -4.8321 | 0 | 0.0060018 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.012731 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.19096 | 0 | 0.0059868 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.012731 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.19096 | 0 | 0.0059868 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.001056 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24606 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.001053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1053 | 100 | -0.24607 | -24.6065
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.001053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1053 | 100 | -0.24607 | -24.6065
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24607 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24607 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24607 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24607 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.013072 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.62746 | 48 | 0.0056458 | 0.271
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.013072 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.60131 | 46 | 0.0056458 | 0.25971
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.013072 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.3726 | 105 | 0.0056458 | 0.59281
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.013091 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.41891 | 0 | 0.0056268 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.013091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -6.0611 | 463 | 0.0056268 | 2.6052
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056188 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056188 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.013099 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.22268 | 17 | 0.0056188 | 0.09552
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056188 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056188 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.013167 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0055508 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.013167 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.3624 | 787 | 0.0055508 | 4.3685
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.013189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.866 | 217.3 | 0.0055288 | 1.2014
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.013189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7037 | 205 | 0.0055288 | 1.1334
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.013189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5927 | 272.4 | 0.0055288 | 1.506
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.000486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.20509 | 422 | -0.24663 | -104.0787
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.000391 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.007038 | 0 | -0.24673 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.000391 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.007038 | 0 | -0.24673 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.000391 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.005865 | 0 | -0.24673 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.013669 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2554 | 165 | 0.0050488 | 0.83305
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 4.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001344 | 0 | -0.24707 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 4.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001392 | 0 | -0.24707 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24712 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24712 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.98343 | 70 | 0.0046688 | 0.32682
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96938 | 69 | 0.0046688 | 0.32215
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96938 | 69 | 0.0046688 | 0.32215
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.95533 | 68 | 0.0046688 | 0.31748
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.014225 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3898 | 168 | 0.0044928 | 0.75479
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.014225 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.2803 | 90 | 0.0044928 | 0.40435
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.2402 | 855 | 0.0044018 | 3.7635
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.2402 | 855 | 0.0044018 | 3.7635
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1803 | 152.3 | 0.0044018 | 0.67039
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1903 | 153 | 0.0044018 | 0.67348
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.000727 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24785 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.014808 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.2462 | 827 | 0.0039098 | 3.2334
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.014808 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.1278 | 819 | 0.0039098 | 3.2021
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.001098 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.019764 | 0 | -0.24822 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.001098 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.019764 | 0 | -0.24822 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.015622 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.18746 | 0 | 0.0030958 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.015622 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.18746 | 0 | 0.0030958 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.015925 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0027928 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.00229 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02748 | 0 | -0.24941 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.00229 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02519 | 0 | -0.24941 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.00229 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02748 | 0 | -0.24941 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.016145 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -9.9292 | 615 | 0.0025728 | 1.5823
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.016145 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -9.4771 | 587 | 0.0025728 | 1.5102
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.016374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4676 | 150.7 | 0.0023438 | 0.35321
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.016374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4725 | 151 | 0.0023438 | 0.35391
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.016374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9047 | 177.4 | 0.0023438 | 0.41579
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.016423 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4881 | 151.5 | 0.0022948 | 0.34766
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.016423 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.5012 | 152.3 | 0.0022948 | 0.3495
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.016423 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9151 | 177.5 | 0.0022948 | 0.40733
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.784 | 224 | 0.0018248 | 0.40876
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8178 | 226 | 0.0018248 | 0.41241
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5813 | 212 | 0.0018248 | 0.38686
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5644 | 211 | 0.0018248 | 0.38503
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.017073 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.8244 | 224 | 0.0016448 | 0.36844
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.003265 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.18937 | 58 | -0.25038 | -14.5222
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.003265 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.29058 | 89 | -0.25038 | -22.2841
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14366 | 44 | -0.25038 | -11.0169
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14366 | 44 | -0.25038 | -11.0169
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14039 | 43 | -0.25038 | -10.7665
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14693 | 45 | -0.25038 | -11.2672
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.017185 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.30933 | 18 | 0.0015328 | 0.02759
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.017185 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.30933 | 18 | 0.0015328 | 0.02759
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.017185 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.65303 | 38 | 0.0015328 | 0.058247
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3827 | 114 | -0.25048 | -28.5542
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.74525 | 222 | -0.25048 | -55.6055
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.61769 | 184 | -0.25048 | -46.0874
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.75197 | 224 | -0.25048 | -56.1064
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.38605 | 115 | -0.25048 | -28.8046
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.017255 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.382 | 196 | 0.0014628 | 0.28671
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.017255 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.9153 | 111 | 0.0014628 | 0.16237
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.003576 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.4161 | 396 | -0.25069 | -99.2748
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.003589 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25071 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.003641 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4819 | 407 | -0.25076 | -102.0589
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.017507 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7885 | 216.4 | 0.0012108 | 0.26202
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.017507 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7833 | 216.1 | 0.0012108 | 0.26165
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.017549 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.1939 | 182 | 0.0011688 | 0.21272
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.017549 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.4937 | 484 | 0.0011688 | 0.5657
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.017572 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.8786 | 50 | 0.0011458 | 0.05729
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.017585 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0011328 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.003756 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.785 | 209 | -0.25087 | -52.4327
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.003756 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.8113 | 216 | -0.25087 | -54.1888
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17278 | 46 | -0.25087 | -11.5402
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17653 | 47 | -0.25087 | -11.7911
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17278 | 46 | -0.25087 | -11.5402
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17278 | 46 | -0.25087 | -11.5402
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.003763 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5504 | 412 | -0.25088 | -103.363
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.003763 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5052 | 400 | -0.25088 | -100.3524
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.003764 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25088 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.003833 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.6252 | 424 | -0.25095 | -106.4032
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.003833 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.629 | 425 | -0.25095 | -106.6542
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.6196 | 0 | 0.0010178 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.301 | 0 | 0.0010178 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.5665 | 0 | 0.0010178 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0623 | 0 | 0.0010178 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.003924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57487 | 146.5 | -0.25104 | -36.7777
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.003924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.58036 | 147.9 | -0.25104 | -37.1291
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.003924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.67885 | 173 | -0.25104 | -43.4303
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.017835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.0005 | 785 | 0.0008828 | 0.693
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.017835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.1788 | 795 | 0.0008828 | 0.70183
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.017835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.9113 | 780 | 0.0008828 | 0.68859
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.004096 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25121 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.004096 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25121 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.004096 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25121 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.004186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64883 | 155 | -0.2513 | -38.9521
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.004186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71162 | 170 | -0.2513 | -42.7217
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.004186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64883 | 155 | -0.2513 | -38.9521
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.004196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.86857 | 207 | -0.25131 | -52.022
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.004196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.90927 | 216.7 | -0.25131 | -54.4598
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.004196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0154 | 242 | -0.25131 | -60.818
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.004197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60437 | 144 | -0.25132 | -36.1894
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.004197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60437 | 144 | -0.25132 | -36.1894
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.004197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71769 | 171 | -0.25132 | -42.9749
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.004285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.3396 | 546 | -0.2514 | -137.2661
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.004285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.2138 | 750 | -0.2514 | -188.5523
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.004359 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25148 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.004359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.16564 | 38 | -0.25148 | -9.5561
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.004359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.084129 | 19.3 | -0.25148 | -4.8535
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.004359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.065385 | 15 | -0.25148 | -3.7722
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.004359 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20487 | 47 | -0.25148 | -11.8194
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.41576 | 94 | -0.25154 | -23.6449
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.18134 | 41 | -0.25154 | -10.3132
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.16807 | 38 | -0.25154 | -9.5586
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.084037 | 19 | -0.25154 | -4.7793
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.41576 | 94 | -0.25154 | -23.6449
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.15923 | 36 | -0.25154 | -9.0555
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.19019 | 43 | -0.25154 | -10.8163
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.097306 | 22 | -0.25154 | -5.5339
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.6546 | 148 | -0.25154 | -37.2281
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.22115 | 50 | -0.25154 | -12.5771
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.24327 | 55 | -0.25154 | -13.8348
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.22115 | 50 | -0.25154 | -12.5771
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.0045 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.1305 | 0 | -0.25162 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.004578 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.17396 | 0 | -0.2517 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.004597 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.17469 | 0 | -0.25172 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.004598 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.11495 | 0 | -0.25172 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.004598 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.11495 | 0 | -0.25172 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.004617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5421 | 334 | -0.25174 | -84.0795
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.004617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5698 | 340 | -0.25174 | -85.5899
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.004617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83106 | 180 | -0.25174 | -45.3123
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.004617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83106 | 180 | -0.25174 | -45.3123
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.004642 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83556 | 180 | -0.25176 | -45.3168
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.004645 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.68885 | 0 | -0.25176 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.004645 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.69025 | 0 | -0.25176 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.004645 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.71069 | 0 | -0.25176 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.004646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.5611 | 336 | -0.25176 | -84.5927
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.004646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83628 | 180 | -0.25176 | -45.3175
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16412 | 0 | -0.25181 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15943 | 0 | -0.25181 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16412 | 0 | -0.25181 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.004698 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.955 | 629 | -0.25182 | -158.3923
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.018544 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.1882 | 118 | 0.0001738 | 0.020509
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.018544 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.1326 | 115 | 0.0001738 | 0.019987
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.018544 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.3105 | 556 | 0.0001738 | 0.096634
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 25 | -0.25185 | -6.2963
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 25 | -0.25185 | -6.2963
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 25 | -0.25185 | -6.2963
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.075728 | 16 | -0.25185 | -4.0296
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 25 | -0.25185 | -6.2963
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 25 | -0.25185 | -6.2963
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 25 | -0.25185 | -6.2963
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.070995 | 15 | -0.25185 | -3.7778
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.004762 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.019048 | 0 | -0.25188 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.75793 | 0 | -0.25192 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.73394 | 0 | -0.25192 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.4797 | 0 | -0.25192 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.69556 | 0 | -0.25192 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.70516 | 0 | -0.25192 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.60922 | 0 | -0.25192 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.004797 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.057564 | 0 | -0.25192 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71295 | 147 | -0.25197 | -37.0393
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6693 | 138 | -0.25197 | -34.7716
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.679 | 140 | -0.25197 | -35.2755
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71295 | 147 | -0.25197 | -37.0393
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.8827 | 182 | -0.25197 | -45.8582
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.9603 | 198 | -0.25197 | -49.8897
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.018811 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -9.3197e-05 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.018811 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -9.3197e-05 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.004979 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.029874 | 0 | -0.2521 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.031 | 161 | -0.0001082 | -0.01742
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0875 | 164 | -0.0001082 | -0.017744
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0875 | 164 | -0.0001082 | -0.017744
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.794 | 414 | -0.0001082 | -0.044794
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0498 | 162 | -0.0001082 | -0.017528
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.031 | 161 | -0.0001082 | -0.01742
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0686 | 163 | -0.0001082 | -0.017636
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.6998 | 409 | -0.0001082 | -0.044253
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.018905 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.3351 | 388 | -0.0001872 | -0.072633
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.018905 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.7361 | 515 | -0.0001872 | -0.096407
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.72065 | 142 | -0.25219 | -35.8114
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73587 | 145 | -0.25219 | -36.568
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76633 | 151 | -0.25219 | -38.0812
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4717 | 290 | -0.25219 | -73.136
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.005087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012209 | 0 | -0.25221 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.005087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012209 | 0 | -0.25221 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.005087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014244 | 0 | -0.25221 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.005104 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.11229 | 22 | -0.25222 | -5.5489
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.005104 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.056144 | 11 | -0.25222 | -2.7744
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.005104 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.056144 | 11 | -0.25222 | -2.7744
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25105 | 47.7 | -0.25238 | -12.0386
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19631 | 37.3 | -0.25238 | -9.4138
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2421 | 46 | -0.25238 | -11.6095
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25262 | 48 | -0.25238 | -12.1143
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1867 | 223.9 | -0.25242 | -56.5164
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1925 | 225 | -0.25242 | -56.7941
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1904 | 224.6 | -0.25242 | -56.6931
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.2015 | 226.7 | -0.25242 | -57.2232
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.005314 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.063768 | 0 | -0.25243 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.005338 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76867 | 144 | -0.25246 | -36.3537
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.005338 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0035 | 188 | -0.25246 | -47.4617
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.019206 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.76824 | 40 | -0.0004882 | -0.019528
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.005375 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0129 | 0 | -0.25249 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.005375 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0129 | 0 | -0.25249 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.019209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.38418 | 20 | -0.0004912 | -0.0098239
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.019209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.48023 | 25 | -0.0004912 | -0.01228
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.019209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.78757 | 41 | -0.0004912 | -0.020139
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.00541 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.39493 | 0 | -0.25253 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.019274 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5226 | 79 | -0.0005562 | -0.04394
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.019274 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.043 | 106 | -0.0005562 | -0.058957
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.019274 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.814 | 146 | -0.0005562 | -0.081205
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.019274 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.4648 | 76 | -0.0005562 | -0.042271
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.019277 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.3855 | 435 | -0.0005592 | -0.24325
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.019295 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -7.6215 | 395 | -0.0005772 | -0.22799
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.019295 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.3933 | 435 | -0.0005772 | -0.25108
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.005503 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.082545 | 0 | -0.25262 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.005503 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12657 | 0 | -0.25262 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.005522 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.044176 | 0 | -0.25264 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.019361 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.3233 | 120 | -0.0006432 | -0.077184
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.1561 | 0 | -0.25269 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.039025 | 0 | -0.25269 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.21743 | 0 | -0.25269 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.083625 | 0 | -0.25269 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.039025 | 0 | -0.25269 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.083625 | 0 | -0.25269 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.21743 | 0 | -0.25269 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.21743 | 0 | -0.25269 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.019532 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.8989 | 558 | -0.0008142 | -0.45432
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.019532 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -11.309 | 579 | -0.0008142 | -0.47142
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.019532 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.7819 | 808 | -0.0008142 | -0.65787
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.019596 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.4697 | 0 | -0.0008782 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.019596 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.5598 | 0 | -0.0008782 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.019596 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7323 | 0 | -0.0008782 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1411 | 160 | -0.0009142 | -0.14627
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0626 | 156 | -0.0009142 | -0.14261
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8479 | 196 | -0.0009142 | -0.17918
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0626 | 156 | -0.0009142 | -0.14261
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0822 | 157 | -0.0009142 | -0.14353
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8871 | 198 | -0.0009142 | -0.18101
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.005846 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28061 | 0 | -0.25296 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.019687 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.2842 | 370 | -0.0009692 | -0.3586
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.7562 | 0 | -0.0009692 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.7759 | 0 | -0.0009692 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -6.0833 | 0 | -0.0009692 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.8152 | 0 | -0.0009692 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.8349 | 0 | -0.0009692 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -6.103 | 0 | -0.0009692 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4676 | 0 | -0.25304 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47944 | 0 | -0.25304 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4676 | 0 | -0.25304 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47352 | 0 | -0.25304 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46405 | 0 | -0.25304 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14797 | 0 | -0.25304 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27227 | 0 | -0.25304 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.16573 | 0 | -0.25304 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.25807 | 0 | -0.25304 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.43801 | 0 | -0.25304 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.019814 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.3684 | 170 | -0.0010962 | -0.18635
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.019814 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.3033 | 520 | -0.0010962 | -0.57002
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.019861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.72 | 288 | -0.0011432 | -0.32924
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.019861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9196 | 147 | -0.0011432 | -0.16805
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.019861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9196 | 147 | -0.0011432 | -0.16805
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.01989 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0011722 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.019914 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.79656 | 0 | -0.0011962 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.019914 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.79656 | 0 | -0.0011962 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.006286 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.050288 | 0 | -0.2534 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.006286 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.050288 | 0 | -0.2534 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31277 | 49 | -0.2535 | -12.4216
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.29362 | 46 | -0.2535 | -11.661
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.29362 | 46 | -0.2535 | -11.661
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3 | 47 | -0.2535 | -11.9145
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.006383 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.98298 | 154 | -0.2535 | -39.0392
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.006383 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.94468 | 148 | -0.2535 | -37.5182
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.30638 | 48 | -0.2535 | -12.1681
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.30638 | 48 | -0.2535 | -12.1681
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.006441 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.9967 | 310 | -0.25356 | -78.6033
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.006441 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.6601 | 413 | -0.25356 | -104.7199
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.020288 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0015702 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.27657 | 42 | -0.2537 | -10.6555
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.28974 | 44 | -0.2537 | -11.1629
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.28974 | 44 | -0.2537 | -11.1629
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3095 | 47 | -0.2537 | -11.924
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.006834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0422 | 152.5 | -0.25395 | -38.7277
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.006834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0217 | 149.5 | -0.25395 | -37.9658
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.006834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.5896 | 232.6 | -0.25395 | -59.0692
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.006862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.90578 | 132 | -0.25398 | -33.5254
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.006862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.91951 | 134 | -0.25398 | -34.0333
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.006862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2164 | 323 | -0.25398 | -82.0356
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3523 | 50 | -0.25416 | -12.7082
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3523 | 50 | -0.25416 | -12.7082
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3523 | 50 | -0.25416 | -12.7082
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3523 | 50 | -0.25416 | -12.7082
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.007171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.133 | 158 | -0.25429 | -40.1777
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.007171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1474 | 160 | -0.25429 | -40.6862
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.007171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.2549 | 175 | -0.25429 | -44.5006
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.007174 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.1063 | 433 | -0.25429 | -110.1085
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.007175 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -4.1902 | 584 | -0.25429 | -148.5071
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.007175 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -4.2691 | 595 | -0.25429 | -151.3044
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.021427 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.4105 | 112.5 | -0.0027092 | -0.30478
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.022061 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0033432 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.022061 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0033432 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.022061 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0033432 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.008368 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -11.1545 | 0 | -0.25549 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.008368 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -11.1127 | 0 | -0.25549 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.64418 | 76 | -0.25559 | -19.4251
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.64418 | 76 | -0.25559 | -19.4251
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.88998 | 105 | -0.25559 | -26.8374
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62722 | 74 | -0.25559 | -18.914
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62722 | 74 | -0.25559 | -18.914
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.86455 | 102 | -0.25559 | -26.0706
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.008561 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.56503 | 66 | -0.25568 | -16.8748
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.022404 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.3442 | 60 | -0.0036862 | -0.22117
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.022404 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4115 | 63 | -0.0036862 | -0.23223
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.008868 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -5.0459 | 569 | -0.25599 | -145.6561
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.008868 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -5.1523 | 581 | -0.25599 | -148.7279
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56804 | 0 | -0.25628 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65417 | 0 | -0.25628 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41229 | 0 | -0.25628 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92536 | 0 | -0.25628 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78793 | 0 | -0.25628 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.80626 | 0 | -0.25628 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4581 | 0 | -0.25628 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16492 | 0 | -0.25628 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86123 | 0 | -0.25628 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64134 | 0 | -0.25628 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57721 | 0 | -0.25628 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65966 | 0 | -0.25628 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5937 | 0 | -0.25628 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92536 | 0 | -0.25628 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88871 | 0 | -0.25628 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.94369 | 0 | -0.25628 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69631 | 0 | -0.25628 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73296 | 0 | -0.25628 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73296 | 0 | -0.25628 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5667 | 0 | -0.25628 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.009304 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66058 | 0 | -0.25642 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.009304 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09304 | 0 | -0.25642 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0462 | 0 | -0.25654 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0462 | 0 | -0.25654 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1216 | 0 | -0.25654 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.032 | 0 | -0.25654 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.023504 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.688 | 242 | -0.0047862 | -1.1583
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.009814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45243 | 0 | -0.25693 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.009855 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.4156 | 651 | -0.25697 | -167.2895
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.009855 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.5582 | 564 | -0.25697 | -144.9328
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.009855 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.913 | 600 | -0.25697 | -154.1838
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.009858 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6069 | 0 | -0.25698 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.009858 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6069 | 0 | -0.25698 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.009858 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4152 | 0 | -0.25698 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.009872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32578 | 0 | -0.25699 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.009931 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.5989 | 161 | -0.25705 | -41.3849
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.009931 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.6485 | 166 | -0.25705 | -42.6701
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.009931 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4629 | 248 | -0.25705 | -63.7482
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.009931 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -5.4223 | 546 | -0.25705 | -140.3488
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.009931 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -6.3856 | 0 | -0.25705 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.009931 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1291 | 13 | -0.25705 | -3.3416
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0124 | 0 | -0.25721 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.93773 | 0 | -0.25721 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0367 | 0 | -0.25721 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0296 | 0 | -0.25721 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.010094 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32301 | 0 | -0.25721 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.010094 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30282 | 0 | -0.25721 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71473 | 0 | -0.25721 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67334 | 0 | -0.25721 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53504 | 0 | -0.25721 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5466 | 0 | -0.25721 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5496 | 0 | -0.25721 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5375 | 0 | -0.25721 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.96912 | 0 | -0.25721 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4632 | 0 | -0.25721 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4038 | 0 | -0.25721 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.010189 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.50945 | 50 | -0.25731 | -12.8654
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.010239 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25736 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93857 | 0 | -0.25743 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90351 | 0 | -0.25743 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89732 | 0 | -0.25743 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56211 | 0 | -0.25743 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12583 | 0 | -0.25743 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67223 | 0 | -0.25746 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.62052 | 0 | -0.25746 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67223 | 0 | -0.25746 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67223 | 0 | -0.25746 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47812 | 46 | -0.25751 | -11.8456
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47812 | 46 | -0.25751 | -11.8456
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47812 | 46 | -0.25751 | -11.8456
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57167 | 55 | -0.25751 | -14.1632
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57167 | 55 | -0.25751 | -14.1632
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.56128 | 54 | -0.25751 | -13.9057
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.010396 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.81089 | 0 | -0.25751 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.010396 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.83168 | 0 | -0.25751 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6986 | 0 | -0.25753 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6351 | 0 | -0.25753 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6393 | 0 | -0.25753 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6341 | 0 | -0.25753 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7998 | 0 | -0.25753 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.010424 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36484 | 0 | -0.25754 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010436 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12523 | 12 | -0.25755 | -3.0906
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.010436 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25755 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.010437 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7639 | 169 | -0.25756 | -43.5268
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.010438 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7223 | 165 | -0.25756 | -42.4967
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.010439 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5554 | 0 | -0.25756 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.010439 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67958 | 0 | -0.25756 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.010441 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.2239 | 213 | -0.25756 | -54.8601
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16916 | 0 | -0.25756 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66829 | 0 | -0.25756 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65993 | 0 | -0.25756 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86251 | 0 | -0.25756 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76853 | 0 | -0.25756 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.010442 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.3808 | 228 | -0.25756 | -58.7237
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.010443 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8797 | 0 | -0.25756 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.010443 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6563 | 0 | -0.25756 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.010443 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6396 | 0 | -0.25756 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74273 | 0 | -0.25758 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75319 | 0 | -0.25758 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40798 | 0 | -0.25758 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31383 | 0 | -0.25758 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.44062 | 42 | -0.25761 | -10.8196
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.44062 | 42 | -0.25761 | -10.8196
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39866 | 38 | -0.25761 | -9.7891
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39866 | 38 | -0.25761 | -9.7891
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.010493 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.427 | 0 | -0.25761 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.010502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8168 | 0 | -0.25762 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.010502 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4178 | 0 | -0.25762 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0976 | 104 | -0.25767 | -26.7979
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0976 | 104 | -0.25767 | -26.7979
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.56992 | 54 | -0.25767 | -13.9143
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.55936 | 53 | -0.25767 | -13.6566
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.56992 | 54 | -0.25767 | -13.9143
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.60158 | 57 | -0.25767 | -14.6873
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.56992 | 54 | -0.25767 | -13.9143
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.56992 | 54 | -0.25767 | -13.9143
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61213 | 58 | -0.25767 | -14.945
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61213 | 58 | -0.25767 | -14.945
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.010562 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -7.7631 | 735 | -0.25768 | -189.3948
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35952 | 0 | -0.25769 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36692 | 0 | -0.25769 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34577 | 0 | -0.25769 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48535 | 0 | -0.25769 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18716 | 0 | -0.25769 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21571 | 0 | -0.25769 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21042 | 0 | -0.25769 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37009 | 0 | -0.25769 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19033 | 0 | -0.25769 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90302 | 0 | -0.25769 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.565 | 0 | -0.25769 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12715 | 12 | -0.25771 | -3.0926
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.010608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.05304 | 0 | -0.25773 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.010608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22277 | 0 | -0.25773 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.010609 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.12731 | 12 | -0.25773 | -3.0927
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68965 | 0 | -0.25773 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70026 | 0 | -0.25773 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7427 | 0 | -0.25773 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66843 | 0 | -0.25773 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65782 | 0 | -0.25773 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1034 | 0 | -0.25773 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.62599 | 0 | -0.25773 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.01061 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -7.8832 | 743 | -0.25773 | -191.4919
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.010621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6675 | 0 | -0.25774 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.010624 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8273 | 172 | -0.25774 | -44.3316
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.010624 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8273 | 172 | -0.25774 | -44.3316
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.010624 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8273 | 172 | -0.25774 | -44.3316
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7351 | 0 | -0.25778 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7202 | 0 | -0.25778 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6936 | 0 | -0.25778 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8691 | 0 | -0.25778 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.010673 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.2479 | 398 | -0.25779 | -102.6008
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59892 | 56 | -0.25781 | -14.4375
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.63101 | 59 | -0.25781 | -15.211
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59892 | 56 | -0.25781 | -14.4375
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59892 | 56 | -0.25781 | -14.4375
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.63101 | 59 | -0.25781 | -15.211
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59892 | 56 | -0.25781 | -14.4375
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8841 | 0 | -0.25801 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.699 | 0 | -0.25801 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6772 | 0 | -0.25801 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6772 | 0 | -0.25801 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.010891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7643 | 0 | -0.25801 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5652 | 20 | -0.0095422 | -0.19084
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5652 | 20 | -0.0095422 | -0.19084
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5652 | 20 | -0.0095422 | -0.19084
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.48042 | 17 | -0.0095422 | -0.16222
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.032845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.7004 | 204 | -0.014127 | -2.8819
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.032845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.6018 | 201 | -0.014127 | -2.8396
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.032845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.9485 | 242 | -0.014127 | -3.4188
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.050862 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -18.6155 | 366 | -0.032144 | -11.7648

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.050862 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -18.6155 | 366 | -0.032144 | -11.7648 | 366 | 11.7648
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.032845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.7004 | 204 | -0.014127 | -2.8819 | 570 | 14.6467
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.032845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.6018 | 201 | -0.014127 | -2.8396 | 771 | 17.4863
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.032845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.9485 | 242 | -0.014127 | -3.4188 | 1013 | 20.9051 | Weighted Shift Factors
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5652 | 20 | -0.0095422 | -0.19084 | 1033 | 21.0959 | west | 0.24712
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5652 | 20 | -0.0095422 | -0.19084 | 1053 | 21.2868 | North | -0.018718
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5652 | 20 | -0.0095422 | -0.19084 | 1073 | 21.4776 |  | 0.26584
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.02826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.48042 | 17 | -0.0095422 | -0.16222 | 1090 | 21.6398
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8841 | 0 | -0.25801 | 0 | 1090 | 21.6398 | Line Rating | 1100
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.699 | 0 | -0.25801 | 0 | 1090 | 21.6398 | Conc Gen | 2174
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6772 | 0 | -0.25801 | 0 | 1090 | 21.6398 | Weighted Imp. | 301.076
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.010891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6772 | 0 | -0.25801 | 0 | 1090 | 21.6398 | PTDF | 0.13849
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.010891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7643 | 0 | -0.25801 | 0 | 1090 | 21.6398
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59892 | 56 | -0.25781 | -14.4375 | 1146 | 36.0774 | Concentration | 0.52096
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.63101 | 59 | -0.25781 | -15.211 | 1205 | 51.2883
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59892 | 56 | -0.25781 | -14.4375 | 1261 | 65.7259
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59892 | 56 | -0.25781 | -14.4375 | 1317 | 80.1634
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.63101 | 59 | -0.25781 | -15.211 | 1376 | 95.3744
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.010695 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59892 | 56 | -0.25781 | -14.4375 | 1432 | 109.8119
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.010673 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.2479 | 398 | -0.25779 | -102.6008 | 1830 | 212.4127
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7351 | 0 | -0.25778 | 0 | 1830 | 212.4127
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7202 | 0 | -0.25778 | 0 | 1830 | 212.4127
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6936 | 0 | -0.25778 | 0 | 1830 | 212.4127
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.010658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8691 | 0 | -0.25778 | 0 | 1830 | 212.4127
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.010624 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8273 | 172 | -0.25774 | -44.3316 | 2002 | 256.7444
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.010624 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8273 | 172 | -0.25774 | -44.3316 | 2174 | 301.076
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.010624 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8273 | 172 | -0.25774 | -44.3316
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.010621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6675 | 0 | -0.25774 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.01061 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -7.8832 | 743 | -0.25773 | -191.4919
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68965 | 0 | -0.25773 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70026 | 0 | -0.25773 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7427 | 0 | -0.25773 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66843 | 0 | -0.25773 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65782 | 0 | -0.25773 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1034 | 0 | -0.25773 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.01061 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.62599 | 0 | -0.25773 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.010609 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.12731 | 0 | -0.25773 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.010608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.05304 | 0 | -0.25773 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.010608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22277 | 0 | -0.25773 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12715 | 12 | -0.25771 | -3.0926
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35952 | 0 | -0.25769 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36692 | 0 | -0.25769 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34577 | 0 | -0.25769 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48535 | 0 | -0.25769 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18716 | 0 | -0.25769 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21571 | 0 | -0.25769 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21042 | 0 | -0.25769 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37009 | 0 | -0.25769 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19033 | 0 | -0.25769 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90302 | 0 | -0.25769 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.010574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.565 | 0 | -0.25769 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.010562 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -7.7631 | 735 | -0.25768 | -189.3948
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0976 | 104 | -0.25767 | -26.7979
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0976 | 104 | -0.25767 | -26.7979
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.56992 | 54 | -0.25767 | -13.9143
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.55936 | 53 | -0.25767 | -13.6566
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.56992 | 54 | -0.25767 | -13.9143
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.60158 | 57 | -0.25767 | -14.6873
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.56992 | 54 | -0.25767 | -13.9143
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.56992 | 54 | -0.25767 | -13.9143
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61213 | 58 | -0.25767 | -14.945
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.010554 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61213 | 58 | -0.25767 | -14.945
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.010502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8168 | 0 | -0.25762 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.010502 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4178 | 0 | -0.25762 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.010493 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.427 | 0 | -0.25761 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.44062 | 42 | -0.25761 | -10.8196
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.44062 | 42 | -0.25761 | -10.8196
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39866 | 38 | -0.25761 | -9.7891
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.010491 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39866 | 38 | -0.25761 | -9.7891
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74273 | 0 | -0.25758 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75319 | 0 | -0.25758 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40798 | 0 | -0.25758 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.010461 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31383 | 0 | -0.25758 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.010443 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8797 | 0 | -0.25756 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.010443 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6563 | 0 | -0.25756 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.010443 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6396 | 0 | -0.25756 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.010442 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.3808 | 228 | -0.25756 | -58.7237
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66829 | 0 | -0.25756 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65993 | 0 | -0.25756 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86251 | 0 | -0.25756 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76853 | 0 | -0.25756 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.010442 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16916 | 0 | -0.25756 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.010441 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.2239 | 213 | -0.25756 | -54.8601
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.010439 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5554 | 0 | -0.25756 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.010439 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67958 | 0 | -0.25756 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.010438 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7223 | 165 | -0.25756 | -42.4967
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.010437 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7639 | 169 | -0.25756 | -43.5268
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010436 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12523 | 12 | -0.25755 | -3.0906
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.010436 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25755 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.010424 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36484 | 0 | -0.25754 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6986 | 0 | -0.25753 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6351 | 0 | -0.25753 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6393 | 0 | -0.25753 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6341 | 0 | -0.25753 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.010408 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7998 | 0 | -0.25753 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.010396 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.81089 | 0 | -0.25751 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.010396 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.83168 | 0 | -0.25751 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47812 | 46 | -0.25751 | -11.8456
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47812 | 46 | -0.25751 | -11.8456
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47812 | 46 | -0.25751 | -11.8456
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57167 | 55 | -0.25751 | -14.1632
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57167 | 55 | -0.25751 | -14.1632
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.010394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.56128 | 54 | -0.25751 | -13.9057
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67223 | 0 | -0.25746 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.62052 | 0 | -0.25746 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67223 | 0 | -0.25746 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.010342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67223 | 0 | -0.25746 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93857 | 0 | -0.25743 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90351 | 0 | -0.25743 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89732 | 0 | -0.25743 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56211 | 0 | -0.25743 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.010314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12583 | 0 | -0.25743 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.010239 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25736 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.010189 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.50945 | 50 | -0.25731 | -12.8654
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71473 | 0 | -0.25721 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67334 | 0 | -0.25721 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53504 | 0 | -0.25721 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5466 | 0 | -0.25721 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5496 | 0 | -0.25721 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5375 | 0 | -0.25721 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.96912 | 0 | -0.25721 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.010095 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4632 | 0 | -0.25721 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.010095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4038 | 0 | -0.25721 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.010094 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32301 | 0 | -0.25721 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.010094 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30282 | 0 | -0.25721 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0124 | 0 | -0.25721 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.93773 | 0 | -0.25721 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0367 | 0 | -0.25721 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.010094 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0296 | 0 | -0.25721 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.009931 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.5989 | 161 | -0.25705 | -41.3849
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.009931 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.6485 | 166 | -0.25705 | -42.6701
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.009931 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4629 | 248 | -0.25705 | -63.7482
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.009931 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -5.4223 | 546 | -0.25705 | -140.3488
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.009931 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -6.3856 | 0 | -0.25705 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.009931 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1291 | 13 | -0.25705 | -3.3416
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.009872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32578 | 0 | -0.25699 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.009858 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6069 | 0 | -0.25698 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.009858 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6069 | 0 | -0.25698 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.009858 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4152 | 0 | -0.25698 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.009855 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.4156 | 0 | -0.25697 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.009855 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.5582 | 0 | -0.25697 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.009855 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.913 | 0 | -0.25697 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.009814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45243 | 0 | -0.25693 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.023504 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.688 | 242 | -0.0047862 | -1.1583
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0462 | 0 | -0.25654 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0462 | 0 | -0.25654 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1216 | 0 | -0.25654 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.009425 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.032 | 0 | -0.25654 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.009304 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66058 | 0 | -0.25642 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.009304 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09304 | 0 | -0.25642 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56804 | 0 | -0.25628 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65417 | 0 | -0.25628 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41229 | 0 | -0.25628 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92536 | 0 | -0.25628 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78793 | 0 | -0.25628 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.80626 | 0 | -0.25628 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4581 | 0 | -0.25628 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16492 | 0 | -0.25628 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86123 | 0 | -0.25628 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64134 | 0 | -0.25628 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57721 | 0 | -0.25628 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65966 | 0 | -0.25628 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5937 | 0 | -0.25628 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92536 | 0 | -0.25628 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88871 | 0 | -0.25628 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.94369 | 0 | -0.25628 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69631 | 0 | -0.25628 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73296 | 0 | -0.25628 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73296 | 0 | -0.25628 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.009162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5667 | 0 | -0.25628 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.008868 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -5.0459 | 0 | -0.25599 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.008868 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -5.1523 | 0 | -0.25599 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.022404 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.3442 | 60 | -0.0036862 | -0.22117
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.022404 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4115 | 63 | -0.0036862 | -0.23223
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.008561 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.56503 | 66 | -0.25568 | -16.8748
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.64418 | 76 | -0.25559 | -19.4251
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.64418 | 76 | -0.25559 | -19.4251
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.88998 | 105 | -0.25559 | -26.8374
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62722 | 74 | -0.25559 | -18.914
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62722 | 74 | -0.25559 | -18.914
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.008476 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.86455 | 102 | -0.25559 | -26.0706
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.008368 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -11.1545 | 0 | -0.25549 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.008368 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -11.1127 | 0 | -0.25549 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.022061 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0033432 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.022061 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0033432 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.022061 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0033432 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.021427 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.4105 | 0 | -0.0027092 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.007175 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -4.1902 | 0 | -0.25429 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.007175 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -4.2691 | 0 | -0.25429 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.007174 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.1063 | 0 | -0.25429 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.007171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.133 | 158 | -0.25429 | -40.1777
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.007171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1474 | 160 | -0.25429 | -40.6862
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.007171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.2549 | 175 | -0.25429 | -44.5006
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3523 | 50 | -0.25416 | -12.7082
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3523 | 50 | -0.25416 | -12.7082
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3523 | 50 | -0.25416 | -12.7082
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.007046 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3523 | 50 | -0.25416 | -12.7082
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.006862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.90578 | 132 | -0.25398 | -33.5254
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.006862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.91951 | 134 | -0.25398 | -34.0333
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.006862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2164 | 323 | -0.25398 | -82.0356
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.006834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0422 | 152.5 | -0.25395 | -38.7277
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.006834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0217 | 149.5 | -0.25395 | -37.9658
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.006834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.5896 | 232.6 | -0.25395 | -59.0692
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.27657 | 42 | -0.2537 | -10.6555
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.28974 | 44 | -0.2537 | -11.1629
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.28974 | 44 | -0.2537 | -11.1629
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.006585 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3095 | 47 | -0.2537 | -11.924
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.020288 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0015702 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.006441 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.9967 | 310 | -0.25356 | -78.6033
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.006441 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.6601 | 413 | -0.25356 | -104.7199
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31277 | 49 | -0.2535 | -12.4216
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.29362 | 46 | -0.2535 | -11.661
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.29362 | 46 | -0.2535 | -11.661
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3 | 47 | -0.2535 | -11.9145
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.006383 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.98298 | 154 | -0.2535 | -39.0392
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.006383 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.94468 | 148 | -0.2535 | -37.5182
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.30638 | 48 | -0.2535 | -12.1681
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.006383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.30638 | 48 | -0.2535 | -12.1681
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.006286 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.050288 | 0 | -0.2534 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.006286 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.050288 | 0 | -0.2534 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.019914 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.79656 | 0 | -0.0011962 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.019914 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.79656 | 0 | -0.0011962 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.01989 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0011722 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.019861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.72 | 288 | -0.0011432 | -0.32924
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.019861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9196 | 147 | -0.0011432 | -0.16805
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.019861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9196 | 147 | -0.0011432 | -0.16805
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.019814 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.3684 | 170 | -0.0010962 | -0.18635
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.019814 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.3033 | 520 | -0.0010962 | -0.57002
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4676 | 0 | -0.25304 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47944 | 0 | -0.25304 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4676 | 0 | -0.25304 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47352 | 0 | -0.25304 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46405 | 0 | -0.25304 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14797 | 0 | -0.25304 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27227 | 0 | -0.25304 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.16573 | 0 | -0.25304 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.25807 | 0 | -0.25304 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.005919 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.43801 | 0 | -0.25304 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.019687 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.2842 | 370 | -0.0009692 | -0.3586
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.7562 | 0 | -0.0009692 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.7759 | 0 | -0.0009692 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -6.0833 | 0 | -0.0009692 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.8152 | 0 | -0.0009692 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.8349 | 0 | -0.0009692 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.019687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -6.103 | 0 | -0.0009692 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.005846 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28061 | 0 | -0.25296 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1411 | 160 | -0.0009142 | -0.14627
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0626 | 156 | -0.0009142 | -0.14261
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8479 | 196 | -0.0009142 | -0.17918
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0626 | 156 | -0.0009142 | -0.14261
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0822 | 157 | -0.0009142 | -0.14353
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.019632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8871 | 198 | -0.0009142 | -0.18101
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.019596 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.4697 | 0 | -0.0008782 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.019596 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.5598 | 0 | -0.0008782 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.019596 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7323 | 0 | -0.0008782 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.019532 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.8989 | 0 | -0.0008142 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.019532 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -11.309 | 0 | -0.0008142 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.019532 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.7819 | 0 | -0.0008142 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.1561 | 0 | -0.25269 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.039025 | 0 | -0.25269 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.21743 | 0 | -0.25269 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.083625 | 0 | -0.25269 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.039025 | 0 | -0.25269 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.083625 | 0 | -0.25269 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.21743 | 0 | -0.25269 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.005575 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.21743 | 0 | -0.25269 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.019361 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.3233 | 0 | -0.0006432 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.005522 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.044176 | 0 | -0.25264 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.005503 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.082545 | 0 | -0.25262 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.005503 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12657 | 0 | -0.25262 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.019295 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -7.6215 | 395 | -0.0005772 | -0.22799
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.019295 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.3933 | 435 | -0.0005772 | -0.25108
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.019277 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.3855 | 435 | -0.0005592 | -0.24325
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.019274 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5226 | 79 | -0.0005562 | -0.04394
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.019274 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.043 | 106 | -0.0005562 | -0.058957
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.019274 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.814 | 146 | -0.0005562 | -0.081205
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.019274 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.4648 | 76 | -0.0005562 | -0.042271
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.00541 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.39493 | 0 | -0.25253 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.019209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.38418 | 20 | -0.0004912 | -0.0098239
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.019209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.48023 | 25 | -0.0004912 | -0.01228
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.019209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.78757 | 41 | -0.0004912 | -0.020139
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.005375 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0129 | 0 | -0.25249 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.005375 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0129 | 0 | -0.25249 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.019206 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.76824 | 40 | -0.0004882 | -0.019528
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.005338 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76867 | 144 | -0.25246 | -36.3537
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.005338 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0035 | 188 | -0.25246 | -47.4617
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.005314 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.063768 | 0 | -0.25243 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1867 | 223.9 | -0.25242 | -56.5164
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1925 | 225 | -0.25242 | -56.7941
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1904 | 224.6 | -0.25242 | -56.6931
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.0053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.2015 | 226.7 | -0.25242 | -57.2232
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25105 | 47.7 | -0.25238 | -12.0386
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19631 | 37.3 | -0.25238 | -9.4138
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2421 | 46 | -0.25238 | -11.6095
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.005263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25262 | 48 | -0.25238 | -12.1143
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.005104 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.11229 | 22 | -0.25222 | -5.5489
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.005104 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.056144 | 11 | -0.25222 | -2.7744
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.005104 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.056144 | 11 | -0.25222 | -2.7744
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.005087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012209 | 0 | -0.25221 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.005087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012209 | 0 | -0.25221 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.005087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014244 | 0 | -0.25221 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.72065 | 142 | -0.25219 | -35.8114
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73587 | 145 | -0.25219 | -36.568
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76633 | 151 | -0.25219 | -38.0812
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.005075 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4717 | 290 | -0.25219 | -73.136
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.018905 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.3351 | 388 | -0.0001872 | -0.072633
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.018905 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.7361 | 515 | -0.0001872 | -0.096407
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.031 | 161 | -0.0001082 | -0.01742
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0875 | 164 | -0.0001082 | -0.017744
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0875 | 164 | -0.0001082 | -0.017744
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.794 | 414 | -0.0001082 | -0.044794
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0498 | 162 | -0.0001082 | -0.017528
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.031 | 161 | -0.0001082 | -0.01742
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0686 | 163 | -0.0001082 | -0.017636
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.018826 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.6998 | 409 | -0.0001082 | -0.044253
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.004979 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.029874 | 0 | -0.2521 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.018811 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -9.3197e-05 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.018811 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -9.3197e-05 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71295 | 147 | -0.25197 | -37.0393
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6693 | 138 | -0.25197 | -34.7716
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.679 | 140 | -0.25197 | -35.2755
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71295 | 147 | -0.25197 | -37.0393
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.8827 | 182 | -0.25197 | -45.8582
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.00485 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.9603 | 198 | -0.25197 | -49.8897
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.75793 | 0 | -0.25192 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.73394 | 0 | -0.25192 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.4797 | 0 | -0.25192 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.69556 | 0 | -0.25192 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.70516 | 0 | -0.25192 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.004797 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.60922 | 0 | -0.25192 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.004797 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.057564 | 0 | -0.25192 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.004762 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.019048 | 0 | -0.25188 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 0 | -0.25185 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 0 | -0.25185 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 0 | -0.25185 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.075728 | 0 | -0.25185 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 0 | -0.25185 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 0 | -0.25185 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11832 | 0 | -0.25185 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.004733 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.070995 | 0 | -0.25185 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.018544 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.1882 | 118 | 0.0001738 | 0.020509
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.018544 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.1326 | 115 | 0.0001738 | 0.019987
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.018544 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.3105 | 556 | 0.0001738 | 0.096634
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.004698 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.955 | 0 | -0.25182 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16412 | 0 | -0.25181 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15943 | 0 | -0.25181 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16412 | 0 | -0.25181 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.004646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.5611 | 336 | -0.25176 | -84.5927
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.004646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83628 | 180 | -0.25176 | -45.3175
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.004645 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.68885 | 0 | -0.25176 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.004645 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.69025 | 0 | -0.25176 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.004645 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.71069 | 0 | -0.25176 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.004642 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83556 | 180 | -0.25176 | -45.3168
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.004617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5421 | 334 | -0.25174 | -84.0795
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.004617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5698 | 340 | -0.25174 | -85.5899
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.004617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83106 | 180 | -0.25174 | -45.3123
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.004617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83106 | 180 | -0.25174 | -45.3123
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.004598 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.11495 | 0 | -0.25172 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.004598 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.11495 | 0 | -0.25172 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.004597 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.17469 | 0 | -0.25172 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.004578 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.17396 | 0 | -0.2517 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.0045 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.1305 | 0 | -0.25162 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.41576 | 0 | -0.25154 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.18134 | 0 | -0.25154 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.16807 | 0 | -0.25154 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.084037 | 0 | -0.25154 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.41576 | 0 | -0.25154 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.15923 | 0 | -0.25154 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.19019 | 0 | -0.25154 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.097306 | 0 | -0.25154 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.6546 | 0 | -0.25154 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.22115 | 0 | -0.25154 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.24327 | 0 | -0.25154 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.004423 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.22115 | 0 | -0.25154 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.004359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.16564 | 38 | -0.25148 | -9.5561
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.004359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.084129 | 19.3 | -0.25148 | -4.8535
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.004359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.065385 | 15 | -0.25148 | -3.7722
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.004359 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20487 | 47 | -0.25148 | -11.8194
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.004359 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25148 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.004285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.3396 | 0 | -0.2514 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.004285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.2138 | 0 | -0.2514 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.004197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60437 | 144 | -0.25132 | -36.1894
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.004197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60437 | 144 | -0.25132 | -36.1894
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.004197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71769 | 171 | -0.25132 | -42.9749
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.004196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.86857 | 207 | -0.25131 | -52.022
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.004196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.90927 | 216.7 | -0.25131 | -54.4598
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.004196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0154 | 242 | -0.25131 | -60.818
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.004186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64883 | 155 | -0.2513 | -38.9521
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.004186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71162 | 170 | -0.2513 | -42.7217
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.004186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64883 | 155 | -0.2513 | -38.9521
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.004096 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25121 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.004096 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25121 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.004096 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25121 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.017835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.0005 | 0 | 0.0008828 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.017835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.1788 | 0 | 0.0008828 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.017835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.9113 | 0 | 0.0008828 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.003924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57487 | 146.5 | -0.25104 | -36.7777
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.003924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.58036 | 147.9 | -0.25104 | -37.1291
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.003924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.67885 | 173 | -0.25104 | -43.4303
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.6196 | 0 | 0.0010178 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.301 | 0 | 0.0010178 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.5665 | 0 | 0.0010178 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0177 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0623 | 0 | 0.0010178 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.003833 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.6252 | 0 | -0.25095 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.003833 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.629 | 0 | -0.25095 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.003764 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25088 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.003763 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5504 | 412 | -0.25088 | -103.363
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.003763 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5052 | 400 | -0.25088 | -100.3524
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.003756 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.785 | 209 | -0.25087 | -52.4327
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.003756 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.8113 | 216 | -0.25087 | -54.1888
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17278 | 46 | -0.25087 | -11.5402
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17653 | 47 | -0.25087 | -11.7911
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17278 | 46 | -0.25087 | -11.5402
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.003756 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17278 | 46 | -0.25087 | -11.5402
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.017585 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0011328 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.017572 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.8786 | 0 | 0.0011458 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.017549 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.1939 | 182 | 0.0011688 | 0.21272
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.017549 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.4937 | 484 | 0.0011688 | 0.5657
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.017507 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7885 | 216.4 | 0.0012108 | 0.26202
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.017507 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7833 | 216.1 | 0.0012108 | 0.26165
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.003641 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4819 | 407 | -0.25076 | -102.0589
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.003589 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25071 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.003576 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.4161 | 0 | -0.25069 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.017255 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.382 | 196 | 0.0014628 | 0.28671
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.017255 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.9153 | 111 | 0.0014628 | 0.16237
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3827 | 0 | -0.25048 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.74525 | 0 | -0.25048 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.61769 | 0 | -0.25048 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.75197 | 0 | -0.25048 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.38605 | 0 | -0.25048 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.017185 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.30933 | 18 | 0.0015328 | 0.02759
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.017185 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.30933 | 18 | 0.0015328 | 0.02759
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.017185 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.65303 | 38 | 0.0015328 | 0.058247
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.003265 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.18937 | 58 | -0.25038 | -14.5222
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.003265 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.29058 | 89 | -0.25038 | -22.2841
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14366 | 44 | -0.25038 | -11.0169
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14366 | 44 | -0.25038 | -11.0169
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14039 | 43 | -0.25038 | -10.7665
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.003265 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14693 | 45 | -0.25038 | -11.2672
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.017073 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.8244 | 224 | 0.0016448 | 0.36844
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.784 | 224 | 0.0018248 | 0.40876
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8178 | 226 | 0.0018248 | 0.41241
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5813 | 212 | 0.0018248 | 0.38686
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.016893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5644 | 211 | 0.0018248 | 0.38503
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.016423 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4881 | 151.5 | 0.0022948 | 0.34766
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.016423 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.5012 | 152.3 | 0.0022948 | 0.3495
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.016423 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9151 | 177.5 | 0.0022948 | 0.40733
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.016374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4676 | 150.7 | 0.0023438 | 0.35321
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.016374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4725 | 151 | 0.0023438 | 0.35391
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.016374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9047 | 177.4 | 0.0023438 | 0.41579
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.016145 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -9.9292 | 0 | 0.0025728 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.016145 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -9.4771 | 0 | 0.0025728 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.00229 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02748 | 0 | -0.24941 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.00229 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02519 | 0 | -0.24941 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.00229 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02748 | 0 | -0.24941 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.015925 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0027928 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.015622 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.18746 | 0 | 0.0030958 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.015622 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.18746 | 0 | 0.0030958 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.001098 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.019764 | 0 | -0.24822 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.001098 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.019764 | 0 | -0.24822 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.014808 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.2462 | 0 | 0.0039098 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.014808 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.1278 | 0 | 0.0039098 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.000727 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24785 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.2402 | 0 | 0.0044018 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.2402 | 0 | 0.0044018 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1803 | 0 | 0.0044018 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.014316 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1903 | 0 | 0.0044018 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.014225 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3898 | 168 | 0.0044928 | 0.75479
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.014225 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.2803 | 90 | 0.0044928 | 0.40435
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.98343 | 70 | 0.0046688 | 0.32682
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96938 | 69 | 0.0046688 | 0.32215
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96938 | 69 | 0.0046688 | 0.32215
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.014049 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.95533 | 68 | 0.0046688 | 0.31748
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.24712 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24712 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24712 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 4.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001344 | 0 | -0.24707 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 4.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001392 | 0 | -0.24707 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.013669 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2554 | 0 | 0.0050488 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.000391 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.007038 | 0 | -0.24673 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.000391 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.007038 | 0 | -0.24673 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.000391 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.005865 | 0 | -0.24673 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.000486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.20509 | 422 | -0.24663 | -104.0787
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.013189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.866 | 217.3 | 0.0055288 | 1.2014
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.013189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7037 | 205 | 0.0055288 | 1.1334
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.013189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5927 | 272.4 | 0.0055288 | 1.506
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.013167 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0055508 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.013167 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.3624 | 787 | 0.0055508 | 4.3685
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056188 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056188 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.013099 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.22268 | 17 | 0.0056188 | 0.09552
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056188 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.013099 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056188 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.013091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -6.0611 | 0 | 0.0056268 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.013091 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.41891 | 0 | 0.0056268 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.013072 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.62746 | 48 | 0.0056458 | 0.271
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.013072 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.60131 | 46 | 0.0056458 | 0.25971
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.013072 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.3726 | 105 | 0.0056458 | 0.59281
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.001053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1053 | 100 | -0.24607 | -24.6065
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.001053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1053 | 100 | -0.24607 | -24.6065
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24607 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24607 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24607 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001053 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24607 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.001056 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24606 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.012731 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.19096 | 0 | 0.0059868 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.012731 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.19096 | 0 | 0.0059868 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.9608 | 0 | 0.0060018 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.9837 | 0 | 0.0060018 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.9837 | 0 | 0.0060018 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.012716 | north | 1 | N | N | Nnorth | Nnorth | 1 | -4.8321 | 0 | 0.0060018 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.012708 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060098 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.012708 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060098 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.012686 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2349 | 255 | 0.0060318 | 1.5381
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.012686 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.8902 | 149 | 0.0060318 | 0.89874
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.012686 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.941 | 153 | 0.0060318 | 0.92287
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.012486 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.91148 | 73 | 0.0062318 | 0.45492
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.012486 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.4858 | 119 | 0.0062318 | 0.74158
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.012486 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.5596 | 205 | 0.0062318 | 1.2775
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.012486 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.2736 | 102 | 0.0062318 | 0.63564
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.012486 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.1987 | 96 | 0.0062318 | 0.59825
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.012357 | north | 3 | N | N | Nnorth | Nnorth | 1 | -14.297 | 0 | 0.0063608 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.012357 | north | 3 | N | N | Nnorth | Nnorth | 1 | -14.3094 | 0 | 0.0063608 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.012318 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.8477 | 150 | 0.0063998 | 0.95997
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.012318 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.98544 | 80 | 0.0063998 | 0.51198
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.002484 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.034031 | 0 | -0.24463 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.004199 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.10078 | 24 | -0.24292 | -5.8301
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.004199 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.10078 | 24 | -0.24292 | -5.8301
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.004199 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.096577 | 23 | -0.24292 | -5.5871
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005811 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.048812 | 8.4 | -0.24131 | -2.027
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.003357 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.3357 | 0 | 0.015361 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.002066 | west | 4 | Y | N | Ywest | Nwest | 1 | -1.3423 | 0 | 0.016652 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.001925 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.4543 | 0 | 0.016793 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.001756 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.7024 | 0 | 0.016962 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.018718 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.018718 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.002903 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.17418 | 0 | 0.021621 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.036668 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21045 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.040613 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.24368 | 0 | -0.20651 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.057571 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8998 | 0 | -0.18955 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.057571 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4393 | 0 | -0.18955 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.057571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18955 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.045609 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.064327 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.076813 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2176 | 0 | 0.095531 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.076813 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8974 | 0 | 0.095531 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.076813 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.0736 | 0 | 0.095531 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.090905 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4084 | 0 | 0.10962 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.11925 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1553 | 0 | 0.13797 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.13254 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.8808 | 0 | 0.15126 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.17126 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.6892 | 0 | 0.18998 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.17126 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2974 | 0 | 0.18998 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.18785 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.1774 | 0 | 0.20657 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.19886 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.21758 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.2582 | 0 | 0.2699 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 1 | 37.552 | 0 | 0.2699 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 1 | 46.7202 | 0 | 0.2699 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.25118 | west | 6 | Y | N | Ywest | Nwest | 1 | 53.879 | 0 | 0.2699 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.25979 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.8738 | 0 | 0.27851 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.26057 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.8876 | 0 | 0.27928 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.26163 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.9772 | 0 | 0.28035 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.26453 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1623 | 0 | 0.28325 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.26498 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.7475 | 0 | 0.2837 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.2752 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8163 | 0 | 0.29392 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.2752 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4394 | 0 | 0.29392 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.27627 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.4408 | 0 | 0.29499 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.27627 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.4408 | 0 | 0.29499 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.27661 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.1289 | 0 | 0.29533 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.27669 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.135 | 0 | 0.29541 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.27709 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.782 | 0 | 0.29581 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.27709 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.1674 | 0 | 0.29581 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.27709 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.0837 | 0 | 0.29581 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.27846 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.567 | 0 | 0.29717 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.27846 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.9858 | 0 | 0.29717 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.27846 | west | 7 | N | N | Nwest | Nwest | 1 | 6.9614 | 0 | 0.29717 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.27846 | west | 7 | N | N | Nwest | Nwest | 1 | 12.7254 | 0 | 0.29717 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.27846 | west | 7 | N | N | Nwest | Nwest | 1 | 12.7254 | 0 | 0.29717 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.27926 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.3757 | 0 | 0.29798 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.27926 | west | 6 | Y | N | Ywest | Nwest | 1 | 33.5112 | 0 | 0.29798 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.27929 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.3433 | 0 | 0.29801 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.27929 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.3433 | 0 | 0.29801 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.28323 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8437 | 0 | 0.30195 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.28983 | west | #N/A | N | N | Nwest | Nwest | 1 | 1.3912 | 0 | 0.30855 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.2905 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.2891 | 0 | 0.30921 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.2905 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.2891 | 0 | 0.30921 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.29129 | west | 6 | Y | N | Ywest | Nwest | 1 | 65.5405 | 0 | 0.31001 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.29304 | west | 8 | N | N | Nwest | Nwest | 1 | 7.5605 | 0 | 0.31176 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.29628 | west | 6 | Y | N | Ywest | Nwest | 1 | 35.553 | 0 | 0.31499 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.29876 | west | 6 | Y | N | Ywest | Nwest | 1 | 35.8512 | 0 | 0.31748 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.4388 | 66 | 0.3284 | 21.6742
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.3679 | 69 | 0.3284 | 22.6594
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.3679 | 69 | 0.3284 | 22.6594
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.7485 | 67 | 0.3284 | 22.0026
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.7485 | 67 | 0.3284 | 22.0026
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.30968 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.1291 | 65 | 0.3284 | 21.3458
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.31008 | west | 6 | Y | N | Ywest | Nwest | 1 | 66.4196 | 0 | 0.3288 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.31015 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.9886 | 0 | 0.32887 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.31085 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.2407 | 0 | 0.32957 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.31102 | west | 6 | Y | N | Ywest | Nwest | 1 | 46.3414 | 0 | 0.32973 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.31277 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.9469 | 0 | 0.33149 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.31277 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3831 | 0 | 0.33149 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.7074 | 66 | 0.33247 | 21.9428
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 20.3937 | 65 | 0.33247 | 21.6103
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.0212 | 67 | 0.33247 | 22.2753
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.0212 | 67 | 0.33247 | 22.2753
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.31375 | west | 13 | Y | Y | Ywest | Ywest | 1 | 21.0212 | 67 | 0.33247 | 22.2753
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.31375 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33247 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.31375 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33247 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 67.4258 | 208.2 | 0.34257 | 71.3228
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 46.0192 | 142.1 | 0.34257 | 48.679
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 42.8779 | 132.4 | 0.34257 | 45.3561
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 44.0437 | 136 | 0.34257 | 46.5894
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 47.6061 | 147 | 0.34257 | 50.3576
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.32385 | west | 9 | Y | Y | Ywest | Ywest | 1 | 68.0087 | 210 | 0.34257 | 71.9394
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 22.6768 | 70 | 0.34267 | 23.987
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 22.6768 | 70 | 0.34267 | 23.987
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 30.0629 | 92.8 | 0.34267 | 31.7999
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.9163 | 80 | 0.34267 | 27.4137
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.9163 | 80 | 0.34267 | 27.4137
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.32395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 37.2547 | 115 | 0.34267 | 39.4073
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.33109 | west | 8 | N | N | Nwest | Nwest | 1 | 23.1761 | 0 | 0.3498 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.33109 | west | 8 | N | N | Nwest | Nwest | 1 | 24.3018 | 0 | 0.3498 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.33109 | west | 8 | N | N | Nwest | Nwest | 1 | 23.3085 | 0 | 0.3498 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 1 | 49.9918 | 0 | 0.352 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 1 | 73.3214 | 0 | 0.352 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 1 | 66.6558 | 0 | 0.352 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.33328 | west | 6 | Y | N | Ywest | Nwest | 1 | 40.6267 | 0 | 0.352 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.592 | 0 | 0.3545 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.097 | 0 | 0.3545 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 45.3311 | 0 | 0.3545 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.9585 | 0 | 0.3545 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 35.2575 | 0 | 0.3545 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.0308 | 0 | 0.3545 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.9733 | 0 | 0.3545 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.33579 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.9733 | 0 | 0.3545 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 1 | 86.8512 | 0 | 0.43427 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.5678 | 0 | 0.43427 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 1 | 103.4734 | 0 | 0.43427 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.41556 | west | 6 | Y | N | Ywest | Nwest | 1 | 81.8645 | 0 | 0.43427 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating
| Temp | Tonkawa - Graham
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1307
| 65 | 1280
| 70 | 1251
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| total | 24709
| avg | 1235.45