## test results
CRE test for: |  | MURRY_P8 - GRHAMSES 138kV [1371 - 1431] | [5 empty] | FAIL
Line Rating: |  | 223
Direcction |  | west | → | north |  | w-n
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | MURRY_P8 - GRHAMSES 138kV [1371 - 1431]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.0054746
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.0010756
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.046923
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.0024321
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | MURRY_P8 - GRHAMSES 138kV [1371 - 1431]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.0060442
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.00099623
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.048351
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0024549
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | MURRY_P8 - GRHAMSES 138kV [1371 - 1431]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.0044784
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.053826
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.0030197
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.049427
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.0013565
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.049378
PTDF tests
west | → | north | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | 0.052967 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.052967 | -0.0044784
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.11035
[6 empty] | Concentration |  | 2.0835 | FAIL
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.041919
[6 empty] | Concentration |  | 0.79141 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 76.701
| Percent of line rating => | [6 empty] | 34.4% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 15.3441
[7 empty] | B1(N-S) | 0.02859 | -0.040127 | -0.068717 | 0.02859
[7 empty] | B2 (N-W) | 0.011142 | -0.81477 | -0.82591 | 0.011142
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.02736 | -0.018975 | -0.046335 | 0.02736
[7 empty] | B4 (S-W) | -0.017359 | -0.77577 | -0.75841 | -0.017359
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.00079085 | 0.020024 | 0.020815 | -0.00079085
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.035279 | 0.79294 | 0.75766 | 0.035279
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | 3.518%
Deployment Error Percent | [6 empty] | B2 | 1.371%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 3.366%
[7 empty] | B4 | -2.136%
[7 empty] | B5 | -0.09731%
[7 empty] | B6 | 4.341%
[7 empty] | Max Abs Error | 4.341% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: MURRY_P8 - GRHAMSES 138kV [1371 - 1431] C:SWEETWATER / MULBERRY - LONGCREEK8 [1420 - 1439] & [1435 - 6230] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: MURRY_P8 - GRHAMSES 138kV [1371 - 1431] C:SWEETWATER / MULBERRY - LONGCREEK8 [1420 - 1439] & [1435 - 6230]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.003354 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -0.85527
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.003354 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -0.49975
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.003864 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.05796
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.003864 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.05796
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.003354 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -0.51316
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.003431 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -0.51465
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.003431 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -0.27448
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.01243 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -0.90739
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.01243 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -1.4792
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.01243 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -2.5482
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.01243 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -1.2679
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.01243 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -1.1933
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.022872 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.27446
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.022872 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.27446
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.004241 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -0.71249
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.004241 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -0.38169
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.012649 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.22768
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.012649 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.22768
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.012649 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.48066
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.010067 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -2.8993
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.010067 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -1.4798
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.010067 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -1.4798
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.00799 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -0.89887
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.004757 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.19028
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.004775 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -0.37722
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.004775 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -0.50615
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.004775 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -0.69715
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.004775 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -0.3629
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.005785 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -0.3471
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.005785 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -0.36445
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.004758 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.09516
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.004758 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.11895
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.004758 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.19508
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.00318 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -1.4723
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 3.2862
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 3.2364
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.336
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.336
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.336
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.049791 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 5.6762
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.049791 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 25.6424
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 3.7132
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 3.882
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 3.882
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 3.7695
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 3.7695
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 3.657
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.04863 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 3.4041
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.04863 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 3.5694
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.04863 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 3.4236
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 7.256
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 10.6421
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.07283 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 7.2102
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.07283 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 4.4426
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.072361 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 10.2029
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.07283 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 1.8208
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.07283 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 3.3283
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.07283 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 3.3283
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.072361 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 8.6833
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.057371 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 1.4802
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.053266 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 5.3532
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.059199 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 7.1039
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.0533 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 3.0914
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.053715 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 11.5058
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.071768 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 10.7652
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.055664 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.36738
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.055664 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.9093
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.071768 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 7.2486
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.060516 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 7.2619
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.010387 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -3.8016
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.06948 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -16.8142
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.010387 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -4.1548
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.010387 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -2.4513
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.010387 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -1.7139
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.006731 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -1.3731
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.006731 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -1.3529
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.006731 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -1.6289
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.24312
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.24312
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.24312
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.20665
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.039371 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -4.7245
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.005833 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -0.34998
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.004894 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -0.36705
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.004894 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -0.38956
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.004894 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -0.43263
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -0.7832
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.76362
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -0.95942
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.76362
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -0.76851
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -0.96921
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.005021 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -0.85357
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.005021 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -2.6109
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.004914 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -1.8182
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.004851 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -2.7069
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.004851 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -2.8087
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.004851 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -3.9196
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.006079 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -0.68085
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.006079 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -0.6079
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.006079 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -2.2979
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.002828 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -0.61452
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.002828 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -0.57974
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.002828 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -0.77035
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.003729 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -2.8713
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -0.32067
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.31609
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.31609
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -0.31151
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.002576 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -2.9804
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.002576 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -2.983
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -0.92019
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -0.92841
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.004253 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -0.92035
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.004253 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -0.91907
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -0.8709
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -0.86679
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.004775 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -1.8861
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.004785 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -2.0815
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.004775 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -2.0771
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.005079 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -0.7009
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.004569 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -0.53914
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.004569 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -0.52543
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.004569 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -2.5404
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.004673 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -1.8131
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.004673 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -2.4066
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.004395 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -3.4501
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.004395 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -3.494
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.004395 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -3.4281
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.004322 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -0.7866
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.004322 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -2.0918
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.004251 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -0.95222
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.004326 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -0.2163
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.00433 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.18186
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.003951 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -2.4299
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.003951 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -2.3192
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.003263 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -1.7522
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.003263 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -2.568
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.003161 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -0.23708
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.003161 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -0.70174
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.002088 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -1.1881
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000803 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -0.16783
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000803 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -0.17345
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.000774 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -0.31502
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.036938
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -0.037741
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.036938
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.036938
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.000819 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -0.34726
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.000819 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -0.34808
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000689 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -0.039962
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000689 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -0.061321
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.030316
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.030316
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.029627
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -0.031005
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.000804 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -0.33125
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.000804 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -0.3216
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.000927 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -0.50614
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.000927 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -0.69525
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.000881 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -0.053741
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.000881 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -0.083695
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.000881 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -0.13303
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.000899 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.13934
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.000899 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -0.15283
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.000899 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.13934
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.001169 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.025718
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.001169 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.012859
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.001169 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.012859
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.057431
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.044909
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.055384
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.057792
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.00052 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.00624
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.00052 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.00572
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.00096 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.02304
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.00096 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.02304
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.00096 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.02208
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.000789 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -0.31244
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.001971 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -2.6273
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.001971 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -2.6175
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.00099 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.03762
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.00099 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.019107
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.00099 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.01485
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.00099 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.04653
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.04679 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 3.5093
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.12384 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 18.5755
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.051151 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 8.6701
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.03542 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 5.313
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.068767 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 4.3323
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.026215 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 17.0319
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.005094 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.20376
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.005094 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.20376
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.000715 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 0.30173
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.001541 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -0.20341
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.001541 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -0.20649
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.001541 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -0.49774
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.001637 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -0.25865
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.001637 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -0.26192
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.001637 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -0.28647
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.00164 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -0.95776
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.00164 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -0.9758
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.00164 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -0.71012
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -0.2604
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -0.26167
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -0.26121
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -0.26365
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.001364 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.010912
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.001364 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.010912
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.000791 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.014238
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.000791 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.014238
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.000791 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.011865
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.001356 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.018577
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.00023 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.00414
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.00023 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.00414
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.00087 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.03045
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.00087 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.02958
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.00087 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.03045
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.000593 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.016604
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.000593 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.017197
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.05035 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.7623
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.05035 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.5105
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.08
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.08
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.08
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.08
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.00105 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.0063
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.001113 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.0026712
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.001113 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.0026712
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.001113 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.0031164
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.001034 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.004136
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.001193 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.0028632
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.001193 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.0028632
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.15626
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -0.14669
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -0.14882
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.15626
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -0.19347
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -0.21047
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.001546 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -0.23577
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.001546 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -0.23113
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.001546 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -0.3596
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -0.15819
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -0.16153
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -0.16821
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -0.32306
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.0129 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.4257
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.0129 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.3225
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.00052 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.00624
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.001238 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -0.090374
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.10776
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -0.11048
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.03584
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.00896
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.10776
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -0.10912
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -0.10694
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.0341
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.062744
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.001062 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -0.668
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.001219 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -0.17554
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.001219 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -0.22917
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.001192 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.014304
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.009105 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.05463
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.001058 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -0.35549
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.001051 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -0.35103
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.001051 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -0.35734
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.001042 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.039596
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.001046 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.02615
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.001046 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.02615
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.001046 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.039748
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.001023 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.029667
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.001057 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -0.15675
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.001057 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -0.15707
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.001057 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -0.16172
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -0.17285
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -0.16738
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -0.1094
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -0.15863
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -0.16082
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -0.13894
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.000891 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -0.13053
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.000891 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -0.13178
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.000891 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -0.15414
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -0.19727
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -0.20652
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -0.23063
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.13723
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.13723
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -0.16296
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.001411 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -0.43741
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.001411 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -0.58274
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.060942
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.063844
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.063844
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.068197
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.068502
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.064308
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.064308
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.065706
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.001398 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.21529
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.001398 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.2069
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.067104
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.067104
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 3.4311
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 3.4311
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 4.5487
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 3.9213
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 3.9213
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 5.6368
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 10.2066
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 6.9662
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 6.4906
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 6.6671
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 7.2064
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 10.2948
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 8.4814
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 5.1335
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 10.1047
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 7.9945
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 9.6746
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 5.8967
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.051616 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 7.6908
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.065402 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 11.7724
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.065402 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 11.7724
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.064839 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 14.5888
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.0482 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 6.025
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.0482 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 6.025
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -0.68796
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -0.69287
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -1.5184
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -0.7027
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -0.70762
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -1.5233
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.004316 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -0.84594
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.004316 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -0.47908
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.004936 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.74929
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.76326
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.76326
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -1.9268
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -0.75395
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.74929
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -0.7586
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -1.9035
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.004645 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.004645 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -0.64528
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -0.5668
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -0.6322
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -1.7396
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.00401 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -0.60431
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.00401 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -0.60551
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.00401 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -0.71137
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -0.60964
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -0.61286
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -0.71426
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.002088 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -1.2131
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -2.9865
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -2.9865
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.003181 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.10179
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.003176 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.15245
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.003176 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.1461
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.038196
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.16233
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.003183 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.054111
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.070026
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.079575
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.003176 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -0.33348
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.0823 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 6.9132
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.046747 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 3.7398
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.04672 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 7.008
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.04672 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 7.008
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.17077
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.16088
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.12784
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -0.36952
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -0.37024
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -0.36735
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.23155
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -0.58853
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.09648
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.24192
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.22407
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.24771
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.24602
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.077184
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.07236
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.24886
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.24886
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -0.2668
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -0.2455
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -0.53198
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -0.53443
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.002514 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.3419
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.002355 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.077715
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.10559
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.10559
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.095532
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.095532
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.002211 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.15698
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.002211 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.02211
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.002351 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.38321
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.002351 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.38321
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.002351 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -0.576
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.16094
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.14856
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.16094
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.16094
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.0025 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.3725
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.0025 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.16275
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.22459
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.2162
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.21472
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.13451
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.03011
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.002544 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -1.8902
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.002532 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -1.861
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.002548 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.43826
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.002548 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.43826
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.002548 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.43826
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.45257
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.002517 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -0.43544
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.002517 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.3398
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.41612
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.41254
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.40615
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -0.68808
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.16006
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.15806
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.20658
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.18407
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -0.40669
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -0.39149
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -0.39249
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -0.39124
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -0.67035
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.01272
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.053424
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -0.47555
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.4811
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.4811
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -1.1719
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.00256 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -1.0189
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.11449
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.11449
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.11449
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.13689
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.13689
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.13441
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.003619 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -2.9929
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.003619 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -2.964
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.002341 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.10792
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.152
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.152
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.21
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.148
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.148
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.204
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.002501 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -0.45018
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.002501 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -0.39666
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.002501 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -0.39266
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.002497 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.087395
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.002449 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -1.1241
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.16536
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.1679
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.17808
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.16027
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.15773
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.26458
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.1501
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.4081
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.40286
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.40286
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002616 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.42379
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.002547 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.39988
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.17793
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.18043
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.097734
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.07518
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.002489 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.19414
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.002489 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.19912
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.040516
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.0025 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -0.4125
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.0025 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -0.4225
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.002501 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -0.53271
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.002501 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -0.57023
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.0025 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.03
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.0025 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.045
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.002436 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.1218
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.26312
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.26312
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.13662
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.13409
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.13662
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.14421
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.13662
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.13662
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.14674
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.14674
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.002541 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.030492
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.1437
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.15139
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.1437
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.1437
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.15139
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.1437
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.002023 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.13352
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00237 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -0.38157
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00237 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -0.39342
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00237 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -0.58776
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00237 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -1.294
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00237 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -1.5239
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.002351 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -1.5305
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.002351 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -1.326
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.002351 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -1.4106
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00237 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.03081
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.002544 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.030528
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.08619
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.087965
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.082894
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.11636
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.044869
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.051714
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.050446
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.088725
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.04563
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.21649
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.37518
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.13479
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.15522
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.09783
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.21957
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.18696
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.19131
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.1087
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.039132
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.20436
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.15218
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.13696
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.15653
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.14088
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.21957
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.21088
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.22392
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.16522
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.17392
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.17392
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -0.37175
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011096
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.045458 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 3.4775
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.04679 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 3.7432
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.04679 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.8716
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.04698 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.7584
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.046754 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 3.7403
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.045726 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 3.6581
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.045391 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 3.8128
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.04698 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.7584
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -0.071478
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.053915 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 6.4698
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.053915 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 12.5622
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.053915 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 9.1763
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -0.13919
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -0.11537
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -0.14045
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -0.072105
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -0.0627
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.13825 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 8.2948
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.013792 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.040116 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.047831 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.22959
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 1.9214
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 5.5081
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 6.9171
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 6.0973
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 5.38
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 4.1247
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.046108 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 6.9162
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 5.1413
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 6.8322
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 8.5002
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 9.8026
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.00099 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.008222 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.000244 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.038192
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.05947
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -0.10094
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.09447
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.041205
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.03819
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.019095
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.09447
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.03618
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.043215
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.02211
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.04992
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.0192
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.00896
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.0192
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.04992
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.04992
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -0.14874
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.05025
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -0.055275
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.05025
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.001094 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.013128
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.001262 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.01893
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.001262 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.029026
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.001347 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.064656
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.001267 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.010136
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.001057 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -0.19026
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.001058 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -0.19044
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.001051 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.18918
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.001051 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.18918
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.000243 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.0243
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.000243 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.0243
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.026975
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.026975
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.026975
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.017264
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.026975
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.026975
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.026975
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.016185
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 0.1215
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 0.1215
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.000848 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.0129 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.000164 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.000813 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: MURRY_P8 - GRHAMSES 138kV [1371 - 1431] C:SWEETWATER / MULBERRY - LONGCREEK8 [1420 - 1439] & [1435 - 6230] | [7 empty] | 76.701
Number of Bus | Name of Bus | ID | Max MW | L: MURRY_P8 - GRHAMSES 138kV [1371 - 1431] C:SWEETWATER / MULBERRY - LONGCREEK8 [1420 - 1439] & [1435 - 6230] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.003354 | north | 0.0021206 | -0.0022784 | -0.050277 | -0.0009219 | 0.0009219 | houston | Y | 0.0021206 | 0.30567
239 | BOSQUESW | 1 | 149 | -0.003354 | north | 0.0021206 | -0.0022784 | -0.050277 | -0.0009219 | 0.0009219 | houston | Y | 0.0021206 | 0.1786
244 | WHITNYDM | 1 | 15 | -0.003864 | north | 0.0016106 | -0.0027884 | -0.050787 | -0.0014319 | 0.0014319 | houston | Y | 0.0016106 | 0.0026803
245 | WHITNYDM | 2 | 15 | -0.003864 | north | 0.0016106 | -0.0027884 | -0.050787 | -0.0014319 | 0.0014319 | houston | Y | 0.0016106 | 0.0026803
247 | BOSQUESW | 2 | 153 | -0.003354 | north | 0.0021206 | -0.0022784 | -0.050277 | -0.0009219 | 0.0009219 | houston | Y | 0.0021206 | 0.1834
251 | BOSQUESW | 2 | 150 | -0.003431 | north | 0.0020436 | -0.0023554 | -0.050354 | -0.0009989 | 0.0009989 | houston | Y | 0.0020436 | 0.1567
253 | BOSQUESW | 2 | 80 | -0.003431 | north | 0.0020436 | -0.0023554 | -0.050354 | -0.0009989 | 0.0009989 | houston | Y | 0.0020436 | 0.083575
332 | RWMILLER | 1 | 73 | -0.01243 | north | -0.0069554 | -0.011354 | -0.059353 | -0.0099979 | 0.0069554 | North | N | 0.0069554 | 0
333 | RWMILLER | 2 | 119 | -0.01243 | north | -0.0069554 | -0.011354 | -0.059353 | -0.0099979 | 0.0069554 | North | N | 0.0069554 | 0
334 | RWMILLER | 3 | 205 | -0.01243 | north | -0.0069554 | -0.011354 | -0.059353 | -0.0099979 | 0.0069554 | North | N | 0.0069554 | 0
335 | RWMILLER | 4 | 102 | -0.01243 | north | -0.0069554 | -0.011354 | -0.059353 | -0.0099979 | 0.0069554 | North | N | 0.0069554 | 0
336 | RWMILLER | 5 | 96 | -0.01243 | north | -0.0069554 | -0.011354 | -0.059353 | -0.0099979 | 0.0069554 | North | N | 0.0069554 | 0
344 | MRSSHPRD | 1 | 12 | -0.022872 | north | -0.017397 | -0.021796 | -0.069795 | -0.02044 | 0.017397 | North | N | 0.017397 | 0
345 | MRSSHPRD | 2 | 12 | -0.022872 | north | -0.017397 | -0.021796 | -0.069795 | -0.02044 | 0.017397 | North | N | 0.017397 | 0
366 | JNSNCNTY | 1 | 168 | -0.004241 | north | 0.0012336 | -0.0031654 | -0.051164 | -0.0018089 | 0.0012336 | North | N | 0.0012336 | 0
367 | JNSNCNTY | 2 | 90 | -0.004241 | north | 0.0012336 | -0.0031654 | -0.051164 | -0.0018089 | 0.0012336 | North | N | 0.0012336 | 0
503 | NTHTEXAS | 1 | 18 | -0.012649 | north | -0.0071744 | -0.011573 | -0.059572 | -0.010217 | 0.0071744 | North | N | 0.0071744 | 0
504 | NTHTEXAS | 2 | 18 | -0.012649 | north | -0.0071744 | -0.011573 | -0.059572 | -0.010217 | 0.0071744 | North | N | 0.0071744 | 0
505 | NTHTEXAS | 3 | 38 | -0.012649 | north | -0.0071744 | -0.011573 | -0.059572 | -0.010217 | 0.0071744 | North | N | 0.0071744 | 0
580 | JCKCNTY8 | 1 | 288 | -0.010067 | north | -0.0045924 | -0.0089914 | -0.05699 | -0.0076349 | 0.0045924 | North | N | 0.0045924 | 0
581 | JCKCNTY8 | 2 | 147 | -0.010067 | north | -0.0045924 | -0.0089914 | -0.05699 | -0.0076349 | 0.0045924 | North | N | 0.0045924 | 0
582 | JCKCNTY8 | 3 | 147 | -0.010067 | north | -0.0045924 | -0.0089914 | -0.05699 | -0.0076349 | 0.0045924 | North | N | 0.0045924 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.00799 | north | -0.0025154 | -0.0069144 | -0.054913 | -0.0055579 | 0.0025154 | North | N | 0.0025154 | 0
837 | NEWMAN_G | 1 | 40 | -0.004757 | north | 0.00071759 | -0.0036814 | -0.05168 | -0.0023249 | 0.00071759 | North | N | 0.00071759 | 0
842 | OLINGER_ | 1 | 79 | -0.004775 | north | 0.00069959 | -0.0036994 | -0.051698 | -0.0023429 | 0.00069959 | North | N | 0.00069959 | 0
843 | OLINGER_ | 1 | 106 | -0.004775 | north | 0.00069959 | -0.0036994 | -0.051698 | -0.0023429 | 0.00069959 | North | N | 0.00069959 | 0
844 | OLINGER_ | 1 | 146 | -0.004775 | north | 0.00069959 | -0.0036994 | -0.051698 | -0.0023429 | 0.00069959 | North | N | 0.00069959 | 0
845 | OLINGER_ | 1 | 76 | -0.004775 | north | 0.00069959 | -0.0036994 | -0.051698 | -0.0023429 | 0.00069959 | North | N | 0.00069959 | 0
923 | SPENCER_ | 1 | 60 | -0.005785 | north | -0.00031041 | -0.0047094 | -0.052708 | -0.0033529 | 0.00031041 | North | N | 0.00031041 | 0
924 | SPENCER_ | 1 | 63 | -0.005785 | north | -0.00031041 | -0.0047094 | -0.052708 | -0.0033529 | 0.00031041 | North | N | 0.00031041 | 0
948 | STEAM1 | 1 | 20 | -0.004758 | north | 0.00071659 | -0.0036824 | -0.051681 | -0.0023259 | 0.00071659 | North | N | 0.00071659 | 0
949 | STEAM2 | 1 | 25 | -0.004758 | north | 0.00071659 | -0.0036824 | -0.051681 | -0.0023259 | 0.00071659 | North | N | 0.00071659 | 0
950 | STEAM3 | 1 | 41 | -0.004758 | north | 0.00071659 | -0.0036824 | -0.051681 | -0.0023259 | 0.00071659 | North | N | 0.00071659 | 0
990 | GIBN_CRE | 1 | 463 | -0.00318 | north | 0.0022946 | -0.0021044 | -0.050103 | -0.0007479 | 0.0007479 | houston | Y | 0.0022946 | 0.71612
1002 | PBCTAGE_ | A | 66 | 0.049791 | west | 0.055266 | 0.050867 | 0.0028683 | 0.052223 | 0.0028683 | west | N | 0.0028683 | 0
1003 | PBCTBGE_ | B | 65 | 0.049791 | west | 0.055266 | 0.050867 | 0.0028683 | 0.052223 | 0.0028683 | west | N | 0.0028683 | 0
1004 | PBCTCGE_ | C | 67 | 0.049791 | west | 0.055266 | 0.050867 | 0.0028683 | 0.052223 | 0.0028683 | west | N | 0.0028683 | 0
1005 | PBCTDGE_ | D | 67 | 0.049791 | west | 0.055266 | 0.050867 | 0.0028683 | 0.052223 | 0.0028683 | west | N | 0.0028683 | 0
1006 | PBCTEGE_ | E | 67 | 0.049791 | west | 0.055266 | 0.050867 | 0.0028683 | 0.052223 | 0.0028683 | west | N | 0.0028683 | 0
1007 | PB5GEN_6 | MB | 114 | 0.049791 | west | 0.055266 | 0.050867 | 0.0028683 | 0.052223 | 0.0028683 | west | N | 0.0028683 | 0
1008 | PB6GEN_7 | MB | 515 | 0.049791 | west | 0.055266 | 0.050867 | 0.0028683 | 0.052223 | 0.0028683 | west | N | 0.0028683 | 0
1039 | MRGNAG_1 | A | 66 | 0.056261 | west | 0.061736 | 0.057337 | 0.0093383 | 0.058693 | 0.0093383 | west | N | 0.0093383 | 0
1040 | MRGNBG_2 | B | 69 | 0.056261 | west | 0.061736 | 0.057337 | 0.0093383 | 0.058693 | 0.0093383 | west | N | 0.0093383 | 0
1041 | MRGNCG_3 | C | 69 | 0.056261 | west | 0.061736 | 0.057337 | 0.0093383 | 0.058693 | 0.0093383 | west | N | 0.0093383 | 0
1042 | MRGNDG_4 | D | 67 | 0.056261 | west | 0.061736 | 0.057337 | 0.0093383 | 0.058693 | 0.0093383 | west | N | 0.0093383 | 0
1043 | MRGNEG_5 | E | 67 | 0.056261 | west | 0.061736 | 0.057337 | 0.0093383 | 0.058693 | 0.0093383 | west | N | 0.0093383 | 0
1044 | MRGNFG_6 | F | 65 | 0.056261 | west | 0.061736 | 0.057337 | 0.0093383 | 0.058693 | 0.0093383 | west | N | 0.0093383 | 0
1045 | CALENG1G | 1 | 70 | 0.04863 | west | 0.054105 | 0.049706 | 0.0017073 | 0.051062 | 0.0017073 | west | N | 0.0017073 | 0
1046 | CALENG2G | 2 | 73.4 | 0.04863 | west | 0.054105 | 0.049706 | 0.0017073 | 0.051062 | 0.0017073 | west | N | 0.0017073 | 0
1047 | CALENG3G | 3 | 70.4 | 0.04863 | west | 0.054105 | 0.049706 | 0.0017073 | 0.051062 | 0.0017073 | west | N | 0.0017073 | 0
1058 | LONGSHOR | 1 | 150 | 0.048373 | west | 0.053848 | 0.049449 | 0.0014503 | 0.050805 | 0.0014503 | west | N | 0.0014503 | 0
1058 | LONGSHOR | 2 | 220 | 0.048373 | west | 0.053848 | 0.049449 | 0.0014503 | 0.050805 | 0.0014503 | west | N | 0.0014503 | 0
1061 | CIELOGEN | 1 | 99 | 0.07283 | west | 0.078305 | 0.073906 | 0.025907 | 0.075262 | 0.025907 | west | N | 0.025907 | 0
1062 | CIELOGEN | 1 | 61 | 0.07283 | west | 0.078305 | 0.073906 | 0.025907 | 0.075262 | 0.025907 | west | N | 0.025907 | 0
1068 | SCURRYCW | 1 | 141 | 0.072361 | west | 0.077836 | 0.073437 | 0.025438 | 0.074793 | 0.025438 | west | N | 0.025438 | 0
1069 | KINDERMG | 1 | 25 | 0.07283 | west | 0.078305 | 0.073906 | 0.025907 | 0.075262 | 0.025907 | west | N | 0.025907 | 0
1070 | KINDERMG | 1 | 45.7 | 0.07283 | west | 0.078305 | 0.073906 | 0.025907 | 0.075262 | 0.025907 | west | N | 0.025907 | 0
1071 | KINDERMG | 1 | 45.7 | 0.07283 | west | 0.078305 | 0.073906 | 0.025907 | 0.075262 | 0.025907 | west | N | 0.025907 | 0
1073 | SCURRYCW | 2 | 120 | 0.072361 | west | 0.077836 | 0.073437 | 0.025438 | 0.074793 | 0.025438 | west | N | 0.025438 | 0
1320 | BSP 1 | 1 | 25.8 | 0.057371 | west | 0.062846 | 0.058447 | 0.010448 | 0.059803 | 0.010448 | west | N | 0.010448 | 0
1326 | STANTONW | 1 | 100.5 | 0.053266 | west | 0.058741 | 0.054342 | 0.0063433 | 0.055698 | 0.0063433 | west | N | 0.0063433 | 0
1327 | WILDHRSE | 1 | 120 | 0.059199 | west | 0.064674 | 0.060275 | 0.012276 | 0.061631 | 0.012276 | west | N | 0.012276 | 0
1328 | OCOTILLO | 1 | 58 | 0.0533 | west | 0.058775 | 0.054376 | 0.0063773 | 0.055732 | 0.0063773 | west | N | 0.0063773 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.053715 | west | 0.05919 | 0.054791 | 0.0067923 | 0.056147 | 0.0067923 | west | N | 0.0067923 | 0
1343 | TRENTIPP | 1 | 150 | 0.071768 | west | 0.077243 | 0.072844 | 0.024845 | 0.0742 | 0.024845 | west | N | 0.024845 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.055664 | west | 0.061139 | 0.05674 | 0.0087413 | 0.058096 | 0.0087413 | west | N | 0.0087413 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.055664 | west | 0.061139 | 0.05674 | 0.0087413 | 0.058096 | 0.0087413 | west | N | 0.0087413 | 0
1354 | AEPWIND_ | 1 | 101 | 0.071768 | west | 0.077243 | 0.072844 | 0.024845 | 0.0742 | 0.024845 | west | N | 0.024845 | 0
1360 | GUNSIGHT | 1 | 120 | 0.060516 | west | 0.065991 | 0.061592 | 0.013593 | 0.062948 | 0.013593 | west | N | 0.013593 | 0
1432 | GRHAMSES | 2 | 366 | -0.010387 | north | -0.0049124 | -0.0093114 | -0.05731 | -0.0079549 | 0.0049124 | North | N | 0.0049124 | 0
1433 | GRHAMSES | 1 | 242 | -0.06948 | north | -0.064005 | -0.068404 | -0.1164 | -0.067048 | 0.064005 | North | N | 0.064005 | 0
1437 | MESQUITW | 1 | 400 | -0.010387 | west | -0.0049124 | -0.0093114 | -0.05731 | -0.0079549 | 0.0049124 | North | Y | 0.05731 | 20.9589
1438 | MESQUITW | 1 | 236 | -0.010387 | west | -0.0049124 | -0.0093114 | -0.05731 | -0.0079549 | 0.0049124 | North | Y | 0.05731 | 12.3658
1442 | COKFIELD | 1 | 165 | -0.010387 | west | -0.0049124 | -0.0093114 | -0.05731 | -0.0079549 | 0.0049124 | North | Y | 0.05731 | 8.6456
1453 | WCPWRCO_ | 1 | 204 | -0.006731 | north | -0.0012564 | -0.0056554 | -0.053654 | -0.0042989 | 0.0012564 | North | N | 0.0012564 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.006731 | north | -0.0012564 | -0.0056554 | -0.053654 | -0.0042989 | 0.0012564 | North | N | 0.0012564 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.006731 | north | -0.0012564 | -0.0056554 | -0.053654 | -0.0042989 | 0.0012564 | North | N | 0.0012564 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.012156 | west | -0.0066814 | -0.01108 | -0.059079 | -0.0097239 | 0.0066814 | North | Y | 0.059079 | 1.0479
1479 | WFCOGEN_ | 2 | 20 | -0.012156 | west | -0.0066814 | -0.01108 | -0.059079 | -0.0097239 | 0.0066814 | North | Y | 0.059079 | 1.0479
1482 | WFCOGEN_ | 1 | 20 | -0.012156 | west | -0.0066814 | -0.01108 | -0.059079 | -0.0097239 | 0.0066814 | North | Y | 0.059079 | 1.0479
1482 | WFCOGEN_ | 2 | 17 | -0.012156 | west | -0.0066814 | -0.01108 | -0.059079 | -0.0097239 | 0.0066814 | North | Y | 0.059079 | 0.89075
1600 | BARTNWND | 1 | 120 | -0.039371 | north | -0.033896 | -0.038295 | -0.086294 | -0.036939 | 0.033896 | North | N | 0.033896 | 0
1643 | SLSTR1PP | 1 | 60 | -0.005833 | north | -0.00035841 | -0.0047574 | -0.052756 | -0.0034009 | 0.00035841 | North | N | 0.00035841 | 0
1675 | PEC_1G | 1 | 75 | -0.004894 | north | 0.00058059 | -0.0038184 | -0.051817 | -0.0024619 | 0.00058059 | North | N | 0.00058059 | 0
1676 | PEC_2G | 2 | 79.6 | -0.004894 | north | 0.00058059 | -0.0038184 | -0.051817 | -0.0024619 | 0.00058059 | North | N | 0.00058059 | 0
1677 | PEC_3G | 3 | 88.4 | -0.004894 | north | 0.00058059 | -0.0038184 | -0.051817 | -0.0024619 | 0.00058059 | North | N | 0.00058059 | 0
1678 | LAMARPWR | 1 | 160 | -0.004895 | north | 0.00057959 | -0.0038194 | -0.051818 | -0.0024629 | 0.00057959 | North | N | 0.00057959 | 0
1679 | LAMARPWR | 2 | 156 | -0.004895 | north | 0.00057959 | -0.0038194 | -0.051818 | -0.0024629 | 0.00057959 | North | N | 0.00057959 | 0
1680 | LAMARPWR | 3 | 196 | -0.004895 | north | 0.00057959 | -0.0038194 | -0.051818 | -0.0024629 | 0.00057959 | North | N | 0.00057959 | 0
1681 | LAMARPWR | 4 | 156 | -0.004895 | north | 0.00057959 | -0.0038194 | -0.051818 | -0.0024629 | 0.00057959 | North | N | 0.00057959 | 0
1682 | LAMARPWR | 5 | 157 | -0.004895 | north | 0.00057959 | -0.0038194 | -0.051818 | -0.0024629 | 0.00057959 | North | N | 0.00057959 | 0
1683 | LAMARPWR | 6 | 198 | -0.004895 | north | 0.00057959 | -0.0038194 | -0.051818 | -0.0024629 | 0.00057959 | North | N | 0.00057959 | 0
1687 | VALLEY_1 | 1 | 170 | -0.005021 | north | 0.00045359 | -0.0039454 | -0.051944 | -0.0025889 | 0.00045359 | North | N | 0.00045359 | 0
1688 | VALLEY_2 | 2 | 520 | -0.005021 | north | 0.00045359 | -0.0039454 | -0.051944 | -0.0025889 | 0.00045359 | North | N | 0.00045359 | 0
1689 | VALLEY_3 | 3 | 370 | -0.004914 | north | 0.00056059 | -0.0038384 | -0.051837 | -0.0024819 | 0.00056059 | North | N | 0.00056059 | 0
1701 | MOSES_1G | 1 | 558 | -0.004851 | north | 0.00062359 | -0.0037754 | -0.051774 | -0.0024189 | 0.00062359 | North | N | 0.00062359 | 0
1702 | MOSES_2G | 2 | 579 | -0.004851 | north | 0.00062359 | -0.0037754 | -0.051774 | -0.0024189 | 0.00062359 | North | N | 0.00062359 | 0
1703 | MOSES_3G | 3 | 808 | -0.004851 | north | 0.00062359 | -0.0037754 | -0.051774 | -0.0024189 | 0.00062359 | North | N | 0.00062359 | 0
1861 | EAGLEMNT | MB | 112 | -0.006079 | north | -0.00060441 | -0.0050034 | -0.053002 | -0.0036469 | 0.00060441 | North | N | 0.00060441 | 0
1862 | EAGLEMNT | MB | 100 | -0.006079 | north | -0.00060441 | -0.0050034 | -0.053002 | -0.0036469 | 0.00060441 | North | N | 0.00060441 | 0
1863 | EAGLEMNT | MB | 378 | -0.006079 | north | -0.00060441 | -0.0050034 | -0.053002 | -0.0036469 | 0.00060441 | North | N | 0.00060441 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.002828 | north | 0.0026466 | -0.0017524 | -0.049751 | -0.0003959 | 0.0003959 | houston | Y | 0.0026466 | 0.48907
1878 | WLFHOLW_ | 2 | 205 | -0.002828 | north | 0.0026466 | -0.0017524 | -0.049751 | -0.0003959 | 0.0003959 | houston | Y | 0.0026466 | 0.46139
1879 | WLFHOLW_ | 3 | 272.4 | -0.002828 | north | 0.0026466 | -0.0017524 | -0.049751 | -0.0003959 | 0.0003959 | houston | Y | 0.0026466 | 0.61309
1889 | DECRDOVA | MB | 770 | -0.003729 | north | 0.0017456 | -0.0026534 | -0.050652 | -0.0012969 | 0.0012969 | houston | Y | 0.0017456 | 0.34549
1892 | DECRDOVA | A | 70 | -0.004581 | north | 0.00089359 | -0.0035054 | -0.051504 | -0.0021489 | 0.00089359 | North | N | 0.00089359 | 0
1893 | DECRDOVA | B | 69 | -0.004581 | north | 0.00089359 | -0.0035054 | -0.051504 | -0.0021489 | 0.00089359 | North | N | 0.00089359 | 0
1894 | DECRDOVA | C | 69 | -0.004581 | north | 0.00089359 | -0.0035054 | -0.051504 | -0.0021489 | 0.00089359 | North | N | 0.00089359 | 0
1895 | DECRDOVA | D | 68 | -0.004581 | north | 0.00089359 | -0.0035054 | -0.051504 | -0.0021489 | 0.00089359 | North | N | 0.00089359 | 0
1898 | COMCHEPK | 1 | 1157 | -0.002576 | north | 0.0028986 | -0.0015004 | -0.049499 | -0.0001439 | 0.0001439 | houston | Y | 0.0028986 | 3.1872
1899 | COMCHEPK | 2 | 1158 | -0.002576 | north | 0.0028986 | -0.0015004 | -0.049499 | -0.0001439 | 0.0001439 | houston | Y | 0.0028986 | 3.1899
1937 | MDLTHELP | 5 | 224 | -0.004108 | north | 0.0013666 | -0.0030324 | -0.051031 | -0.0016759 | 0.0013666 | North | N | 0.0013666 | 0
1938 | MDLTHELP | 6 | 226 | -0.004108 | north | 0.0013666 | -0.0030324 | -0.051031 | -0.0016759 | 0.0013666 | North | N | 0.0013666 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.004253 | north | 0.0012216 | -0.0031774 | -0.051176 | -0.0018209 | 0.0012216 | North | N | 0.0012216 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.004253 | north | 0.0012216 | -0.0031774 | -0.051176 | -0.0018209 | 0.0012216 | North | N | 0.0012216 | 0
1943 | MDLTHELP | 3 | 212 | -0.004108 | north | 0.0013666 | -0.0030324 | -0.051031 | -0.0016759 | 0.0013666 | North | N | 0.0013666 | 0
1944 | MDLTHELP | 4 | 211 | -0.004108 | north | 0.0013666 | -0.0030324 | -0.051031 | -0.0016759 | 0.0013666 | North | N | 0.0013666 | 0
1947 | HANDLEY_ | 3 | 395 | -0.004775 | north | 0.00069959 | -0.0036994 | -0.051698 | -0.0023429 | 0.00069959 | North | N | 0.00069959 | 0
1948 | HANDLEY_ | 4 | 435 | -0.004785 | north | 0.00068959 | -0.0037094 | -0.051708 | -0.0023529 | 0.00068959 | North | N | 0.00068959 | 0
1949 | HANDLEY_ | 5 | 435 | -0.004775 | north | 0.00069959 | -0.0036994 | -0.051698 | -0.0023429 | 0.00069959 | North | N | 0.00069959 | 0
2371 | COLLIN_1 | MB | 138 | -0.005079 | north | 0.00039559 | -0.0040034 | -0.052002 | -0.0026469 | 0.00039559 | North | N | 0.00039559 | 0
2413 | MTCK6_G | 6 | 118 | -0.004569 | north | 0.00090559 | -0.0034934 | -0.051492 | -0.0021369 | 0.00090559 | North | N | 0.00090559 | 0
2414 | MTCK7_G | 7 | 115 | -0.004569 | north | 0.00090559 | -0.0034934 | -0.051492 | -0.0021369 | 0.00090559 | North | N | 0.00090559 | 0
2417 | MTCK8_G | 8 | 556 | -0.004569 | north | 0.00090559 | -0.0034934 | -0.051492 | -0.0021369 | 0.00090559 | North | N | 0.00090559 | 0
2451 | LKHB1_G | 1 | 388 | -0.004673 | north | 0.00080159 | -0.0035974 | -0.051596 | -0.0022409 | 0.00080159 | North | N | 0.00080159 | 0
2452 | LKHB2_G | 2 | 515 | -0.004673 | north | 0.00080159 | -0.0035974 | -0.051596 | -0.0022409 | 0.00080159 | North | N | 0.00080159 | 0
3097 | MARTLAKE | 1 | 785 | -0.004395 | north | 0.0010796 | -0.0033194 | -0.051318 | -0.0019629 | 0.0010796 | North | N | 0.0010796 | 0
3098 | MARTLAKE | 2 | 795 | -0.004395 | north | 0.0010796 | -0.0033194 | -0.051318 | -0.0019629 | 0.0010796 | North | N | 0.0010796 | 0
3099 | MARTLAKE | 3 | 780 | -0.004395 | north | 0.0010796 | -0.0033194 | -0.051318 | -0.0019629 | 0.0010796 | North | N | 0.0010796 | 0
3107 | STRYKER_ | 1 | 182 | -0.004322 | north | 0.0011526 | -0.0032464 | -0.051245 | -0.0018899 | 0.0011526 | North | N | 0.0011526 | 0
3108 | STRYKER_ | 2 | 484 | -0.004322 | north | 0.0011526 | -0.0032464 | -0.051245 | -0.0018899 | 0.0011526 | North | N | 0.0011526 | 0
3126 | TRINIDAD | 1 | 224 | -0.004251 | north | 0.0012236 | -0.0031754 | -0.051174 | -0.0018189 | 0.0012236 | North | N | 0.0012236 | 0
3309 | ASPN_G | 1 | 50 | -0.004326 | north | 0.0011486 | -0.0032504 | -0.051249 | -0.0018939 | 0.0011486 | North | N | 0.0011486 | 0
3348 | CHAMPION | MB | 42 | -0.00433 | north | 0.0011446 | -0.0032544 | -0.051253 | -0.0018979 | 0.0011446 | North | N | 0.0011446 | 0
3381 | BBRN_1G | 1 | 615 | -0.003951 | north | 0.0015236 | -0.0028754 | -0.050874 | -0.0015189 | 0.0015189 | houston | Y | 0.0015236 | 0.0028832
3382 | BBRN_2G | 2 | 587 | -0.003951 | north | 0.0015236 | -0.0028754 | -0.050874 | -0.0015189 | 0.0015189 | houston | Y | 0.0015236 | 0.0027519
3403 | THOUSE_1 | MB | 537 | -0.003263 | north | 0.0022116 | -0.0021874 | -0.050186 | -0.0008309 | 0.0008309 | houston | Y | 0.0022116 | 0.74143
3404 | THOUSE_2 | 2 | 787 | -0.003263 | north | 0.0022116 | -0.0021874 | -0.050186 | -0.0008309 | 0.0008309 | houston | Y | 0.0022116 | 1.0866
3416 | LAKE_CRK | MB | 75 | -0.003161 | north | 0.0023136 | -0.0020854 | -0.050084 | -0.0007289 | 0.0007289 | houston | Y | 0.0023136 | 0.11885
3417 | LAKE_CRK | MB | 222 | -0.003161 | north | 0.0023136 | -0.0020854 | -0.050084 | -0.0007289 | 0.0007289 | houston | Y | 0.0023136 | 0.3518
3432 | SANDOW_4 | 4 | 569 | -0.002088 | south | 0.0033866 | -0.0010124 | -0.049011 | 0.0003441 | 0.0003441 | houston | Y | 0.0010124 | 0.38028
5026 | BRAUNIG_ | 1 | 209 | -0.000803 | south | 0.0046716 | 0.00027256 | -0.047726 | 0.0016291 | 0.00027256 | south | N | 0.00027256 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.000803 | south | 0.0046716 | 0.00027256 | -0.047726 | 0.0016291 | 0.00027256 | south | N | 0.00027256 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.000774 | south | 0.0047006 | 0.00030156 | -0.047697 | 0.0016581 | 0.00030156 | south | N | 0.00030156 | 0
5031 | BRA_VHBC | 1 | 46 | -0.000803 | south | 0.0046716 | 0.00027256 | -0.047726 | 0.0016291 | 0.00027256 | south | N | 0.00027256 | 0
5032 | BRA_VHBC | 2 | 47 | -0.000803 | south | 0.0046716 | 0.00027256 | -0.047726 | 0.0016291 | 0.00027256 | south | N | 0.00027256 | 0
5033 | BRA_VHBC | 3 | 46 | -0.000803 | south | 0.0046716 | 0.00027256 | -0.047726 | 0.0016291 | 0.00027256 | south | N | 0.00027256 | 0
5034 | BRA_VHBC | 4 | 46 | -0.000803 | south | 0.0046716 | 0.00027256 | -0.047726 | 0.0016291 | 0.00027256 | south | N | 0.00027256 | 0
5111 | CALAVER_ | 1 | 424 | -0.000819 | south | 0.0046556 | 0.00025656 | -0.047742 | 0.0016131 | 0.00025656 | south | N | 0.00025656 | 0
5112 | CALAVER_ | 2 | 425 | -0.000819 | south | 0.0046556 | 0.00025656 | -0.047742 | 0.0016131 | 0.00025656 | south | N | 0.00025656 | 0
5264 | LEON_LCP | 3 | 58 | -0.000689 | south | 0.0047856 | 0.00038656 | -0.047612 | 0.0017431 | 0.00038656 | south | N | 0.00038656 | 0
5265 | LEON_LCP | 4 | 89 | -0.000689 | south | 0.0047856 | 0.00038656 | -0.047612 | 0.0017431 | 0.00038656 | south | N | 0.00038656 | 0
5266 | LEON_LCP | 1 | 44 | -0.000689 | south | 0.0047856 | 0.00038656 | -0.047612 | 0.0017431 | 0.00038656 | south | N | 0.00038656 | 0
5267 | LEON_LCP | 2 | 44 | -0.000689 | south | 0.0047856 | 0.00038656 | -0.047612 | 0.0017431 | 0.00038656 | south | N | 0.00038656 | 0
5268 | LEON_LCP | 3 | 43 | -0.000689 | south | 0.0047856 | 0.00038656 | -0.047612 | 0.0017431 | 0.00038656 | south | N | 0.00038656 | 0
5269 | LEON_LCP | 4 | 45 | -0.000689 | south | 0.0047856 | 0.00038656 | -0.047612 | 0.0017431 | 0.00038656 | south | N | 0.00038656 | 0
5396 | CALAVER_ | 1 | 412 | -0.000804 | south | 0.0046706 | 0.00027156 | -0.047727 | 0.0016281 | 0.00027156 | south | N | 0.00027156 | 0
5397 | CALAVER_ | 2 | 400 | -0.000804 | south | 0.0046706 | 0.00027156 | -0.047727 | 0.0016281 | 0.00027156 | south | N | 0.00027156 | 0
5401 | CALAVER_ | 1 | 546 | -0.000927 | south | 0.0045476 | 0.00014856 | -0.04785 | 0.0015051 | 0.00014856 | south | N | 0.00014856 | 0
5402 | CALAVER_ | 2 | 750 | -0.000927 | south | 0.0045476 | 0.00014856 | -0.04785 | 0.0015051 | 0.00014856 | south | N | 0.00014856 | 0
5436 | TUTTL_WB | MB | 61 | -0.000881 | south | 0.0045936 | 0.00019456 | -0.047804 | 0.0015511 | 0.00019456 | south | N | 0.00019456 | 0
5438 | TUTTL_WB | MB | 95 | -0.000881 | south | 0.0045936 | 0.00019456 | -0.047804 | 0.0015511 | 0.00019456 | south | N | 0.00019456 | 0
5439 | TUTTL_WB | MB | 151 | -0.000881 | south | 0.0045936 | 0.00019456 | -0.047804 | 0.0015511 | 0.00019456 | south | N | 0.00019456 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.000899 | south | 0.0045756 | 0.00017656 | -0.047822 | 0.0015331 | 0.00017656 | south | N | 0.00017656 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.000899 | south | 0.0045756 | 0.00017656 | -0.047822 | 0.0015331 | 0.00017656 | south | N | 0.00017656 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.000899 | south | 0.0045756 | 0.00017656 | -0.047822 | 0.0015331 | 0.00017656 | south | N | 0.00017656 | 0
5503 | RAYBURNG | 1 | 22 | -0.001169 | south | 0.0043056 | -9.3436e-05 | -0.048092 | 0.0012631 | 9.3436e-05 | south | N | 9.3436e-05 | 0
5505 | RAYBURNG | 1 | 11 | -0.001169 | south | 0.0043056 | -9.3436e-05 | -0.048092 | 0.0012631 | 9.3436e-05 | south | N | 9.3436e-05 | 0
5506 | RAYBURNG | 1 | 11 | -0.001169 | south | 0.0043056 | -9.3436e-05 | -0.048092 | 0.0012631 | 9.3436e-05 | south | N | 9.3436e-05 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.001204 | south | 0.0042706 | -0.00012844 | -0.048127 | 0.0012281 | 0.00012844 | south | N | 0.00012844 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.001204 | south | 0.0042706 | -0.00012844 | -0.048127 | 0.0012281 | 0.00012844 | south | N | 0.00012844 | 0
5511 | RAYBURNC | 1 | 46 | -0.001204 | south | 0.0042706 | -0.00012844 | -0.048127 | 0.0012281 | 0.00012844 | south | N | 0.00012844 | 0
5512 | RAYBURNC | 1 | 48 | -0.001204 | south | 0.0042706 | -0.00012844 | -0.048127 | 0.0012281 | 0.00012844 | south | N | 0.00012844 | 0
5728 | FALCONHY | 2 | 12 | -0.00052 | south | 0.0049546 | 0.00055556 | -0.047443 | 0.0019121 | 0.00055556 | south | N | 0.00055556 | 0
5729 | FALCONHY | 3 | 11 | -0.00052 | south | 0.0049546 | 0.00055556 | -0.047443 | 0.0019121 | 0.00055556 | south | N | 0.00055556 | 0
5890 | PEARSALL | 1 | 24 | 0.00096 | south | 0.0064346 | 0.0020356 | -0.045963 | 0.0033921 | 0.0020356 | south | N | 0.0020356 | 0
5891 | PEARSALL | 1 | 24 | 0.00096 | south | 0.0064346 | 0.0020356 | -0.045963 | 0.0033921 | 0.0020356 | south | N | 0.0020356 | 0
5892 | PEARSALL | 1 | 23 | 0.00096 | south | 0.0064346 | 0.0020356 | -0.045963 | 0.0033921 | 0.0020356 | south | N | 0.0020356 | 0
5903 | SANMIGUE | 1 | 396 | -0.000789 | south | 0.0046856 | 0.00028656 | -0.047712 | 0.0016431 | 0.00028656 | south | N | 0.00028656 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.001971 | houston | 0.0035036 | -0.00089544 | -0.048894 | 0.0004611 | 0.0004611 | houston | N | 0.0004611 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.001971 | houston | 0.0035036 | -0.00089544 | -0.048894 | 0.0004611 | 0.0004611 | houston | N | 0.0004611 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | Y | 0.0054746 | 2.6394
5932 | SI_RAY9 | 9 | 38 | -0.00099 | south | 0.0044846 | 8.5564e-05 | -0.047913 | 0.0014421 | 8.5564e-05 | south | N | 8.5564e-05 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.00099 | south | 0.0044846 | 8.5564e-05 | -0.047913 | 0.0014421 | 8.5564e-05 | south | N | 8.5564e-05 | 0
5934 | SI_RAY5 | 5 | 15 | -0.00099 | south | 0.0044846 | 8.5564e-05 | -0.047913 | 0.0014421 | 8.5564e-05 | south | N | 8.5564e-05 | 0
5935 | SI_RAY10 | 10 | 47 | -0.00099 | south | 0.0044846 | 8.5564e-05 | -0.047913 | 0.0014421 | 8.5564e-05 | south | N | 8.5564e-05 | 0
6016 | SWMESA | 1 | 75 | 0.04679 | west | 0.052265 | 0.047866 | -0.0001327 | 0.049222 | 0.0001327 | west | N | 0.0001327 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | Y | 0.046923 | 10.0864
6144 | MCADOO1A | 1 | 150 | 0.12384 | west | 0.12931 | 0.12491 | 0.076914 | 0.12627 | 0.076914 | west | N | 0.076914 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.051151 | west | 0.056626 | 0.052227 | 0.0042283 | 0.053583 | 0.0042283 | west | N | 0.0042283 | 0
6476 | LANGFORD | 1 | 150 | 0.03542 | west | 0.040895 | 0.036496 | -0.011503 | 0.037852 | 0.011503 | west | N | 0.011503 | 0
6637 | SNYDERW1 | 1 | 63 | 0.068767 | west | 0.074242 | 0.069843 | 0.021844 | 0.071199 | 0.021844 | west | N | 0.021844 | 0
6752 | OKLA0A | 1 | 649.7 | 0.026215 | west | 0.03169 | 0.027291 | -0.020708 | 0.028647 | 0.020708 | west | N | 0.020708 | 0
6948 | DENISNDM | 1 | 40 | -0.005094 | north | 0.00038059 | -0.0040184 | -0.052017 | -0.0026619 | 0.00038059 | North | N | 0.00038059 | 0
6948 | DENISNDM | 2 | 40 | -0.005094 | north | 0.00038059 | -0.0040184 | -0.052017 | -0.0026619 | 0.00038059 | North | N | 0.00038059 | 0
7000 | L_FERGUS | 1 | 422 | 0.000715 | south | 0.0061896 | 0.0017906 | -0.046208 | 0.0031471 | 0.0017906 | south | N | 0.0017906 | 0
7004 | L_SIMGID | 1 | 132 | -0.001541 | south | 0.0039336 | -0.00046544 | -0.048464 | 0.0008911 | 0.00046544 | south | N | 0.00046544 | 0
7005 | L_SIMGID | 2 | 134 | -0.001541 | south | 0.0039336 | -0.00046544 | -0.048464 | 0.0008911 | 0.00046544 | south | N | 0.00046544 | 0
7006 | L_SIMGID | 3 | 323 | -0.001541 | south | 0.0039336 | -0.00046544 | -0.048464 | 0.0008911 | 0.00046544 | south | N | 0.00046544 | 0
7007 | L_LOSTPI | 1 | 158 | -0.001637 | south | 0.0038376 | -0.00056144 | -0.04856 | 0.0007951 | 0.00056144 | south | N | 0.00056144 | 0
7008 | L_LOSTPI | 2 | 160 | -0.001637 | south | 0.0038376 | -0.00056144 | -0.04856 | 0.0007951 | 0.00056144 | south | N | 0.00056144 | 0
7009 | L_LOSTPI | 3 | 175 | -0.001637 | south | 0.0038376 | -0.00056144 | -0.04856 | 0.0007951 | 0.00056144 | south | N | 0.00056144 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.00164 | south | 0.0038346 | -0.00056444 | -0.048563 | 0.0007921 | 0.00056444 | south | N | 0.00056444 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.00164 | south | 0.0038346 | -0.00056444 | -0.048563 | 0.0007921 | 0.00056444 | south | N | 0.00056444 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.00164 | south | 0.0038346 | -0.00056444 | -0.048563 | 0.0007921 | 0.00056444 | south | N | 0.00056444 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.001163 | south | 0.0043116 | -8.7436e-05 | -0.048086 | 0.0012691 | 8.7436e-05 | south | N | 8.7436e-05 | 0
7015 | L_HAYSEN | 2 | 225 | -0.001163 | south | 0.0043116 | -8.7436e-05 | -0.048086 | 0.0012691 | 8.7436e-05 | south | N | 8.7436e-05 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.001163 | south | 0.0043116 | -8.7436e-05 | -0.048086 | 0.0012691 | 8.7436e-05 | south | N | 8.7436e-05 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.001163 | south | 0.0043116 | -8.7436e-05 | -0.048086 | 0.0012691 | 8.7436e-05 | south | N | 8.7436e-05 | 0
7020 | L_AUSTPL | 1 | 8 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
7020 | L_AUSTPL | 2 | 8 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
7022 | L_BUCHAN | 1 | 18 | 0.000791 | south | 0.0062656 | 0.0018666 | -0.046132 | 0.0032231 | 0.0018666 | south | N | 0.0018666 | 0
7023 | L_BUCHAN | 2 | 18 | 0.000791 | south | 0.0062656 | 0.0018666 | -0.046132 | 0.0032231 | 0.0018666 | south | N | 0.0018666 | 0
7024 | L_BUCHAN | 3 | 15 | 0.000791 | south | 0.0062656 | 0.0018666 | -0.046132 | 0.0032231 | 0.0018666 | south | N | 0.0018666 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.001356 | south | 0.0068306 | 0.0024316 | -0.045567 | 0.0037881 | 0.0024316 | south | N | 0.0024316 | 0
7028 | L_MARBFA | 1 | 18 | 0.00023 | south | 0.0057046 | 0.0013056 | -0.046693 | 0.0026621 | 0.0013056 | south | N | 0.0013056 | 0
7029 | L_MARBFA | 2 | 18 | 0.00023 | south | 0.0057046 | 0.0013056 | -0.046693 | 0.0026621 | 0.0013056 | south | N | 0.0013056 | 0
7031 | L_MARSFO | 1 | 35 | -0.00087 | south | 0.0046046 | 0.00020556 | -0.047793 | 0.0015621 | 0.00020556 | south | N | 0.00020556 | 0
7032 | L_MARSFO | 2 | 34 | -0.00087 | south | 0.0046046 | 0.00020556 | -0.047793 | 0.0015621 | 0.00020556 | south | N | 0.00020556 | 0
7033 | L_MARSFO | 3 | 35 | -0.00087 | south | 0.0046046 | 0.00020556 | -0.047793 | 0.0015621 | 0.00020556 | south | N | 0.00020556 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.000593 | south | 0.0060676 | 0.0016686 | -0.04633 | 0.0030251 | 0.0016686 | south | N | 0.0016686 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.000593 | south | 0.0060676 | 0.0016686 | -0.04633 | 0.0030251 | 0.0016686 | south | N | 0.0016686 | 0
7038 | L_DELAWA | 1 | 35 | 0.05035 | west | 0.055825 | 0.051426 | 0.0034273 | 0.052782 | 0.0034273 | west | N | 0.0034273 | 0
7038 | L_DELAWA | 2 | 30 | 0.05035 | west | 0.055825 | 0.051426 | 0.0034273 | 0.052782 | 0.0034273 | west | N | 0.0034273 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.0016 | south | 0.0038746 | -0.00052444 | -0.048523 | 0.0008321 | 0.00052444 | south | N | 0.00052444 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.0016 | south | 0.0038746 | -0.00052444 | -0.048523 | 0.0008321 | 0.00052444 | south | N | 0.00052444 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.0016 | south | 0.0038746 | -0.00052444 | -0.048523 | 0.0008321 | 0.00052444 | south | N | 0.00052444 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.0016 | south | 0.0038746 | -0.00052444 | -0.048523 | 0.0008321 | 0.00052444 | south | N | 0.00052444 | 0
7487 | L_CANYHY | 1 | 6 | -0.00105 | south | 0.0044246 | 2.5564e-05 | -0.047973 | 0.0013821 | 2.5564e-05 | south | N | 2.5564e-05 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.001113 | south | 0.0043616 | -3.7436e-05 | -0.048036 | 0.0013191 | 3.7436e-05 | south | N | 3.7436e-05 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.001113 | south | 0.0043616 | -3.7436e-05 | -0.048036 | 0.0013191 | 3.7436e-05 | south | N | 3.7436e-05 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.001113 | south | 0.0043616 | -3.7436e-05 | -0.048036 | 0.0013191 | 3.7436e-05 | south | N | 3.7436e-05 | 0
7609 | L_SCHUMA | 1 | 4 | -0.001034 | south | 0.0044406 | 4.1564e-05 | -0.047957 | 0.0013981 | 4.1564e-05 | south | N | 4.1564e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.001193 | south | 0.0042816 | -0.00011744 | -0.048116 | 0.0012391 | 0.00011744 | south | N | 0.00011744 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.001193 | south | 0.0042816 | -0.00011744 | -0.048116 | 0.0012391 | 0.00011744 | south | N | 0.00011744 | 0
7800 | L_GUADGE | 1 | 147 | -0.001063 | south | 0.0044116 | 1.2564e-05 | -0.047986 | 0.0013691 | 1.2564e-05 | south | N | 1.2564e-05 | 0
7801 | L_GUADGE | 2 | 138 | -0.001063 | south | 0.0044116 | 1.2564e-05 | -0.047986 | 0.0013691 | 1.2564e-05 | south | N | 1.2564e-05 | 0
7802 | L_GUADGE | 3 | 140 | -0.001063 | south | 0.0044116 | 1.2564e-05 | -0.047986 | 0.0013691 | 1.2564e-05 | south | N | 1.2564e-05 | 0
7803 | L_GUADGE | 4 | 147 | -0.001063 | south | 0.0044116 | 1.2564e-05 | -0.047986 | 0.0013691 | 1.2564e-05 | south | N | 1.2564e-05 | 0
7804 | L_GUADGE | 5 | 182 | -0.001063 | south | 0.0044116 | 1.2564e-05 | -0.047986 | 0.0013691 | 1.2564e-05 | south | N | 1.2564e-05 | 0
7805 | L_GUADGE | 6 | 198 | -0.001063 | south | 0.0044116 | 1.2564e-05 | -0.047986 | 0.0013691 | 1.2564e-05 | south | N | 1.2564e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.001546 | south | 0.0039286 | -0.00047044 | -0.048469 | 0.0008861 | 0.00047044 | south | N | 0.00047044 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.001546 | south | 0.0039286 | -0.00047044 | -0.048469 | 0.0008861 | 0.00047044 | south | N | 0.00047044 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.001546 | south | 0.0039286 | -0.00047044 | -0.048469 | 0.0008861 | 0.00047044 | south | N | 0.00047044 | 0
7810 | L_RIONOG | 1 | 142 | -0.001114 | south | 0.0043606 | -3.8436e-05 | -0.048037 | 0.0013181 | 3.8436e-05 | south | N | 3.8436e-05 | 0
7811 | L_RIONOG | 2 | 145 | -0.001114 | south | 0.0043606 | -3.8436e-05 | -0.048037 | 0.0013181 | 3.8436e-05 | south | N | 3.8436e-05 | 0
7812 | L_RIONOG | 3 | 151 | -0.001114 | south | 0.0043606 | -3.8436e-05 | -0.048037 | 0.0013181 | 3.8436e-05 | south | N | 3.8436e-05 | 0
7813 | L_RIONOG | 4 | 290 | -0.001114 | south | 0.0043606 | -3.8436e-05 | -0.048037 | 0.0013181 | 3.8436e-05 | south | N | 3.8436e-05 | 0
8032 | AMISTADH | 1 | 33 | 0.0129 | south | 0.018375 | 0.013976 | -0.034023 | 0.015332 | 0.013976 | south | N | 0.013976 | 0
8033 | AMISTADH | 2 | 25 | 0.0129 | south | 0.018375 | 0.013976 | -0.034023 | 0.015332 | 0.013976 | south | N | 0.013976 | 0
8048 | FALCONHY | 1 | 12 | -0.00052 | south | 0.0049546 | 0.00055556 | -0.047443 | 0.0019121 | 0.00055556 | south | N | 0.00055556 | 0
8066 | DUP1V#1 | 1 | 73 | -0.001238 | south | 0.0042366 | -0.00016244 | -0.048161 | 0.0011941 | 0.00016244 | south | N | 0.00016244 | 0
8134 | FOR69CG0 | 1 | 79 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
8138 | FOR69CG0 | 2 | 81 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
8139 | JOS #1 | MB | 255 | 0 | south | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | N | 0.0010756 | 0
8147 | UCAR #2 | 10 | 28 | -0.00128 | south | 0.0041946 | -0.00020444 | -0.048203 | 0.0011521 | 0.00020444 | south | N | 0.00020444 | 0
8148 | UCAR #1 | 2 | 7 | -0.00128 | south | 0.0041946 | -0.00020444 | -0.048203 | 0.0011521 | 0.00020444 | south | N | 0.00020444 | 0
8153 | FOR69CG0 | 3 | 79 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
8154 | FOR69CG0 | 4 | 80 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
8156 | FOR69CG0 | 6 | 25 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
8157 | FOR69CG0 | 7 | 46 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
8161 | COLETOU1 | 1 | 629 | -0.001062 | south | 0.0044126 | 1.3564e-05 | -0.047985 | 0.0013701 | 1.3564e-05 | south | N | 1.3564e-05 | 0
8173 | VICEC51A | 5 | 144 | -0.001219 | south | 0.0042556 | -0.00014344 | -0.048142 | 0.0012131 | 0.00014344 | south | N | 0.00014344 | 0
8174 | VICEC61A | 6 | 188 | -0.001219 | south | 0.0042556 | -0.00014344 | -0.048142 | 0.0012131 | 0.00014344 | south | N | 0.00014344 | 0
8189 | CUERO 2 | 1 | 12 | -0.001192 | south | 0.0042826 | -0.00011644 | -0.048115 | 0.0012401 | 0.00011644 | south | N | 0.00011644 | 0
8262 | ELPS | 1 | 6 | 0.009105 | south | 0.01458 | 0.010181 | -0.037818 | 0.011537 | 0.010181 | south | N | 0.010181 | 0
8285 | LAR #1 | MB | 32 | 0 | south | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | N | 0.0010756 | 0
8287 | LAR #2 | MB | 32 | 0 | south | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | N | 0.0010756 | 0
8288 | LAR #3 | MB | 105 | 0 | south | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | N | 0.0010756 | 0
8388 | BATES0A | MB | 70 | 0 | south | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | N | 0.0010756 | 0
8393 | BATES0B | MB | 110 | 0 | south | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | N | 0.0010756 | 0
8442 | NBEC71A | 1 | 336 | -0.001058 | south | 0.0044166 | 1.7564e-05 | -0.047981 | 0.0013741 | 1.7564e-05 | south | N | 1.7564e-05 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | N | 0.0010756 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | 0.0054746 | 0.0010756 | -0.046923 | 0.0024321 | 0.0010756 | south | N | 0.0010756 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.001051 | south | 0.0044236 | 2.4564e-05 | -0.047974 | 0.0013811 | 2.4564e-05 | south | N | 2.4564e-05 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.001051 | south | 0.0044236 | 2.4564e-05 | -0.047974 | 0.0013811 | 2.4564e-05 | south | N | 2.4564e-05 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.001042 | south | 0.0044326 | 3.3564e-05 | -0.047965 | 0.0013901 | 3.3564e-05 | south | N | 3.3564e-05 | 0
8506 | VAL #1 | 1 | 25 | -0.001046 | south | 0.0044286 | 2.9564e-05 | -0.047969 | 0.0013861 | 2.9564e-05 | south | N | 2.9564e-05 | 0
8507 | VAL #2 | 2 | 25 | -0.001046 | south | 0.0044286 | 2.9564e-05 | -0.047969 | 0.0013861 | 2.9564e-05 | south | N | 2.9564e-05 | 0
8511 | OXY_CC0A | 1 | 38 | -0.001046 | south | 0.0044286 | 2.9564e-05 | -0.047969 | 0.0013861 | 2.9564e-05 | south | N | 2.9564e-05 | 0
8517 | CELANEBI | 1 | 29 | -0.001023 | south | 0.0044516 | 5.2564e-05 | -0.047946 | 0.0014091 | 5.2564e-05 | south | N | 5.2564e-05 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.001057 | south | 0.0044176 | 1.8564e-05 | -0.04798 | 0.0013751 | 1.8564e-05 | south | N | 1.8564e-05 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.001057 | south | 0.0044176 | 1.8564e-05 | -0.04798 | 0.0013751 | 1.8564e-05 | south | N | 1.8564e-05 | 0
8562 | CNOPST1 | 3 | 153 | -0.001057 | south | 0.0044176 | 1.8564e-05 | -0.04798 | 0.0013751 | 1.8564e-05 | south | N | 1.8564e-05 | 0
8926 | LGE_GT10 | 1 | 158 | -0.001094 | south | 0.0043806 | -1.8436e-05 | -0.048017 | 0.0013381 | 1.8436e-05 | south | N | 1.8436e-05 | 0
8927 | LGE_GT20 | 2 | 153 | -0.001094 | south | 0.0043806 | -1.8436e-05 | -0.048017 | 0.0013381 | 1.8436e-05 | south | N | 1.8436e-05 | 0
8928 | LGE_STG0 | 3 | 100 | -0.001094 | south | 0.0043806 | -1.8436e-05 | -0.048017 | 0.0013381 | 1.8436e-05 | south | N | 1.8436e-05 | 0
8930 | ICPGN10A | 1 | 145 | -0.001094 | south | 0.0043806 | -1.8436e-05 | -0.048017 | 0.0013381 | 1.8436e-05 | south | N | 1.8436e-05 | 0
8931 | ICPGN20A | 2 | 147 | -0.001094 | south | 0.0043806 | -1.8436e-05 | -0.048017 | 0.0013381 | 1.8436e-05 | south | N | 1.8436e-05 | 0
8932 | ICPGN30A | 3 | 127 | -0.001094 | south | 0.0043806 | -1.8436e-05 | -0.048017 | 0.0013381 | 1.8436e-05 | south | N | 1.8436e-05 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.000891 | south | 0.0045836 | 0.00018456 | -0.047814 | 0.0015411 | 0.00018456 | south | N | 0.00018456 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.000891 | south | 0.0045836 | 0.00018456 | -0.047814 | 0.0015411 | 0.00018456 | south | N | 0.00018456 | 0
8935 | FGNTS201 | 3 | 173 | -0.000891 | south | 0.0045836 | 0.00018456 | -0.047814 | 0.0015411 | 0.00018456 | south | N | 0.00018456 | 0
8936 | MVGN#1 | 1 | 207 | -0.000953 | south | 0.0045216 | 0.00012256 | -0.047876 | 0.0014791 | 0.00012256 | south | N | 0.00012256 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.000953 | south | 0.0045216 | 0.00012256 | -0.047876 | 0.0014791 | 0.00012256 | south | N | 0.00012256 | 0
8938 | MVGN#3 | 3 | 242 | -0.000953 | south | 0.0045216 | 0.00012256 | -0.047876 | 0.0014791 | 0.00012256 | south | N | 0.00012256 | 0
8981 | HECN1 | 1 | 144 | -0.000953 | south | 0.0045216 | 0.00012256 | -0.047876 | 0.0014791 | 0.00012256 | south | N | 0.00012256 | 0
8982 | HECN2 | 2 | 144 | -0.000953 | south | 0.0045216 | 0.00012256 | -0.047876 | 0.0014791 | 0.00012256 | south | N | 0.00012256 | 0
8983 | HECN3 | 3 | 171 | -0.000953 | south | 0.0045216 | 0.00012256 | -0.047876 | 0.0014791 | 0.00012256 | south | N | 0.00012256 | 0
9000 | DECKR_G1 | 1 | 310 | -0.001411 | south | 0.0040636 | -0.00033544 | -0.048334 | 0.0010211 | 0.00033544 | south | N | 0.00033544 | 0
9001 | DECKR_G2 | 2 | 413 | -0.001411 | south | 0.0040636 | -0.00033544 | -0.048334 | 0.0010211 | 0.00033544 | south | N | 0.00033544 | 0
9002 | DECKR_G3 | 3 | 42 | -0.001451 | south | 0.0040236 | -0.00037544 | -0.048374 | 0.0009811 | 0.00037544 | south | N | 0.00037544 | 0
9003 | DECKR_G4 | 4 | 44 | -0.001451 | south | 0.0040236 | -0.00037544 | -0.048374 | 0.0009811 | 0.00037544 | south | N | 0.00037544 | 0
9004 | DECKR_G5 | 5 | 44 | -0.001451 | south | 0.0040236 | -0.00037544 | -0.048374 | 0.0009811 | 0.00037544 | south | N | 0.00037544 | 0
9005 | DECKR_G6 | 6 | 47 | -0.001451 | south | 0.0040236 | -0.00037544 | -0.048374 | 0.0009811 | 0.00037544 | south | N | 0.00037544 | 0
9016 | SANDH_G1 | 1 | 49 | -0.001398 | south | 0.0040766 | -0.00032244 | -0.048321 | 0.0010341 | 0.00032244 | south | N | 0.00032244 | 0
9017 | SANDH_G2 | 2 | 46 | -0.001398 | south | 0.0040766 | -0.00032244 | -0.048321 | 0.0010341 | 0.00032244 | south | N | 0.00032244 | 0
9018 | SANDH_G3 | 3 | 46 | -0.001398 | south | 0.0040766 | -0.00032244 | -0.048321 | 0.0010341 | 0.00032244 | south | N | 0.00032244 | 0
9019 | SANDH_G4 | 4 | 47 | -0.001398 | south | 0.0040766 | -0.00032244 | -0.048321 | 0.0010341 | 0.00032244 | south | N | 0.00032244 | 0
9020 | SANDHG5A | 5A | 154 | -0.001398 | south | 0.0040766 | -0.00032244 | -0.048321 | 0.0010341 | 0.00032244 | south | N | 0.00032244 | 0
9021 | SANDHG5C | 5C | 148 | -0.001398 | south | 0.0040766 | -0.00032244 | -0.048321 | 0.0010341 | 0.00032244 | south | N | 0.00032244 | 0
9022 | SANDH_G6 | 6 | 48 | -0.001398 | south | 0.0040766 | -0.00032244 | -0.048321 | 0.0010341 | 0.00032244 | south | N | 0.00032244 | 0
9023 | SANDH_G7 | 7 | 48 | -0.001398 | south | 0.0040766 | -0.00032244 | -0.048321 | 0.0010341 | 0.00032244 | south | N | 0.00032244 | 0
11001 | NAV1CT | 1 | 70 | 0.049016 | west | 0.054491 | 0.050092 | 0.0020933 | 0.051448 | 0.0020933 | west | N | 0.0020933 | 0
11009 | NAV2CT | 1 | 70 | 0.049016 | west | 0.054491 | 0.050092 | 0.0020933 | 0.051448 | 0.0020933 | west | N | 0.0020933 | 0
11011 | NAV3ST | 1 | 92.8 | 0.049016 | west | 0.054491 | 0.050092 | 0.0020933 | 0.051448 | 0.0020933 | west | N | 0.0020933 | 0
11012 | NAV4CT | 1 | 80 | 0.049016 | west | 0.054491 | 0.050092 | 0.0020933 | 0.051448 | 0.0020933 | west | N | 0.0020933 | 0
11013 | NAV5CT | 1 | 80 | 0.049016 | west | 0.054491 | 0.050092 | 0.0020933 | 0.051448 | 0.0020933 | west | N | 0.0020933 | 0
11014 | NAV6ST | 1 | 115 | 0.049016 | west | 0.054491 | 0.050092 | 0.0020933 | 0.051448 | 0.0020933 | west | N | 0.0020933 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.049023 | west | 0.054498 | 0.050099 | 0.0021003 | 0.051455 | 0.0021003 | west | N | 0.0021003 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.049023 | west | 0.054498 | 0.050099 | 0.0021003 | 0.051455 | 0.0021003 | west | N | 0.0021003 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.049023 | west | 0.054498 | 0.050099 | 0.0021003 | 0.051455 | 0.0021003 | west | N | 0.0021003 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.049023 | west | 0.054498 | 0.050099 | 0.0021003 | 0.051455 | 0.0021003 | west | N | 0.0021003 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.049023 | west | 0.054498 | 0.050099 | 0.0021003 | 0.051455 | 0.0021003 | west | N | 0.0021003 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.049023 | west | 0.054498 | 0.050099 | 0.0021003 | 0.051455 | 0.0021003 | west | N | 0.0021003 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.040581 | west | 0.046056 | 0.041657 | -0.0063417 | 0.043013 | 0.0063417 | west | N | 0.0063417 | 0
11057 | CHAMPION | 1 | 126.5 | 0.040581 | west | 0.046056 | 0.041657 | -0.0063417 | 0.043013 | 0.0063417 | west | N | 0.0063417 | 0
11058 | PYRON_1G | 1 | 249 | 0.040581 | west | 0.046056 | 0.041657 | -0.0063417 | 0.043013 | 0.0063417 | west | N | 0.0063417 | 0
11059 | INADALE_ | 1 | 197 | 0.040581 | west | 0.046056 | 0.041657 | -0.0063417 | 0.043013 | 0.0063417 | west | N | 0.0063417 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.048373 | west | 0.053848 | 0.049449 | 0.0014503 | 0.050805 | 0.0014503 | west | N | 0.0014503 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.048373 | west | 0.053848 | 0.049449 | 0.0014503 | 0.050805 | 0.0014503 | west | N | 0.0014503 | 0
11147 | NOTREES_ | 1 | 149 | 0.051616 | west | 0.057091 | 0.052692 | 0.0046933 | 0.054048 | 0.0046933 | west | N | 0.0046933 | 0
11309 | BULLCREK | 1 | 180 | 0.065402 | west | 0.070877 | 0.066478 | 0.018479 | 0.067834 | 0.018479 | west | N | 0.018479 | 0
11310 | BULLCREK | 1 | 180 | 0.065402 | west | 0.070877 | 0.066478 | 0.018479 | 0.067834 | 0.018479 | west | N | 0.018479 | 0
11320 | COYOTE_1 | 1 | 225 | 0.064839 | west | 0.070314 | 0.065915 | 0.017916 | 0.067271 | 0.017916 | west | N | 0.017916 | 0
11415 | LORAINE_ | 1 | 125 | 0.0482 | west | 0.053675 | 0.049276 | 0.0012773 | 0.050632 | 0.0012773 | west | N | 0.0012773 | 0
11416 | LORAINE_ | 1 | 125 | 0.0482 | west | 0.053675 | 0.049276 | 0.0012773 | 0.050632 | 0.0012773 | west | N | 0.0012773 | 0
11691 | KMICHICT | 1 | 140 | -0.004914 | north | 0.00056059 | -0.0038384 | -0.051837 | -0.0024819 | 0.00056059 | North | N | 0.00056059 | 0
11692 | KMICHICT | 2 | 141 | -0.004914 | north | 0.00056059 | -0.0038384 | -0.051837 | -0.0024819 | 0.00056059 | North | N | 0.00056059 | 0
11693 | KMICHIST | 3 | 309 | -0.004914 | north | 0.00056059 | -0.0038384 | -0.051837 | -0.0024819 | 0.00056059 | North | N | 0.00056059 | 0
11694 | KMICHICT | 4 | 143 | -0.004914 | north | 0.00056059 | -0.0038384 | -0.051837 | -0.0024819 | 0.00056059 | North | N | 0.00056059 | 0
11695 | KMICHICT | 5 | 144 | -0.004914 | north | 0.00056059 | -0.0038384 | -0.051837 | -0.0024819 | 0.00056059 | North | N | 0.00056059 | 0
11696 | KMICHIST | 6 | 310 | -0.004914 | north | 0.00056059 | -0.0038384 | -0.051837 | -0.0024819 | 0.00056059 | North | N | 0.00056059 | 0
12322 | ENNSTRAC | 1 | 196 | -0.004316 | north | 0.0011586 | -0.0032404 | -0.051239 | -0.0018839 | 0.0011586 | North | N | 0.0011586 | 0
12323 | ENNSTRAC | 2 | 111 | -0.004316 | north | 0.0011586 | -0.0032404 | -0.051239 | -0.0018839 | 0.0011586 | North | N | 0.0011586 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.004936 | north | 0.00053859 | -0.0038604 | -0.051859 | -0.0025039 | 0.00053859 | North | N | 0.00053859 | 0
12411 | FPLEFR1A | 1 | 161 | -0.004654 | north | 0.00082059 | -0.0035784 | -0.051577 | -0.0022219 | 0.00082059 | North | N | 0.00082059 | 0
12412 | FPLEFR1B | 2 | 164 | -0.004654 | north | 0.00082059 | -0.0035784 | -0.051577 | -0.0022219 | 0.00082059 | North | N | 0.00082059 | 0
12413 | FPLEFR1C | 3 | 164 | -0.004654 | north | 0.00082059 | -0.0035784 | -0.051577 | -0.0022219 | 0.00082059 | North | N | 0.00082059 | 0
12414 | FPLEFR1S | 4 | 414 | -0.004654 | north | 0.00082059 | -0.0035784 | -0.051577 | -0.0022219 | 0.00082059 | North | N | 0.00082059 | 0
12421 | FPLEFR2A | 1 | 162 | -0.004654 | north | 0.00082059 | -0.0035784 | -0.051577 | -0.0022219 | 0.00082059 | North | N | 0.00082059 | 0
12422 | FPLEFR2B | 2 | 161 | -0.004654 | north | 0.00082059 | -0.0035784 | -0.051577 | -0.0022219 | 0.00082059 | North | N | 0.00082059 | 0
12423 | FPLEFR2C | 3 | 163 | -0.004654 | north | 0.00082059 | -0.0035784 | -0.051577 | -0.0022219 | 0.00082059 | North | N | 0.00082059 | 0
12424 | FPLEFR2S | 4 | 409 | -0.004654 | north | 0.00082059 | -0.0035784 | -0.051577 | -0.0022219 | 0.00082059 | North | N | 0.00082059 | 0
12440 | PARKD_1S | 1 | 0 | -0.004645 | north | 0.00082959 | -0.0035694 | -0.051568 | -0.0022129 | 0.00082959 | North | N | 0.00082959 | 0
12449 | PARKD_2S | 1 | 0 | -0.004645 | north | 0.00082959 | -0.0035694 | -0.051568 | -0.0022129 | 0.00082959 | North | N | 0.00082959 | 0
13116 | TGATEWAY | 1 | 148 | -0.00436 | north | 0.0011146 | -0.0032844 | -0.051283 | -0.0019279 | 0.0011146 | North | N | 0.0011146 | 0
13117 | TGATEWAY | 2 | 130 | -0.00436 | north | 0.0011146 | -0.0032844 | -0.051283 | -0.0019279 | 0.0011146 | North | N | 0.0011146 | 0
13118 | TGATEWAY | 3 | 145 | -0.00436 | north | 0.0011146 | -0.0032844 | -0.051283 | -0.0019279 | 0.0011146 | North | N | 0.0011146 | 0
13119 | TGATEWAY | 4 | 399 | -0.00436 | north | 0.0011146 | -0.0032844 | -0.051283 | -0.0019279 | 0.0011146 | North | N | 0.0011146 | 0
13131 | CALFREST | 1 | 150.7 | -0.00401 | north | 0.0014646 | -0.0029344 | -0.050933 | -0.0015779 | 0.0014646 | North | N | 0.0014646 | 0
13132 | CALFREST | 2 | 151 | -0.00401 | north | 0.0014646 | -0.0029344 | -0.050933 | -0.0015779 | 0.0014646 | North | N | 0.0014646 | 0
13133 | CALFREST | 3 | 177.4 | -0.00401 | north | 0.0014646 | -0.0029344 | -0.050933 | -0.0015779 | 0.0014646 | North | N | 0.0014646 | 0
13134 | CALFREST | 4 | 151.5 | -0.004024 | north | 0.0014506 | -0.0029484 | -0.050947 | -0.0015919 | 0.0014506 | North | N | 0.0014506 | 0
13135 | CALFREST | 5 | 152.3 | -0.004024 | north | 0.0014506 | -0.0029484 | -0.050947 | -0.0015919 | 0.0014506 | North | N | 0.0014506 | 0
13136 | CALFREST | 6 | 177.5 | -0.004024 | north | 0.0014506 | -0.0029484 | -0.050947 | -0.0015919 | 0.0014506 | North | N | 0.0014506 | 0
13432 | SANDOW_5 | 5 | 581 | -0.002088 | south | 0.0033866 | -0.0010124 | -0.049011 | 0.0003441 | 0.0003441 | houston | Y | 0.0010124 | 0.3883
13691 | OAKGROVE | 1 | 855 | -0.003493 | north | 0.0019816 | -0.0024174 | -0.050416 | -0.0010609 | 0.0010609 | houston | Y | 0.0019816 | 0.78719
13692 | OAKGROVE | 2 | 855 | -0.003493 | north | 0.0019816 | -0.0024174 | -0.050416 | -0.0010609 | 0.0010609 | houston | Y | 0.0019816 | 0.78719
32798 | BRYN_TAM | 1 | 32 | -0.003181 | north | 0.0022936 | -0.0021054 | -0.050104 | -0.0007489 | 0.0007489 | houston | Y | 0.0022936 | 0.04943
32883 | BRYN_DNS | 1 | 48 | -0.003176 | north | 0.0022986 | -0.0021004 | -0.050099 | -0.0007439 | 0.0007439 | houston | Y | 0.0022986 | 0.074625
32884 | BRYN_DNS | 1 | 46 | -0.003176 | north | 0.0022986 | -0.0021004 | -0.050099 | -0.0007439 | 0.0007439 | houston | Y | 0.0022986 | 0.071516
32886 | BRYN_ATK | MB | 12 | -0.003183 | north | 0.0022916 | -0.0021074 | -0.050106 | -0.0007509 | 0.0007509 | houston | Y | 0.0022916 | 0.018488
32887 | BRYN_ATK | MB | 51 | -0.003183 | north | 0.0022916 | -0.0021074 | -0.050106 | -0.0007509 | 0.0007509 | houston | Y | 0.0022916 | 0.078575
32888 | BRYN_ATK | 1 | 17 | -0.003183 | north | 0.0022916 | -0.0021074 | -0.050106 | -0.0007509 | 0.0007509 | houston | Y | 0.0022916 | 0.026192
32890 | BRYN_ATK | MB | 22 | -0.003183 | north | 0.0022916 | -0.0021074 | -0.050106 | -0.0007509 | 0.0007509 | houston | Y | 0.0022916 | 0.033895
32891 | BRYN_ATK | MB | 25 | -0.003183 | north | 0.0022916 | -0.0021074 | -0.050106 | -0.0007509 | 0.0007509 | houston | Y | 0.0022916 | 0.038517
32892 | BRYN_DNS | 1 | 105 | -0.003176 | north | 0.0022986 | -0.0021004 | -0.050099 | -0.0007439 | 0.0007439 | houston | Y | 0.0022986 | 0.16324
36998 | RDCNYNG1 | 1 | 84 | 0.0823 | west | 0.087775 | 0.083376 | 0.035377 | 0.084732 | 0.035377 | west | N | 0.035377 | 0
38332 | WDWRDU2 | 1 | 80 | 0.046747 | west | 0.052222 | 0.047823 | -0.0001757 | 0.049179 | 0.0001757 | west | N | 0.0001757 | 0
38437 | TNSRBNMS | 1 | 150 | 0.04672 | west | 0.052195 | 0.047796 | -0.0002027 | 0.049152 | 0.0002027 | west | N | 0.0002027 | 0
38438 | TNSRBNMS | 1 | 150 | 0.04672 | west | 0.052195 | 0.047796 | -0.0002027 | 0.049152 | 0.0002027 | west | N | 0.0002027 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38600 | TNBP_CGN | 5 | 53 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38614 | TNBPAMCG | 4 | 96 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38615 | TNBPAMCG | 1 | 244 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38690 | TNBP_CGN | 3 | 40 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
39470 | TNDOWCGN | 1 | 32 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
39480 | TNDOWCGN | 1 | 30 | -0.002412 | houston | 0.0030626 | -0.0013364 | -0.049335 | 2.0103e-05 | 2.0103e-05 | houston | N | 2.0103e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.002242 | houston | 0.0032326 | -0.0011664 | -0.049165 | 0.0001901 | 0.0001901 | houston | N | 0.0001901 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.002242 | houston | 0.0032326 | -0.0011664 | -0.049165 | 0.0001901 | 0.0001901 | houston | N | 0.0001901 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.002242 | houston | 0.0032326 | -0.0011664 | -0.049165 | 0.0001901 | 0.0001901 | houston | N | 0.0001901 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.002242 | houston | 0.0032326 | -0.0011664 | -0.049165 | 0.0001901 | 0.0001901 | houston | N | 0.0001901 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.003493 | north | 0.0019816 | -0.0024174 | -0.050416 | -0.0010609 | 0.0010609 | houston | Y | 0.0019816 | 0.14022
39970 | TNTNPONE | 1 | 153 | -0.003493 | north | 0.0019816 | -0.0024174 | -0.050416 | -0.0010609 | 0.0010609 | houston | Y | 0.0019816 | 0.14087
48500 | APD_GT1_ | 1 | 136 | -0.002514 | houston | 0.0029606 | -0.0014384 | -0.049437 | -8.1897e-05 | 8.1897e-05 | houston | N | 8.1897e-05 | 0
48510 | AK_GT1__ | 1 | 33 | -0.002355 | houston | 0.0031196 | -0.0012794 | -0.049278 | 7.7103e-05 | 7.7103e-05 | houston | N | 7.7103e-05 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.002514 | houston | 0.0029606 | -0.0014384 | -0.049437 | -8.1897e-05 | 8.1897e-05 | houston | N | 8.1897e-05 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.002514 | houston | 0.0029606 | -0.0014384 | -0.049437 | -8.1897e-05 | 8.1897e-05 | houston | N | 8.1897e-05 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.002514 | houston | 0.0029606 | -0.0014384 | -0.049437 | -8.1897e-05 | 8.1897e-05 | houston | N | 8.1897e-05 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.002514 | houston | 0.0029606 | -0.0014384 | -0.049437 | -8.1897e-05 | 8.1897e-05 | houston | N | 8.1897e-05 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.002211 | houston | 0.0032636 | -0.0011354 | -0.049134 | 0.0002211 | 0.0002211 | houston | N | 0.0002211 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.002211 | houston | 0.0032636 | -0.0011354 | -0.049134 | 0.0002211 | 0.0002211 | houston | N | 0.0002211 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.002351 | houston | 0.0031236 | -0.0012754 | -0.049274 | 8.1103e-05 | 8.1103e-05 | houston | N | 8.1103e-05 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.002351 | houston | 0.0031236 | -0.0012754 | -0.049274 | 8.1103e-05 | 8.1103e-05 | houston | N | 8.1103e-05 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.002351 | houston | 0.0031236 | -0.0012754 | -0.049274 | 8.1103e-05 | 8.1103e-05 | houston | N | 8.1103e-05 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.002476 | houston | 0.0029986 | -0.0014004 | -0.049399 | -4.3897e-05 | 4.3897e-05 | houston | N | 4.3897e-05 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.002476 | houston | 0.0029986 | -0.0014004 | -0.049399 | -4.3897e-05 | 4.3897e-05 | houston | N | 4.3897e-05 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.002476 | houston | 0.0029986 | -0.0014004 | -0.049399 | -4.3897e-05 | 4.3897e-05 | houston | N | 4.3897e-05 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.002476 | houston | 0.0029986 | -0.0014004 | -0.049399 | -4.3897e-05 | 4.3897e-05 | houston | N | 4.3897e-05 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.0025 | houston | 0.0029746 | -0.0014244 | -0.049423 | -6.7897e-05 | 6.7897e-05 | houston | N | 6.7897e-05 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.0025 | houston | 0.0029746 | -0.0014244 | -0.049423 | -6.7897e-05 | 6.7897e-05 | houston | N | 6.7897e-05 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.002468 | houston | 0.0030066 | -0.0013924 | -0.049391 | -3.5897e-05 | 3.5897e-05 | houston | N | 3.5897e-05 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.002468 | houston | 0.0030066 | -0.0013924 | -0.049391 | -3.5897e-05 | 3.5897e-05 | houston | N | 3.5897e-05 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.002468 | houston | 0.0030066 | -0.0013924 | -0.049391 | -3.5897e-05 | 3.5897e-05 | houston | N | 3.5897e-05 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.002468 | houston | 0.0030066 | -0.0013924 | -0.049391 | -3.5897e-05 | 3.5897e-05 | houston | N | 3.5897e-05 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.002468 | houston | 0.0030066 | -0.0013924 | -0.049391 | -3.5897e-05 | 3.5897e-05 | houston | N | 3.5897e-05 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.002532 | houston | 0.0029426 | -0.0014564 | -0.049455 | -9.9897e-05 | 9.9897e-05 | houston | N | 9.9897e-05 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.002548 | houston | 0.0029266 | -0.0014724 | -0.049471 | -0.0001159 | 0.0001159 | houston | N | 0.0001159 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.002548 | houston | 0.0029266 | -0.0014724 | -0.049471 | -0.0001159 | 0.0001159 | houston | N | 0.0001159 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.002548 | houston | 0.0029266 | -0.0014724 | -0.049471 | -0.0001159 | 0.0001159 | houston | N | 0.0001159 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.002616 | houston | 0.0028586 | -0.0015404 | -0.049539 | -0.0001839 | 0.0001839 | houston | N | 0.0001839 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.002517 | houston | 0.0029576 | -0.0014414 | -0.04944 | -8.4897e-05 | 8.4897e-05 | houston | N | 8.4897e-05 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.002517 | houston | 0.0029576 | -0.0014414 | -0.04944 | -8.4897e-05 | 8.4897e-05 | houston | N | 8.4897e-05 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.002556 | houston | 0.0029186 | -0.0014804 | -0.049479 | -0.0001239 | 0.0001239 | houston | N | 0.0001239 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.002556 | houston | 0.0029186 | -0.0014804 | -0.049479 | -0.0001239 | 0.0001239 | houston | N | 0.0001239 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.002556 | houston | 0.0029186 | -0.0014804 | -0.049479 | -0.0001239 | 0.0001239 | houston | N | 0.0001239 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.002556 | houston | 0.0029186 | -0.0014804 | -0.049479 | -0.0001239 | 0.0001239 | houston | N | 0.0001239 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.002492 | houston | 0.0029826 | -0.0014164 | -0.049415 | -5.9897e-05 | 5.9897e-05 | houston | N | 5.9897e-05 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.002492 | houston | 0.0029826 | -0.0014164 | -0.049415 | -5.9897e-05 | 5.9897e-05 | houston | N | 5.9897e-05 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.002492 | houston | 0.0029826 | -0.0014164 | -0.049415 | -5.9897e-05 | 5.9897e-05 | houston | N | 5.9897e-05 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.002492 | houston | 0.0029826 | -0.0014164 | -0.049415 | -5.9897e-05 | 5.9897e-05 | houston | N | 5.9897e-05 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.002492 | houston | 0.0029826 | -0.0014164 | -0.049415 | -5.9897e-05 | 5.9897e-05 | houston | N | 5.9897e-05 | 0
48651 | EP_1_2 | 1 | 5 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48651 | EP_1_2 | 2 | 21 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.003084 | north | 0.0023906 | -0.0020084 | -0.050007 | -0.0006519 | 0.0006519 | houston | Y | 0.0023906 | 0.26811
48672 | FTR_GT2_ | 2 | 156 | -0.003084 | north | 0.0023906 | -0.0020084 | -0.050007 | -0.0006519 | 0.0006519 | houston | Y | 0.0023906 | 0.27124
48673 | FTR_GT3_ | 3 | 156 | -0.003084 | north | 0.0023906 | -0.0020084 | -0.050007 | -0.0006519 | 0.0006519 | houston | Y | 0.0023906 | 0.27124
48674 | FTR_CN4_ | 4 | 380 | -0.003084 | north | 0.0023906 | -0.0020084 | -0.050007 | -0.0006519 | 0.0006519 | houston | Y | 0.0023906 | 0.6607
48690 | GBY_GN5_ | 5 | 398 | -0.00256 | houston | 0.0029146 | -0.0014844 | -0.049483 | -0.0001279 | 0.0001279 | houston | N | 0.0001279 | 0
48691 | GBY_7374 | A | 46 | -0.002489 | houston | 0.0029856 | -0.0014134 | -0.049412 | -5.6897e-05 | 5.6897e-05 | houston | N | 5.6897e-05 | 0
48691 | GBY_7374 | B | 46 | -0.002489 | houston | 0.0029856 | -0.0014134 | -0.049412 | -5.6897e-05 | 5.6897e-05 | houston | N | 5.6897e-05 | 0
48692 | GBY_8182 | C | 46 | -0.002489 | houston | 0.0029856 | -0.0014134 | -0.049412 | -5.6897e-05 | 5.6897e-05 | houston | N | 5.6897e-05 | 0
48692 | GBY_8182 | D | 55 | -0.002489 | houston | 0.0029856 | -0.0014134 | -0.049412 | -5.6897e-05 | 5.6897e-05 | houston | N | 5.6897e-05 | 0
48693 | GBY_8384 | E | 55 | -0.002489 | houston | 0.0029856 | -0.0014134 | -0.049412 | -5.6897e-05 | 5.6897e-05 | houston | N | 5.6897e-05 | 0
48693 | GBY_8384 | F | 54 | -0.002489 | houston | 0.0029856 | -0.0014134 | -0.049412 | -5.6897e-05 | 5.6897e-05 | houston | N | 5.6897e-05 | 0
48721 | LEG_1___ | 1 | 827 | -0.003619 | north | 0.0018556 | -0.0025434 | -0.050542 | -0.0011869 | 0.0011869 | houston | Y | 0.0018556 | 0.55301
48722 | LEG_2___ | 2 | 819 | -0.003619 | north | 0.0018556 | -0.0025434 | -0.050542 | -0.0011869 | 0.0011869 | houston | Y | 0.0018556 | 0.54766
48730 | MNS_GT | 1 | 46.1 | -0.002341 | houston | 0.0031336 | -0.0012654 | -0.049264 | 9.1103e-05 | 9.1103e-05 | houston | N | 9.1103e-05 | 0
48731 | CBE_GT1 | 1 | 76 | -0.002 | houston | 0.0034746 | -0.00092444 | -0.048923 | 0.0004321 | 0.0004321 | houston | N | 0.0004321 | 0
48732 | CBE_GT2 | 1 | 76 | -0.002 | houston | 0.0034746 | -0.00092444 | -0.048923 | 0.0004321 | 0.0004321 | houston | N | 0.0004321 | 0
48733 | CBE_ST12 | 1 | 105 | -0.002 | houston | 0.0034746 | -0.00092444 | -0.048923 | 0.0004321 | 0.0004321 | houston | N | 0.0004321 | 0
48734 | CBE_GT3 | 1 | 74 | -0.002 | houston | 0.0034746 | -0.00092444 | -0.048923 | 0.0004321 | 0.0004321 | houston | N | 0.0004321 | 0
48735 | CBE_GT4 | 1 | 74 | -0.002 | houston | 0.0034746 | -0.00092444 | -0.048923 | 0.0004321 | 0.0004321 | houston | N | 0.0004321 | 0
48736 | CBE_ST34 | 1 | 102 | -0.002 | houston | 0.0034746 | -0.00092444 | -0.048923 | 0.0004321 | 0.0004321 | houston | N | 0.0004321 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48761 | PR_GT1__ | 1 | 35 | -0.002497 | houston | 0.0029776 | -0.0014214 | -0.04942 | -6.4897e-05 | 6.4897e-05 | houston | N | 6.4897e-05 | 0
48772 | PHR_GN2_ | MB | 459 | -0.002449 | houston | 0.0030256 | -0.0013734 | -0.049372 | -1.6897e-05 | 1.6897e-05 | houston | N | 1.6897e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.002616 | houston | 0.0028586 | -0.0015404 | -0.049539 | -0.0001839 | 0.0001839 | houston | N | 0.0001839 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.002616 | houston | 0.0028586 | -0.0015404 | -0.049539 | -0.0001839 | 0.0001839 | houston | N | 0.0001839 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.002616 | houston | 0.0028586 | -0.0015404 | -0.049539 | -0.0001839 | 0.0001839 | houston | N | 0.0001839 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.002616 | houston | 0.0028586 | -0.0015404 | -0.049539 | -0.0001839 | 0.0001839 | houston | N | 0.0001839 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.002547 | houston | 0.0029276 | -0.0014714 | -0.04947 | -0.0001149 | 0.0001149 | houston | N | 0.0001149 | 0
48820 | SHELLG1_ | 1 | 71 | -0.002506 | houston | 0.0029686 | -0.0014304 | -0.049429 | -7.3897e-05 | 7.3897e-05 | houston | N | 7.3897e-05 | 0
48821 | SHELLG2 | 2 | 72 | -0.002506 | houston | 0.0029686 | -0.0014304 | -0.049429 | -7.3897e-05 | 7.3897e-05 | houston | N | 7.3897e-05 | 0
48822 | SHELLG3_ | 1 | 39 | -0.002506 | houston | 0.0029686 | -0.0014304 | -0.049429 | -7.3897e-05 | 7.3897e-05 | houston | N | 7.3897e-05 | 0
48822 | SHELLG3_ | 2 | 30 | -0.002506 | houston | 0.0029686 | -0.0014304 | -0.049429 | -7.3897e-05 | 7.3897e-05 | houston | N | 7.3897e-05 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.002489 | houston | 0.0029856 | -0.0014134 | -0.049412 | -5.6897e-05 | 5.6897e-05 | houston | N | 5.6897e-05 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.002489 | houston | 0.0029856 | -0.0014134 | -0.049412 | -5.6897e-05 | 5.6897e-05 | houston | N | 5.6897e-05 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.0025 | houston | 0.0029746 | -0.0014244 | -0.049423 | -6.7897e-05 | 6.7897e-05 | houston | N | 6.7897e-05 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.0025 | houston | 0.0029746 | -0.0014244 | -0.049423 | -6.7897e-05 | 6.7897e-05 | houston | N | 6.7897e-05 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.002501 | houston | 0.0029736 | -0.0014254 | -0.049424 | -6.8897e-05 | 6.8897e-05 | houston | N | 6.8897e-05 | 0
48855 | SRB_GT21 | B2 | 12 | -0.0025 | houston | 0.0029746 | -0.0014244 | -0.049423 | -6.7897e-05 | 6.7897e-05 | houston | N | 6.7897e-05 | 0
48855 | SRB_GT21 | MB | 18 | -0.0025 | houston | 0.0029746 | -0.0014244 | -0.049423 | -6.7897e-05 | 6.7897e-05 | houston | N | 6.7897e-05 | 0
48865 | TECO_GT1 | 1 | 50 | -0.002436 | houston | 0.0030386 | -0.0013604 | -0.049359 | -3.8972e-06 | 3.8972e-06 | houston | N | 3.8972e-06 | 0
48873 | THW_ST3_ | 3 | 104 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48874 | THW_ST4_ | 4 | 104 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48875 | THW_3132 | A | 54 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48875 | THW_3132 | B | 53 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48877 | THW_3334 | C | 54 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48877 | THW_3334 | D | 57 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48879 | THW_4142 | E | 54 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48879 | THW_4142 | F | 54 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48881 | THW_4344 | G | 58 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48881 | THW_4344 | H | 58 | -0.00253 | houston | 0.0029446 | -0.0014544 | -0.049453 | -9.7897e-05 | 9.7897e-05 | houston | N | 9.7897e-05 | 0
48883 | THW_GT1_ | B2 | 12 | -0.002541 | houston | 0.0029336 | -0.0014654 | -0.049464 | -0.0001089 | 0.0001089 | houston | N | 0.0001089 | 0
48885 | THW_5152 | A | 56 | -0.002566 | houston | 0.0029086 | -0.0014904 | -0.049489 | -0.0001339 | 0.0001339 | houston | N | 0.0001339 | 0
48885 | THW_5152 | B | 59 | -0.002566 | houston | 0.0029086 | -0.0014904 | -0.049489 | -0.0001339 | 0.0001339 | houston | N | 0.0001339 | 0
48886 | THW_5354 | C | 56 | -0.002566 | houston | 0.0029086 | -0.0014904 | -0.049489 | -0.0001339 | 0.0001339 | houston | N | 0.0001339 | 0
48886 | THW_5354 | D | 56 | -0.002566 | houston | 0.0029086 | -0.0014904 | -0.049489 | -0.0001339 | 0.0001339 | houston | N | 0.0001339 | 0
48887 | THW_5556 | E | 59 | -0.002566 | houston | 0.0029086 | -0.0014904 | -0.049489 | -0.0001339 | 0.0001339 | houston | N | 0.0001339 | 0
48887 | THW_5556 | F | 56 | -0.002566 | houston | 0.0029086 | -0.0014904 | -0.049489 | -0.0001339 | 0.0001339 | houston | N | 0.0001339 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.002023 | houston | 0.0034516 | -0.00094744 | -0.048946 | 0.0004091 | 0.0004091 | houston | N | 0.0004091 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.00237 | houston | 0.0031046 | -0.0012944 | -0.049293 | 6.2103e-05 | 6.2103e-05 | houston | N | 6.2103e-05 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.00237 | houston | 0.0031046 | -0.0012944 | -0.049293 | 6.2103e-05 | 6.2103e-05 | houston | N | 6.2103e-05 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.00237 | houston | 0.0031046 | -0.0012944 | -0.049293 | 6.2103e-05 | 6.2103e-05 | houston | N | 6.2103e-05 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.00237 | houston | 0.0031046 | -0.0012944 | -0.049293 | 6.2103e-05 | 6.2103e-05 | houston | N | 6.2103e-05 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.00237 | houston | 0.0031046 | -0.0012944 | -0.049293 | 6.2103e-05 | 6.2103e-05 | houston | N | 6.2103e-05 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.002351 | houston | 0.0031236 | -0.0012754 | -0.049274 | 8.1103e-05 | 8.1103e-05 | houston | N | 8.1103e-05 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.002351 | houston | 0.0031236 | -0.0012754 | -0.049274 | 8.1103e-05 | 8.1103e-05 | houston | N | 8.1103e-05 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.002351 | houston | 0.0031236 | -0.0012754 | -0.049274 | 8.1103e-05 | 8.1103e-05 | houston | N | 8.1103e-05 | 0
48929 | WAPGT21_ | B1 | 13 | -0.00237 | houston | 0.0031046 | -0.0012944 | -0.049293 | 6.2103e-05 | 6.2103e-05 | houston | N | 6.2103e-05 | 0
48940 | WARVUE_G | G1 | 12 | -0.002544 | houston | 0.0029306 | -0.0014684 | -0.049467 | -0.0001119 | 0.0001119 | houston | N | 0.0001119 | 0
49803 | EXN_15GT | 1 | 34 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49826 | EXN938GT | 5 | 45.9 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49828 | EXN941GT | 10 | 17.7 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49829 | EXN942GT | 11 | 20.4 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49830 | EXN943GT | 12 | 19.9 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49831 | EXN944GT | 13 | 35 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49832 | EXN945GT | 9 | 18 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49837 | EXN_GT | 4 | 85.4 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49838 | EXN_14GT | 14 | 148 | -0.002535 | houston | 0.0029396 | -0.0014594 | -0.049458 | -0.0001029 | 0.0001029 | houston | N | 0.0001029 | 0
49851 | DOW17000 | 37 | 62 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49858 | DOW38100 | 31 | 71.4 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49859 | DOW38200 | 33 | 45 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49860 | DOW38300 | 32 | 101 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49862 | DOW39100 | 36 | 86 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49863 | DOW39200 | 35 | 88 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49865 | DOW41000 | 41 | 50 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49866 | DOW42000 | 42 | 18 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49869 | DOW49000 | 45 | 94 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49870 | DOW61000 | 61 | 70 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49871 | DOW62000 | 62 | 63 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49872 | DOW63000 | 63 | 72 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49873 | DOW64000 | 64 | 64.8 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49876 | DOW65000 | 65 | 101 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49877 | DOW66000 | 66 | 97 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49878 | DOW67000 | 67 | 103 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49882 | DOW81000 | 81 | 76 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49884 | DOW82000 | 82 | 80 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49885 | DOW83000 | 83 | 80 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
49886 | DOW84000 | 84 | 171 | -0.002174 | houston | 0.0033006 | -0.0010984 | -0.049097 | 0.0002581 | 0.0002581 | houston | N | 0.0002581 | 0
58909 | PEARSALL | 1 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58909 | PEARSALL | 2 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58909 | PEARSALL | 3 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58909 | PEARSALL | 4 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58909 | PEARSALL | 5 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58909 | PEARSALL | 6 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58919 | PEARSALL | 1 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58919 | PEARSALL | 2 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58919 | PEARSALL | 3 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58919 | PEARSALL | 4 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58919 | PEARSALL | 5 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58919 | PEARSALL | 6 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58929 | PEARSALL | 1 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58929 | PEARSALL | 2 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58929 | PEARSALL | 3 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58929 | PEARSALL | 4 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58929 | PEARSALL | 5 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58929 | PEARSALL | 6 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58949 | PEARSALL | 1 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58949 | PEARSALL | 2 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58949 | PEARSALL | 3 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58949 | PEARSALL | 4 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58949 | PEARSALL | 5 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
58949 | PEARSALL | 6 | 8.4 | 0.001321 | south | 0.0067956 | 0.0023966 | -0.045602 | 0.0037531 | 0.0023966 | south | N | 0.0023966 | 0
60000 | DSKY2 | 1 | 76.5 | 0.045458 | west | 0.050933 | 0.046534 | -0.0014647 | 0.04789 | 0.0014647 | west | N | 0.0014647 | 0
60003 | KING_NE1 | 1 | 80 | 0.04679 | west | 0.052265 | 0.047866 | -0.0001327 | 0.049222 | 0.0001327 | west | N | 0.0001327 | 0
60005 | KING_SE1 | 1 | 40 | 0.04679 | west | 0.052265 | 0.047866 | -0.0001327 | 0.049222 | 0.0001327 | west | N | 0.0001327 | 0
60007 | KING_SW1 | 1 | 80 | 0.04698 | west | 0.052455 | 0.048056 | 5.7295e-05 | 0.049412 | 5.7295e-05 | west | N | 5.7295e-05 | 0
60016 | WOODWRD1 | 1 | 80 | 0.046754 | west | 0.052229 | 0.04783 | -0.0001687 | 0.049186 | 0.0001687 | west | N | 0.0001687 | 0
60017 | ORNNWP1 | 1 | 80 | 0.045726 | west | 0.051201 | 0.046802 | -0.0011967 | 0.048158 | 0.0011967 | west | N | 0.0011967 | 0
60018 | DSKY1 | 1 | 84 | 0.045391 | west | 0.050866 | 0.046467 | -0.0015317 | 0.047823 | 0.0015317 | west | N | 0.0015317 | 0
60019 | KING_NW1 | 1 | 80 | 0.04698 | west | 0.052455 | 0.048056 | 5.7295e-05 | 0.049412 | 5.7295e-05 | west | N | 5.7295e-05 | 0
60057 | CALLAHAN | 1 | 114 | -0.000627 | south | 0.0048476 | 0.00044856 | -0.04755 | 0.0018051 | 0.00044856 | south | N | 0.00044856 | 0
60058 | BUFF_GAP | 1 | 120 | 0.053915 | west | 0.05939 | 0.054991 | 0.0069923 | 0.056347 | 0.0069923 | west | N | 0.0069923 | 0
60060 | CIRELLO | 1 | 233 | 0.053915 | west | 0.05939 | 0.054991 | 0.0069923 | 0.056347 | 0.0069923 | west | N | 0.0069923 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.053915 | west | 0.05939 | 0.054991 | 0.0069923 | 0.056347 | 0.0069923 | west | N | 0.0069923 | 0
60066 | H_HOLLOW | 1 | 222 | -0.000627 | south | 0.0048476 | 0.00044856 | -0.04755 | 0.0018051 | 0.00044856 | south | N | 0.00044856 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.000627 | south | 0.0048476 | 0.00044856 | -0.04755 | 0.0018051 | 0.00044856 | south | N | 0.00044856 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.000627 | south | 0.0048476 | 0.00044856 | -0.04755 | 0.0018051 | 0.00044856 | south | N | 0.00044856 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.000627 | south | 0.0048476 | 0.00044856 | -0.04755 | 0.0018051 | 0.00044856 | south | N | 0.00044856 | 0
60074 | HORSH5 | 1 | 100 | -0.000627 | south | 0.0048476 | 0.00044856 | -0.04755 | 0.0018051 | 0.00044856 | south | N | 0.00044856 | 0
60081 | WHRLWIND | 1 | 60 | 0.13825 | west | 0.14372 | 0.13932 | 0.091324 | 0.14068 | 0.091324 | west | N | 0.091324 | 0
60201 | RIO DRCS | F | 0 | 0.013792 | south | 0.019267 | 0.014868 | -0.033131 | 0.016224 | 0.014868 | south | N | 0.014868 | 0
60202 | FRIEND_R | F | 0 | 0.040116 | west | 0.045591 | 0.041192 | -0.0068067 | 0.042548 | 0.0068067 | west | N | 0.0068067 | 0
60203 | PRES0A | BT | 4.8 | 0.047831 | west | 0.053306 | 0.048907 | 0.0009083 | 0.050263 | 0.0009083 | west | N | 0.0009083 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.051238 | west | 0.056713 | 0.052314 | 0.0043153 | 0.05367 | 0.0043153 | west | N | 0.0043153 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.051238 | west | 0.056713 | 0.052314 | 0.0043153 | 0.05367 | 0.0043153 | west | N | 0.0043153 | 0
71057 | L_SWEETW | W1 | 135 | 0.051238 | west | 0.056713 | 0.052314 | 0.0043153 | 0.05367 | 0.0043153 | west | N | 0.0043153 | 0
71059 | L_SWEETW | W1 | 119 | 0.051238 | west | 0.056713 | 0.052314 | 0.0043153 | 0.05367 | 0.0043153 | west | N | 0.0043153 | 0
71060 | L_SWEETW | W1 | 105 | 0.051238 | west | 0.056713 | 0.052314 | 0.0043153 | 0.05367 | 0.0043153 | west | N | 0.0043153 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.051238 | west | 0.056713 | 0.052314 | 0.0043153 | 0.05367 | 0.0043153 | west | N | 0.0043153 | 0
76031 | L_GASCCR | W1 | 150 | 0.046108 | west | 0.051583 | 0.047184 | -0.0008147 | 0.04854 | 0.0008147 | west | N | 0.0008147 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.0457 | west | 0.051175 | 0.046776 | -0.0012227 | 0.048132 | 0.0012227 | west | N | 0.0012227 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.0457 | west | 0.051175 | 0.046776 | -0.0012227 | 0.048132 | 0.0012227 | west | N | 0.0012227 | 0
76096 | L_CAPRSI | W1 | 186 | 0.0457 | west | 0.051175 | 0.046776 | -0.0012227 | 0.048132 | 0.0012227 | west | N | 0.0012227 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.0457 | west | 0.051175 | 0.046776 | -0.0012227 | 0.048132 | 0.0012227 | west | N | 0.0012227 | 0
80003 | MILHWYS | F | 0 | -0.00099 | south | 0.0044846 | 8.5564e-05 | -0.047913 | 0.0014421 | 8.5564e-05 | south | N | 8.5564e-05 | 0
80010 | EPLVT1 | F | 0 | 0.008222 | south | 0.013697 | 0.0092976 | -0.038701 | 0.010654 | 0.0092976 | south | N | 0.0092976 | 0
80012 | LAR | F | 0 | 0.000244 | south | 0.0057186 | 0.0013196 | -0.046679 | 0.0026761 | 0.0013196 | south | N | 0.0013196 | 0
80051 | FORPVCM0 | 8 | 28 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
80053 | FOR69CG0 | 10 | 74 | -0.001364 | south | 0.0041106 | -0.00028844 | -0.048287 | 0.0010681 | 0.00028844 | south | N | 0.00028844 | 0
80080 | GWINDT11 | 1 | 94 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80080 | GWINDT11 | 2 | 41 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80080 | GWINDT11 | 3 | 38 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80080 | GWINDT11 | 4 | 19 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80081 | GWINDT21 | 1 | 94 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80081 | GWINDT21 | 2 | 36 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80081 | GWINDT21 | 3 | 43 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80081 | GWINDT21 | 4 | 22 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80137 | CSDR89 | 8 | 39 | -0.00128 | south | 0.0041946 | -0.00020444 | -0.048203 | 0.0011521 | 0.00020444 | south | N | 0.00020444 | 0
80137 | CSDR89 | 9 | 15 | -0.00128 | south | 0.0041946 | -0.00020444 | -0.048203 | 0.0011521 | 0.00020444 | south | N | 0.00020444 | 0
80138 | CSDR7 | 7 | 7 | -0.00128 | south | 0.0041946 | -0.00020444 | -0.048203 | 0.0011521 | 0.00020444 | south | N | 0.00020444 | 0
80139 | CSDR56 | 5 | 15 | -0.00128 | south | 0.0041946 | -0.00020444 | -0.048203 | 0.0011521 | 0.00020444 | south | N | 0.00020444 | 0
80139 | CSDR56 | 6 | 39 | -0.00128 | south | 0.0041946 | -0.00020444 | -0.048203 | 0.0011521 | 0.00020444 | south | N | 0.00020444 | 0
80140 | CSDR11 | 11 | 39 | -0.00128 | south | 0.0041946 | -0.00020444 | -0.048203 | 0.0011521 | 0.00020444 | south | N | 0.00020444 | 0
80180 | PNSCALT1 | 1 | 148 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80180 | PNSCALT1 | 2 | 50 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80181 | PNSCALT2 | 1 | 55 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80181 | PNSCALT2 | 2 | 50 | -0.001005 | south | 0.0044696 | 7.0564e-05 | -0.047928 | 0.0014271 | 7.0564e-05 | south | N | 7.0564e-05 | 0
80223 | REYSHR G | 1 | 12 | -0.001094 | south | 0.0043806 | -1.8436e-05 | -0.048017 | 0.0013381 | 1.8436e-05 | south | N | 1.8436e-05 | 0
80224 | VISTRONG | 1 | 15 | -0.001262 | south | 0.0042126 | -0.00018644 | -0.048185 | 0.0011701 | 0.00018644 | south | N | 0.00018644 | 0
80225 | VISTRONG | 2 | 23 | -0.001262 | south | 0.0042126 | -0.00018644 | -0.048185 | 0.0011701 | 0.00018644 | south | N | 0.00018644 | 0
80226 | ALCOA G | 1 | 48 | -0.001347 | south | 0.0041276 | -0.00027144 | -0.04827 | 0.0010851 | 0.00027144 | south | N | 0.00027144 | 0
80227 | AIRCO G | 1 | 8 | -0.001267 | south | 0.0042076 | -0.00019144 | -0.04819 | 0.0011651 | 0.00019144 | south | N | 0.00019144 | 0
80261 | NBEC81A | 1 | 180 | -0.001057 | south | 0.0044176 | 1.8564e-05 | -0.04798 | 0.0013751 | 1.8564e-05 | south | N | 1.8564e-05 | 0
80262 | NBEC91A | 1 | 180 | -0.001058 | south | 0.0044166 | 1.7564e-05 | -0.047981 | 0.0013741 | 1.7564e-05 | south | N | 1.7564e-05 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.001051 | south | 0.0044236 | 2.4564e-05 | -0.047974 | 0.0013811 | 2.4564e-05 | south | N | 2.4564e-05 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.001051 | south | 0.0044236 | 2.4564e-05 | -0.047974 | 0.0013811 | 2.4564e-05 | south | N | 2.4564e-05 | 0
80265 | LARECU40 | 4 | 100 | 0.000243 | south | 0.0057176 | 0.0013186 | -0.04668 | 0.0026751 | 0.0013186 | south | N | 0.0013186 | 0
80266 | LARECU50 | 5 | 100 | 0.000243 | south | 0.0057176 | 0.0013186 | -0.04668 | 0.0026751 | 0.0013186 | south | N | 0.0013186 | 0
80291 | PAPALOTE | 1 | 25 | -0.001079 | south | 0.0043956 | -3.4363e-06 | -0.048002 | 0.0013531 | 3.4363e-06 | south | N | 3.4363e-06 | 0
80291 | PAPALOTE | 2 | 25 | -0.001079 | south | 0.0043956 | -3.4363e-06 | -0.048002 | 0.0013531 | 3.4363e-06 | south | N | 3.4363e-06 | 0
80291 | PAPALOTE | 3 | 25 | -0.001079 | south | 0.0043956 | -3.4363e-06 | -0.048002 | 0.0013531 | 3.4363e-06 | south | N | 3.4363e-06 | 0
80291 | PAPALOTE | 4 | 16 | -0.001079 | south | 0.0043956 | -3.4363e-06 | -0.048002 | 0.0013531 | 3.4363e-06 | south | N | 3.4363e-06 | 0
80294 | PAPALOTE | 5 | 25 | -0.001079 | south | 0.0043956 | -3.4363e-06 | -0.048002 | 0.0013531 | 3.4363e-06 | south | N | 3.4363e-06 | 0
80294 | PAPALOTE | 6 | 25 | -0.001079 | south | 0.0043956 | -3.4363e-06 | -0.048002 | 0.0013531 | 3.4363e-06 | south | N | 3.4363e-06 | 0
80294 | PAPALOTE | 7 | 25 | -0.001079 | south | 0.0043956 | -3.4363e-06 | -0.048002 | 0.0013531 | 3.4363e-06 | south | N | 3.4363e-06 | 0
80294 | PAPALOTE | 8 | 15 | -0.001079 | south | 0.0043956 | -3.4363e-06 | -0.048002 | 0.0013531 | 3.4363e-06 | south | N | 3.4363e-06 | 0
86104 | CID-138 | EQ | 0 | 0.000243 | south | 0.0057176 | 0.0013186 | -0.04668 | 0.0026751 | 0.0013186 | south | N | 0.0013186 | 0
86105 | CID-230 | EQ | 500 | 0.000243 | south | 0.0057176 | 0.0013186 | -0.04668 | 0.0026751 | 0.0013186 | south | N | 0.0013186 | 0
86106 | CUF-230 | EQ | 500 | 0.000243 | south | 0.0057176 | 0.0013186 | -0.04668 | 0.0026751 | 0.0013186 | south | N | 0.0013186 | 0
86107 | CUF-138 | EQ | 0 | 0.000243 | south | 0.0057176 | 0.0013186 | -0.04668 | 0.0026751 | 0.0013186 | south | N | 0.0013186 | 0
88198 | BEEVILLE | F | 0 | -0.000848 | south | 0.0046266 | 0.00022756 | -0.047771 | 0.0015841 | 0.00022756 | south | N | 0.00022756 | 0
88253 | HAMILTON | F | 0 | 0.0129 | south | 0.018375 | 0.013976 | -0.034023 | 0.015332 | 0.013976 | south | N | 0.013976 | 0
88299 | ZAPATA | F | 0 | -0.000164 | south | 0.0053106 | 0.00091156 | -0.047087 | 0.0022681 | 0.00091156 | south | N | 0.00091156 | 0
88508 | FALFURRI | F | 0 | -0.000813 | south | 0.0046616 | 0.00026256 | -0.047736 | 0.0016191 | 0.00026256 | south | N | 0.00026256 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: MURRY_P8 - GRHAMSES 138kV [1371 - 1431] C:SWEETWATER / MULBERRY - LONGCREEK8 [1420 - 1439] & [1435 - 6230] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.13825 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2948 | 60 | 0.14429 | 8.6575 | 60 | 8.6575
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12384 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5755 | 150 | 0.12988 | 19.4822 | 210 | 28.1396
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.0823 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9132 | 84 | 0.088344 | 7.4209 | 294 | 35.5606
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.07283 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2102 | 99 | 0.078874 | 7.8085 | 393 | 43.3691 | Weighted Shift Factors
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.07283 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4426 | 61 | 0.078874 | 4.8113 |  |  | west | 0.046923
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.07283 | west | 7 | N | N | Nwest | Nwest | 1 | 1.8208 | 0 | 0.078874 | 0 |  |  | north | -0.0060442
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.07283 | west | 7 | N | N | Nwest | Nwest | 1 | 3.3283 | 0 | 0.078874 | 0 |  |  |  | 0.052967
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.07283 | west | 7 | N | N | Nwest | Nwest | 1 | 3.3283 | 0 | 0.078874 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.072361 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.2029 | 141 | 0.078405 | 11.0551 |  |  | Line Rating | 223
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.072361 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6833 | 120 | 0.078405 | 9.4086 |  |  | Conc Gen | 393
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.071768 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7652 | 150 | 0.077812 | 11.6718 |  |  | Weighted Imp. | 43.3691
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.071768 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2486 | 101 | 0.077812 | 7.859 |  |  | PTDF | 0.11035
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.068767 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3323 | 63 | 0.074811 | 4.7131
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.065402 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7724 | 180 | 0.071446 | 12.8603 |  |  | Concentration | 2.0835
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.065402 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7724 | 180 | 0.071446 | 12.8603
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.064839 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.5888 | 225 | 0.070883 | 15.9487
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.060516 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2619 | 120 | 0.06656 | 7.9872
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.059199 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1039 | 120 | 0.065243 | 7.8292
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.057371 | west | 8 | N | N | Nwest | Nwest | 1 | 1.4802 | 0 | 0.063415 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7132 | 66 | 0.062305 | 4.1121
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.882 | 69 | 0.062305 | 4.2991
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.882 | 69 | 0.062305 | 4.2991
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7695 | 67 | 0.062305 | 4.1744
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7695 | 67 | 0.062305 | 4.1744
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.657 | 65 | 0.062305 | 4.0498
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.055664 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.36738 | 6.6 | 0.061708 | 0.40727
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.055664 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9093 | 34.3 | 0.061708 | 2.1166
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.053915 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4698 | 120 | 0.059959 | 7.1951
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.053915 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5622 | 233 | 0.059959 | 13.9705
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.053915 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1763 | 170.2 | 0.059959 | 10.205
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.053715 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.5058 | 214.2 | 0.059759 | 12.8004
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.0533 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0914 | 58 | 0.059344 | 3.442
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.053266 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3532 | 100.5 | 0.05931 | 5.9607
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.051616 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6908 | 149 | 0.05766 | 8.5914
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9214 | 37.5 | 0.057282 | 2.1481
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5081 | 107.5 | 0.057282 | 6.1578
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9171 | 135 | 0.057282 | 7.7331
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0973 | 119 | 0.057282 | 6.8166
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.38 | 105 | 0.057282 | 6.0146
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1247 | 80.5 | 0.057282 | 4.6112
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.051151 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6701 | 169.5 | 0.057195 | 9.6946
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.05035 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7623 | 35 | 0.056394 | 1.9738
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.05035 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5105 | 30 | 0.056394 | 1.6918
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.2862 | 66 | 0.055835 | 3.6851
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.2364 | 65 | 0.055835 | 3.6293
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.336 | 67 | 0.055835 | 3.741
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.336 | 67 | 0.055835 | 3.741
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.336 | 67 | 0.055835 | 3.741
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.049791 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.055835 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.049791 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.055835 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.2066 | 208.2 | 0.055067 | 11.465
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.9662 | 142.1 | 0.055067 | 7.825
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.4906 | 132.4 | 0.055067 | 7.2909
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.6671 | 136 | 0.055067 | 7.4891
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.2064 | 147 | 0.055067 | 8.0949
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.2948 | 210 | 0.055067 | 11.5641
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.4311 | 70 | 0.05506 | 3.8542
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.4311 | 70 | 0.05506 | 3.8542
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5487 | 92.8 | 0.05506 | 5.1096
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.9213 | 80 | 0.05506 | 4.4048
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.9213 | 80 | 0.05506 | 4.4048
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.6368 | 115 | 0.05506 | 6.3319
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.04863 | west | 8 | N | N | Nwest | Nwest | 1 | 3.4041 | 0 | 0.054674 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.04863 | west | 8 | N | N | Nwest | Nwest | 1 | 3.5694 | 0 | 0.054674 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.04863 | west | 8 | N | N | Nwest | Nwest | 1 | 3.4236 | 0 | 0.054674 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.256 | 150 | 0.054417 | 8.1626
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6421 | 220 | 0.054417 | 11.9718
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6746 | 200 | 0.054417 | 10.8834
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8967 | 121.9 | 0.054417 | 6.6335
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.0482 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.025 | 125 | 0.054244 | 6.7805
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.0482 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.025 | 125 | 0.054244 | 6.7805
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.047831 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.22959 | 0 | 0.053875 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.04698 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7584 | 80 | 0.053024 | 4.2419
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.04698 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7584 | 80 | 0.053024 | 4.2419
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.04679 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5093 | 75 | 0.052834 | 3.9626
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.04679 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7432 | 80 | 0.052834 | 4.2267
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.04679 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8716 | 40 | 0.052834 | 2.1134
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046754 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7403 | 80 | 0.052798 | 4.2239
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.046747 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7398 | 80 | 0.052791 | 4.2233
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.04672 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.008 | 150 | 0.052764 | 7.9146
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.04672 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.008 | 150 | 0.052764 | 7.9146
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.046108 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9162 | 150 | 0.052152 | 7.8228
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.045726 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6581 | 80 | 0.05177 | 4.1416
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1413 | 112.5 | 0.051744 | 5.8212
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8322 | 149.5 | 0.051744 | 7.7358
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5002 | 186 | 0.051744 | 9.6244
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.8026 | 214.5 | 0.051744 | 11.0991
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.045458 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4775 | 76.5 | 0.051502 | 3.9399
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.045391 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8128 | 84 | 0.051435 | 4.3206
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.4814 | 209 | 0.046625 | 9.7447
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1335 | 126.5 | 0.046625 | 5.8981
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.1047 | 249 | 0.046625 | 11.6097
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9945 | 197 | 0.046625 | 9.1852
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.040116 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.04616 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.03542 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.313 | 150 | 0.041464 | 6.2196
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.026215 | west | 4 | Y | N | Ywest | Nwest | 1 | 17.0319 | 649.7 | 0.032259 | 20.9588
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.013792 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.019836 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.0129 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.4257 | 0 | -0.034023 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.0129 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3225 | 0 | -0.034023 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.0129 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034023 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.009105 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.05463 | 0 | -0.037818 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.008222 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.038701 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0060442 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0060442 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.0627 | 100 | 0.0054172 | 0.54172
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.002576 | north | 3 | N | N | Nnorth | Nnorth | 1 | -2.9804 | 0 | 0.0034682 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.002576 | north | 3 | N | N | Nnorth | Nnorth | 1 | -2.983 | 0 | 0.0034682 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.002828 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.61452 | 217.3 | 0.0032162 | 0.69887
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.002828 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.57974 | 205 | 0.0032162 | 0.65931
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.002828 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.77035 | 272.4 | 0.0032162 | 0.87608
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.47555 | 0 | 0.0029602 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.4811 | 0 | 0.0029602 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.4811 | 0 | 0.0029602 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.1719 | 0 | 0.0029602 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.003161 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028832 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.003161 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028832 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.003176 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.15245 | 48 | 0.0028682 | 0.13767
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.003176 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.1461 | 46 | 0.0028682 | 0.13194
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.003176 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.33348 | 105 | 0.0028682 | 0.30116
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.00318 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.4723 | 463 | 0.0028642 | 1.3261
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.003181 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.10179 | 0 | 0.0028632 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028612 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028612 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.003183 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.054111 | 17 | 0.0028612 | 0.04864
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028612 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028612 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.003263 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0027812 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.003263 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.568 | 787 | 0.0027812 | 2.1888
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.003354 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.85527 | 255 | 0.0026902 | 0.68599
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.003354 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.49975 | 149 | 0.0026902 | 0.40083
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.003354 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.51316 | 153 | 0.0026902 | 0.4116
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.003431 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.51465 | 150 | 0.0026132 | 0.39197
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.003431 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.27448 | 80 | 0.0026132 | 0.20905
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.9865 | 855 | 0.0025512 | 2.1812
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.9865 | 855 | 0.0025512 | 2.1812
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.53198 | 152.3 | 0.0025512 | 0.38854
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.53443 | 153 | 0.0025512 | 0.39033
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.001356 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018577 | 0 | -0.045567 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.003619 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.9929 | 827 | 0.0024252 | 2.0056
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.003619 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.964 | 819 | 0.0024252 | 1.9862
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.003729 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0023152 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.003864 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.05796 | 0 | 0.0021802 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.003864 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.05796 | 0 | 0.0021802 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.003951 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.4299 | 615 | 0.0020932 | 1.2873
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.003951 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.3192 | 587 | 0.0020932 | 1.2287
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.00096 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.02304 | 24 | -0.045963 | -1.1031
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.00096 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.02304 | 24 | -0.045963 | -1.1031
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.00096 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.02208 | 23 | -0.045963 | -1.0571
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.00401 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.60431 | 150.7 | 0.0020342 | 0.30655
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.00401 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.60551 | 151 | 0.0020342 | 0.30716
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.00401 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71137 | 177.4 | 0.0020342 | 0.36086
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.60964 | 151.5 | 0.0020202 | 0.30606
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.61286 | 152.3 | 0.0020202 | 0.30767
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71426 | 177.5 | 0.0020202 | 0.35858
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.92019 | 224 | 0.0019362 | 0.4337
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.92841 | 226 | 0.0019362 | 0.43757
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.8709 | 212 | 0.0019362 | 0.41047
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.86679 | 211 | 0.0019362 | 0.40853
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.000791 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.014238 | 0 | -0.046132 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.000791 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.014238 | 0 | -0.046132 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.000791 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011865 | 0 | -0.046132 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.004241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71249 | 168 | 0.0018032 | 0.30293
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.004241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.38169 | 90 | 0.0018032 | 0.16228
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.004251 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.95222 | 224 | 0.0017932 | 0.40167
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.004253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.92035 | 216.4 | 0.0017912 | 0.38761
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.004253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.91907 | 216.1 | 0.0017912 | 0.38707
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.000715 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.30173 | 422 | -0.046208 | -19.4997
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.004316 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.84594 | 196 | 0.0017282 | 0.33872
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.004316 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47908 | 111 | 0.0017282 | 0.19183
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.004322 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.7866 | 182 | 0.0017222 | 0.31343
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.004322 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.0918 | 484 | 0.0017222 | 0.83353
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.004326 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.2163 | 50 | 0.0017182 | 0.085908
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.00433 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0017142 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.64528 | 0 | 0.0016842 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.5668 | 0 | 0.0016842 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.6322 | 0 | 0.0016842 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.7396 | 0 | 0.0016842 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.000593 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.016604 | 0 | -0.04633 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.000593 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.017197 | 0 | -0.04633 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.004395 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.4501 | 785 | 0.0016492 | 1.2946
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.004395 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.494 | 795 | 0.0016492 | 1.3111
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.004395 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.4281 | 780 | 0.0016492 | 1.2863
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.004569 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.53914 | 118 | 0.0014752 | 0.17407
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.004569 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.52543 | 115 | 0.0014752 | 0.16964
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.004569 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.5404 | 556 | 0.0014752 | 0.82019
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.32067 | 70 | 0.0014632 | 0.10242
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.31609 | 69 | 0.0014632 | 0.10096
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.31609 | 69 | 0.0014632 | 0.10096
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.31151 | 68 | 0.0014632 | 0.099495
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.004645 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0013992 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.004645 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0013992 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.74929 | 161 | 0.0013902 | 0.22382
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76326 | 164 | 0.0013902 | 0.22799
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76326 | 164 | 0.0013902 | 0.22799
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.9268 | 414 | 0.0013902 | 0.57553
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.75395 | 162 | 0.0013902 | 0.22521
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.74929 | 161 | 0.0013902 | 0.22382
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.7586 | 163 | 0.0013902 | 0.2266
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.9035 | 409 | 0.0013902 | 0.56858
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.004673 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.8131 | 388 | 0.0013712 | 0.53201
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.004673 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.4066 | 515 | 0.0013712 | 0.70615
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.000244 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.046679 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.000243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0243 | 100 | -0.04668 | -4.668
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.000243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0243 | 100 | -0.04668 | -4.668
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.04668 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.04668 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.04668 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.04668 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.00023 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00414 | 0 | -0.046693 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.00023 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00414 | 0 | -0.046693 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.004757 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.19028 | 40 | 0.0012872 | 0.051487
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.004758 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.09516 | 20 | 0.0012862 | 0.025723
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.004758 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.11895 | 25 | 0.0012862 | 0.032154
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.004758 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.19508 | 41 | 0.0012862 | 0.052733
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.004775 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.37722 | 79 | 0.0012692 | 0.10026
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.004775 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.50615 | 106 | 0.0012692 | 0.13453
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.004775 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.69715 | 146 | 0.0012692 | 0.1853
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.004775 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.3629 | 76 | 0.0012692 | 0.096457
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.004775 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.8861 | 395 | 0.0012692 | 0.50132
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.004775 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.0771 | 435 | 0.0012692 | 0.55209
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.004785 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.0815 | 435 | 0.0012592 | 0.54774
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.004851 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.7069 | 558 | 0.0011932 | 0.66579
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.004851 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.8087 | 579 | 0.0011932 | 0.69084
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.004851 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.9196 | 808 | 0.0011932 | 0.96408
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.004894 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.36705 | 0 | 0.0011502 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.004894 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.38956 | 0 | 0.0011502 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.004894 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.43263 | 0 | 0.0011502 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.7832 | 160 | 0.0011492 | 0.18387
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76362 | 156 | 0.0011492 | 0.17927
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.95942 | 196 | 0.0011492 | 0.22524
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76362 | 156 | 0.0011492 | 0.17927
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76851 | 157 | 0.0011492 | 0.18042
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.96921 | 198 | 0.0011492 | 0.22753
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.004914 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.8182 | 370 | 0.0011302 | 0.41816
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.68796 | 0 | 0.0011302 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.69287 | 0 | 0.0011302 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.5184 | 0 | 0.0011302 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.7027 | 0 | 0.0011302 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.70762 | 0 | 0.0011302 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.5233 | 0 | 0.0011302 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.004936 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0011082 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.046923 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.046923 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.005021 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.85357 | 170 | 0.0010232 | 0.17394
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.005021 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.6109 | 520 | 0.0010232 | 0.53205
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.005079 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00096517 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.005094 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.20376 | 0 | 0.00095017 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.005094 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.20376 | 0 | 0.00095017 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.000164 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.047087 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.00052 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00624 | 0 | -0.047443 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.00052 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00572 | 0 | -0.047443 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.00052 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00624 | 0 | -0.047443 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.071478 | 114 | -0.04755 | -5.4207
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.13919 | 222 | -0.04755 | -10.556
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11537 | 184 | -0.04755 | -8.7491
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.14045 | 224 | -0.04755 | -10.6511
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.072105 | 115 | -0.04755 | -5.4682
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.000689 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.039962 | 58 | -0.047612 | -2.7615
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.000689 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.061321 | 89 | -0.047612 | -4.2374
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.030316 | 44 | -0.047612 | -2.0949
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.030316 | 44 | -0.047612 | -2.0949
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.029627 | 43 | -0.047612 | -2.0473
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.031005 | 45 | -0.047612 | -2.1425
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.000774 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31502 | 407 | -0.047697 | -19.4126
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.000789 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.31244 | 396 | -0.047712 | -18.8938
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.000803 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.16783 | 209 | -0.047726 | -9.9747
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.000803 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.17345 | 216 | -0.047726 | -10.3088
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.036938 | 46 | -0.047726 | -2.1954
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.037741 | 47 | -0.047726 | -2.2431
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.036938 | 46 | -0.047726 | -2.1954
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.036938 | 46 | -0.047726 | -2.1954
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.000804 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.33125 | 412 | -0.047727 | -19.6634
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.000804 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.3216 | 400 | -0.047727 | -19.0907
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.000813 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.047736 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.005785 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.3471 | 60 | 0.00025917 | 0.01555
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.005785 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.36445 | 63 | 0.00025917 | 0.016327
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.000819 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.34726 | 424 | -0.047742 | -20.2425
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.000819 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.34808 | 425 | -0.047742 | -20.2902
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.000848 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.047771 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.005833 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.34998 | 60 | 0.00021117 | 0.01267
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.00087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03045 | 0 | -0.047793 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.00087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02958 | 0 | -0.047793 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.00087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03045 | 0 | -0.047793 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.000881 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.047804 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.000881 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.047804 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.000881 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.047804 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.000891 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13053 | 146.5 | -0.047814 | -7.0047
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.000891 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13178 | 147.9 | -0.047814 | -7.0716
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.000891 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15414 | 173 | -0.047814 | -8.2718
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000899 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13934 | 155 | -0.047822 | -7.4124
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.000899 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15283 | 170 | -0.047822 | -8.1297
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000899 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13934 | 155 | -0.047822 | -7.4124
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.000927 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.50614 | 546 | -0.04785 | -26.1259
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.000927 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.69525 | 750 | -0.04785 | -35.8873
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19727 | 207 | -0.047876 | -9.9103
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.20652 | 216.7 | -0.047876 | -10.3747
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.23063 | 242 | -0.047876 | -11.5859
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13723 | 144 | -0.047876 | -6.8941
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13723 | 144 | -0.047876 | -6.8941
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16296 | 171 | -0.047876 | -8.1867
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.00099 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.047913 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.00099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.03762 | 38 | -0.047913 | -1.8207
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.00099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.019107 | 19.3 | -0.047913 | -0.92472
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.00099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.01485 | 15 | -0.047913 | -0.71869
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.00099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.04653 | 47 | -0.047913 | -2.2519
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09447 | 94 | -0.047928 | -4.5052
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.041205 | 41 | -0.047928 | -1.965
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.03819 | 38 | -0.047928 | -1.8213
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.019095 | 19 | -0.047928 | -0.91063
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09447 | 94 | -0.047928 | -4.5052
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.03618 | 36 | -0.047928 | -1.7254
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.043215 | 43 | -0.047928 | -2.0609
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.02211 | 22 | -0.047928 | -1.0544
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.14874 | 148 | -0.047928 | -7.0933
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05025 | 50 | -0.047928 | -2.3964
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.055275 | 55 | -0.047928 | -2.636
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05025 | 50 | -0.047928 | -2.3964
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.001023 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.029667 | 0 | -0.047946 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.001034 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004136 | 0 | -0.047957 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.001042 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.039596 | 0 | -0.047965 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.001046 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.039748 | 0 | -0.047969 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.001046 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02615 | 0 | -0.047969 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.001046 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02615 | 0 | -0.047969 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.00105 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0063 | 0 | -0.047973 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.001051 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.35103 | 334 | -0.047974 | -16.0232
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.001051 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.35734 | 340 | -0.047974 | -16.3111
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.001051 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.18918 | 180 | -0.047974 | -8.6353
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.001051 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.18918 | 180 | -0.047974 | -8.6353
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.001057 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19026 | 180 | -0.04798 | -8.6363
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.001057 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.15675 | 0 | -0.04798 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.001057 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.15707 | 0 | -0.04798 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.001057 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.16172 | 0 | -0.04798 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.001058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.35549 | 336 | -0.047981 | -16.1215
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.001058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19044 | 180 | -0.047981 | -8.6365
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.001062 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.668 | 629 | -0.047985 | -30.1824
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15626 | 147 | -0.047986 | -7.0539
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.14669 | 138 | -0.047986 | -6.622
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.14882 | 140 | -0.047986 | -6.718
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15626 | 147 | -0.047986 | -7.0539
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19347 | 182 | -0.047986 | -8.7334
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.21047 | 198 | -0.047986 | -9.5012
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 25 | -0.048002 | -1.2
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 25 | -0.048002 | -1.2
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 25 | -0.048002 | -1.2
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.017264 | 16 | -0.048002 | -0.76803
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 25 | -0.048002 | -1.2
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 25 | -0.048002 | -1.2
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 25 | -0.048002 | -1.2
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.016185 | 15 | -0.048002 | -0.72003
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.17285 | 0 | -0.048017 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.16738 | 0 | -0.048017 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.1094 | 0 | -0.048017 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.15863 | 0 | -0.048017 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.16082 | 0 | -0.048017 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.13894 | 0 | -0.048017 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.001094 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.013128 | 0 | -0.048017 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.006079 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -3.4835e-05 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.006079 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -3.4835e-05 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.006079 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -3.4835e-05 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.001113 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0026712 | 0 | -0.048036 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.001113 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0026712 | 0 | -0.048036 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.001113 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0031164 | 0 | -0.048036 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15819 | 142 | -0.048037 | -6.8212
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16153 | 145 | -0.048037 | -6.9653
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16821 | 151 | -0.048037 | -7.2535
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.32306 | 290 | -0.048037 | -13.9306
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2604 | 223.9 | -0.048086 | -10.7664
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.26167 | 225 | -0.048086 | -10.8193
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.26121 | 224.6 | -0.048086 | -10.8
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.26365 | 226.7 | -0.048086 | -10.901
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.001169 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.025718 | 22 | -0.048092 | -1.058
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.001169 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.012859 | 11 | -0.048092 | -0.52901
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.001169 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.012859 | 11 | -0.048092 | -0.52901
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.001192 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014304 | 0 | -0.048115 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.001193 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0028632 | 0 | -0.048116 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.001193 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0028632 | 0 | -0.048116 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.057431 | 47.7 | -0.048127 | -2.2956
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.044909 | 37.3 | -0.048127 | -1.7951
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.055384 | 46 | -0.048127 | -2.2138
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.057792 | 48 | -0.048127 | -2.3101
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.001219 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.17554 | 144 | -0.048142 | -6.9324
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.001219 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.22917 | 188 | -0.048142 | -9.0506
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.001238 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.090374 | 0 | -0.048161 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.001262 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.01893 | 0 | -0.048185 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.001262 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.029026 | 0 | -0.048185 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.001267 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.010136 | 0 | -0.04819 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.03584 | 0 | -0.048203 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00896 | 0 | -0.048203 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.04992 | 0 | -0.048203 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0192 | 0 | -0.048203 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00896 | 0 | -0.048203 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0192 | 0 | -0.048203 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.04992 | 0 | -0.048203 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.04992 | 0 | -0.048203 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.001347 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.064656 | 0 | -0.04827 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.001364 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010912 | 0 | -0.048287 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.001364 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010912 | 0 | -0.048287 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10776 | 0 | -0.048287 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.11048 | 0 | -0.048287 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10776 | 0 | -0.048287 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10912 | 0 | -0.048287 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10694 | 0 | -0.048287 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0341 | 0 | -0.048287 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.062744 | 0 | -0.048287 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.038192 | 0 | -0.048287 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.05947 | 0 | -0.048287 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10094 | 0 | -0.048287 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.068502 | 49 | -0.048321 | -2.3677
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.064308 | 46 | -0.048321 | -2.2228
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.064308 | 46 | -0.048321 | -2.2228
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.065706 | 47 | -0.048321 | -2.2711
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.001398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.21529 | 154 | -0.048321 | -7.4414
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.001398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2069 | 148 | -0.048321 | -7.1515
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.067104 | 48 | -0.048321 | -2.3194
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.067104 | 48 | -0.048321 | -2.3194
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.001411 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.43741 | 310 | -0.048334 | -14.9834
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.001411 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.58274 | 413 | -0.048334 | -19.9618
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.060942 | 42 | -0.048374 | -2.0317
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.063844 | 44 | -0.048374 | -2.1284
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.063844 | 44 | -0.048374 | -2.1284
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.068197 | 47 | -0.048374 | -2.2736
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.001541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.20341 | 132 | -0.048464 | -6.3972
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.001541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.20649 | 134 | -0.048464 | -6.4941
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.001541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.49774 | 323 | -0.048464 | -15.6538
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.001546 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.23577 | 152.5 | -0.048469 | -7.3915
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.001546 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.23113 | 149.5 | -0.048469 | -7.2461
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.001546 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.3596 | 232.6 | -0.048469 | -11.2738
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08 | 50 | -0.048523 | -2.4261
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08 | 50 | -0.048523 | -2.4261
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08 | 50 | -0.048523 | -2.4261
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08 | 50 | -0.048523 | -2.4261
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.001637 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25865 | 158 | -0.04856 | -7.6724
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.001637 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.26192 | 160 | -0.04856 | -7.7696
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.001637 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.28647 | 175 | -0.04856 | -8.4979
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.00164 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.95776 | 584 | -0.048563 | -28.3606
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.00164 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.9758 | 595 | -0.048563 | -28.8948
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.00164 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.71012 | 433 | -0.048563 | -21.0277
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.006731 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.3731 | 204 | -0.00068683 | -0.14011
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.006731 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.3529 | 201 | -0.00068683 | -0.13805
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.006731 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.6289 | 242 | -0.00068683 | -0.16621
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.001971 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -2.6273 | 0 | -0.048894 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.001971 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -2.6175 | 0 | -0.048894 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.152 | 76 | -0.048923 | -3.7181
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.152 | 76 | -0.048923 | -3.7181
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.21 | 105 | -0.048923 | -5.1369
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.148 | 74 | -0.048923 | -3.6203
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.148 | 74 | -0.048923 | -3.6203
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.204 | 102 | -0.048923 | -4.9901
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.002023 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13352 | 66 | -0.048946 | -3.2304
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.002088 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.1881 | 569 | -0.049011 | -27.8871
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.002088 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.2131 | 581 | -0.049011 | -28.4752
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13479 | 0 | -0.049097 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15522 | 0 | -0.049097 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09783 | 0 | -0.049097 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21957 | 0 | -0.049097 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18696 | 0 | -0.049097 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19131 | 0 | -0.049097 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1087 | 0 | -0.049097 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.039132 | 0 | -0.049097 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20436 | 0 | -0.049097 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15218 | 0 | -0.049097 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13696 | 0 | -0.049097 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15653 | 0 | -0.049097 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14088 | 0 | -0.049097 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21957 | 0 | -0.049097 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21088 | 0 | -0.049097 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22392 | 0 | -0.049097 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16522 | 0 | -0.049097 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17392 | 0 | -0.049097 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17392 | 0 | -0.049097 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37175 | 0 | -0.049097 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.002211 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15698 | 0 | -0.049134 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.002211 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02211 | 0 | -0.049134 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24886 | 0 | -0.049165 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24886 | 0 | -0.049165 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.2668 | 0 | -0.049165 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.2455 | 0 | -0.049165 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.002341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10792 | 0 | -0.049264 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.002351 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.5305 | 651 | -0.049274 | -32.0772
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.002351 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.326 | 564 | -0.049274 | -27.7904
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.002351 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.4106 | 600 | -0.049274 | -29.5642
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.002351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.38321 | 0 | -0.049274 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.002351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.38321 | 0 | -0.049274 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.002351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.576 | 0 | -0.049274 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.002355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.077715 | 0 | -0.049278 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.00237 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.38157 | 161 | -0.049293 | -7.9361
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.00237 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.39342 | 166 | -0.049293 | -8.1826
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.00237 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.58776 | 248 | -0.049293 | -12.2246
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.00237 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.294 | 546 | -0.049293 | -26.9138
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.00237 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -1.5239 | 0 | -0.049293 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.00237 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.03081 | 13 | -0.049293 | -0.64081
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24192 | 0 | -0.049335 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.22407 | 0 | -0.049335 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24771 | 0 | -0.049335 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24602 | 0 | -0.049335 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.077184 | 0 | -0.049335 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07236 | 0 | -0.049335 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17077 | 0 | -0.049335 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16088 | 0 | -0.049335 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12784 | 0 | -0.049335 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.36952 | 0 | -0.049335 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.37024 | 0 | -0.049335 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.36735 | 0 | -0.049335 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.23155 | 0 | -0.049335 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.58853 | 0 | -0.049335 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09648 | 0 | -0.049335 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.002436 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1218 | 50 | -0.049359 | -2.4679
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.002449 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.049372 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22459 | 0 | -0.049391 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2162 | 0 | -0.049391 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21472 | 0 | -0.049391 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13451 | 0 | -0.049391 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03011 | 0 | -0.049391 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16094 | 0 | -0.049399 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14856 | 0 | -0.049399 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16094 | 0 | -0.049399 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16094 | 0 | -0.049399 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11449 | 46 | -0.049412 | -2.2729
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11449 | 46 | -0.049412 | -2.2729
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11449 | 46 | -0.049412 | -2.2729
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13689 | 55 | -0.049412 | -2.7176
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13689 | 55 | -0.049412 | -2.7176
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13441 | 54 | -0.049412 | -2.6682
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.002489 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19414 | 0 | -0.049412 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.002489 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19912 | 0 | -0.049412 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40669 | 0 | -0.049415 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39149 | 0 | -0.049415 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39249 | 0 | -0.049415 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39124 | 0 | -0.049415 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67035 | 0 | -0.049415 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.002497 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.087395 | 0 | -0.04942 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.0025 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.03 | 12 | -0.049423 | -0.59307
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.0025 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.049423 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.0025 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.4225 | 169 | -0.049423 | -8.3524
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.0025 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.4125 | 165 | -0.049423 | -8.1547
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.0025 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3725 | 0 | -0.049423 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.0025 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16275 | 0 | -0.049423 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.002501 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.53271 | 213 | -0.049424 | -10.5272
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.040516 | 0 | -0.049424 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16006 | 0 | -0.049424 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15806 | 0 | -0.049424 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20658 | 0 | -0.049424 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18407 | 0 | -0.049424 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.002501 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.57023 | 228 | -0.049424 | -11.2686
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.002501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45018 | 0 | -0.049424 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.002501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39666 | 0 | -0.049424 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.002501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39266 | 0 | -0.049424 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17793 | 0 | -0.049429 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18043 | 0 | -0.049429 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.097734 | 0 | -0.049429 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07518 | 0 | -0.049429 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.002514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.3419 | 0 | -0.049437 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10559 | 42 | -0.049437 | -2.0763
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10559 | 42 | -0.049437 | -2.0763
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.095532 | 38 | -0.049437 | -1.8786
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.095532 | 38 | -0.049437 | -1.8786
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.002517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43544 | 0 | -0.04944 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.002517 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.3398 | 0 | -0.04944 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.26312 | 104 | -0.049453 | -5.1431
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.26312 | 104 | -0.049453 | -5.1431
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13662 | 54 | -0.049453 | -2.6704
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13409 | 53 | -0.049453 | -2.621
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13662 | 54 | -0.049453 | -2.6704
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.14421 | 57 | -0.049453 | -2.8188
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13662 | 54 | -0.049453 | -2.6704
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13662 | 54 | -0.049453 | -2.6704
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.14674 | 58 | -0.049453 | -2.8683
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.14674 | 58 | -0.049453 | -2.8683
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.002532 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.861 | 735 | -0.049455 | -36.3492
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.08619 | 0 | -0.049458 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.087965 | 0 | -0.049458 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.082894 | 0 | -0.049458 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11636 | 0 | -0.049458 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.044869 | 0 | -0.049458 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.051714 | 0 | -0.049458 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.050446 | 0 | -0.049458 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.088725 | 0 | -0.049458 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04563 | 0 | -0.049458 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21649 | 0 | -0.049458 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37518 | 0 | -0.049458 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002541 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.030492 | 12 | -0.049464 | -0.59356
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01272 | 0 | -0.049467 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.053424 | 0 | -0.049467 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16536 | 0 | -0.049467 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1679 | 0 | -0.049467 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17808 | 0 | -0.049467 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16027 | 0 | -0.049467 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15773 | 0 | -0.049467 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26458 | 0 | -0.049467 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1501 | 0 | -0.049467 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.002544 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.030528 | 12 | -0.049467 | -0.5936
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.002544 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.8902 | 743 | -0.049467 | -36.7538
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.002547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39988 | 0 | -0.04947 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.002548 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.43826 | 172 | -0.049471 | -8.509
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.002548 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.43826 | 172 | -0.049471 | -8.509
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.002548 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.43826 | 172 | -0.049471 | -8.509
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41612 | 0 | -0.049479 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41254 | 0 | -0.049479 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40615 | 0 | -0.049479 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68808 | 0 | -0.049479 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.00256 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0189 | 398 | -0.049483 | -19.6941
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1437 | 56 | -0.049489 | -2.7714
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.15139 | 59 | -0.049489 | -2.9198
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1437 | 56 | -0.049489 | -2.7714
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1437 | 56 | -0.049489 | -2.7714
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.15139 | 59 | -0.049489 | -2.9198
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1437 | 56 | -0.049489 | -2.7714
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45257 | 0 | -0.049539 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4081 | 0 | -0.049539 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40286 | 0 | -0.049539 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40286 | 0 | -0.049539 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.002616 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42379 | 0 | -0.049539 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.00799 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.89887 | 112.5 | -0.0019458 | -0.21891
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.010067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8993 | 288 | -0.0040228 | -1.1586
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.010067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.4798 | 147 | -0.0040228 | -0.59136
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.010067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.4798 | 147 | -0.0040228 | -0.59136
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.010387 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1548 | 400 | -0.0043428 | -1.7371
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.010387 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4513 | 236 | -0.0043428 | -1.0249
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.010387 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7139 | 165 | -0.0043428 | -0.71657
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.010387 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.8016 | 366 | -0.0043428 | -1.5895
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.24312 | 20 | -0.0061118 | -0.12224
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.24312 | 20 | -0.0061118 | -0.12224
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.24312 | 20 | -0.0061118 | -0.12224
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.20665 | 17 | -0.0061118 | -0.1039
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.01243 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.90739 | 73 | -0.0063858 | -0.46617
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.01243 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.4792 | 119 | -0.0063858 | -0.75991
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.01243 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.5482 | 205 | -0.0063858 | -1.3091
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.01243 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.2679 | 102 | -0.0063858 | -0.65136
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.01243 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.1933 | 96 | -0.0063858 | -0.61304
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.012649 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.22768 | 18 | -0.0066048 | -0.11889
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.012649 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.22768 | 18 | -0.0066048 | -0.11889
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.012649 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.48066 | 38 | -0.0066048 | -0.25098
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.022872 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27446 | 0 | -0.016828 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.022872 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27446 | 0 | -0.016828 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.039371 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -4.7245 | 120 | -0.033327 | -3.9992
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.06948 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -16.8142 | 242 | -0.063436 | -15.3515

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: MURRY_P8 - GRHAMSES 138kV [1371 - 1431] C:SWEETWATER / MULBERRY - LONGCREEK8 [1420 - 1439] & [1435 - 6230] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.06948 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -16.8142 | 242 | -0.063436 | -15.3515 | 242 | 15.3515
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.039371 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -4.7245 | 0 | -0.033327 | 0 | 242 | 15.3515
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.022872 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27446 | 0 | -0.016828 | 0 | 242 | 15.3515
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.022872 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27446 | 0 | -0.016828 | 0 | 242 | 15.3515 | Weighted Shift Factors
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.012649 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.22768 | 18 | -0.0066048 | -0.11889 | 260 | 15.4704 | west | 0.046923
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.012649 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.22768 | 18 | -0.0066048 | -0.11889 | 278 | 15.5892 | north | -0.0060442
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.012649 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.48066 | 38 | -0.0066048 | -0.25098 | 316 | 15.8402 |  | 0.052967
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.01243 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.90739 | 73 | -0.0063858 | -0.46617 | 389 | 16.3064
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.01243 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.4792 | 119 | -0.0063858 | -0.75991 |  |  | Line Rating | 223
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.01243 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.5482 | 205 | -0.0063858 | -1.3091 |  |  | Conc Gen | 389
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.01243 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.2679 | 102 | -0.0063858 | -0.65136 |  |  | Weighted Imp. | 16.3064
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.01243 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.1933 | 96 | -0.0063858 | -0.61304 |  |  | PTDF | 0.041919
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.24312 | 20 | -0.0061118 | -0.12224
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.24312 | 20 | -0.0061118 | -0.12224 |  |  | Concentration | 0.79141
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.24312 | 20 | -0.0061118 | -0.12224
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.012156 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.20665 | 17 | -0.0061118 | -0.1039
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.010387 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.8016 | 366 | -0.0043428 | -1.5895
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.010387 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7139 | 0 | -0.0043428 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.010387 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4513 | 0 | -0.0043428 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.010387 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1548 | 0 | -0.0043428 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.010067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8993 | 288 | -0.0040228 | -1.1586
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.010067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.4798 | 147 | -0.0040228 | -0.59136
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.010067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.4798 | 147 | -0.0040228 | -0.59136
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.00799 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.89887 | 0 | -0.0019458 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45257 | 0 | -0.049539 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4081 | 0 | -0.049539 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40286 | 0 | -0.049539 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002616 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40286 | 0 | -0.049539 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.002616 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42379 | 0 | -0.049539 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1437 | 56 | -0.049489 | -2.7714
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.15139 | 59 | -0.049489 | -2.9198
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1437 | 56 | -0.049489 | -2.7714
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1437 | 56 | -0.049489 | -2.7714
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.15139 | 59 | -0.049489 | -2.9198
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.002566 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.1437 | 56 | -0.049489 | -2.7714
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.00256 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0189 | 398 | -0.049483 | -19.6941
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41612 | 0 | -0.049479 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41254 | 0 | -0.049479 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40615 | 0 | -0.049479 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.002556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68808 | 0 | -0.049479 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.002548 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.43826 | 172 | -0.049471 | -8.509
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.002548 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.43826 | 172 | -0.049471 | -8.509
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.002548 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.43826 | 172 | -0.049471 | -8.509
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.002547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39988 | 0 | -0.04947 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.002544 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.8902 | 743 | -0.049467 | -36.7538
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.002544 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.030528 | 0 | -0.049467 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16536 | 0 | -0.049467 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1679 | 0 | -0.049467 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17808 | 0 | -0.049467 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16027 | 0 | -0.049467 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15773 | 0 | -0.049467 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26458 | 0 | -0.049467 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1501 | 0 | -0.049467 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01272 | 0 | -0.049467 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.002544 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.053424 | 0 | -0.049467 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002541 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.030492 | 12 | -0.049464 | -0.59356
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.08619 | 0 | -0.049458 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.087965 | 0 | -0.049458 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.082894 | 0 | -0.049458 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11636 | 0 | -0.049458 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.044869 | 0 | -0.049458 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.051714 | 0 | -0.049458 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.050446 | 0 | -0.049458 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.088725 | 0 | -0.049458 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04563 | 0 | -0.049458 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21649 | 0 | -0.049458 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.002535 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37518 | 0 | -0.049458 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.002532 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.861 | 735 | -0.049455 | -36.3492
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.26312 | 104 | -0.049453 | -5.1431
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.26312 | 104 | -0.049453 | -5.1431
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13662 | 54 | -0.049453 | -2.6704
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13409 | 53 | -0.049453 | -2.621
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13662 | 54 | -0.049453 | -2.6704
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.14421 | 57 | -0.049453 | -2.8188
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13662 | 54 | -0.049453 | -2.6704
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13662 | 54 | -0.049453 | -2.6704
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.14674 | 58 | -0.049453 | -2.8683
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.00253 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.14674 | 58 | -0.049453 | -2.8683
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.002517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43544 | 0 | -0.04944 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.002517 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.3398 | 0 | -0.04944 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10559 | 42 | -0.049437 | -2.0763
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10559 | 42 | -0.049437 | -2.0763
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.095532 | 38 | -0.049437 | -1.8786
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.002514 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.095532 | 38 | -0.049437 | -1.8786
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.002514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.3419 | 0 | -0.049437 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17793 | 0 | -0.049429 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18043 | 0 | -0.049429 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.097734 | 0 | -0.049429 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.002506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07518 | 0 | -0.049429 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.002501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45018 | 0 | -0.049424 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.002501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39666 | 0 | -0.049424 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.002501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39266 | 0 | -0.049424 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.002501 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.57023 | 228 | -0.049424 | -11.2686
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16006 | 0 | -0.049424 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15806 | 0 | -0.049424 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20658 | 0 | -0.049424 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18407 | 0 | -0.049424 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.002501 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.040516 | 0 | -0.049424 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.002501 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.53271 | 213 | -0.049424 | -10.5272
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.0025 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3725 | 0 | -0.049423 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.0025 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16275 | 0 | -0.049423 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.0025 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.4125 | 165 | -0.049423 | -8.1547
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.0025 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.4225 | 169 | -0.049423 | -8.3524
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.0025 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.03 | 12 | -0.049423 | -0.59307
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.0025 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.049423 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.002497 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.087395 | 0 | -0.04942 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40669 | 0 | -0.049415 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39149 | 0 | -0.049415 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39249 | 0 | -0.049415 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39124 | 0 | -0.049415 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.002492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67035 | 0 | -0.049415 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.002489 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19414 | 0 | -0.049412 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.002489 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19912 | 0 | -0.049412 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11449 | 46 | -0.049412 | -2.2729
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11449 | 46 | -0.049412 | -2.2729
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11449 | 46 | -0.049412 | -2.2729
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13689 | 55 | -0.049412 | -2.7176
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13689 | 55 | -0.049412 | -2.7176
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.002489 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13441 | 54 | -0.049412 | -2.6682
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16094 | 0 | -0.049399 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14856 | 0 | -0.049399 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16094 | 0 | -0.049399 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.002476 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16094 | 0 | -0.049399 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22459 | 0 | -0.049391 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2162 | 0 | -0.049391 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21472 | 0 | -0.049391 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13451 | 0 | -0.049391 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.002468 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03011 | 0 | -0.049391 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.002449 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.049372 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.002436 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1218 | 50 | -0.049359 | -2.4679
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17077 | 0 | -0.049335 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16088 | 0 | -0.049335 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12784 | 0 | -0.049335 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.36952 | 0 | -0.049335 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.37024 | 0 | -0.049335 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.36735 | 0 | -0.049335 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.23155 | 0 | -0.049335 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.58853 | 0 | -0.049335 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09648 | 0 | -0.049335 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.077184 | 0 | -0.049335 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.002412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07236 | 0 | -0.049335 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24192 | 0 | -0.049335 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.22407 | 0 | -0.049335 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24771 | 0 | -0.049335 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.002412 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24602 | 0 | -0.049335 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.00237 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.38157 | 161 | -0.049293 | -7.9361
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.00237 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.39342 | 166 | -0.049293 | -8.1826
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.00237 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.58776 | 248 | -0.049293 | -12.2246
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.00237 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.294 | 546 | -0.049293 | -26.9138
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.00237 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -1.5239 | 0 | -0.049293 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.00237 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.03081 | 13 | -0.049293 | -0.64081
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.002355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.077715 | 0 | -0.049278 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.002351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.38321 | 0 | -0.049274 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.002351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.38321 | 0 | -0.049274 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.002351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.576 | 0 | -0.049274 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.002351 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.5305 | 0 | -0.049274 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.002351 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.326 | 0 | -0.049274 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.002351 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.4106 | 0 | -0.049274 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.002341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10792 | 0 | -0.049264 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24886 | 0 | -0.049165 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.24886 | 0 | -0.049165 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.2668 | 0 | -0.049165 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.002242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.2455 | 0 | -0.049165 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.002211 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15698 | 0 | -0.049134 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.002211 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02211 | 0 | -0.049134 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13479 | 0 | -0.049097 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15522 | 0 | -0.049097 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09783 | 0 | -0.049097 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21957 | 0 | -0.049097 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18696 | 0 | -0.049097 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19131 | 0 | -0.049097 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1087 | 0 | -0.049097 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.039132 | 0 | -0.049097 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20436 | 0 | -0.049097 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15218 | 0 | -0.049097 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13696 | 0 | -0.049097 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15653 | 0 | -0.049097 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14088 | 0 | -0.049097 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21957 | 0 | -0.049097 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21088 | 0 | -0.049097 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22392 | 0 | -0.049097 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16522 | 0 | -0.049097 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17392 | 0 | -0.049097 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17392 | 0 | -0.049097 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.002174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37175 | 0 | -0.049097 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.002088 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.1881 | 0 | -0.049011 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.002088 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.2131 | 0 | -0.049011 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.002023 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13352 | 66 | -0.048946 | -3.2304
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.152 | 76 | -0.048923 | -3.7181
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.152 | 76 | -0.048923 | -3.7181
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.21 | 105 | -0.048923 | -5.1369
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.148 | 74 | -0.048923 | -3.6203
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.148 | 74 | -0.048923 | -3.6203
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.204 | 102 | -0.048923 | -4.9901
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.001971 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -2.6273 | 0 | -0.048894 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.001971 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -2.6175 | 0 | -0.048894 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.006731 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.3731 | 204 | -0.00068683 | -0.14011
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.006731 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.3529 | 201 | -0.00068683 | -0.13805
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.006731 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.6289 | 242 | -0.00068683 | -0.16621
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.00164 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.71012 | 0 | -0.048563 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.00164 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.95776 | 0 | -0.048563 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.00164 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.9758 | 0 | -0.048563 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.001637 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25865 | 158 | -0.04856 | -7.6724
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.001637 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.26192 | 160 | -0.04856 | -7.7696
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.001637 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.28647 | 175 | -0.04856 | -8.4979
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08 | 50 | -0.048523 | -2.4261
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08 | 50 | -0.048523 | -2.4261
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08 | 50 | -0.048523 | -2.4261
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.0016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08 | 50 | -0.048523 | -2.4261
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.001546 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.23577 | 152.5 | -0.048469 | -7.3915
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.001546 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.23113 | 149.5 | -0.048469 | -7.2461
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.001546 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.3596 | 232.6 | -0.048469 | -11.2738
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.001541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.20341 | 132 | -0.048464 | -6.3972
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.001541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.20649 | 134 | -0.048464 | -6.4941
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.001541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.49774 | 323 | -0.048464 | -15.6538
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.060942 | 42 | -0.048374 | -2.0317
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.063844 | 44 | -0.048374 | -2.1284
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.063844 | 44 | -0.048374 | -2.1284
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.001451 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.068197 | 47 | -0.048374 | -2.2736
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.001411 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.43741 | 310 | -0.048334 | -14.9834
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.001411 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.58274 | 413 | -0.048334 | -19.9618
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.068502 | 49 | -0.048321 | -2.3677
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.064308 | 46 | -0.048321 | -2.2228
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.064308 | 46 | -0.048321 | -2.2228
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.065706 | 47 | -0.048321 | -2.2711
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.001398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.21529 | 154 | -0.048321 | -7.4414
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.001398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2069 | 148 | -0.048321 | -7.1515
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.067104 | 48 | -0.048321 | -2.3194
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.001398 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.067104 | 48 | -0.048321 | -2.3194
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10776 | 0 | -0.048287 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.11048 | 0 | -0.048287 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10776 | 0 | -0.048287 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10912 | 0 | -0.048287 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10694 | 0 | -0.048287 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0341 | 0 | -0.048287 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.062744 | 0 | -0.048287 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.038192 | 0 | -0.048287 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.05947 | 0 | -0.048287 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.001364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10094 | 0 | -0.048287 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.001364 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010912 | 0 | -0.048287 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.001364 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010912 | 0 | -0.048287 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.001347 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.064656 | 0 | -0.04827 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.03584 | 0 | -0.048203 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00896 | 0 | -0.048203 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.04992 | 0 | -0.048203 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0192 | 0 | -0.048203 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00896 | 0 | -0.048203 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0192 | 0 | -0.048203 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.04992 | 0 | -0.048203 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.00128 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.04992 | 0 | -0.048203 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.001267 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.010136 | 0 | -0.04819 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.001262 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.01893 | 0 | -0.048185 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.001262 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.029026 | 0 | -0.048185 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.001238 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.090374 | 0 | -0.048161 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.001219 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.17554 | 144 | -0.048142 | -6.9324
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.001219 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.22917 | 188 | -0.048142 | -9.0506
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.057431 | 47.7 | -0.048127 | -2.2956
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.044909 | 37.3 | -0.048127 | -1.7951
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.055384 | 46 | -0.048127 | -2.2138
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.001204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.057792 | 48 | -0.048127 | -2.3101
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.001193 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0028632 | 0 | -0.048116 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.001193 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0028632 | 0 | -0.048116 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.001192 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014304 | 0 | -0.048115 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.001169 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.025718 | 22 | -0.048092 | -1.058
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.001169 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.012859 | 11 | -0.048092 | -0.52901
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.001169 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.012859 | 11 | -0.048092 | -0.52901
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2604 | 223.9 | -0.048086 | -10.7664
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.26167 | 225 | -0.048086 | -10.8193
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.26121 | 224.6 | -0.048086 | -10.8
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.001163 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.26365 | 226.7 | -0.048086 | -10.901
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15819 | 142 | -0.048037 | -6.8212
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16153 | 145 | -0.048037 | -6.9653
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16821 | 151 | -0.048037 | -7.2535
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.001114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.32306 | 290 | -0.048037 | -13.9306
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.001113 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0026712 | 0 | -0.048036 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.001113 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0026712 | 0 | -0.048036 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.001113 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0031164 | 0 | -0.048036 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.006079 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -3.4835e-05 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.006079 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -3.4835e-05 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.006079 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -3.4835e-05 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.17285 | 0 | -0.048017 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.16738 | 0 | -0.048017 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.1094 | 0 | -0.048017 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.15863 | 0 | -0.048017 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.16082 | 0 | -0.048017 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.001094 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.13894 | 0 | -0.048017 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.001094 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.013128 | 0 | -0.048017 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 0 | -0.048002 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 0 | -0.048002 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 0 | -0.048002 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.017264 | 0 | -0.048002 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 0 | -0.048002 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 0 | -0.048002 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.026975 | 0 | -0.048002 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.001079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.016185 | 0 | -0.048002 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15626 | 147 | -0.047986 | -7.0539
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.14669 | 138 | -0.047986 | -6.622
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.14882 | 140 | -0.047986 | -6.718
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15626 | 147 | -0.047986 | -7.0539
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19347 | 182 | -0.047986 | -8.7334
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.001063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.21047 | 198 | -0.047986 | -9.5012
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.001062 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.668 | 0 | -0.047985 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.001058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.35549 | 336 | -0.047981 | -16.1215
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.001058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19044 | 180 | -0.047981 | -8.6365
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.001057 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.15675 | 0 | -0.04798 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.001057 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.15707 | 0 | -0.04798 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.001057 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.16172 | 0 | -0.04798 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.001057 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19026 | 180 | -0.04798 | -8.6363
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.001051 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.35103 | 334 | -0.047974 | -16.0232
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.001051 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.35734 | 340 | -0.047974 | -16.3111
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.001051 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.18918 | 180 | -0.047974 | -8.6353
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.001051 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.18918 | 180 | -0.047974 | -8.6353
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.00105 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0063 | 0 | -0.047973 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.001046 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02615 | 0 | -0.047969 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.001046 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02615 | 0 | -0.047969 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.001046 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.039748 | 0 | -0.047969 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.001042 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.039596 | 0 | -0.047965 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.001034 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004136 | 0 | -0.047957 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.001023 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.029667 | 0 | -0.047946 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09447 | 0 | -0.047928 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.041205 | 0 | -0.047928 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.03819 | 0 | -0.047928 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.019095 | 0 | -0.047928 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09447 | 0 | -0.047928 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.03618 | 0 | -0.047928 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.043215 | 0 | -0.047928 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.02211 | 0 | -0.047928 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.14874 | 0 | -0.047928 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05025 | 0 | -0.047928 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.055275 | 0 | -0.047928 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.001005 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05025 | 0 | -0.047928 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.00099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.03762 | 38 | -0.047913 | -1.8207
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.00099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.019107 | 19.3 | -0.047913 | -0.92472
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.00099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.01485 | 15 | -0.047913 | -0.71869
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.00099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.04653 | 47 | -0.047913 | -2.2519
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.00099 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.047913 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13723 | 144 | -0.047876 | -6.8941
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13723 | 144 | -0.047876 | -6.8941
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16296 | 171 | -0.047876 | -8.1867
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.19727 | 207 | -0.047876 | -9.9103
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.20652 | 216.7 | -0.047876 | -10.3747
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.000953 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.23063 | 242 | -0.047876 | -11.5859
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.000927 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.50614 | 0 | -0.04785 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.000927 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.69525 | 0 | -0.04785 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000899 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13934 | 155 | -0.047822 | -7.4124
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.000899 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15283 | 170 | -0.047822 | -8.1297
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000899 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13934 | 155 | -0.047822 | -7.4124
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.000891 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13053 | 146.5 | -0.047814 | -7.0047
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.000891 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13178 | 147.9 | -0.047814 | -7.0716
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.000891 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.15414 | 173 | -0.047814 | -8.2718
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.000881 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.047804 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.000881 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.047804 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.000881 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.047804 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.00087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03045 | 0 | -0.047793 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.00087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02958 | 0 | -0.047793 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.00087 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03045 | 0 | -0.047793 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.005833 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.34998 | 0 | 0.00021117 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.000848 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.047771 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.000819 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.34726 | 0 | -0.047742 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.000819 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.34808 | 0 | -0.047742 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.005785 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.3471 | 60 | 0.00025917 | 0.01555
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.005785 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.36445 | 63 | 0.00025917 | 0.016327
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.000813 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.047736 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.000804 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.33125 | 412 | -0.047727 | -19.6634
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.000804 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.3216 | 400 | -0.047727 | -19.0907
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.000803 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.16783 | 209 | -0.047726 | -9.9747
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.000803 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.17345 | 216 | -0.047726 | -10.3088
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.036938 | 46 | -0.047726 | -2.1954
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.037741 | 47 | -0.047726 | -2.2431
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.036938 | 46 | -0.047726 | -2.1954
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.000803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.036938 | 46 | -0.047726 | -2.1954
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.000789 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.31244 | 0 | -0.047712 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.000774 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31502 | 407 | -0.047697 | -19.4126
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.000689 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.039962 | 58 | -0.047612 | -2.7615
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.000689 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.061321 | 89 | -0.047612 | -4.2374
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.030316 | 44 | -0.047612 | -2.0949
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.030316 | 44 | -0.047612 | -2.0949
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.029627 | 43 | -0.047612 | -2.0473
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.000689 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.031005 | 45 | -0.047612 | -2.1425
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.071478 | 0 | -0.04755 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.13919 | 0 | -0.04755 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.11537 | 0 | -0.04755 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.14045 | 0 | -0.04755 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.072105 | 0 | -0.04755 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.00052 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00624 | 0 | -0.047443 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.00052 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00572 | 0 | -0.047443 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.00052 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00624 | 0 | -0.047443 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.000164 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.047087 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.005094 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.20376 | 0 | 0.00095017 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.005094 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.20376 | 0 | 0.00095017 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.005079 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00096517 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.005021 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.85357 | 170 | 0.0010232 | 0.17394
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.005021 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.6109 | 520 | 0.0010232 | 0.53205
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.046923 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.046923 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.046923 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.004936 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0011082 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.004914 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.8182 | 370 | 0.0011302 | 0.41816
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.68796 | 0 | 0.0011302 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.69287 | 0 | 0.0011302 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.5184 | 0 | 0.0011302 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.7027 | 0 | 0.0011302 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.70762 | 0 | 0.0011302 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.004914 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.5233 | 0 | 0.0011302 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.7832 | 160 | 0.0011492 | 0.18387
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76362 | 156 | 0.0011492 | 0.17927
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.95942 | 196 | 0.0011492 | 0.22524
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76362 | 156 | 0.0011492 | 0.17927
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76851 | 157 | 0.0011492 | 0.18042
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.004895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.96921 | 198 | 0.0011492 | 0.22753
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.004894 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.36705 | 0 | 0.0011502 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.004894 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.38956 | 0 | 0.0011502 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.004894 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.43263 | 0 | 0.0011502 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.004851 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.7069 | 0 | 0.0011932 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.004851 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.8087 | 0 | 0.0011932 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.004851 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.9196 | 0 | 0.0011932 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.004785 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.0815 | 435 | 0.0012592 | 0.54774
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.004775 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.8861 | 395 | 0.0012692 | 0.50132
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.004775 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.0771 | 435 | 0.0012692 | 0.55209
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.004775 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.37722 | 79 | 0.0012692 | 0.10026
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.004775 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.50615 | 106 | 0.0012692 | 0.13453
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.004775 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.69715 | 146 | 0.0012692 | 0.1853
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.004775 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.3629 | 76 | 0.0012692 | 0.096457
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.004758 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.09516 | 20 | 0.0012862 | 0.025723
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.004758 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.11895 | 25 | 0.0012862 | 0.032154
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.004758 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.19508 | 41 | 0.0012862 | 0.052733
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.004757 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.19028 | 40 | 0.0012872 | 0.051487
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.00023 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00414 | 0 | -0.046693 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.00023 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00414 | 0 | -0.046693 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.000243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0243 | 100 | -0.04668 | -4.668
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.000243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0243 | 100 | -0.04668 | -4.668
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.04668 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.04668 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.04668 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.000243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.04668 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.000244 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.046679 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.004673 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.8131 | 388 | 0.0013712 | 0.53201
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.004673 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.4066 | 515 | 0.0013712 | 0.70615
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.74929 | 161 | 0.0013902 | 0.22382
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76326 | 164 | 0.0013902 | 0.22799
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.76326 | 164 | 0.0013902 | 0.22799
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.9268 | 414 | 0.0013902 | 0.57553
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.75395 | 162 | 0.0013902 | 0.22521
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.74929 | 161 | 0.0013902 | 0.22382
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.7586 | 163 | 0.0013902 | 0.2266
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.004654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.9035 | 409 | 0.0013902 | 0.56858
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.004645 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0013992 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.004645 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0013992 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.32067 | 70 | 0.0014632 | 0.10242
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.31609 | 69 | 0.0014632 | 0.10096
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.31609 | 69 | 0.0014632 | 0.10096
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.004581 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.31151 | 68 | 0.0014632 | 0.099495
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.004569 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.53914 | 118 | 0.0014752 | 0.17407
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.004569 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.52543 | 115 | 0.0014752 | 0.16964
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.004569 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.5404 | 556 | 0.0014752 | 0.82019
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.004395 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.4501 | 0 | 0.0016492 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.004395 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.494 | 0 | 0.0016492 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.004395 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.4281 | 0 | 0.0016492 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.000593 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.016604 | 0 | -0.04633 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.000593 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.017197 | 0 | -0.04633 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.64528 | 0 | 0.0016842 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.5668 | 0 | 0.0016842 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.6322 | 0 | 0.0016842 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.00436 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.7396 | 0 | 0.0016842 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.00433 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0017142 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.004326 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.2163 | 0 | 0.0017182 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.004322 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.7866 | 182 | 0.0017222 | 0.31343
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.004322 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.0918 | 484 | 0.0017222 | 0.83353
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.004316 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.84594 | 196 | 0.0017282 | 0.33872
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.004316 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47908 | 111 | 0.0017282 | 0.19183
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.000715 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.30173 | 422 | -0.046208 | -19.4997
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.004253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.92035 | 216.4 | 0.0017912 | 0.38761
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.004253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.91907 | 216.1 | 0.0017912 | 0.38707
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.004251 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.95222 | 224 | 0.0017932 | 0.40167
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.004241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71249 | 168 | 0.0018032 | 0.30293
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.004241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.38169 | 90 | 0.0018032 | 0.16228
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.000791 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.014238 | 0 | -0.046132 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.000791 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.014238 | 0 | -0.046132 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.000791 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011865 | 0 | -0.046132 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.92019 | 224 | 0.0019362 | 0.4337
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.92841 | 226 | 0.0019362 | 0.43757
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.8709 | 212 | 0.0019362 | 0.41047
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.004108 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.86679 | 211 | 0.0019362 | 0.40853
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.60964 | 151.5 | 0.0020202 | 0.30606
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.61286 | 152.3 | 0.0020202 | 0.30767
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71426 | 177.5 | 0.0020202 | 0.35858
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.00401 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.60431 | 150.7 | 0.0020342 | 0.30655
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.00401 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.60551 | 151 | 0.0020342 | 0.30716
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.00401 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71137 | 177.4 | 0.0020342 | 0.36086
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.00096 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.02304 | 24 | -0.045963 | -1.1031
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.00096 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.02304 | 24 | -0.045963 | -1.1031
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.00096 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.02208 | 23 | -0.045963 | -1.0571
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.003951 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.4299 | 0 | 0.0020932 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.003951 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.3192 | 0 | 0.0020932 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.003864 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.05796 | 0 | 0.0021802 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.003864 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.05796 | 0 | 0.0021802 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.003729 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0023152 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001321 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011096 | 8.4 | -0.045602 | -0.38305
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.003619 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.9929 | 0 | 0.0024252 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.003619 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.964 | 0 | 0.0024252 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.001356 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018577 | 0 | -0.045567 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.9865 | 0 | 0.0025512 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.9865 | 0 | 0.0025512 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.53198 | 0 | 0.0025512 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.003493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.53443 | 0 | 0.0025512 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.003431 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.51465 | 150 | 0.0026132 | 0.39197
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.003431 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.27448 | 80 | 0.0026132 | 0.20905
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.003354 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.85527 | 255 | 0.0026902 | 0.68599
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.003354 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.49975 | 149 | 0.0026902 | 0.40083
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.003354 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.51316 | 153 | 0.0026902 | 0.4116
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.003263 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0027812 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.003263 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.568 | 787 | 0.0027812 | 2.1888
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028612 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028612 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.003183 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.054111 | 17 | 0.0028612 | 0.04864
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028612 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.003183 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028612 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.003181 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.10179 | 0 | 0.0028632 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.00318 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.4723 | 0 | 0.0028642 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.003176 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.15245 | 48 | 0.0028682 | 0.13767
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.003176 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.1461 | 46 | 0.0028682 | 0.13194
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.003176 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.33348 | 105 | 0.0028682 | 0.30116
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.003161 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028832 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.003161 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028832 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.47555 | 0 | 0.0029602 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.4811 | 0 | 0.0029602 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.4811 | 0 | 0.0029602 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.003084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.1719 | 0 | 0.0029602 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.002828 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.61452 | 217.3 | 0.0032162 | 0.69887
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.002828 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.57974 | 205 | 0.0032162 | 0.65931
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.002828 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.77035 | 272.4 | 0.0032162 | 0.87608
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.002576 | north | 3 | N | N | Nnorth | Nnorth | 1 | -2.9804 | 0 | 0.0034682 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.002576 | north | 3 | N | N | Nnorth | Nnorth | 1 | -2.983 | 0 | 0.0034682 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.000627 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.0627 | 0 | 0.0054172 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0060442 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0060442 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.008222 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.038701 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.009105 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.05463 | 0 | -0.037818 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.0129 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.4257 | 0 | -0.034023 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.0129 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3225 | 0 | -0.034023 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.0129 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034023 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.013792 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.019836 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.026215 | west | 4 | Y | N | Ywest | Nwest | 1 | 17.0319 | 0 | 0.032259 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.03542 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.313 | 0 | 0.041464 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.040116 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.04616 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.4814 | 0 | 0.046625 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1335 | 0 | 0.046625 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.1047 | 0 | 0.046625 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.040581 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9945 | 0 | 0.046625 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.045391 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8128 | 0 | 0.051435 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.045458 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4775 | 0 | 0.051502 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1413 | 0 | 0.051744 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8322 | 0 | 0.051744 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5002 | 0 | 0.051744 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.0457 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.8026 | 0 | 0.051744 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.045726 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6581 | 0 | 0.05177 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.046108 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9162 | 0 | 0.052152 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.04672 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.008 | 0 | 0.052764 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.04672 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.008 | 0 | 0.052764 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.046747 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7398 | 0 | 0.052791 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046754 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7403 | 0 | 0.052798 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.04679 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5093 | 0 | 0.052834 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.04679 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7432 | 0 | 0.052834 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.04679 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8716 | 0 | 0.052834 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.04698 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7584 | 0 | 0.053024 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.04698 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7584 | 0 | 0.053024 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.047831 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.22959 | 0 | 0.053875 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.0482 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.025 | 0 | 0.054244 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.0482 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.025 | 0 | 0.054244 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.256 | 0 | 0.054417 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6421 | 0 | 0.054417 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6746 | 0 | 0.054417 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.048373 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8967 | 0 | 0.054417 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.04863 | west | 8 | N | N | Nwest | Nwest | 1 | 3.4041 | 0 | 0.054674 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.04863 | west | 8 | N | N | Nwest | Nwest | 1 | 3.5694 | 0 | 0.054674 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.04863 | west | 8 | N | N | Nwest | Nwest | 1 | 3.4236 | 0 | 0.054674 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.4311 | 70 | 0.05506 | 3.8542
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.4311 | 70 | 0.05506 | 3.8542
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5487 | 92.8 | 0.05506 | 5.1096
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.9213 | 80 | 0.05506 | 4.4048
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.9213 | 80 | 0.05506 | 4.4048
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.049016 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.6368 | 115 | 0.05506 | 6.3319
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.2066 | 208.2 | 0.055067 | 11.465
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.9662 | 142.1 | 0.055067 | 7.825
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.4906 | 132.4 | 0.055067 | 7.2909
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.6671 | 136 | 0.055067 | 7.4891
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.2064 | 147 | 0.055067 | 8.0949
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.049023 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.2948 | 210 | 0.055067 | 11.5641
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.2862 | 66 | 0.055835 | 3.6851
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.2364 | 65 | 0.055835 | 3.6293
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.336 | 67 | 0.055835 | 3.741
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.336 | 67 | 0.055835 | 3.741
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.049791 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.336 | 67 | 0.055835 | 3.741
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.049791 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.055835 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.049791 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.055835 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.05035 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7623 | 0 | 0.056394 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.05035 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5105 | 0 | 0.056394 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.051151 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6701 | 0 | 0.057195 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9214 | 0 | 0.057282 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5081 | 0 | 0.057282 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9171 | 0 | 0.057282 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0973 | 0 | 0.057282 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.38 | 0 | 0.057282 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.051238 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1247 | 0 | 0.057282 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.051616 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6908 | 0 | 0.05766 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.053266 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3532 | 0 | 0.05931 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.0533 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0914 | 0 | 0.059344 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.053715 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.5058 | 0 | 0.059759 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.053915 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4698 | 0 | 0.059959 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.053915 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5622 | 0 | 0.059959 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.053915 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1763 | 0 | 0.059959 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.055664 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.36738 | 0 | 0.061708 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.055664 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9093 | 0 | 0.061708 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7132 | 66 | 0.062305 | 4.1121
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.882 | 69 | 0.062305 | 4.2991
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.882 | 69 | 0.062305 | 4.2991
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7695 | 67 | 0.062305 | 4.1744
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7695 | 67 | 0.062305 | 4.1744
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.056261 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.657 | 65 | 0.062305 | 4.0498
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.057371 | west | 8 | N | N | Nwest | Nwest | 1 | 1.4802 | 0 | 0.063415 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.059199 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1039 | 0 | 0.065243 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.060516 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2619 | 0 | 0.06656 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.064839 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.5888 | 0 | 0.070883 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.065402 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7724 | 0 | 0.071446 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.065402 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7724 | 0 | 0.071446 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.068767 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3323 | 0 | 0.074811 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.071768 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7652 | 0 | 0.077812 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.071768 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2486 | 0 | 0.077812 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.072361 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.2029 | 0 | 0.078405 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.072361 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6833 | 0 | 0.078405 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.07283 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2102 | 0 | 0.078874 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.07283 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4426 | 0 | 0.078874 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.07283 | west | 7 | N | N | Nwest | Nwest | 1 | 1.8208 | 0 | 0.078874 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.07283 | west | 7 | N | N | Nwest | Nwest | 1 | 3.3283 | 0 | 0.078874 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.07283 | west | 7 | N | N | Nwest | Nwest | 1 | 3.3283 | 0 | 0.078874 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.0823 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9132 | 0 | 0.088344 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12384 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5755 | 0 | 0.12988 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.13825 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2948 | 0 | 0.14429 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating
| Temp | murray - graham
| 20 | 233
| 25 | 233
| 30 | 233
| 35 | 233
| 40 | 233
| 45 | 233
| 50 | 233
| 55 | 233
| 60 | 233
| 65 | 227
| 70 | 222
| 75 | 217
| 80 | 212
| 85 | 207
| 90 | 202
| 95 | 196
| 100 | 191
| 105 | 185
| 110 | 179
| 115 | 173
| total | 4308
| avg | 215.4