ERCOT Operations Report

August 2009 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 8/15/2009 21:18 | 59.87 | 60 | Multiple Unit trips with 500 MW & with 175 MW |
| 8/27/2009 16:22 | 59.88 | 96 | Unit trip with 725 MW |
| 8/27/2009 17:05 | 59.88 | 61 | Unit trip with 540 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 8/7/09 14:13:59 | 8/7/09 14:21:03 | 0:07:04 | 337.94 | Unit Trip |
| 8/15/09 21:18:55 | 8/15/09 21:35:39 | 0:16:44 | 712.81 |  |
| 8/15/09 22:00:41 | 8/15/09 22:16:33 | 0:15:52 | 332.6 | Slow Unit Response. SCE change -1050 MW in 4m. |
| 8/23/09 19:05:50 | 8/23/09 19:24:02 | 0:18:12 | 348.49 | Unit Trip |
| 8/25/09 15:19:18 | 8/25/09 15:26:18 | 0:07:00 | 337.94 | Unit Trip |
| 8/27/09 16:22:12 | 8/27/09 16:49:58 | 0:27:46 | 644.17 |  |
| 8/27/09 17:05:18 | 8/27/09 17:21:30 | 0:16:12 | 691.68 |  |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | RPRS S1+S2 | RMR | Total |
| --- | --- | --- | --- | --- | --- | --- |
| DFW | 24 | 16 | 65 | 81 | 0 | 105 |
| North | 8 | 34 | 47 | 81 | 0 | 89 |
| Western | 4 | 5 | 69 | 74 | 10 | 88 |
| Houston | 4 | 5 | 66 | 71 | 0 | 75 |
| Austin | 0 | 14 | 14 | 28 | 0 | 28 |
| San Antonio | 0 | 5 | 5 | 10 | 0 | 10 |
| E RIO | 1 | 6 | 0 | 6 | 0 | 7 |
| South | 0 | 0 | 1 | 1 | 0 | 1 |
| Bryan Area | 0 | 0 | 1 | 1 | 0 | 1 |
| Northeast | 0 | 0 | 1 | 1 | 0 | 1 |
| Laredo | 0 | 0 | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 0 | 0 | 0 | 0 | 0 |
| Total | 41 | 85 | 269 | 354 | 10 | 405 |

| Historical Totals | Aug-09 | Aug-08 | Jul-09 |
| --- | --- | --- | --- |
| Austin | 14 | 33 | 5 |
| Bryan Area | 0 | 0 | 0 |
| Corpus | 0 | 1 | 0 |
| DFW | 40 | 12 | 28 |
| E RIO | 7 | 0 | 9 |
| Houston | 9 | 0 | 37 |
| Laredo | 0 | 12 | 0 |
| North | 42 | 57 | 46 |
| Northeast | 0 | 0 | 2 |
| San Antonio | 5 | 0 | 14 |
| South | 0 | 2 | 13 |
| W RIO | 0 | 0 | 0 |
| Western | 19 | 9 | 19 |
| Total | 136 | 126 | 173 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| San Miguel - Dilley Switch 138KV | Derby - Pearsall 69KV | 31 |
| Austrop - Daffin & Decker 138KV | Austrop - Decker 138KV | 25 |
| Temple Pecan Creek - Tradinghouse and Lake Creek - Temple Switch 345KV | San Angelo Power Station - Shrew 138KV | 19 |
| Aspermont - Spur 138KV | Jayton - Spur 69KV | 14 |
| Graham - Long Creek 345KV | San Angelo Power Station - Shrew 138KV | 7 |
| Big Brown SES - Jewett 345KV | Big Brown SES - Jewett 345KV | 4 |
| Morgan Creek SES - Quail Switch and Longshore Switching Station 345KV | Stanton East Switching Station - Big Spring West138KV | 4 |
| Enterprise - Trinidad and Martin Lake - Stryker Creek 345KV | Nacogdoches Southeast 345/138KV | 4 |
| North Denton - West Denton 138KV | West Denton - Teasley 138KV | 4 |
| South Abilene - South West Eskota 138KV | Merkel - Trent 69KV | 4 |
| North Denton 138/69KV Auto #1 | North Denton 138/69KV Auto #2 | 3 |
| San Miguel - San Miguel Switchyard 138KV | Dilley Switch 138/68KV autotransformer A1 | 3 |
| Sandow Switch - Temple Switch 345KV | Hearne AT1 transformer 138/69KV | 3 |
| Morgan Creek SES - Quail Switch and Longshore Switching Station 345KV | Midland East - Stanton East Switching Station 138KV | 2 |
| Aspermont - Spur 138KV | Spur 138/69KV AT | 2 |
| Base Case | Cauthorn - Sonora 138KV | 2 |
| Lamesa 138/69KV Auto | Ackerly Vealmoor Switch - Ackerly 69KV | 2 |
| San Miguel Switchyard 345/138KV autotransformer A | San Miguel Switchyard 345/138KV autotransformer B | 2 |
| STP - Blessing 345KV | Columbus - Stafford Hill 69KV | 2 |
| Jack County - Reno 138KV | Decatur - Decatur Tap 138KV | 1 |
| Trinidad SES - Stryker SES and Mt. Enterprise 345 KV | Stryker Creek SES - Stryker Cherokee POI | 1 |
| Aransas Pass - Ingleside 138KV | Gregory - Rincon 69KV | 1 |
| Dilley Switch - North Laredo 138KV | Asherton - North Laredo 138KV | 1 |
| Garfield - Onion Creek and Hicross 138KV | Austrop 345/138KV AT1 | 1 |
| Hicross - Pilot Knob & Garfield 138KV | Grove - Advance 138KV | 1 |
| Jack County - Reno 138KV | Decatur - Rhome 138KV | 1 |
| Olinger - Ben Davis & Elm grove 138KV | Olinger - Firewheel 138KV | 1 |
| Roanoke Switch - West Denton and Lewisville Switch 345KV | West Denton - Teasley 138KV | 1 |
| Teasley - West Denton 138KV | Airport - West Denton 138 KV | 1 |
| Zorn - McCarty Lane 138KV | Henne - Comal 138KV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West-North | 10 |
| North-Houston | 4 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 08/04/2009 | Transmission and Security Desk V4 R4 | 432 |
| 08/04/2009 | Frequency Control Desk V4 R4 | 431 |
| 08/04/2009 | Shift Supervisor Desk V4 R4 | 430 |
| 08/04/2009 | Operating Period Desk V3 R4 | 429 |
| 08/04/2009 | Day-Ahead V4 R4 | 428 |

## Blackout/Load Shed Incidences

None

EEA

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

08/27  14:58	Held Real-time Balancing deployments for IE 15:15, resumed with IE 15:45 deployments.

08/26  22:30	Held IE 22:30 Real-time Balancing Market deployments for IE 22:45 which failed to execute, resumed with IE 23:00.Held Real-time Balancing deployments for interval ending 22:, resumed with interval ending 15:45 deployments.

Communication

None

## ERCOT peak (Unofficial)

08/20 	   17:00 62,045 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2006 | 2007 | 2008 | 2009 |
| January | 4.79 | 4.55 | 3.30 | 4.11 |
| February | 4.81 | 3.75 | 3.59 | 3.49 |
| March | 4.95 | 2.70 | 3.29 | 3.24 |
| April | 5.59 | 3.00 | 2.45 | 2.66 |
| May | 3.59 | 3.22 | 3.01 | 2.90 |
| June | 2.65 | 4.46 | 2.81 | 2.89 |
| July | 2.62 | 4.29 | 2.55 | 2.83 |
| August | 2.09 | 3.11 | 3.66 | 3.07 |
| September | 4.03 | 3.78 | 4.99 | NA |
| October | 3.63 | 3.08 | 2.79 | NA |
| November | 3.28 | 2.95 | 2.60 | NA |
| December | 3.44 | 3.74 | 4.54 | NA |
| Annual Average | 3.79 | 3.55 | 3.29 | 3.14 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 8/4/09 | 2:00 | 18:00 | OCN issued for projected reserve capacity shortage for HE 1700 - 1800. |
| 8/5/09 | 2:00 | 11:00 | OCN issued for projected reserve capacity shortage for HE 1600 - 1900. |
| 8/5/09 | 11:00 | 18:15 | Watch issued for a projected capacity reserve shortage for HE 1600 - 1900. |
| 8/5/09 | 13:00 | 18:30 | OCN issued for projected Balancing Energy Service Bid shortage for HE 1400 - 2000. |
| 8/5/09 | 13:30 | 18:15 | Advisory issued for ARRS below 3000 MW. |
| 8/6/09 | 14:47 | 17:30 | OCN issued for projected Balancing Energy Service Bid shortage for HE 1400 - 2000. |
| 8/6/09 | 15:35 | 17:30 | Advisory issued for ARRS below 3000 MW. |
| 8/10/09 | 12:45 | 15:00 | OCN issued for projected reserve capacity shortage for HE 1600 & 1700. |
| 8/14/09 | 3:50 | 15:00 | OCN issued for the projected reserve capacity shortage for HE 1400 - 1700. |
| 8/15/09 | 10:00 | 10:30 | OCN issued for the projected reserve capacity shortage for HE 1400 - 1700. |
| 8/15/09 | 10:30 | 15:00 | Watch issued for the projected reserve capacity shortage for HE 1400 - 1700. |
| 8/15/09 | 15:10 | 18:37 | Advisory issued for ARRS below 3000 MW. |
| 8/17/09 | 8:30 | 11:30 | Watch issued due to projected reserve capacity shortage for hours 1500 to 1700. |
| 8/17/09 | 4:06 | 8:30 | OCN issued due to projected reserve capacity shortage for HE 1500 - 1700. |
| 8/19/09 | 10:00 | 15:15 | Watch issued for projected reserve capacity shortage for HE 1600 - 1800. |
| 8/19/09 | 4:00 | 10:00 | OCN issued for projected reserve capacity shortage for HE 1600 - 1800. |
| 8/19/09 | 16:35 | 18:00 | Advisory issued for ARRS below 3000 MW. |
| 8/20/09 | 14:37 | 17:54 | Advisory issued for ARRS below 3000 MW. |
| 8/21/09 | 16:15 | 18:15 | Advisory issued for ARRS below 3000 MW. |
| 8/22/09 | 9:05 | 18:00 | OCN issued due to projected reserve capacity shortage for hours 1600 - 1800. |
| 8/23/09 | 15:30 | 18:45 | Advisory issued for ARRS below 3000 MW. |
| 8/25/09 | 15:20 | 18:13 | Advisory issued for ARRS below 3000 MW. |
| 8/23/09 | 13:54 | 19:00 | OCN issued due to projected reserve capacity shortage for hours 1600 - 1900. |
| 8/27/09 | 17:10 | 18:00 | Advisory issued for ARRS below 3000 MW. |

Transmission Watch

08/04  14:00	ERCOT issued a Transmission Watch issued due to the forced outage and the post contingency loss of Dilley Switch - San Miguel 138KV overloads Derby - Pearsall 69KV.  ERCOT received emergency energy from CFE across the Laredo VFT.

08/05  13:10	ERCOT issued a Transmission Watch issued due to the forced outage and the post contingency loss of Dilley Switch - San Miguel 138KV overloads Derby - Pearsall 69KV.  ERCOT received emergency energy from CFE across the Laredo VFT.

08/13  11:40	ERCOT issued a Transmission Watch issued due to the forced outage and the post contingency loss of Dilley Switch - North Laredo 138KV overloads North Laredo - Asherton 138KV.  ERCOT received emergency energy from CFE across the Laredo VFT and Eagle Pass DC Tie.

08/13  16:00	ERCOT issued a Transmission Watch issued due to the forced outage and the post contingency loss of Dilley Switch - North Laredo 138KV overloads North Laredo - Asherton 138KV.  ERCOT received emergency energy from CFE across the Laredo VFT.

08/20  07:45	ERCOT issued a Transmission Watch issued for the Willow Valley Switch - Lamesa area due to a planned outage.  A block load transfer of up to 2 MW of ERCOT load to Southwest Power Pool (SPP) was performed.

08/20  16:10	ERCOT issued a Transmission Watch due to a planned transmission outage.  The loss of the San Angelo College Hills 138/69KV autotransformer overloads San Angelo Concho 138/69KV autotransformer.

08/24  14:24	ERCOT issued a Transmission Watch issued for the post contingency loss of Hicross - Pilot Knob & Garfield 138KV overloads Grove - Advance 138KV and Advance - Burleson AEN 138KV caused by forced outage in area.

08/24  15:00	ERCOT issued a Transmission Watch issued for the post contingency loss of Austrop - Daffin & Decker 138KV overloads Decker - Sprinkle 138KV caused by forced outage in area.

Emergency Notice

08/31  13:30	Market Emergency Notice issued due to the procurement of the Ancillary Service Market for 9/1/09 did not meet the time requirement.

Texas RE Event Analysis

08/06   02:37   ERCOT EMS System down due to network traffic error.

08/07   03:05   ERCOT EMS System down due to network traffic error.

08/09   09:08   Loss of three 138 kV lines

08/11   16:17   Stanton Wind Farm SPS activated.

08/31  13:30	Market Emergency Notice issued for Ancillary Services Market delay.