## test results
CRE test for: |  | 46290 ROTHWOOD74 - 40900 KING___345 | [5 empty] | FAIL
Line Rating: |  | 1710
Direction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 46290 ROTHWOOD74 - 40900 KING___345
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.073604
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.019236
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.062809
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.10868
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 46290 ROTHWOOD74 - 40900 KING___345
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.069196
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.020661
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.062956
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.11369
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 46290 ROTHWOOD74 - 40900 KING___345
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.094265
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.010648
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.18729
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.082192
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.089443
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.1765
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.18729 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.18729 | 0.094265
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.20789
[6 empty] | Concentration |  | 1.11 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.21047
[6 empty] | Concentration |  | 1.1237 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 32.3211
| Percent of line rating => | [6 empty] | 1.89% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.8365
[7 empty] | B1(N-S) | 0.055239 | 0.22835 | 0.17311 | 0.055239
[7 empty] | B2 (N-W) | 0.0065784 | 0.026133 | 0.019554 | 0.0065784
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.048347 | -0.19929 | -0.15094 | -0.048347
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.045722 | 0.11854 | 0.16426 | -0.045722
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0066645 | 0.31747 | 0.32413 | -0.0066645
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 16.06%
Deployment Error Percent | [6 empty] | B2 | 1.913%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -14.06%
[7 empty] | B5 | -13.29%
[7 empty] | B6 | -1.938%
[7 empty] | Max Abs Error | 16.06% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | W-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:46290 ROTHWOOD74 - 40900 KING___345 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:46290 ROTHWOOD74 - 40900 KING___345 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.054461 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 13.8876
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.054461 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 8.1147
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.057669 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.86503
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.057669 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.86503
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.054461 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 8.3325
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.055436 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 8.3154
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.055436 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 4.4349
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.06607 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 4.8231
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.06607 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 7.8623
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.06607 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 13.5443
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.06607 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 6.7391
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.06607 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 6.3427
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.066729 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.80075
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.066729 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.80075
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.06651 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 11.1737
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.06651 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 5.9859
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.067305 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.2115
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.067305 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.2115
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.067305 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 2.5576
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.068072 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 19.6047
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.068072 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 10.0066
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.068072 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 10.0066
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.068988 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 7.7611
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.071497 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 2.8599
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.071494 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 5.648
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.071494 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 7.5784
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.071494 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 10.4381
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.071494 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 5.4335
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.069682 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 4.1809
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.069682 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 4.39
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.071582 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 1.4316
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.071582 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 1.7895
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.071582 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 2.9349
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.10486 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 48.5493
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 4.1039
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 4.0417
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 4.1661
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 4.1661
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 4.1661
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.06218 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 7.0885
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.06218 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 32.0227
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 4.1862
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 4.3765
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 4.3765
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 4.2496
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 4.2496
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 4.1228
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.063252 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 4.4276
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.063252 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 4.6427
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.063252 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 4.4529
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 9.5028
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 13.9374
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.063486 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 6.2851
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.063486 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 3.8726
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.063476 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 8.9501
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.063486 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 1.5872
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.063486 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 2.9013
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.063486 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 2.9013
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.063476 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 7.6171
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.062949 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 1.6241
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.062836 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 6.315
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.063142 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 7.577
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.062825 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 3.6439
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.06291 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 13.4753
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.063613 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 9.5419
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.062513 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.41259
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.062513 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 2.1442
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.063613 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 6.4249
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.063156 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 7.5787
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.066683 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 24.406
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.066309 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 16.0468
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.065061 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 26.0244
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.065064 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 15.3551
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.065452 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 10.7996
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.067686 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 13.8079
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.067686 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 13.6049
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.067686 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 16.38
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.3351
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.3351
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.3351
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 1.1348
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.066644 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 7.9973
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.064014 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 3.8408
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.071364 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 5.3523
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.071364 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 5.6806
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.071364 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 6.3086
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 11.4118
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 11.1265
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 13.9795
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 11.1265
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 11.1979
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 14.1222
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.07114 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 12.0938
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.07114 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 36.9928
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.071268 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 26.3692
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.071422 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 39.8535
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.071422 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 41.3533
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.071422 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 57.709
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.068747 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 7.6997
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.068747 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 6.8747
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.068747 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 25.9864
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.067658 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 14.7021
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.067658 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 13.8699
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.067658 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 18.43
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.067806 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 52.2106
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 4.6851
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 4.6182
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 4.6182
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 4.5512
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.067492 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 78.0882
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.067492 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 78.1557
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 15.2602
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 15.3965
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.0688 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 14.8883
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.0688 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 14.8677
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 14.4427
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 14.3746
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.068902 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 27.2163
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.069043 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 30.0337
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.068902 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 29.9724
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.070731 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 9.7609
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.070901 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 8.3663
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.070901 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 8.1536
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.070901 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 39.421
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.071665 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 27.806
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.071665 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 36.9075
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.074082 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 58.1544
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.074082 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 58.8952
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.074082 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 57.784
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.074693 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 13.5941
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.074693 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 36.1514
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.072199 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 16.1726
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.074654 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 3.7327
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.074624 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 3.1342
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.078422 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 48.2295
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.078422 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 46.0337
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.05334 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 28.6436
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.05334 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 41.9786
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.052588 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 3.9441
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.052588 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 11.6745
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.018966 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 10.7917
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022567 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -4.7165
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022567 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -4.8745
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.022486 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -9.1518
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0381
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -1.0606
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0381
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0381
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.022523 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -9.5498
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.022523 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -9.5723
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022513 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -1.3058
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022513 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -2.0037
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.99057
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.99057
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.96806
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.0131
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.022488 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -9.2651
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.022488 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -8.9952
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.023846 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -13.0199
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.023846 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -17.8845
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.022611 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -1.3793
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.022611 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -2.148
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.022611 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -3.4143
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.023266 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.6062
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.023266 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -3.9552
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.023266 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.6062
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.039484 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.86865
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.039484 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.43432
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.039484 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.43432
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -1.8613
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -1.4554
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -1.7949
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -1.873
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.033909 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.40691
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.033909 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.373
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.023671 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.5681
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.023671 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.5681
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.023671 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.54443
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.027673 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -10.9585
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.069926 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -93.2114
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.069926 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -92.8617
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.037246 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -1.4153
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.037246 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.71885
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.037246 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.55869
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.037246 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -1.7506
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.058695 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 4.4021
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.063931 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 9.5897
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.062291 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 10.5583
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.045265 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 6.7897
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.063451 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 3.9974
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.065785 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 42.7405
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.071038 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 2.8415
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.071038 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 2.8415
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.003066 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 1.2939
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.002359 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -0.31139
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.002359 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -0.31611
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.002359 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -0.76196
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.00475 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -0.7505
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.00475 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -0.76
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.00475 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -0.83125
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.012231 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -7.1429
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.012231 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -7.2774
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.012363 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -5.3532
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -3.5658
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -3.5833
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -3.577
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -3.6104
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.000275 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.0022
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.000275 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.0022
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.007815 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.14067
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.007815 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.14067
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.007815 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.11722
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.006937 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.095037
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.002518 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.045324
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.002518 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.045324
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001274 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.04459
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001274 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.043316
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001274 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.04459
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.003305 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.09254
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.003305 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.095845
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.062211 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 2.1774
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.062211 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.8663
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.3619
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.3619
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.3619
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.3619
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.01243 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.07458
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.017816 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.042758
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.017816 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.042758
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.017816 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.049885
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.019262 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.077048
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.018327 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.043985
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.018327 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.043985
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.2046
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -3.0084
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -3.052
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.2046
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -3.9676
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -4.3164
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004354 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -0.66399
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004354 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -0.65092
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004354 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -1.0127
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -2.6902
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -2.747
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -2.8607
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -5.494
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.000601 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.019833
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.000601 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.015025
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.033909 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.40691
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.038924 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -2.8415
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -3.4709
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -3.5588
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -1.1563
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.28908
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -3.4709
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -3.5149
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -3.4446
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.0984
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -2.0211
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.034742 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -21.8527
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.038056 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -5.4801
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.038056 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -7.1545
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.023191 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.27829
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.008171 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.049026
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.038246 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -12.8507
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.038063 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -12.713
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.038063 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -12.9414
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.037895 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -1.44
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.037996 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.9499
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.037996 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.9499
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.037938 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -1.4416
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.037533 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -1.0885
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.038236 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -5.6704
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.038236 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -5.6819
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.038236 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -5.8501
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -6.1783
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -5.9828
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -3.9103
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -5.6699
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -5.7481
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -4.9661
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.036509 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -5.3486
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.036509 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -5.3997
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.036509 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -6.3161
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.036937 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -7.646
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.036937 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -8.0042
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.036937 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -8.9388
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.03694 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -5.3194
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.03694 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -5.3194
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.03694 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -6.3167
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.000294 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 0.09114
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.000294 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 0.12142
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.04746
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.04972
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.04972
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.05311
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.041209
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.038686
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.038686
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.039527
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000841 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.12951
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000841 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.12447
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.040368
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.040368
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 4.3966
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 4.3966
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 5.8286
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 5.0246
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 5.0246
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 7.2229
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 13.0754
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 8.9242
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 8.315
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 8.5411
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 9.2319
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 13.1884
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 13.3578
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 8.085
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 15.9143
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 12.5909
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 12.6704
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 7.7226
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.062317 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 9.2852
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.063246 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 11.3843
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.063246 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 11.3843
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.063214 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 14.2232
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.063682 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 7.9603
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.063682 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 7.9603
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 9.9775
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 10.0488
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 22.0218
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 10.1913
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 10.2626
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 22.0931
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.070349 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 13.7884
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.070349 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 7.8087
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.070879 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 11.6081
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 11.8244
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 11.8244
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 29.8494
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 11.6802
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 11.6081
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 11.7523
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 29.4889
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.071533 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.071533 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 11.0069
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 9.6682
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 10.7838
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 29.674
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.077738 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 11.7151
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.077738 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 11.7384
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.077738 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 13.7907
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.077609 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 11.7578
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.077609 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 11.8199
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.077609 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 13.7756
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.018966 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 11.0192
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 78.324
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 78.324
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.097791 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 3.1293
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.095389 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 4.5787
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.095389 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 4.3879
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 1.1709
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 4.9765
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.097579 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 1.6588
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 2.1467
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 2.4395
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.095389 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 10.0158
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.063568 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 5.3397
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.058632 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 4.6906
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.0586 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 8.79
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.0586 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 8.79
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -7.8164
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -7.3637
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -5.8513
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -16.9134
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -16.9466
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -16.8141
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -10.5985
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -26.9378
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -4.416
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -11.0688
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -10.2522
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -11.3337
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -11.2564
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.11036 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -3.5315
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.11036 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -3.3107
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -9.2676
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -9.2676
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -9.9355
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -9.1424
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 13.9517
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 14.0159
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.12763 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -17.3573
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.10067 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -3.3222
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -5.5582
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -5.5582
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -5.0288
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -5.0288
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.084304 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -5.9856
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.084304 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.84304
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.090864 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -14.8108
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.090864 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -14.8108
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.090864 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -22.2617
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -7.9567
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -7.3447
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -7.9567
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -7.9567
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.12812 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -19.0903
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.12812 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -8.3408
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -10.9992
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -10.5882
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -10.5157
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -6.5874
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -1.4746
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.14147 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -105.1137
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.138 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -101.4263
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.14647 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -25.1934
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.14647 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -25.1934
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.14647 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -25.1934
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -31.7785
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.12872 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -22.2689
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.12872 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -17.3775
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -24.6565
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -24.4445
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -24.0659
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -40.7711
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -8.2076
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -8.105
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -10.593
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -9.4388
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -21.6452
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -20.8362
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -20.8892
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -20.8229
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -35.6775
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.13438 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.67192
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.13438 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -2.8221
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 13.1582
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 13.3118
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 13.3118
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 32.4262
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.13647 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -54.3143
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -4.9773
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -4.9773
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -4.9773
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -5.9511
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -5.9511
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -5.8429
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.086419 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 71.4685
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.086419 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 70.7772
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.098451 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -4.5386
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -4.3786
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -4.3786
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -6.0494
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -4.2634
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -4.2634
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -5.8765
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.12844 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -23.1187
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.12844 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -20.3701
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.12844 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -20.1646
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.12672 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -4.4352
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.11795 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -54.139
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -8.4824
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -8.6129
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -9.1349
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -8.2214
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -8.0909
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -13.5718
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -7.6994
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -28.6558
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -28.2884
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -28.2884
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18369 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -29.7579
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.13155 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -20.653
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -9.221
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -9.3509
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -5.065
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -3.8962
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.12491 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -9.7427
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.12491 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -9.9925
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.12821 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -2.077
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.12794 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -21.1106
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.12787 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -21.6094
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.12816 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -27.2979
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.12831 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -29.2556
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.12782 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -1.5338
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.12782 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -2.3007
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.10481 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -5.2406
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -9.2852
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -9.2852
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -4.8212
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -4.7319
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -4.8212
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -5.089
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -4.8212
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -4.8212
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -5.1783
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -5.1783
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.089959 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -1.0795
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -6.234
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -6.5679
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -6.234
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -6.234
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -6.5679
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -6.234
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.065836 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -4.3452
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.088868 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -14.3077
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.088868 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -14.7521
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.088868 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -22.0393
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.088868 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -48.5219
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.088868 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -57.1421
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.090811 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -59.118
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.090811 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -51.2174
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.090811 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -54.4866
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.088868 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -1.1553
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.13777 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -1.6532
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -4.6087
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -4.7036
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -4.4325
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -6.2217
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -2.3992
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -2.7652
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -2.6974
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -4.7443
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -2.4399
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -11.576
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -20.0614
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -5.2006
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -5.9891
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -3.7746
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -8.472
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -7.2138
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -7.3815
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -4.194
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -1.5099
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -7.8848
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -5.8717
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -5.2845
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -6.0394
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -5.4355
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -8.472
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -8.1365
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -8.6397
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -6.375
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -6.7105
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -6.7105
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -14.3437
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.19155
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.057112 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 4.3691
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.058695 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 4.6956
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.058695 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 2.3478
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.058951 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 4.7161
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.05864 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 4.6912
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.057325 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 4.586
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.056894 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 4.7791
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.058951 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 4.7161
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -1.9746
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.063213 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 7.5856
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.063213 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 14.7286
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.063213 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 10.7589
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -3.8453
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -3.1871
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -3.8799
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -1.9919
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -1.7321
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.064395 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 3.8637
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.015554 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.050032 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.059895 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.2875
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 2.3949
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 6.8653
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 8.6215
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 7.5997
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 6.7056
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 5.141
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.062829 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 9.4244
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 7.0536
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 9.3735
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 11.662
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 13.4489
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.037245 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.009932 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.02767 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -1.2302
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -1.9156
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -3.2513
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -3.512
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -1.5318
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -1.4198
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.70988
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -3.512
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -1.345
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -1.6066
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.82196
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.6106
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.61945
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.28908
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.61945
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.6106
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.6106
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -5.5296
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -1.8681
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -2.0549
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -1.8681
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.039103 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.46924
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.040465 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.60698
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.040465 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.9307
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.043316 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -2.0792
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.041044 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.32835
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.03822 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -6.8796
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.038246 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -6.8843
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.038063 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -6.8513
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.038063 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -6.8513
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.027667 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -2.7667
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.027667 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -2.7667
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.96942
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.96942
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.96942
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.62043
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.96942
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.96942
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.96942
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.58166
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.027667 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.027667 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -13.8335
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.027667 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -13.8335
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.027667 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.032998 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.000601 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.031422 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.035259 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:46290 ROTHWOOD74 - 40900 KING___345 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | [7 empty] | 32.3211
Number of Bus | Name of Bus | ID | Max MW | L:46290 ROTHWOOD74 - 40900 KING___345 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.054461 | north | Y | -0.019143 | 0.073697 | -0.0083476 | 0.16314 | 0.0083476 | west | Y | 0.019143 | 2.7527
239 | BOSQUESW | 1 | 149 | 0.054461 | north | Y | -0.019143 | 0.073697 | -0.0083476 | 0.16314 | 0.0083476 | west | Y | 0.019143 | 1.6084
244 | WHITNYDM | 1 | 15 | 0.057669 | north | N | -0.015935 | 0.076905 | -0.0051396 | 0.16635 | 0.0051396 | west | Y | 0.015935 | 0
245 | WHITNYDM | 2 | 15 | 0.057669 | north | N | -0.015935 | 0.076905 | -0.0051396 | 0.16635 | 0.0051396 | west | Y | 0.015935 | 0
247 | BOSQUESW | 2 | 153 | 0.054461 | north | Y | -0.019143 | 0.073697 | -0.0083476 | 0.16314 | 0.0083476 | west | Y | 0.019143 | 1.6516
251 | BOSQUESW | 2 | 150 | 0.055436 | north | Y | -0.018168 | 0.074672 | -0.0073726 | 0.16412 | 0.0073726 | west | Y | 0.018168 | 1.6192
253 | BOSQUESW | 2 | 80 | 0.055436 | north | Y | -0.018168 | 0.074672 | -0.0073726 | 0.16412 | 0.0073726 | west | Y | 0.018168 | 0.86359
332 | RWMILLER | 1 | 73 | 0.06607 | north | Y | -0.0075335 | 0.085306 | 0.0032614 | 0.17475 | 0.0032614 | west | Y | 0.0075335 | 0.31187
333 | RWMILLER | 2 | 119 | 0.06607 | north | Y | -0.0075335 | 0.085306 | 0.0032614 | 0.17475 | 0.0032614 | west | Y | 0.0075335 | 0.50838
334 | RWMILLER | 3 | 205 | 0.06607 | north | Y | -0.0075335 | 0.085306 | 0.0032614 | 0.17475 | 0.0032614 | west | Y | 0.0075335 | 0.87579
335 | RWMILLER | 4 | 102 | 0.06607 | north | Y | -0.0075335 | 0.085306 | 0.0032614 | 0.17475 | 0.0032614 | west | Y | 0.0075335 | 0.43576
336 | RWMILLER | 5 | 96 | 0.06607 | north | Y | -0.0075335 | 0.085306 | 0.0032614 | 0.17475 | 0.0032614 | west | Y | 0.0075335 | 0.41013
344 | MRSSHPRD | 1 | 12 | 0.066729 | north | N | -0.0068745 | 0.085965 | 0.0039204 | 0.17541 | 0.0039204 | west | Y | 0.0068745 | 0
345 | MRSSHPRD | 2 | 12 | 0.066729 | north | N | -0.0068745 | 0.085965 | 0.0039204 | 0.17541 | 0.0039204 | west | Y | 0.0068745 | 0
366 | JNSNCNTY | 1 | 168 | 0.06651 | north | Y | -0.0070935 | 0.085746 | 0.0037014 | 0.17519 | 0.0037014 | west | Y | 0.0070935 | 0.56988
367 | JNSNCNTY | 2 | 90 | 0.06651 | north | Y | -0.0070935 | 0.085746 | 0.0037014 | 0.17519 | 0.0037014 | west | Y | 0.0070935 | 0.30529
503 | NTHTEXAS | 1 | 18 | 0.067305 | north | Y | -0.0062985 | 0.086541 | 0.0044964 | 0.17598 | 0.0044964 | west | Y | 0.0062985 | 0.032438
504 | NTHTEXAS | 2 | 18 | 0.067305 | north | Y | -0.0062985 | 0.086541 | 0.0044964 | 0.17598 | 0.0044964 | west | Y | 0.0062985 | 0.032438
505 | NTHTEXAS | 3 | 38 | 0.067305 | north | Y | -0.0062985 | 0.086541 | 0.0044964 | 0.17598 | 0.0044964 | west | Y | 0.0062985 | 0.068481
580 | JCKCNTY8 | 1 | 288 | 0.068072 | north | Y | -0.0055315 | 0.087308 | 0.0052634 | 0.17675 | 0.0052634 | west | Y | 0.0055315 | 0.077224
581 | JCKCNTY8 | 2 | 147 | 0.068072 | north | Y | -0.0055315 | 0.087308 | 0.0052634 | 0.17675 | 0.0052634 | west | Y | 0.0055315 | 0.039416
582 | JCKCNTY8 | 3 | 147 | 0.068072 | north | Y | -0.0055315 | 0.087308 | 0.0052634 | 0.17675 | 0.0052634 | west | Y | 0.0055315 | 0.039416
728 | WOLFRIDG | 1 | 112.5 | 0.068988 | north | Y | -0.0046155 | 0.088224 | 0.0061794 | 0.17767 | 0.0046155 | North | N | 0.0046155 | 0
837 | NEWMAN_G | 1 | 40 | 0.071497 | north | Y | -0.0021065 | 0.090733 | 0.0086884 | 0.18018 | 0.0021065 | North | N | 0.0021065 | 0
842 | OLINGER_ | 1 | 79 | 0.071494 | north | Y | -0.0021095 | 0.09073 | 0.0086854 | 0.18017 | 0.0021095 | North | N | 0.0021095 | 0
843 | OLINGER_ | 1 | 106 | 0.071494 | north | Y | -0.0021095 | 0.09073 | 0.0086854 | 0.18017 | 0.0021095 | North | N | 0.0021095 | 0
844 | OLINGER_ | 1 | 146 | 0.071494 | north | Y | -0.0021095 | 0.09073 | 0.0086854 | 0.18017 | 0.0021095 | North | N | 0.0021095 | 0
845 | OLINGER_ | 1 | 76 | 0.071494 | north | Y | -0.0021095 | 0.09073 | 0.0086854 | 0.18017 | 0.0021095 | North | N | 0.0021095 | 0
923 | SPENCER_ | 1 | 60 | 0.069682 | north | Y | -0.0039215 | 0.088918 | 0.0068734 | 0.17836 | 0.0039215 | North | N | 0.0039215 | 0
924 | SPENCER_ | 1 | 63 | 0.069682 | north | Y | -0.0039215 | 0.088918 | 0.0068734 | 0.17836 | 0.0039215 | North | N | 0.0039215 | 0
948 | STEAM1 | 1 | 20 | 0.071582 | north | Y | -0.0020215 | 0.090818 | 0.0087734 | 0.18026 | 0.0020215 | North | N | 0.0020215 | 0
949 | STEAM2 | 1 | 25 | 0.071582 | north | Y | -0.0020215 | 0.090818 | 0.0087734 | 0.18026 | 0.0020215 | North | N | 0.0020215 | 0
950 | STEAM3 | 1 | 41 | 0.071582 | north | Y | -0.0020215 | 0.090818 | 0.0087734 | 0.18026 | 0.0020215 | North | N | 0.0020215 | 0
990 | GIBN_CRE | 1 | 463 | 0.10486 | north | Y | 0.031254 | 0.12409 | 0.042049 | 0.21354 | 0.031254 | North | N | 0.031254 | 0
1002 | PBCTAGE_ | A | 66 | 0.06218 | west | Y | -0.011424 | 0.081416 | -0.00062863 | 0.17086 | 0.00062863 | west | N | 0.00062863 | 0
1003 | PBCTBGE_ | B | 65 | 0.06218 | west | Y | -0.011424 | 0.081416 | -0.00062863 | 0.17086 | 0.00062863 | west | N | 0.00062863 | 0
1004 | PBCTCGE_ | C | 67 | 0.06218 | west | Y | -0.011424 | 0.081416 | -0.00062863 | 0.17086 | 0.00062863 | west | N | 0.00062863 | 0
1005 | PBCTDGE_ | D | 67 | 0.06218 | west | Y | -0.011424 | 0.081416 | -0.00062863 | 0.17086 | 0.00062863 | west | N | 0.00062863 | 0
1006 | PBCTEGE_ | E | 67 | 0.06218 | west | Y | -0.011424 | 0.081416 | -0.00062863 | 0.17086 | 0.00062863 | west | N | 0.00062863 | 0
1007 | PB5GEN_6 | MB | 114 | 0.06218 | west | Y | -0.011424 | 0.081416 | -0.00062863 | 0.17086 | 0.00062863 | west | N | 0.00062863 | 0
1008 | PB6GEN_7 | MB | 515 | 0.06218 | west | Y | -0.011424 | 0.081416 | -0.00062863 | 0.17086 | 0.00062863 | west | N | 0.00062863 | 0
1039 | MRGNAG_1 | A | 66 | 0.063427 | west | Y | -0.010177 | 0.082663 | 0.00061837 | 0.17211 | 0.00061837 | west | N | 0.00061837 | 0
1040 | MRGNBG_2 | B | 69 | 0.063427 | west | Y | -0.010177 | 0.082663 | 0.00061837 | 0.17211 | 0.00061837 | west | N | 0.00061837 | 0
1041 | MRGNCG_3 | C | 69 | 0.063427 | west | Y | -0.010177 | 0.082663 | 0.00061837 | 0.17211 | 0.00061837 | west | N | 0.00061837 | 0
1042 | MRGNDG_4 | D | 67 | 0.063427 | west | Y | -0.010177 | 0.082663 | 0.00061837 | 0.17211 | 0.00061837 | west | N | 0.00061837 | 0
1043 | MRGNEG_5 | E | 67 | 0.063427 | west | Y | -0.010177 | 0.082663 | 0.00061837 | 0.17211 | 0.00061837 | west | N | 0.00061837 | 0
1044 | MRGNFG_6 | F | 65 | 0.063427 | west | Y | -0.010177 | 0.082663 | 0.00061837 | 0.17211 | 0.00061837 | west | N | 0.00061837 | 0
1045 | CALENG1G | 1 | 70 | 0.063252 | west | N | -0.010352 | 0.082488 | 0.00044337 | 0.17193 | 0.00044337 | west | N | 0.00044337 | 0
1046 | CALENG2G | 2 | 73.4 | 0.063252 | west | N | -0.010352 | 0.082488 | 0.00044337 | 0.17193 | 0.00044337 | west | N | 0.00044337 | 0
1047 | CALENG3G | 3 | 70.4 | 0.063252 | west | N | -0.010352 | 0.082488 | 0.00044337 | 0.17193 | 0.00044337 | west | N | 0.00044337 | 0
1058 | LONGSHOR | 1 | 150 | 0.063352 | west | Y | -0.010252 | 0.082588 | 0.00054337 | 0.17203 | 0.00054337 | west | N | 0.00054337 | 0
1058 | LONGSHOR | 2 | 220 | 0.063352 | west | Y | -0.010252 | 0.082588 | 0.00054337 | 0.17203 | 0.00054337 | west | N | 0.00054337 | 0
1061 | CIELOGEN | 1 | 99 | 0.063486 | west | Y | -0.010118 | 0.082722 | 0.00067737 | 0.17217 | 0.00067737 | west | N | 0.00067737 | 0
1062 | CIELOGEN | 1 | 61 | 0.063486 | west | Y | -0.010118 | 0.082722 | 0.00067737 | 0.17217 | 0.00067737 | west | N | 0.00067737 | 0
1068 | SCURRYCW | 1 | 141 | 0.063476 | west | Y | -0.010128 | 0.082712 | 0.00066737 | 0.17216 | 0.00066737 | west | N | 0.00066737 | 0
1069 | KINDERMG | 1 | 25 | 0.063486 | west | N | -0.010118 | 0.082722 | 0.00067737 | 0.17217 | 0.00067737 | west | N | 0.00067737 | 0
1070 | KINDERMG | 1 | 45.7 | 0.063486 | west | N | -0.010118 | 0.082722 | 0.00067737 | 0.17217 | 0.00067737 | west | N | 0.00067737 | 0
1071 | KINDERMG | 1 | 45.7 | 0.063486 | west | N | -0.010118 | 0.082722 | 0.00067737 | 0.17217 | 0.00067737 | west | N | 0.00067737 | 0
1073 | SCURRYCW | 2 | 120 | 0.063476 | west | Y | -0.010128 | 0.082712 | 0.00066737 | 0.17216 | 0.00066737 | west | N | 0.00066737 | 0
1320 | BSP 1 | 1 | 25.8 | 0.062949 | west | N | -0.010655 | 0.082185 | 0.00014037 | 0.17163 | 0.00014037 | west | N | 0.00014037 | 0
1326 | STANTONW | 1 | 100.5 | 0.062836 | west | Y | -0.010768 | 0.082072 | 2.7372e-05 | 0.17152 | 2.7372e-05 | west | N | 2.7372e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.063142 | west | Y | -0.010462 | 0.082378 | 0.00033337 | 0.17182 | 0.00033337 | west | N | 0.00033337 | 0
1328 | OCOTILLO | 1 | 58 | 0.062825 | west | Y | -0.010779 | 0.082061 | 1.6372e-05 | 0.1715 | 1.6372e-05 | west | N | 1.6372e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.06291 | west | Y | -0.010694 | 0.082146 | 0.00010137 | 0.17159 | 0.00010137 | west | N | 0.00010137 | 0
1343 | TRENTIPP | 1 | 150 | 0.063613 | west | Y | -0.0099905 | 0.082849 | 0.00080437 | 0.17229 | 0.00080437 | west | N | 0.00080437 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.062513 | west | Y | -0.011091 | 0.081749 | -0.00029563 | 0.17119 | 0.00029563 | west | N | 0.00029563 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.062513 | west | Y | -0.011091 | 0.081749 | -0.00029563 | 0.17119 | 0.00029563 | west | N | 0.00029563 | 0
1354 | AEPWIND_ | 1 | 101 | 0.063613 | west | Y | -0.0099905 | 0.082849 | 0.00080437 | 0.17229 | 0.00080437 | west | N | 0.00080437 | 0
1360 | GUNSIGHT | 1 | 120 | 0.063156 | west | Y | -0.010448 | 0.082392 | 0.00034737 | 0.17184 | 0.00034737 | west | N | 0.00034737 | 0
1432 | GRHAMSES | 2 | 366 | 0.066683 | north | Y | -0.0069205 | 0.085919 | 0.0038744 | 0.17536 | 0.0038744 | west | Y | 0.0069205 | 1.1149
1433 | GRHAMSES | 1 | 242 | 0.066309 | north | Y | -0.0072945 | 0.085545 | 0.0035004 | 0.17499 | 0.0035004 | west | Y | 0.0072945 | 0.91818
1437 | MESQUITW | 1 | 400 | 0.065061 | west | Y | -0.0085425 | 0.084297 | 0.0022524 | 0.17374 | 0.0022524 | west | N | 0.0022524 | 0
1438 | MESQUITW | 1 | 236 | 0.065064 | west | Y | -0.0085395 | 0.0843 | 0.0022554 | 0.17374 | 0.0022554 | west | N | 0.0022554 | 0
1442 | COKFIELD | 1 | 165 | 0.065452 | west | Y | -0.0081515 | 0.084688 | 0.0026434 | 0.17413 | 0.0026434 | west | N | 0.0026434 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.067686 | north | Y | -0.0059175 | 0.086922 | 0.0048774 | 0.17637 | 0.0048774 | west | Y | 0.0059175 | 0.21219
1454 | WCPWRCO_ | 2 | 201 | 0.067686 | north | Y | -0.0059175 | 0.086922 | 0.0048774 | 0.17637 | 0.0048774 | west | Y | 0.0059175 | 0.20907
1455 | WCPWRCO_ | 3 | 242 | 0.067686 | north | Y | -0.0059175 | 0.086922 | 0.0048774 | 0.17637 | 0.0048774 | west | Y | 0.0059175 | 0.25171
1479 | WFCOGEN_ | 1 | 20 | 0.066755 | west | Y | -0.0068485 | 0.085991 | 0.0039464 | 0.17543 | 0.0039464 | west | N | 0.0039464 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.066755 | west | Y | -0.0068485 | 0.085991 | 0.0039464 | 0.17543 | 0.0039464 | west | N | 0.0039464 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.066755 | west | Y | -0.0068485 | 0.085991 | 0.0039464 | 0.17543 | 0.0039464 | west | N | 0.0039464 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.066755 | west | Y | -0.0068485 | 0.085991 | 0.0039464 | 0.17543 | 0.0039464 | west | N | 0.0039464 | 0
1600 | BARTNWND | 1 | 120 | 0.066644 | north | Y | -0.0069595 | 0.08588 | 0.0038354 | 0.17532 | 0.0038354 | west | Y | 0.0069595 | 0.3749
1643 | SLSTR1PP | 1 | 60 | 0.064014 | north | Y | -0.0095895 | 0.08325 | 0.0012054 | 0.17269 | 0.0012054 | west | Y | 0.0095895 | 0.50305
1675 | PEC_1G | 1 | 75 | 0.071364 | north | N | -0.0022395 | 0.0906 | 0.0085554 | 0.18004 | 0.0022395 | North | N | 0.0022395 | 0
1676 | PEC_2G | 2 | 79.6 | 0.071364 | north | N | -0.0022395 | 0.0906 | 0.0085554 | 0.18004 | 0.0022395 | North | N | 0.0022395 | 0
1677 | PEC_3G | 3 | 88.4 | 0.071364 | north | N | -0.0022395 | 0.0906 | 0.0085554 | 0.18004 | 0.0022395 | North | N | 0.0022395 | 0
1678 | LAMARPWR | 1 | 160 | 0.071324 | north | Y | -0.0022795 | 0.09056 | 0.0085154 | 0.18 | 0.0022795 | North | N | 0.0022795 | 0
1679 | LAMARPWR | 2 | 156 | 0.071324 | north | Y | -0.0022795 | 0.09056 | 0.0085154 | 0.18 | 0.0022795 | North | N | 0.0022795 | 0
1680 | LAMARPWR | 3 | 196 | 0.071324 | north | Y | -0.0022795 | 0.09056 | 0.0085154 | 0.18 | 0.0022795 | North | N | 0.0022795 | 0
1681 | LAMARPWR | 4 | 156 | 0.071324 | north | Y | -0.0022795 | 0.09056 | 0.0085154 | 0.18 | 0.0022795 | North | N | 0.0022795 | 0
1682 | LAMARPWR | 5 | 157 | 0.071324 | north | Y | -0.0022795 | 0.09056 | 0.0085154 | 0.18 | 0.0022795 | North | N | 0.0022795 | 0
1683 | LAMARPWR | 6 | 198 | 0.071324 | north | Y | -0.0022795 | 0.09056 | 0.0085154 | 0.18 | 0.0022795 | North | N | 0.0022795 | 0
1687 | VALLEY_1 | 1 | 170 | 0.07114 | north | Y | -0.0024635 | 0.090376 | 0.0083314 | 0.17982 | 0.0024635 | North | N | 0.0024635 | 0
1688 | VALLEY_2 | 2 | 520 | 0.07114 | north | Y | -0.0024635 | 0.090376 | 0.0083314 | 0.17982 | 0.0024635 | North | N | 0.0024635 | 0
1689 | VALLEY_3 | 3 | 370 | 0.071268 | north | Y | -0.0023355 | 0.090504 | 0.0084594 | 0.17995 | 0.0023355 | North | N | 0.0023355 | 0
1701 | MOSES_1G | 1 | 558 | 0.071422 | north | Y | -0.0021815 | 0.090658 | 0.0086134 | 0.1801 | 0.0021815 | North | N | 0.0021815 | 0
1702 | MOSES_2G | 2 | 579 | 0.071422 | north | Y | -0.0021815 | 0.090658 | 0.0086134 | 0.1801 | 0.0021815 | North | N | 0.0021815 | 0
1703 | MOSES_3G | 3 | 808 | 0.071422 | north | Y | -0.0021815 | 0.090658 | 0.0086134 | 0.1801 | 0.0021815 | North | N | 0.0021815 | 0
1861 | EAGLEMNT | MB | 112 | 0.068747 | north | Y | -0.0048565 | 0.087983 | 0.0059384 | 0.17743 | 0.0048565 | North | N | 0.0048565 | 0
1862 | EAGLEMNT | MB | 100 | 0.068747 | north | Y | -0.0048565 | 0.087983 | 0.0059384 | 0.17743 | 0.0048565 | North | N | 0.0048565 | 0
1863 | EAGLEMNT | MB | 378 | 0.068747 | north | Y | -0.0048565 | 0.087983 | 0.0059384 | 0.17743 | 0.0048565 | North | N | 0.0048565 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.067658 | north | Y | -0.0059455 | 0.086894 | 0.0048494 | 0.17634 | 0.0048494 | west | Y | 0.0059455 | 0.23819
1878 | WLFHOLW_ | 2 | 205 | 0.067658 | north | Y | -0.0059455 | 0.086894 | 0.0048494 | 0.17634 | 0.0048494 | west | Y | 0.0059455 | 0.22471
1879 | WLFHOLW_ | 3 | 272.4 | 0.067658 | north | Y | -0.0059455 | 0.086894 | 0.0048494 | 0.17634 | 0.0048494 | west | Y | 0.0059455 | 0.29859
1889 | DECRDOVA | MB | 770 | 0.067806 | north | Y | -0.0057975 | 0.087042 | 0.0049974 | 0.17649 | 0.0049974 | west | Y | 0.0057975 | 0
1892 | DECRDOVA | A | 70 | 0.06693 | north | Y | -0.0066735 | 0.086166 | 0.0041214 | 0.17561 | 0.0041214 | west | Y | 0.0066735 | 0.17865
1893 | DECRDOVA | B | 69 | 0.06693 | north | Y | -0.0066735 | 0.086166 | 0.0041214 | 0.17561 | 0.0041214 | west | Y | 0.0066735 | 0.1761
1894 | DECRDOVA | C | 69 | 0.06693 | north | Y | -0.0066735 | 0.086166 | 0.0041214 | 0.17561 | 0.0041214 | west | Y | 0.0066735 | 0.1761
1895 | DECRDOVA | D | 68 | 0.06693 | north | Y | -0.0066735 | 0.086166 | 0.0041214 | 0.17561 | 0.0041214 | west | Y | 0.0066735 | 0.17355
1898 | COMCHEPK | 1 | 1157 | 0.067492 | north | N | -0.0061115 | 0.086728 | 0.0046834 | 0.17617 | 0.0046834 | west | Y | 0.0061115 | 0
1899 | COMCHEPK | 2 | 1158 | 0.067492 | north | N | -0.0061115 | 0.086728 | 0.0046834 | 0.17617 | 0.0046834 | west | Y | 0.0061115 | 0
1937 | MDLTHELP | 5 | 224 | 0.068126 | north | Y | -0.0054775 | 0.087362 | 0.0053174 | 0.17681 | 0.0053174 | west | Y | 0.0054775 | 0.035871
1938 | MDLTHELP | 6 | 226 | 0.068126 | north | Y | -0.0054775 | 0.087362 | 0.0053174 | 0.17681 | 0.0053174 | west | Y | 0.0054775 | 0.036191
1941 | MDLTHELP | 1 | 216.4 | 0.0688 | north | Y | -0.0048035 | 0.088036 | 0.0059914 | 0.17748 | 0.0048035 | North | N | 0.0048035 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.0688 | north | Y | -0.0048035 | 0.088036 | 0.0059914 | 0.17748 | 0.0048035 | North | N | 0.0048035 | 0
1943 | MDLTHELP | 3 | 212 | 0.068126 | north | Y | -0.0054775 | 0.087362 | 0.0053174 | 0.17681 | 0.0053174 | west | Y | 0.0054775 | 0.033949
1944 | MDLTHELP | 4 | 211 | 0.068126 | north | Y | -0.0054775 | 0.087362 | 0.0053174 | 0.17681 | 0.0053174 | west | Y | 0.0054775 | 0.033789
1947 | HANDLEY_ | 3 | 395 | 0.068902 | north | Y | -0.0047015 | 0.088138 | 0.0060934 | 0.17758 | 0.0047015 | North | N | 0.0047015 | 0
1948 | HANDLEY_ | 4 | 435 | 0.069043 | north | Y | -0.0045605 | 0.088279 | 0.0062344 | 0.17772 | 0.0045605 | North | N | 0.0045605 | 0
1949 | HANDLEY_ | 5 | 435 | 0.068902 | north | Y | -0.0047015 | 0.088138 | 0.0060934 | 0.17758 | 0.0047015 | North | N | 0.0047015 | 0
2371 | COLLIN_1 | MB | 138 | 0.070731 | north | Y | -0.0028725 | 0.089967 | 0.0079224 | 0.17941 | 0.0028725 | North | N | 0.0028725 | 0
2413 | MTCK6_G | 6 | 118 | 0.070901 | north | Y | -0.0027025 | 0.090137 | 0.0080924 | 0.17958 | 0.0027025 | North | N | 0.0027025 | 0
2414 | MTCK7_G | 7 | 115 | 0.070901 | north | Y | -0.0027025 | 0.090137 | 0.0080924 | 0.17958 | 0.0027025 | North | N | 0.0027025 | 0
2417 | MTCK8_G | 8 | 556 | 0.070901 | north | Y | -0.0027025 | 0.090137 | 0.0080924 | 0.17958 | 0.0027025 | North | N | 0.0027025 | 0
2451 | LKHB1_G | 1 | 388 | 0.071665 | north | Y | -0.0019385 | 0.090901 | 0.0088564 | 0.18034 | 0.0019385 | North | N | 0.0019385 | 0
2452 | LKHB2_G | 2 | 515 | 0.071665 | north | Y | -0.0019385 | 0.090901 | 0.0088564 | 0.18034 | 0.0019385 | North | N | 0.0019385 | 0
3097 | MARTLAKE | 1 | 785 | 0.074082 | north | Y | 0.00047849 | 0.093318 | 0.011273 | 0.18276 | 0.00047849 | North | N | 0.00047849 | 0
3098 | MARTLAKE | 2 | 795 | 0.074082 | north | Y | 0.00047849 | 0.093318 | 0.011273 | 0.18276 | 0.00047849 | North | N | 0.00047849 | 0
3099 | MARTLAKE | 3 | 780 | 0.074082 | north | Y | 0.00047849 | 0.093318 | 0.011273 | 0.18276 | 0.00047849 | North | N | 0.00047849 | 0
3107 | STRYKER_ | 1 | 182 | 0.074693 | north | Y | 0.0010895 | 0.093929 | 0.011884 | 0.18337 | 0.0010895 | North | N | 0.0010895 | 0
3108 | STRYKER_ | 2 | 484 | 0.074693 | north | Y | 0.0010895 | 0.093929 | 0.011884 | 0.18337 | 0.0010895 | North | N | 0.0010895 | 0
3126 | TRINIDAD | 1 | 224 | 0.072199 | north | Y | -0.0014045 | 0.091435 | 0.0093904 | 0.18088 | 0.0014045 | North | N | 0.0014045 | 0
3309 | ASPN_G | 1 | 50 | 0.074654 | north | Y | 0.0010505 | 0.09389 | 0.011845 | 0.18333 | 0.0010505 | North | N | 0.0010505 | 0
3348 | CHAMPION | MB | 42 | 0.074624 | north | N | 0.0010205 | 0.09386 | 0.011815 | 0.1833 | 0.0010205 | North | N | 0.0010205 | 0
3381 | BBRN_1G | 1 | 615 | 0.078422 | north | Y | 0.0048185 | 0.097658 | 0.015613 | 0.1871 | 0.0048185 | North | N | 0.0048185 | 0
3382 | BBRN_2G | 2 | 587 | 0.078422 | north | Y | 0.0048185 | 0.097658 | 0.015613 | 0.1871 | 0.0048185 | North | N | 0.0048185 | 0
3403 | THOUSE_1 | MB | 537 | 0.05334 | north | Y | -0.020264 | 0.072576 | -0.0094686 | 0.16202 | 0.0094686 | west | Y | 0.020264 | 0
3404 | THOUSE_2 | 2 | 787 | 0.05334 | north | Y | -0.020264 | 0.072576 | -0.0094686 | 0.16202 | 0.0094686 | west | Y | 0.020264 | 8.4956
3416 | LAKE_CRK | MB | 75 | 0.052588 | north | Y | -0.021016 | 0.071824 | -0.010221 | 0.16127 | 0.010221 | west | Y | 0.021016 | 0
3417 | LAKE_CRK | MB | 222 | 0.052588 | north | Y | -0.021016 | 0.071824 | -0.010221 | 0.16127 | 0.010221 | west | Y | 0.021016 | 0
3432 | SANDOW_4 | 4 | 569 | 0.018966 | south | Y | -0.054638 | 0.038202 | -0.043843 | 0.12765 | 0.038202 | south | N | 0.038202 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.022567 | south | Y | -0.096171 | -0.0033306 | -0.085376 | 0.086112 | 0.0033306 | south | N | 0.0033306 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.022567 | south | Y | -0.096171 | -0.0033306 | -0.085376 | 0.086112 | 0.0033306 | south | N | 0.0033306 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.022486 | south | Y | -0.09609 | -0.0032496 | -0.085295 | 0.086193 | 0.0032496 | south | N | 0.0032496 | 0
5031 | BRA_VHBC | 1 | 46 | -0.022567 | south | Y | -0.096171 | -0.0033306 | -0.085376 | 0.086112 | 0.0033306 | south | N | 0.0033306 | 0
5032 | BRA_VHBC | 2 | 47 | -0.022567 | south | Y | -0.096171 | -0.0033306 | -0.085376 | 0.086112 | 0.0033306 | south | N | 0.0033306 | 0
5033 | BRA_VHBC | 3 | 46 | -0.022567 | south | Y | -0.096171 | -0.0033306 | -0.085376 | 0.086112 | 0.0033306 | south | N | 0.0033306 | 0
5034 | BRA_VHBC | 4 | 46 | -0.022567 | south | Y | -0.096171 | -0.0033306 | -0.085376 | 0.086112 | 0.0033306 | south | N | 0.0033306 | 0
5111 | CALAVER_ | 1 | 424 | -0.022523 | south | Y | -0.096127 | -0.0032866 | -0.085332 | 0.086156 | 0.0032866 | south | N | 0.0032866 | 0
5112 | CALAVER_ | 2 | 425 | -0.022523 | south | Y | -0.096127 | -0.0032866 | -0.085332 | 0.086156 | 0.0032866 | south | N | 0.0032866 | 0
5264 | LEON_LCP | 3 | 58 | -0.022513 | south | Y | -0.096117 | -0.0032766 | -0.085322 | 0.086166 | 0.0032766 | south | N | 0.0032766 | 0
5265 | LEON_LCP | 4 | 89 | -0.022513 | south | Y | -0.096117 | -0.0032766 | -0.085322 | 0.086166 | 0.0032766 | south | N | 0.0032766 | 0
5266 | LEON_LCP | 1 | 44 | -0.022513 | south | Y | -0.096117 | -0.0032766 | -0.085322 | 0.086166 | 0.0032766 | south | N | 0.0032766 | 0
5267 | LEON_LCP | 2 | 44 | -0.022513 | south | Y | -0.096117 | -0.0032766 | -0.085322 | 0.086166 | 0.0032766 | south | N | 0.0032766 | 0
5268 | LEON_LCP | 3 | 43 | -0.022513 | south | Y | -0.096117 | -0.0032766 | -0.085322 | 0.086166 | 0.0032766 | south | N | 0.0032766 | 0
5269 | LEON_LCP | 4 | 45 | -0.022513 | south | Y | -0.096117 | -0.0032766 | -0.085322 | 0.086166 | 0.0032766 | south | N | 0.0032766 | 0
5396 | CALAVER_ | 1 | 412 | -0.022488 | south | Y | -0.096092 | -0.0032516 | -0.085297 | 0.086191 | 0.0032516 | south | N | 0.0032516 | 0
5397 | CALAVER_ | 2 | 400 | -0.022488 | south | Y | -0.096092 | -0.0032516 | -0.085297 | 0.086191 | 0.0032516 | south | N | 0.0032516 | 0
5401 | CALAVER_ | 1 | 546 | -0.023846 | south | Y | -0.09745 | -0.0046096 | -0.086655 | 0.084833 | 0.0046096 | south | N | 0.0046096 | 0
5402 | CALAVER_ | 2 | 750 | -0.023846 | south | Y | -0.09745 | -0.0046096 | -0.086655 | 0.084833 | 0.0046096 | south | N | 0.0046096 | 0
5436 | TUTTL_WB | MB | 61 | -0.022611 | south | Y | -0.096215 | -0.0033746 | -0.08542 | 0.086068 | 0.0033746 | south | N | 0.0033746 | 0
5438 | TUTTL_WB | MB | 95 | -0.022611 | south | Y | -0.096215 | -0.0033746 | -0.08542 | 0.086068 | 0.0033746 | south | N | 0.0033746 | 0
5439 | TUTTL_WB | MB | 151 | -0.022611 | south | Y | -0.096215 | -0.0033746 | -0.08542 | 0.086068 | 0.0033746 | south | N | 0.0033746 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.023266 | south | Y | -0.09687 | -0.0040296 | -0.086075 | 0.085413 | 0.0040296 | south | N | 0.0040296 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.023266 | south | Y | -0.09687 | -0.0040296 | -0.086075 | 0.085413 | 0.0040296 | south | N | 0.0040296 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.023266 | south | Y | -0.09687 | -0.0040296 | -0.086075 | 0.085413 | 0.0040296 | south | N | 0.0040296 | 0
5503 | RAYBURNG | 1 | 22 | -0.039484 | south | Y | -0.11309 | -0.020248 | -0.10229 | 0.069195 | 0.020248 | south | N | 0.020248 | 0
5505 | RAYBURNG | 1 | 11 | -0.039484 | south | Y | -0.11309 | -0.020248 | -0.10229 | 0.069195 | 0.020248 | south | N | 0.020248 | 0
5506 | RAYBURNG | 1 | 11 | -0.039484 | south | Y | -0.11309 | -0.020248 | -0.10229 | 0.069195 | 0.020248 | south | N | 0.020248 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.03902 | south | Y | -0.11262 | -0.019784 | -0.10183 | 0.069659 | 0.019784 | south | N | 0.019784 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.03902 | south | Y | -0.11262 | -0.019784 | -0.10183 | 0.069659 | 0.019784 | south | N | 0.019784 | 0
5511 | RAYBURNC | 1 | 46 | -0.03902 | south | Y | -0.11262 | -0.019784 | -0.10183 | 0.069659 | 0.019784 | south | N | 0.019784 | 0
5512 | RAYBURNC | 1 | 48 | -0.03902 | south | Y | -0.11262 | -0.019784 | -0.10183 | 0.069659 | 0.019784 | south | N | 0.019784 | 0
5728 | FALCONHY | 2 | 12 | -0.033909 | south | N | -0.10751 | -0.014673 | -0.096718 | 0.07477 | 0.014673 | south | N | 0.014673 | 0
5729 | FALCONHY | 3 | 11 | -0.033909 | south | N | -0.10751 | -0.014673 | -0.096718 | 0.07477 | 0.014673 | south | N | 0.014673 | 0
5890 | PEARSALL | 1 | 24 | -0.023671 | south | Y | -0.097275 | -0.0044346 | -0.08648 | 0.085008 | 0.0044346 | south | N | 0.0044346 | 0
5891 | PEARSALL | 1 | 24 | -0.023671 | south | Y | -0.097275 | -0.0044346 | -0.08648 | 0.085008 | 0.0044346 | south | N | 0.0044346 | 0
5892 | PEARSALL | 1 | 23 | -0.023671 | south | Y | -0.097275 | -0.0044346 | -0.08648 | 0.085008 | 0.0044346 | south | N | 0.0044346 | 0
5903 | SANMIGUE | 1 | 396 | -0.027673 | south | Y | -0.10128 | -0.0084366 | -0.090482 | 0.081006 | 0.0084366 | south | N | 0.0084366 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.069926 | houston | N | -0.14353 | -0.05069 | -0.13273 | 0.038753 | 0.038753 | houston | N | 0.038753 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.069926 | houston | N | -0.14353 | -0.05069 | -0.13273 | 0.038753 | 0.038753 | houston | N | 0.038753 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | Y | 0.073604 | 0
5932 | SI_RAY9 | 9 | 38 | -0.037246 | south | Y | -0.11085 | -0.01801 | -0.10005 | 0.071433 | 0.01801 | south | N | 0.01801 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.037246 | south | Y | -0.11085 | -0.01801 | -0.10005 | 0.071433 | 0.01801 | south | N | 0.01801 | 0
5934 | SI_RAY5 | 5 | 15 | -0.037246 | south | Y | -0.11085 | -0.01801 | -0.10005 | 0.071433 | 0.01801 | south | N | 0.01801 | 0
5935 | SI_RAY10 | 10 | 47 | -0.037246 | south | Y | -0.11085 | -0.01801 | -0.10005 | 0.071433 | 0.01801 | south | N | 0.01801 | 0
6016 | SWMESA | 1 | 75 | 0.058695 | west | Y | -0.014909 | 0.077931 | -0.0041136 | 0.16737 | 0.0041136 | west | N | 0.0041136 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | Y | 0.062809 | 0
6144 | MCADOO1A | 1 | 150 | 0.063931 | west | Y | -0.0096725 | 0.083167 | 0.0011224 | 0.17261 | 0.0011224 | west | N | 0.0011224 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.062291 | west | Y | -0.011313 | 0.081527 | -0.00051763 | 0.17097 | 0.00051763 | west | N | 0.00051763 | 0
6476 | LANGFORD | 1 | 150 | 0.045265 | west | Y | -0.028339 | 0.064501 | -0.017544 | 0.15394 | 0.017544 | west | N | 0.017544 | 0
6637 | SNYDERW1 | 1 | 63 | 0.063451 | west | Y | -0.010153 | 0.082687 | 0.00064237 | 0.17213 | 0.00064237 | west | N | 0.00064237 | 0
6752 | OKLA0A | 1 | 649.7 | 0.065785 | west | Y | -0.0078185 | 0.085021 | 0.0029764 | 0.17446 | 0.0029764 | west | N | 0.0029764 | 0
6948 | DENISNDM | 1 | 40 | 0.071038 | north | N | -0.0025655 | 0.090274 | 0.0082294 | 0.17972 | 0.0025655 | North | N | 0.0025655 | 0
6948 | DENISNDM | 2 | 40 | 0.071038 | north | N | -0.0025655 | 0.090274 | 0.0082294 | 0.17972 | 0.0025655 | North | N | 0.0025655 | 0
7000 | L_FERGUS | 1 | 422 | 0.003066 | south | Y | -0.070538 | 0.022302 | -0.059743 | 0.11175 | 0.022302 | south | N | 0.022302 | 0
7004 | L_SIMGID | 1 | 132 | -0.002359 | south | Y | -0.075963 | 0.016877 | -0.065168 | 0.10632 | 0.016877 | south | N | 0.016877 | 0
7005 | L_SIMGID | 2 | 134 | -0.002359 | south | Y | -0.075963 | 0.016877 | -0.065168 | 0.10632 | 0.016877 | south | N | 0.016877 | 0
7006 | L_SIMGID | 3 | 323 | -0.002359 | south | Y | -0.075963 | 0.016877 | -0.065168 | 0.10632 | 0.016877 | south | N | 0.016877 | 0
7007 | L_LOSTPI | 1 | 158 | -0.00475 | south | Y | -0.078354 | 0.014486 | -0.067559 | 0.10393 | 0.014486 | south | N | 0.014486 | 0
7008 | L_LOSTPI | 2 | 160 | -0.00475 | south | Y | -0.078354 | 0.014486 | -0.067559 | 0.10393 | 0.014486 | south | N | 0.014486 | 0
7009 | L_LOSTPI | 3 | 175 | -0.00475 | south | Y | -0.078354 | 0.014486 | -0.067559 | 0.10393 | 0.014486 | south | N | 0.014486 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.012231 | south | Y | -0.085835 | 0.0070054 | -0.07504 | 0.096448 | 0.0070054 | south | N | 0.0070054 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.012231 | south | Y | -0.085835 | 0.0070054 | -0.07504 | 0.096448 | 0.0070054 | south | N | 0.0070054 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.012363 | south | Y | -0.085967 | 0.0068734 | -0.075172 | 0.096316 | 0.0068734 | south | N | 0.0068734 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.015926 | south | Y | -0.08953 | 0.0033104 | -0.078735 | 0.092753 | 0.0033104 | south | N | 0.0033104 | 0
7015 | L_HAYSEN | 2 | 225 | -0.015926 | south | Y | -0.08953 | 0.0033104 | -0.078735 | 0.092753 | 0.0033104 | south | N | 0.0033104 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.015926 | south | Y | -0.08953 | 0.0033104 | -0.078735 | 0.092753 | 0.0033104 | south | N | 0.0033104 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.015926 | south | Y | -0.08953 | 0.0033104 | -0.078735 | 0.092753 | 0.0033104 | south | N | 0.0033104 | 0
7020 | L_AUSTPL | 1 | 8 | 0.000275 | south | N | -0.073329 | 0.019511 | -0.062534 | 0.10895 | 0.019511 | south | N | 0.019511 | 0
7020 | L_AUSTPL | 2 | 8 | 0.000275 | south | N | -0.073329 | 0.019511 | -0.062534 | 0.10895 | 0.019511 | south | N | 0.019511 | 0
7022 | L_BUCHAN | 1 | 18 | 0.007815 | south | N | -0.065789 | 0.027051 | -0.054994 | 0.11649 | 0.027051 | south | N | 0.027051 | 0
7023 | L_BUCHAN | 2 | 18 | 0.007815 | south | N | -0.065789 | 0.027051 | -0.054994 | 0.11649 | 0.027051 | south | N | 0.027051 | 0
7024 | L_BUCHAN | 3 | 15 | 0.007815 | south | N | -0.065789 | 0.027051 | -0.054994 | 0.11649 | 0.027051 | south | N | 0.027051 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.006937 | south | N | -0.066667 | 0.026173 | -0.055872 | 0.11562 | 0.026173 | south | N | 0.026173 | 0
7028 | L_MARBFA | 1 | 18 | 0.002518 | south | N | -0.071086 | 0.021754 | -0.060291 | 0.1112 | 0.021754 | south | N | 0.021754 | 0
7029 | L_MARBFA | 2 | 18 | 0.002518 | south | N | -0.071086 | 0.021754 | -0.060291 | 0.1112 | 0.021754 | south | N | 0.021754 | 0
7031 | L_MARSFO | 1 | 35 | 0.001274 | south | N | -0.07233 | 0.02051 | -0.061535 | 0.10995 | 0.02051 | south | N | 0.02051 | 0
7032 | L_MARSFO | 2 | 34 | 0.001274 | south | N | -0.07233 | 0.02051 | -0.061535 | 0.10995 | 0.02051 | south | N | 0.02051 | 0
7033 | L_MARSFO | 3 | 35 | 0.001274 | south | N | -0.07233 | 0.02051 | -0.061535 | 0.10995 | 0.02051 | south | N | 0.02051 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.003305 | south | N | -0.070299 | 0.022541 | -0.059504 | 0.11198 | 0.022541 | south | N | 0.022541 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.003305 | south | N | -0.070299 | 0.022541 | -0.059504 | 0.11198 | 0.022541 | south | N | 0.022541 | 0
7038 | L_DELAWA | 1 | 35 | 0.062211 | west | Y | -0.011393 | 0.081447 | -0.00059763 | 0.17089 | 0.00059763 | west | N | 0.00059763 | 0
7038 | L_DELAWA | 2 | 30 | 0.062211 | west | Y | -0.011393 | 0.081447 | -0.00059763 | 0.17089 | 0.00059763 | west | N | 0.00059763 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.007238 | south | Y | -0.080842 | 0.011998 | -0.070047 | 0.10144 | 0.011998 | south | N | 0.011998 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.007238 | south | Y | -0.080842 | 0.011998 | -0.070047 | 0.10144 | 0.011998 | south | N | 0.011998 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.007238 | south | Y | -0.080842 | 0.011998 | -0.070047 | 0.10144 | 0.011998 | south | N | 0.011998 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.007238 | south | Y | -0.080842 | 0.011998 | -0.070047 | 0.10144 | 0.011998 | south | N | 0.011998 | 0
7487 | L_CANYHY | 1 | 6 | -0.01243 | south | N | -0.086034 | 0.0068064 | -0.075239 | 0.096249 | 0.0068064 | south | N | 0.0068064 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.017816 | south | N | -0.09142 | 0.0014204 | -0.080625 | 0.090863 | 0.0014204 | south | N | 0.0014204 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.017816 | south | N | -0.09142 | 0.0014204 | -0.080625 | 0.090863 | 0.0014204 | south | N | 0.0014204 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.017816 | south | N | -0.09142 | 0.0014204 | -0.080625 | 0.090863 | 0.0014204 | south | N | 0.0014204 | 0
7609 | L_SCHUMA | 1 | 4 | -0.019262 | south | N | -0.092866 | -2.5551e-05 | -0.082071 | 0.089417 | 2.5551e-05 | south | N | 2.5551e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.018327 | south | N | -0.091931 | 0.00090945 | -0.081136 | 0.090352 | 0.00090945 | south | N | 0.00090945 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.018327 | south | N | -0.091931 | 0.00090945 | -0.081136 | 0.090352 | 0.00090945 | south | N | 0.00090945 | 0
7800 | L_GUADGE | 1 | 147 | -0.0218 | south | Y | -0.095404 | -0.0025636 | -0.084609 | 0.086879 | 0.0025636 | south | N | 0.0025636 | 0
7801 | L_GUADGE | 2 | 138 | -0.0218 | south | Y | -0.095404 | -0.0025636 | -0.084609 | 0.086879 | 0.0025636 | south | N | 0.0025636 | 0
7802 | L_GUADGE | 3 | 140 | -0.0218 | south | Y | -0.095404 | -0.0025636 | -0.084609 | 0.086879 | 0.0025636 | south | N | 0.0025636 | 0
7803 | L_GUADGE | 4 | 147 | -0.0218 | south | Y | -0.095404 | -0.0025636 | -0.084609 | 0.086879 | 0.0025636 | south | N | 0.0025636 | 0
7804 | L_GUADGE | 5 | 182 | -0.0218 | south | Y | -0.095404 | -0.0025636 | -0.084609 | 0.086879 | 0.0025636 | south | N | 0.0025636 | 0
7805 | L_GUADGE | 6 | 198 | -0.0218 | south | Y | -0.095404 | -0.0025636 | -0.084609 | 0.086879 | 0.0025636 | south | N | 0.0025636 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.004354 | south | Y | -0.077958 | 0.014882 | -0.067163 | 0.10433 | 0.014882 | south | N | 0.014882 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.004354 | south | Y | -0.077958 | 0.014882 | -0.067163 | 0.10433 | 0.014882 | south | N | 0.014882 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.004354 | south | Y | -0.077958 | 0.014882 | -0.067163 | 0.10433 | 0.014882 | south | N | 0.014882 | 0
7810 | L_RIONOG | 1 | 142 | -0.018945 | south | Y | -0.092549 | 0.00029145 | -0.081754 | 0.089734 | 0.00029145 | south | N | 0.00029145 | 0
7811 | L_RIONOG | 2 | 145 | -0.018945 | south | Y | -0.092549 | 0.00029145 | -0.081754 | 0.089734 | 0.00029145 | south | N | 0.00029145 | 0
7812 | L_RIONOG | 3 | 151 | -0.018945 | south | Y | -0.092549 | 0.00029145 | -0.081754 | 0.089734 | 0.00029145 | south | N | 0.00029145 | 0
7813 | L_RIONOG | 4 | 290 | -0.018945 | south | Y | -0.092549 | 0.00029145 | -0.081754 | 0.089734 | 0.00029145 | south | N | 0.00029145 | 0
8032 | AMISTADH | 1 | 33 | -0.000601 | south | N | -0.074205 | 0.018635 | -0.06341 | 0.10808 | 0.018635 | south | N | 0.018635 | 0
8033 | AMISTADH | 2 | 25 | -0.000601 | south | N | -0.074205 | 0.018635 | -0.06341 | 0.10808 | 0.018635 | south | N | 0.018635 | 0
8048 | FALCONHY | 1 | 12 | -0.033909 | south | N | -0.10751 | -0.014673 | -0.096718 | 0.07477 | 0.014673 | south | N | 0.014673 | 0
8066 | DUP1V#1 | 1 | 73 | -0.038924 | south | N | -0.11253 | -0.019688 | -0.10173 | 0.069755 | 0.019688 | south | N | 0.019688 | 0
8134 | FOR69CG0 | 1 | 79 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
8138 | FOR69CG0 | 2 | 81 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | N | 0.019236 | 0
8147 | UCAR #2 | 10 | 28 | -0.041297 | south | N | -0.1149 | -0.022061 | -0.10411 | 0.067382 | 0.022061 | south | N | 0.022061 | 0
8148 | UCAR #1 | 2 | 7 | -0.041297 | south | N | -0.1149 | -0.022061 | -0.10411 | 0.067382 | 0.022061 | south | N | 0.022061 | 0
8153 | FOR69CG0 | 3 | 79 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
8154 | FOR69CG0 | 4 | 80 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
8156 | FOR69CG0 | 6 | 25 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
8157 | FOR69CG0 | 7 | 46 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
8161 | COLETOU1 | 1 | 629 | -0.034742 | south | Y | -0.10835 | -0.015506 | -0.097551 | 0.073937 | 0.015506 | south | N | 0.015506 | 0
8173 | VICEC51A | 5 | 144 | -0.038056 | south | Y | -0.11166 | -0.01882 | -0.10086 | 0.070623 | 0.01882 | south | N | 0.01882 | 0
8174 | VICEC61A | 6 | 188 | -0.038056 | south | Y | -0.11166 | -0.01882 | -0.10086 | 0.070623 | 0.01882 | south | N | 0.01882 | 0
8189 | CUERO 2 | 1 | 12 | -0.023191 | south | N | -0.096795 | -0.0039546 | -0.086 | 0.085488 | 0.0039546 | south | N | 0.0039546 | 0
8262 | ELPS | 1 | 6 | -0.008171 | south | N | -0.081775 | 0.011065 | -0.07098 | 0.10051 | 0.011065 | south | N | 0.011065 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | N | 0.019236 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | N | 0.019236 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | N | 0.019236 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | N | 0.019236 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | N | 0.019236 | 0
8442 | NBEC71A | 1 | 336 | -0.038246 | south | Y | -0.11185 | -0.01901 | -0.10105 | 0.070433 | 0.01901 | south | N | 0.01901 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | N | 0.019236 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.073604 | 0.019236 | -0.062809 | 0.10868 | 0.019236 | south | N | 0.019236 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.038063 | south | Y | -0.11167 | -0.018827 | -0.10087 | 0.070616 | 0.018827 | south | N | 0.018827 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.038063 | south | Y | -0.11167 | -0.018827 | -0.10087 | 0.070616 | 0.018827 | south | N | 0.018827 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.037895 | south | N | -0.1115 | -0.018659 | -0.1007 | 0.070784 | 0.018659 | south | N | 0.018659 | 0
8506 | VAL #1 | 1 | 25 | -0.037996 | south | N | -0.1116 | -0.01876 | -0.1008 | 0.070683 | 0.01876 | south | N | 0.01876 | 0
8507 | VAL #2 | 2 | 25 | -0.037996 | south | N | -0.1116 | -0.01876 | -0.1008 | 0.070683 | 0.01876 | south | N | 0.01876 | 0
8511 | OXY_CC0A | 1 | 38 | -0.037938 | south | N | -0.11154 | -0.018702 | -0.10075 | 0.070741 | 0.018702 | south | N | 0.018702 | 0
8517 | CELANEBI | 1 | 29 | -0.037533 | south | N | -0.11114 | -0.018297 | -0.10034 | 0.071146 | 0.018297 | south | N | 0.018297 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.038236 | south | N | -0.11184 | -0.019 | -0.10104 | 0.070443 | 0.019 | south | N | 0.019 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.038236 | south | N | -0.11184 | -0.019 | -0.10104 | 0.070443 | 0.019 | south | N | 0.019 | 0
8562 | CNOPST1 | 3 | 153 | -0.038236 | south | N | -0.11184 | -0.019 | -0.10104 | 0.070443 | 0.019 | south | N | 0.019 | 0
8926 | LGE_GT10 | 1 | 158 | -0.039103 | south | N | -0.11271 | -0.019867 | -0.10191 | 0.069576 | 0.019867 | south | N | 0.019867 | 0
8927 | LGE_GT20 | 2 | 153 | -0.039103 | south | N | -0.11271 | -0.019867 | -0.10191 | 0.069576 | 0.019867 | south | N | 0.019867 | 0
8928 | LGE_STG0 | 3 | 100 | -0.039103 | south | N | -0.11271 | -0.019867 | -0.10191 | 0.069576 | 0.019867 | south | N | 0.019867 | 0
8930 | ICPGN10A | 1 | 145 | -0.039103 | south | N | -0.11271 | -0.019867 | -0.10191 | 0.069576 | 0.019867 | south | N | 0.019867 | 0
8931 | ICPGN20A | 2 | 147 | -0.039103 | south | N | -0.11271 | -0.019867 | -0.10191 | 0.069576 | 0.019867 | south | N | 0.019867 | 0
8932 | ICPGN30A | 3 | 127 | -0.039103 | south | N | -0.11271 | -0.019867 | -0.10191 | 0.069576 | 0.019867 | south | N | 0.019867 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.036509 | south | Y | -0.11011 | -0.017273 | -0.099318 | 0.07217 | 0.017273 | south | N | 0.017273 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.036509 | south | Y | -0.11011 | -0.017273 | -0.099318 | 0.07217 | 0.017273 | south | N | 0.017273 | 0
8935 | FGNTS201 | 3 | 173 | -0.036509 | south | Y | -0.11011 | -0.017273 | -0.099318 | 0.07217 | 0.017273 | south | N | 0.017273 | 0
8936 | MVGN#1 | 1 | 207 | -0.036937 | south | Y | -0.11054 | -0.017701 | -0.099746 | 0.071742 | 0.017701 | south | N | 0.017701 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.036937 | south | Y | -0.11054 | -0.017701 | -0.099746 | 0.071742 | 0.017701 | south | N | 0.017701 | 0
8938 | MVGN#3 | 3 | 242 | -0.036937 | south | Y | -0.11054 | -0.017701 | -0.099746 | 0.071742 | 0.017701 | south | N | 0.017701 | 0
8981 | HECN1 | 1 | 144 | -0.03694 | south | Y | -0.11054 | -0.017704 | -0.099749 | 0.071739 | 0.017704 | south | N | 0.017704 | 0
8982 | HECN2 | 2 | 144 | -0.03694 | south | Y | -0.11054 | -0.017704 | -0.099749 | 0.071739 | 0.017704 | south | N | 0.017704 | 0
8983 | HECN3 | 3 | 171 | -0.03694 | south | Y | -0.11054 | -0.017704 | -0.099749 | 0.071739 | 0.017704 | south | N | 0.017704 | 0
9000 | DECKR_G1 | 1 | 310 | 0.000294 | south | Y | -0.07331 | 0.01953 | -0.062515 | 0.10897 | 0.01953 | south | N | 0.01953 | 0
9001 | DECKR_G2 | 2 | 413 | 0.000294 | south | Y | -0.07331 | 0.01953 | -0.062515 | 0.10897 | 0.01953 | south | N | 0.01953 | 0
9002 | DECKR_G3 | 3 | 42 | 0.00113 | south | Y | -0.072474 | 0.020366 | -0.061679 | 0.10981 | 0.020366 | south | N | 0.020366 | 0
9003 | DECKR_G4 | 4 | 44 | 0.00113 | south | Y | -0.072474 | 0.020366 | -0.061679 | 0.10981 | 0.020366 | south | N | 0.020366 | 0
9004 | DECKR_G5 | 5 | 44 | 0.00113 | south | Y | -0.072474 | 0.020366 | -0.061679 | 0.10981 | 0.020366 | south | N | 0.020366 | 0
9005 | DECKR_G6 | 6 | 47 | 0.00113 | south | Y | -0.072474 | 0.020366 | -0.061679 | 0.10981 | 0.020366 | south | N | 0.020366 | 0
9016 | SANDH_G1 | 1 | 49 | -0.000841 | south | Y | -0.074445 | 0.018395 | -0.06365 | 0.10784 | 0.018395 | south | N | 0.018395 | 0
9017 | SANDH_G2 | 2 | 46 | -0.000841 | south | Y | -0.074445 | 0.018395 | -0.06365 | 0.10784 | 0.018395 | south | N | 0.018395 | 0
9018 | SANDH_G3 | 3 | 46 | -0.000841 | south | Y | -0.074445 | 0.018395 | -0.06365 | 0.10784 | 0.018395 | south | N | 0.018395 | 0
9019 | SANDH_G4 | 4 | 47 | -0.000841 | south | Y | -0.074445 | 0.018395 | -0.06365 | 0.10784 | 0.018395 | south | N | 0.018395 | 0
9020 | SANDHG5A | 5A | 154 | -0.000841 | south | Y | -0.074445 | 0.018395 | -0.06365 | 0.10784 | 0.018395 | south | N | 0.018395 | 0
9021 | SANDHG5C | 5C | 148 | -0.000841 | south | Y | -0.074445 | 0.018395 | -0.06365 | 0.10784 | 0.018395 | south | N | 0.018395 | 0
9022 | SANDH_G6 | 6 | 48 | -0.000841 | south | Y | -0.074445 | 0.018395 | -0.06365 | 0.10784 | 0.018395 | south | N | 0.018395 | 0
9023 | SANDH_G7 | 7 | 48 | -0.000841 | south | Y | -0.074445 | 0.018395 | -0.06365 | 0.10784 | 0.018395 | south | N | 0.018395 | 0
11001 | NAV1CT | 1 | 70 | 0.062808 | west | Y | -0.010796 | 0.082044 | -6.2822e-07 | 0.17149 | 6.2822e-07 | west | N | 6.2822e-07 | 0
11009 | NAV2CT | 1 | 70 | 0.062808 | west | Y | -0.010796 | 0.082044 | -6.2822e-07 | 0.17149 | 6.2822e-07 | west | N | 6.2822e-07 | 0
11011 | NAV3ST | 1 | 92.8 | 0.062808 | west | Y | -0.010796 | 0.082044 | -6.2822e-07 | 0.17149 | 6.2822e-07 | west | N | 6.2822e-07 | 0
11012 | NAV4CT | 1 | 80 | 0.062808 | west | Y | -0.010796 | 0.082044 | -6.2822e-07 | 0.17149 | 6.2822e-07 | west | N | 6.2822e-07 | 0
11013 | NAV5CT | 1 | 80 | 0.062808 | west | Y | -0.010796 | 0.082044 | -6.2822e-07 | 0.17149 | 6.2822e-07 | west | N | 6.2822e-07 | 0
11014 | NAV6ST | 1 | 115 | 0.062808 | west | Y | -0.010796 | 0.082044 | -6.2822e-07 | 0.17149 | 6.2822e-07 | west | N | 6.2822e-07 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.062802 | west | Y | -0.010802 | 0.082038 | -6.6282e-06 | 0.17148 | 6.6282e-06 | west | N | 6.6282e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.062802 | west | Y | -0.010802 | 0.082038 | -6.6282e-06 | 0.17148 | 6.6282e-06 | west | N | 6.6282e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.062802 | west | Y | -0.010802 | 0.082038 | -6.6282e-06 | 0.17148 | 6.6282e-06 | west | N | 6.6282e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.062802 | west | Y | -0.010802 | 0.082038 | -6.6282e-06 | 0.17148 | 6.6282e-06 | west | N | 6.6282e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.062802 | west | Y | -0.010802 | 0.082038 | -6.6282e-06 | 0.17148 | 6.6282e-06 | west | N | 6.6282e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.062802 | west | Y | -0.010802 | 0.082038 | -6.6282e-06 | 0.17148 | 6.6282e-06 | west | N | 6.6282e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.063913 | west | Y | -0.0096905 | 0.083149 | 0.0011044 | 0.17259 | 0.0011044 | west | N | 0.0011044 | 0
11057 | CHAMPION | 1 | 126.5 | 0.063913 | west | Y | -0.0096905 | 0.083149 | 0.0011044 | 0.17259 | 0.0011044 | west | N | 0.0011044 | 0
11058 | PYRON_1G | 1 | 249 | 0.063913 | west | Y | -0.0096905 | 0.083149 | 0.0011044 | 0.17259 | 0.0011044 | west | N | 0.0011044 | 0
11059 | INADALE_ | 1 | 197 | 0.063913 | west | Y | -0.0096905 | 0.083149 | 0.0011044 | 0.17259 | 0.0011044 | west | N | 0.0011044 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.063352 | west | Y | -0.010252 | 0.082588 | 0.00054337 | 0.17203 | 0.00054337 | west | N | 0.00054337 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.063352 | west | Y | -0.010252 | 0.082588 | 0.00054337 | 0.17203 | 0.00054337 | west | N | 0.00054337 | 0
11147 | NOTREES_ | 1 | 149 | 0.062317 | west | Y | -0.011287 | 0.081553 | -0.00049163 | 0.171 | 0.00049163 | west | N | 0.00049163 | 0
11309 | BULLCREK | 1 | 180 | 0.063246 | west | Y | -0.010358 | 0.082482 | 0.00043737 | 0.17193 | 0.00043737 | west | N | 0.00043737 | 0
11310 | BULLCREK | 1 | 180 | 0.063246 | west | Y | -0.010358 | 0.082482 | 0.00043737 | 0.17193 | 0.00043737 | west | N | 0.00043737 | 0
11320 | COYOTE_1 | 1 | 225 | 0.063214 | west | Y | -0.01039 | 0.08245 | 0.00040537 | 0.17189 | 0.00040537 | west | N | 0.00040537 | 0
11415 | LORAINE_ | 1 | 125 | 0.063682 | west | Y | -0.0099215 | 0.082918 | 0.00087337 | 0.17236 | 0.00087337 | west | N | 0.00087337 | 0
11416 | LORAINE_ | 1 | 125 | 0.063682 | west | Y | -0.0099215 | 0.082918 | 0.00087337 | 0.17236 | 0.00087337 | west | N | 0.00087337 | 0
11691 | KMICHICT | 1 | 140 | 0.071268 | north | N | -0.0023355 | 0.090504 | 0.0084594 | 0.17995 | 0.0023355 | North | N | 0.0023355 | 0
11692 | KMICHICT | 2 | 141 | 0.071268 | north | N | -0.0023355 | 0.090504 | 0.0084594 | 0.17995 | 0.0023355 | North | N | 0.0023355 | 0
11693 | KMICHIST | 3 | 309 | 0.071268 | north | N | -0.0023355 | 0.090504 | 0.0084594 | 0.17995 | 0.0023355 | North | N | 0.0023355 | 0
11694 | KMICHICT | 4 | 143 | 0.071268 | north | N | -0.0023355 | 0.090504 | 0.0084594 | 0.17995 | 0.0023355 | North | N | 0.0023355 | 0
11695 | KMICHICT | 5 | 144 | 0.071268 | north | N | -0.0023355 | 0.090504 | 0.0084594 | 0.17995 | 0.0023355 | North | N | 0.0023355 | 0
11696 | KMICHIST | 6 | 310 | 0.071268 | north | N | -0.0023355 | 0.090504 | 0.0084594 | 0.17995 | 0.0023355 | North | N | 0.0023355 | 0
12322 | ENNSTRAC | 1 | 196 | 0.070349 | north | Y | -0.0032545 | 0.089585 | 0.0075404 | 0.17903 | 0.0032545 | North | N | 0.0032545 | 0
12323 | ENNSTRAC | 2 | 111 | 0.070349 | north | Y | -0.0032545 | 0.089585 | 0.0075404 | 0.17903 | 0.0032545 | North | N | 0.0032545 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.070879 | north | N | -0.0027245 | 0.090115 | 0.0080704 | 0.17956 | 0.0027245 | North | N | 0.0027245 | 0
12411 | FPLEFR1A | 1 | 161 | 0.0721 | north | Y | -0.0015035 | 0.091336 | 0.0092914 | 0.18078 | 0.0015035 | North | N | 0.0015035 | 0
12412 | FPLEFR1B | 2 | 164 | 0.0721 | north | Y | -0.0015035 | 0.091336 | 0.0092914 | 0.18078 | 0.0015035 | North | N | 0.0015035 | 0
12413 | FPLEFR1C | 3 | 164 | 0.0721 | north | Y | -0.0015035 | 0.091336 | 0.0092914 | 0.18078 | 0.0015035 | North | N | 0.0015035 | 0
12414 | FPLEFR1S | 4 | 414 | 0.0721 | north | Y | -0.0015035 | 0.091336 | 0.0092914 | 0.18078 | 0.0015035 | North | N | 0.0015035 | 0
12421 | FPLEFR2A | 1 | 162 | 0.0721 | north | Y | -0.0015035 | 0.091336 | 0.0092914 | 0.18078 | 0.0015035 | North | N | 0.0015035 | 0
12422 | FPLEFR2B | 2 | 161 | 0.0721 | north | Y | -0.0015035 | 0.091336 | 0.0092914 | 0.18078 | 0.0015035 | North | N | 0.0015035 | 0
12423 | FPLEFR2C | 3 | 163 | 0.0721 | north | Y | -0.0015035 | 0.091336 | 0.0092914 | 0.18078 | 0.0015035 | North | N | 0.0015035 | 0
12424 | FPLEFR2S | 4 | 409 | 0.0721 | north | Y | -0.0015035 | 0.091336 | 0.0092914 | 0.18078 | 0.0015035 | North | N | 0.0015035 | 0
12440 | PARKD_1S | 1 | 0 | 0.071533 | north | N | -0.0020705 | 0.090769 | 0.0087244 | 0.18021 | 0.0020705 | North | N | 0.0020705 | 0
12449 | PARKD_2S | 1 | 0 | 0.071533 | north | N | -0.0020705 | 0.090769 | 0.0087244 | 0.18021 | 0.0020705 | North | N | 0.0020705 | 0
13116 | TGATEWAY | 1 | 148 | 0.074371 | north | N | 0.00076749 | 0.093607 | 0.011562 | 0.18305 | 0.00076749 | North | N | 0.00076749 | 0
13117 | TGATEWAY | 2 | 130 | 0.074371 | north | N | 0.00076749 | 0.093607 | 0.011562 | 0.18305 | 0.00076749 | North | N | 0.00076749 | 0
13118 | TGATEWAY | 3 | 145 | 0.074371 | north | N | 0.00076749 | 0.093607 | 0.011562 | 0.18305 | 0.00076749 | North | N | 0.00076749 | 0
13119 | TGATEWAY | 4 | 399 | 0.074371 | north | N | 0.00076749 | 0.093607 | 0.011562 | 0.18305 | 0.00076749 | North | N | 0.00076749 | 0
13131 | CALFREST | 1 | 150.7 | 0.077738 | north | Y | 0.0041345 | 0.096974 | 0.014929 | 0.18642 | 0.0041345 | North | N | 0.0041345 | 0
13132 | CALFREST | 2 | 151 | 0.077738 | north | Y | 0.0041345 | 0.096974 | 0.014929 | 0.18642 | 0.0041345 | North | N | 0.0041345 | 0
13133 | CALFREST | 3 | 177.4 | 0.077738 | north | Y | 0.0041345 | 0.096974 | 0.014929 | 0.18642 | 0.0041345 | North | N | 0.0041345 | 0
13134 | CALFREST | 4 | 151.5 | 0.077609 | north | Y | 0.0040055 | 0.096845 | 0.0148 | 0.18629 | 0.0040055 | North | N | 0.0040055 | 0
13135 | CALFREST | 5 | 152.3 | 0.077609 | north | Y | 0.0040055 | 0.096845 | 0.0148 | 0.18629 | 0.0040055 | North | N | 0.0040055 | 0
13136 | CALFREST | 6 | 177.5 | 0.077609 | north | Y | 0.0040055 | 0.096845 | 0.0148 | 0.18629 | 0.0040055 | North | N | 0.0040055 | 0
13432 | SANDOW_5 | 5 | 581 | 0.018966 | south | Y | -0.054638 | 0.038202 | -0.043843 | 0.12765 | 0.038202 | south | N | 0.038202 | 0
13691 | OAKGROVE | 1 | 855 | 0.091607 | north | Y | 0.018003 | 0.11084 | 0.028798 | 0.20029 | 0.018003 | North | N | 0.018003 | 0
13692 | OAKGROVE | 2 | 855 | 0.091607 | north | Y | 0.018003 | 0.11084 | 0.028798 | 0.20029 | 0.018003 | North | N | 0.018003 | 0
32798 | BRYN_TAM | 1 | 32 | 0.097791 | north | N | 0.024187 | 0.11703 | 0.034982 | 0.20647 | 0.024187 | North | N | 0.024187 | 0
32883 | BRYN_DNS | 1 | 48 | 0.095389 | north | Y | 0.021785 | 0.11463 | 0.03258 | 0.20407 | 0.021785 | North | N | 0.021785 | 0
32884 | BRYN_DNS | 1 | 46 | 0.095389 | north | Y | 0.021785 | 0.11463 | 0.03258 | 0.20407 | 0.021785 | North | N | 0.021785 | 0
32886 | BRYN_ATK | MB | 12 | 0.097579 | north | Y | 0.023975 | 0.11682 | 0.03477 | 0.20626 | 0.023975 | North | N | 0.023975 | 0
32887 | BRYN_ATK | MB | 51 | 0.097579 | north | Y | 0.023975 | 0.11682 | 0.03477 | 0.20626 | 0.023975 | North | N | 0.023975 | 0
32888 | BRYN_ATK | 1 | 17 | 0.097579 | north | Y | 0.023975 | 0.11682 | 0.03477 | 0.20626 | 0.023975 | North | N | 0.023975 | 0
32890 | BRYN_ATK | MB | 22 | 0.097579 | north | Y | 0.023975 | 0.11682 | 0.03477 | 0.20626 | 0.023975 | North | N | 0.023975 | 0
32891 | BRYN_ATK | MB | 25 | 0.097579 | north | Y | 0.023975 | 0.11682 | 0.03477 | 0.20626 | 0.023975 | North | N | 0.023975 | 0
32892 | BRYN_DNS | 1 | 105 | 0.095389 | north | Y | 0.021785 | 0.11463 | 0.03258 | 0.20407 | 0.021785 | North | N | 0.021785 | 0
36998 | RDCNYNG1 | 1 | 84 | 0.063568 | west | Y | -0.010036 | 0.082804 | 0.00075937 | 0.17225 | 0.00075937 | west | N | 0.00075937 | 0
38332 | WDWRDU2 | 1 | 80 | 0.058632 | west | Y | -0.014972 | 0.077868 | -0.0041766 | 0.16731 | 0.0041766 | west | N | 0.0041766 | 0
38437 | TNSRBNMS | 1 | 150 | 0.0586 | west | Y | -0.015004 | 0.077836 | -0.0042086 | 0.16728 | 0.0042086 | west | N | 0.0042086 | 0
38438 | TNSRBNMS | 1 | 150 | 0.0586 | west | Y | -0.015004 | 0.077836 | -0.0042086 | 0.16728 | 0.0042086 | west | N | 0.0042086 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.1104 | houston | N | -0.184 | -0.091165 | -0.17321 | -0.0017215 | 0.0017215 | houston | N | 0.0017215 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.1104 | houston | N | -0.184 | -0.091165 | -0.17321 | -0.0017215 | 0.0017215 | houston | N | 0.0017215 | 0
38600 | TNBP_CGN | 5 | 53 | -0.1104 | houston | N | -0.184 | -0.091165 | -0.17321 | -0.0017215 | 0.0017215 | houston | N | 0.0017215 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.1104 | houston | N | -0.184 | -0.091165 | -0.17321 | -0.0017215 | 0.0017215 | houston | N | 0.0017215 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.1104 | houston | N | -0.184 | -0.091165 | -0.17321 | -0.0017215 | 0.0017215 | houston | N | 0.0017215 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.1104 | houston | N | -0.184 | -0.091165 | -0.17321 | -0.0017215 | 0.0017215 | houston | N | 0.0017215 | 0
38614 | TNBPAMCG | 4 | 96 | -0.1104 | houston | N | -0.184 | -0.091165 | -0.17321 | -0.0017215 | 0.0017215 | houston | N | 0.0017215 | 0
38615 | TNBPAMCG | 1 | 244 | -0.1104 | houston | N | -0.184 | -0.091165 | -0.17321 | -0.0017215 | 0.0017215 | houston | N | 0.0017215 | 0
38690 | TNBP_CGN | 3 | 40 | -0.1104 | houston | N | -0.184 | -0.091165 | -0.17321 | -0.0017215 | 0.0017215 | houston | N | 0.0017215 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.11036 | houston | N | -0.18396 | -0.091121 | -0.17317 | -0.0016775 | 0.0016775 | houston | N | 0.0016775 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.11036 | houston | N | -0.18396 | -0.091121 | -0.17317 | -0.0016775 | 0.0016775 | houston | N | 0.0016775 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.11036 | houston | N | -0.18396 | -0.091121 | -0.17317 | -0.0016775 | 0.0016775 | houston | N | 0.0016775 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.11036 | houston | N | -0.18396 | -0.091121 | -0.17317 | -0.0016775 | 0.0016775 | houston | N | 0.0016775 | 0
39470 | TNDOWCGN | 1 | 32 | -0.11036 | houston | N | -0.18396 | -0.091122 | -0.17317 | -0.0016785 | 0.0016785 | houston | N | 0.0016785 | 0
39480 | TNDOWCGN | 1 | 30 | -0.11036 | houston | N | -0.18396 | -0.091122 | -0.17317 | -0.0016785 | 0.0016785 | houston | N | 0.0016785 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.083492 | houston | N | -0.1571 | -0.064256 | -0.1463 | 0.025187 | 0.025187 | houston | N | 0.025187 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.083492 | houston | N | -0.1571 | -0.064256 | -0.1463 | 0.025187 | 0.025187 | houston | N | 0.025187 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.083492 | houston | N | -0.1571 | -0.064256 | -0.1463 | 0.025187 | 0.025187 | houston | N | 0.025187 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.083492 | houston | N | -0.1571 | -0.064256 | -0.1463 | 0.025187 | 0.025187 | houston | N | 0.025187 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.091607 | north | Y | 0.018003 | 0.11084 | 0.028798 | 0.20029 | 0.018003 | North | N | 0.018003 | 0
39970 | TNTNPONE | 1 | 153 | 0.091607 | north | Y | 0.018003 | 0.11084 | 0.028798 | 0.20029 | 0.018003 | North | N | 0.018003 | 0
48500 | APD_GT1_ | 1 | 136 | -0.12763 | houston | N | -0.20123 | -0.10839 | -0.19044 | -0.018948 | 0.018948 | houston | N | 0.018948 | 0
48510 | AK_GT1__ | 1 | 33 | -0.10067 | houston | N | -0.17428 | -0.081436 | -0.16348 | 0.0080075 | 0.0080075 | houston | N | 0.0080075 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.13234 | houston | Y | -0.20594 | -0.1131 | -0.19515 | -0.023658 | 0.023658 | houston | N | 0.023658 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.13234 | houston | Y | -0.20594 | -0.1131 | -0.19515 | -0.023658 | 0.023658 | houston | N | 0.023658 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.13234 | houston | Y | -0.20594 | -0.1131 | -0.19515 | -0.023658 | 0.023658 | houston | N | 0.023658 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.13234 | houston | Y | -0.20594 | -0.1131 | -0.19515 | -0.023658 | 0.023658 | houston | N | 0.023658 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.084304 | houston | N | -0.15791 | -0.065068 | -0.14711 | 0.024375 | 0.024375 | houston | N | 0.024375 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.084304 | houston | N | -0.15791 | -0.065068 | -0.14711 | 0.024375 | 0.024375 | houston | N | 0.024375 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.090864 | houston | N | -0.16447 | -0.071628 | -0.15367 | 0.017815 | 0.017815 | houston | N | 0.017815 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.090864 | houston | N | -0.16447 | -0.071628 | -0.15367 | 0.017815 | 0.017815 | houston | N | 0.017815 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.090864 | houston | N | -0.16447 | -0.071628 | -0.15367 | 0.017815 | 0.017815 | houston | N | 0.017815 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.12241 | houston | N | -0.19601 | -0.10317 | -0.18522 | -0.013732 | 0.013732 | houston | N | 0.013732 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.12241 | houston | N | -0.19601 | -0.10317 | -0.18522 | -0.013732 | 0.013732 | houston | N | 0.013732 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.12241 | houston | N | -0.19601 | -0.10317 | -0.18522 | -0.013732 | 0.013732 | houston | N | 0.013732 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.12241 | houston | N | -0.19601 | -0.10317 | -0.18522 | -0.013732 | 0.013732 | houston | N | 0.013732 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.12812 | houston | N | -0.20173 | -0.10889 | -0.19093 | -0.019444 | 0.019444 | houston | N | 0.019444 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.12812 | houston | N | -0.20173 | -0.10889 | -0.19093 | -0.019444 | 0.019444 | houston | N | 0.019444 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.12087 | houston | N | -0.19447 | -0.10163 | -0.18368 | -0.012191 | 0.012191 | houston | N | 0.012191 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.12087 | houston | N | -0.19447 | -0.10163 | -0.18368 | -0.012191 | 0.012191 | houston | N | 0.012191 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.12087 | houston | N | -0.19447 | -0.10163 | -0.18368 | -0.012191 | 0.012191 | houston | N | 0.012191 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.12087 | houston | N | -0.19447 | -0.10163 | -0.18368 | -0.012191 | 0.012191 | houston | N | 0.012191 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.12087 | houston | N | -0.19447 | -0.10163 | -0.18368 | -0.012191 | 0.012191 | houston | N | 0.012191 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.14147 | houston | Y | -0.21508 | -0.12224 | -0.20428 | -0.032793 | 0.032793 | houston | N | 0.032793 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.138 | houston | Y | -0.2116 | -0.11876 | -0.2008 | -0.029316 | 0.029316 | houston | N | 0.029316 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.14647 | houston | Y | -0.22008 | -0.12724 | -0.20928 | -0.037794 | 0.037794 | houston | N | 0.037794 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.14647 | houston | Y | -0.22008 | -0.12724 | -0.20928 | -0.037794 | 0.037794 | houston | N | 0.037794 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.14647 | houston | Y | -0.22008 | -0.12724 | -0.20928 | -0.037794 | 0.037794 | houston | N | 0.037794 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.18369 | houston | N | -0.25729 | -0.16445 | -0.2465 | -0.075012 | 0.075012 | houston | N | 0.075012 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.12872 | houston | N | -0.20233 | -0.10949 | -0.19153 | -0.020043 | 0.020043 | houston | N | 0.020043 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.12872 | houston | N | -0.20233 | -0.10949 | -0.19153 | -0.020043 | 0.020043 | houston | N | 0.020043 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.15145 | houston | N | -0.22506 | -0.13222 | -0.21426 | -0.042774 | 0.042774 | houston | N | 0.042774 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.15145 | houston | N | -0.22506 | -0.13222 | -0.21426 | -0.042774 | 0.042774 | houston | N | 0.042774 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.15145 | houston | N | -0.22506 | -0.13222 | -0.21426 | -0.042774 | 0.042774 | houston | N | 0.042774 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.15145 | houston | N | -0.22506 | -0.13222 | -0.21426 | -0.042774 | 0.042774 | houston | N | 0.042774 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.12824 | houston | N | -0.20185 | -0.10901 | -0.19105 | -0.019565 | 0.019565 | houston | N | 0.019565 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.12824 | houston | N | -0.20185 | -0.10901 | -0.19105 | -0.019565 | 0.019565 | houston | N | 0.019565 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.12824 | houston | N | -0.20185 | -0.10901 | -0.19105 | -0.019565 | 0.019565 | houston | N | 0.019565 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.12824 | houston | N | -0.20185 | -0.10901 | -0.19105 | -0.019565 | 0.019565 | houston | N | 0.019565 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.13263 | houston | N | -0.20623 | -0.11339 | -0.19544 | -0.023951 | 0.023951 | houston | N | 0.023951 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.13263 | houston | N | -0.20623 | -0.11339 | -0.19544 | -0.023951 | 0.023951 | houston | N | 0.023951 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.13263 | houston | N | -0.20623 | -0.11339 | -0.19544 | -0.023951 | 0.023951 | houston | N | 0.023951 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.13263 | houston | N | -0.20623 | -0.11339 | -0.19544 | -0.023951 | 0.023951 | houston | N | 0.023951 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.13263 | houston | N | -0.20623 | -0.11339 | -0.19544 | -0.023951 | 0.023951 | houston | N | 0.023951 | 0
48651 | EP_1_2 | 1 | 5 | -0.13438 | houston | N | -0.20799 | -0.11515 | -0.19719 | -0.025705 | 0.025705 | houston | N | 0.025705 | 0
48651 | EP_1_2 | 2 | 21 | -0.13438 | houston | N | -0.20799 | -0.11515 | -0.19719 | -0.025705 | 0.025705 | houston | N | 0.025705 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.085332 | north | N | 0.011728 | 0.10457 | 0.022523 | 0.19401 | 0.011728 | North | N | 0.011728 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.085332 | north | N | 0.011728 | 0.10457 | 0.022523 | 0.19401 | 0.011728 | North | N | 0.011728 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.085332 | north | N | 0.011728 | 0.10457 | 0.022523 | 0.19401 | 0.011728 | North | N | 0.011728 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.085332 | north | N | 0.011728 | 0.10457 | 0.022523 | 0.19401 | 0.011728 | North | N | 0.011728 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.13647 | houston | Y | -0.21007 | -0.11723 | -0.19928 | -0.027789 | 0.027789 | houston | N | 0.027789 | 0
48691 | GBY_7374 | A | 46 | -0.1082 | houston | Y | -0.18181 | -0.088966 | -0.17101 | 0.00047749 | 0.00047749 | houston | N | 0.00047749 | 0
48691 | GBY_7374 | B | 46 | -0.1082 | houston | Y | -0.18181 | -0.088966 | -0.17101 | 0.00047749 | 0.00047749 | houston | N | 0.00047749 | 0
48692 | GBY_8182 | C | 46 | -0.1082 | houston | Y | -0.18181 | -0.088966 | -0.17101 | 0.00047749 | 0.00047749 | houston | N | 0.00047749 | 0
48692 | GBY_8182 | D | 55 | -0.1082 | houston | Y | -0.18181 | -0.088966 | -0.17101 | 0.00047749 | 0.00047749 | houston | N | 0.00047749 | 0
48693 | GBY_8384 | E | 55 | -0.1082 | houston | Y | -0.18181 | -0.088966 | -0.17101 | 0.00047749 | 0.00047749 | houston | N | 0.00047749 | 0
48693 | GBY_8384 | F | 54 | -0.1082 | houston | Y | -0.18181 | -0.088966 | -0.17101 | 0.00047749 | 0.00047749 | houston | N | 0.00047749 | 0
48721 | LEG_1___ | 1 | 827 | 0.086419 | north | Y | 0.012815 | 0.10566 | 0.02361 | 0.1951 | 0.012815 | North | N | 0.012815 | 0
48722 | LEG_2___ | 2 | 819 | 0.086419 | north | Y | 0.012815 | 0.10566 | 0.02361 | 0.1951 | 0.012815 | North | N | 0.012815 | 0
48730 | MNS_GT | 1 | 46.1 | -0.098451 | houston | N | -0.17205 | -0.079215 | -0.16126 | 0.010228 | 0.010228 | houston | N | 0.010228 | 0
48731 | CBE_GT1 | 1 | 76 | -0.057613 | houston | Y | -0.13122 | -0.038377 | -0.12042 | 0.051066 | 0.038377 | south | Y | 0.051066 | 0.96444
48732 | CBE_GT2 | 1 | 76 | -0.057613 | houston | Y | -0.13122 | -0.038377 | -0.12042 | 0.051066 | 0.038377 | south | Y | 0.051066 | 0.96444
48733 | CBE_ST12 | 1 | 105 | -0.057613 | houston | Y | -0.13122 | -0.038377 | -0.12042 | 0.051066 | 0.038377 | south | Y | 0.051066 | 1.3324
48734 | CBE_GT3 | 1 | 74 | -0.057613 | houston | Y | -0.13122 | -0.038377 | -0.12042 | 0.051066 | 0.038377 | south | Y | 0.051066 | 0.93906
48735 | CBE_GT4 | 1 | 74 | -0.057613 | houston | Y | -0.13122 | -0.038377 | -0.12042 | 0.051066 | 0.038377 | south | Y | 0.051066 | 0.93906
48736 | CBE_ST34 | 1 | 102 | -0.057613 | houston | Y | -0.13122 | -0.038377 | -0.12042 | 0.051066 | 0.038377 | south | Y | 0.051066 | 1.2944
48740 | PSG_GN2_ | 1 | 180 | -0.12844 | houston | N | -0.20204 | -0.1092 | -0.19125 | -0.019758 | 0.019758 | houston | N | 0.019758 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.12844 | houston | N | -0.20204 | -0.1092 | -0.19125 | -0.019758 | 0.019758 | houston | N | 0.019758 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.12844 | houston | N | -0.20204 | -0.1092 | -0.19125 | -0.019758 | 0.019758 | houston | N | 0.019758 | 0
48761 | PR_GT1__ | 1 | 35 | -0.12672 | houston | N | -0.20032 | -0.10748 | -0.18953 | -0.01804 | 0.01804 | houston | N | 0.01804 | 0
48772 | PHR_GN2_ | MB | 459 | -0.11795 | houston | Y | -0.19155 | -0.098714 | -0.18076 | -0.0092705 | 0.0092705 | houston | N | 0.0092705 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.1305 | houston | N | -0.2041 | -0.11126 | -0.19331 | -0.021819 | 0.021819 | houston | N | 0.021819 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.1305 | houston | N | -0.2041 | -0.11126 | -0.19331 | -0.021819 | 0.021819 | houston | N | 0.021819 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.1305 | houston | N | -0.2041 | -0.11126 | -0.19331 | -0.021819 | 0.021819 | houston | N | 0.021819 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.1305 | houston | N | -0.2041 | -0.11126 | -0.19331 | -0.021819 | 0.021819 | houston | N | 0.021819 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.1305 | houston | N | -0.2041 | -0.11126 | -0.19331 | -0.021819 | 0.021819 | houston | N | 0.021819 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.1305 | houston | N | -0.2041 | -0.11126 | -0.19331 | -0.021819 | 0.021819 | houston | N | 0.021819 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.1305 | houston | N | -0.2041 | -0.11126 | -0.19331 | -0.021819 | 0.021819 | houston | N | 0.021819 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.18369 | houston | N | -0.25729 | -0.16445 | -0.2465 | -0.075012 | 0.075012 | houston | N | 0.075012 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.18369 | houston | N | -0.25729 | -0.16445 | -0.2465 | -0.075012 | 0.075012 | houston | N | 0.075012 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.18369 | houston | N | -0.25729 | -0.16445 | -0.2465 | -0.075012 | 0.075012 | houston | N | 0.075012 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.18369 | houston | N | -0.25729 | -0.16445 | -0.2465 | -0.075012 | 0.075012 | houston | N | 0.075012 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.13155 | houston | N | -0.20515 | -0.11231 | -0.19436 | -0.022869 | 0.022869 | houston | N | 0.022869 | 0
48820 | SHELLG1_ | 1 | 71 | -0.12987 | houston | N | -0.20348 | -0.11064 | -0.19268 | -0.021194 | 0.021194 | houston | N | 0.021194 | 0
48821 | SHELLG2 | 2 | 72 | -0.12987 | houston | N | -0.20348 | -0.11064 | -0.19268 | -0.021194 | 0.021194 | houston | N | 0.021194 | 0
48822 | SHELLG3_ | 1 | 39 | -0.12987 | houston | N | -0.20348 | -0.11064 | -0.19268 | -0.021194 | 0.021194 | houston | N | 0.021194 | 0
48822 | SHELLG3_ | 2 | 30 | -0.12987 | houston | N | -0.20348 | -0.11064 | -0.19268 | -0.021194 | 0.021194 | houston | N | 0.021194 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.12491 | houston | N | -0.19851 | -0.10567 | -0.18771 | -0.016227 | 0.016227 | houston | N | 0.016227 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.12491 | houston | N | -0.19851 | -0.10567 | -0.18771 | -0.016227 | 0.016227 | houston | N | 0.016227 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.12821 | houston | N | -0.20181 | -0.10897 | -0.19102 | -0.019529 | 0.019529 | houston | N | 0.019529 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.12794 | houston | Y | -0.20155 | -0.10871 | -0.19075 | -0.019264 | 0.019264 | houston | N | 0.019264 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.12787 | houston | Y | -0.20147 | -0.10863 | -0.19067 | -0.019187 | 0.019187 | houston | N | 0.019187 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.12816 | houston | Y | -0.20176 | -0.10892 | -0.19097 | -0.01948 | 0.01948 | houston | N | 0.01948 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.12831 | houston | Y | -0.20192 | -0.10908 | -0.19112 | -0.019635 | 0.019635 | houston | N | 0.019635 | 0
48855 | SRB_GT21 | B2 | 12 | -0.12782 | houston | Y | -0.20142 | -0.10858 | -0.19063 | -0.01914 | 0.01914 | houston | N | 0.01914 | 0
48855 | SRB_GT21 | MB | 18 | -0.12782 | houston | Y | -0.20142 | -0.10858 | -0.19063 | -0.01914 | 0.01914 | houston | N | 0.01914 | 0
48865 | TECO_GT1 | 1 | 50 | -0.10481 | houston | Y | -0.17842 | -0.085576 | -0.16762 | 0.0038675 | 0.0038675 | houston | N | 0.0038675 | 0
48873 | THW_ST3_ | 3 | 104 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48874 | THW_ST4_ | 4 | 104 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48875 | THW_3132 | A | 54 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48875 | THW_3132 | B | 53 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48877 | THW_3334 | C | 54 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48877 | THW_3334 | D | 57 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48879 | THW_4142 | E | 54 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48879 | THW_4142 | F | 54 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48881 | THW_4344 | G | 58 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48881 | THW_4344 | H | 58 | -0.089281 | houston | Y | -0.16288 | -0.070045 | -0.15209 | 0.019398 | 0.019398 | houston | N | 0.019398 | 0
48883 | THW_GT1_ | B2 | 12 | -0.089959 | houston | Y | -0.16356 | -0.070723 | -0.15277 | 0.01872 | 0.01872 | houston | N | 0.01872 | 0
48885 | THW_5152 | A | 56 | -0.11132 | houston | Y | -0.18492 | -0.092085 | -0.17413 | -0.0026415 | 0.0026415 | houston | N | 0.0026415 | 0
48885 | THW_5152 | B | 59 | -0.11132 | houston | Y | -0.18492 | -0.092085 | -0.17413 | -0.0026415 | 0.0026415 | houston | N | 0.0026415 | 0
48886 | THW_5354 | C | 56 | -0.11132 | houston | Y | -0.18492 | -0.092085 | -0.17413 | -0.0026415 | 0.0026415 | houston | N | 0.0026415 | 0
48886 | THW_5354 | D | 56 | -0.11132 | houston | Y | -0.18492 | -0.092085 | -0.17413 | -0.0026415 | 0.0026415 | houston | N | 0.0026415 | 0
48887 | THW_5556 | E | 59 | -0.11132 | houston | Y | -0.18492 | -0.092085 | -0.17413 | -0.0026415 | 0.0026415 | houston | N | 0.0026415 | 0
48887 | THW_5556 | F | 56 | -0.11132 | houston | Y | -0.18492 | -0.092085 | -0.17413 | -0.0026415 | 0.0026415 | houston | N | 0.0026415 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.065836 | houston | Y | -0.13944 | -0.0466 | -0.12864 | 0.042843 | 0.042843 | houston | N | 0.042843 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.088868 | houston | Y | -0.16247 | -0.069632 | -0.15168 | 0.019811 | 0.019811 | houston | N | 0.019811 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.088868 | houston | Y | -0.16247 | -0.069632 | -0.15168 | 0.019811 | 0.019811 | houston | N | 0.019811 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.088868 | houston | Y | -0.16247 | -0.069632 | -0.15168 | 0.019811 | 0.019811 | houston | N | 0.019811 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.088868 | houston | Y | -0.16247 | -0.069632 | -0.15168 | 0.019811 | 0.019811 | houston | N | 0.019811 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.088868 | houston | N | -0.16247 | -0.069632 | -0.15168 | 0.019811 | 0.019811 | houston | N | 0.019811 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.090811 | houston | Y | -0.16441 | -0.071575 | -0.15362 | 0.017868 | 0.017868 | houston | N | 0.017868 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.090811 | houston | Y | -0.16441 | -0.071575 | -0.15362 | 0.017868 | 0.017868 | houston | N | 0.017868 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.090811 | houston | Y | -0.16441 | -0.071575 | -0.15362 | 0.017868 | 0.017868 | houston | N | 0.017868 | 0
48929 | WAPGT21_ | B1 | 13 | -0.088868 | houston | Y | -0.16247 | -0.069632 | -0.15168 | 0.019811 | 0.019811 | houston | N | 0.019811 | 0
48940 | WARVUE_G | G1 | 12 | -0.13777 | houston | Y | -0.21137 | -0.11853 | -0.20058 | -0.029091 | 0.029091 | houston | N | 0.029091 | 0
49803 | EXN_15GT | 1 | 34 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49826 | EXN938GT | 5 | 45.9 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49828 | EXN941GT | 10 | 17.7 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49829 | EXN942GT | 11 | 20.4 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49830 | EXN943GT | 12 | 19.9 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49831 | EXN944GT | 13 | 35 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49832 | EXN945GT | 9 | 18 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49837 | EXN_GT | 4 | 85.4 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49838 | EXN_14GT | 14 | 148 | -0.13555 | houston | N | -0.20915 | -0.11631 | -0.19836 | -0.026871 | 0.026871 | houston | N | 0.026871 | 0
49851 | DOW17000 | 37 | 62 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49858 | DOW38100 | 31 | 71.4 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49859 | DOW38200 | 33 | 45 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49860 | DOW38300 | 32 | 101 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49862 | DOW39100 | 36 | 86 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49863 | DOW39200 | 35 | 88 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49865 | DOW41000 | 41 | 50 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49866 | DOW42000 | 42 | 18 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49869 | DOW49000 | 45 | 94 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49870 | DOW61000 | 61 | 70 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49871 | DOW62000 | 62 | 63 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49872 | DOW63000 | 63 | 72 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49873 | DOW64000 | 64 | 64.8 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49876 | DOW65000 | 65 | 101 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49877 | DOW66000 | 66 | 97 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49878 | DOW67000 | 67 | 103 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49882 | DOW81000 | 81 | 76 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49884 | DOW82000 | 82 | 80 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49885 | DOW83000 | 83 | 80 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
49886 | DOW84000 | 84 | 171 | -0.083881 | houston | N | -0.15748 | -0.064645 | -0.14669 | 0.024798 | 0.024798 | houston | N | 0.024798 | 0
58909 | PEARSALL | 1 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58909 | PEARSALL | 2 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58909 | PEARSALL | 3 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58909 | PEARSALL | 4 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58909 | PEARSALL | 5 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58909 | PEARSALL | 6 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58919 | PEARSALL | 1 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58919 | PEARSALL | 2 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58919 | PEARSALL | 3 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58919 | PEARSALL | 4 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58919 | PEARSALL | 5 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58919 | PEARSALL | 6 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58929 | PEARSALL | 1 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58929 | PEARSALL | 2 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58929 | PEARSALL | 3 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58929 | PEARSALL | 4 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58929 | PEARSALL | 5 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58929 | PEARSALL | 6 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58949 | PEARSALL | 1 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58949 | PEARSALL | 2 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58949 | PEARSALL | 3 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58949 | PEARSALL | 4 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58949 | PEARSALL | 5 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
58949 | PEARSALL | 6 | 8.4 | -0.022803 | south | Y | -0.096407 | -0.0035666 | -0.085612 | 0.085876 | 0.0035666 | south | N | 0.0035666 | 0
60000 | DSKY2 | 1 | 76.5 | 0.057112 | west | Y | -0.016492 | 0.076348 | -0.0056966 | 0.16579 | 0.0056966 | west | N | 0.0056966 | 0
60003 | KING_NE1 | 1 | 80 | 0.058695 | west | Y | -0.014909 | 0.077931 | -0.0041136 | 0.16737 | 0.0041136 | west | N | 0.0041136 | 0
60005 | KING_SE1 | 1 | 40 | 0.058695 | west | Y | -0.014909 | 0.077931 | -0.0041136 | 0.16737 | 0.0041136 | west | N | 0.0041136 | 0
60007 | KING_SW1 | 1 | 80 | 0.058951 | west | Y | -0.014653 | 0.078187 | -0.0038576 | 0.16763 | 0.0038576 | west | N | 0.0038576 | 0
60016 | WOODWRD1 | 1 | 80 | 0.05864 | west | Y | -0.014964 | 0.077876 | -0.0041686 | 0.16732 | 0.0041686 | west | N | 0.0041686 | 0
60017 | ORNNWP1 | 1 | 80 | 0.057325 | west | Y | -0.016279 | 0.076561 | -0.0054836 | 0.166 | 0.0054836 | west | N | 0.0054836 | 0
60018 | DSKY1 | 1 | 84 | 0.056894 | west | Y | -0.01671 | 0.07613 | -0.0059146 | 0.16557 | 0.0059146 | west | N | 0.0059146 | 0
60019 | KING_NW1 | 1 | 80 | 0.058951 | west | Y | -0.014653 | 0.078187 | -0.0038576 | 0.16763 | 0.0038576 | west | N | 0.0038576 | 0
60057 | CALLAHAN | 1 | 114 | -0.017321 | south | Y | -0.090925 | 0.0019154 | -0.08013 | 0.091358 | 0.0019154 | south | N | 0.0019154 | 0
60058 | BUFF_GAP | 1 | 120 | 0.063213 | west | Y | -0.010391 | 0.082449 | 0.00040437 | 0.17189 | 0.00040437 | west | N | 0.00040437 | 0
60060 | CIRELLO | 1 | 233 | 0.063213 | west | Y | -0.010391 | 0.082449 | 0.00040437 | 0.17189 | 0.00040437 | west | N | 0.00040437 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.063213 | west | Y | -0.010391 | 0.082449 | 0.00040437 | 0.17189 | 0.00040437 | west | N | 0.00040437 | 0
60066 | H_HOLLOW | 1 | 222 | -0.017321 | south | Y | -0.090925 | 0.0019154 | -0.08013 | 0.091358 | 0.0019154 | south | N | 0.0019154 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.017321 | south | Y | -0.090925 | 0.0019154 | -0.08013 | 0.091358 | 0.0019154 | south | N | 0.0019154 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.017321 | south | Y | -0.090925 | 0.0019154 | -0.08013 | 0.091358 | 0.0019154 | south | N | 0.0019154 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.017321 | south | Y | -0.090925 | 0.0019154 | -0.08013 | 0.091358 | 0.0019154 | south | N | 0.0019154 | 0
60074 | HORSH5 | 1 | 100 | -0.017321 | south | Y | -0.090925 | 0.0019154 | -0.08013 | 0.091358 | 0.0019154 | south | N | 0.0019154 | 0
60081 | WHRLWIND | 1 | 60 | 0.064395 | west | Y | -0.0092085 | 0.083631 | 0.0015864 | 0.17307 | 0.0015864 | west | N | 0.0015864 | 0
60201 | RIO DRCS | F | 0 | 0.015554 | south | N | -0.05805 | 0.03479 | -0.047255 | 0.12423 | 0.03479 | south | N | 0.03479 | 0
60202 | FRIEND_R | F | 0 | 0.050032 | west | N | -0.023572 | 0.069268 | -0.012777 | 0.15871 | 0.012777 | west | N | 0.012777 | 0
60203 | PRES0A | BT | 4.8 | 0.059895 | west | N | -0.013709 | 0.079131 | -0.0029136 | 0.16857 | 0.0029136 | west | N | 0.0029136 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.063863 | west | Y | -0.0097405 | 0.083099 | 0.0010544 | 0.17254 | 0.0010544 | west | N | 0.0010544 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.063863 | west | Y | -0.0097405 | 0.083099 | 0.0010544 | 0.17254 | 0.0010544 | west | N | 0.0010544 | 0
71057 | L_SWEETW | W1 | 135 | 0.063863 | west | Y | -0.0097405 | 0.083099 | 0.0010544 | 0.17254 | 0.0010544 | west | N | 0.0010544 | 0
71059 | L_SWEETW | W1 | 119 | 0.063863 | west | Y | -0.0097405 | 0.083099 | 0.0010544 | 0.17254 | 0.0010544 | west | N | 0.0010544 | 0
71060 | L_SWEETW | W1 | 105 | 0.063863 | west | Y | -0.0097405 | 0.083099 | 0.0010544 | 0.17254 | 0.0010544 | west | N | 0.0010544 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.063863 | west | Y | -0.0097405 | 0.083099 | 0.0010544 | 0.17254 | 0.0010544 | west | N | 0.0010544 | 0
76031 | L_GASCCR | W1 | 150 | 0.062829 | west | Y | -0.010775 | 0.082065 | 2.0372e-05 | 0.17151 | 2.0372e-05 | west | N | 2.0372e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.062699 | west | Y | -0.010905 | 0.081935 | -0.00010963 | 0.17138 | 0.00010963 | west | N | 0.00010963 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.062699 | west | Y | -0.010905 | 0.081935 | -0.00010963 | 0.17138 | 0.00010963 | west | N | 0.00010963 | 0
76096 | L_CAPRSI | W1 | 186 | 0.062699 | west | Y | -0.010905 | 0.081935 | -0.00010963 | 0.17138 | 0.00010963 | west | N | 0.00010963 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.062699 | west | Y | -0.010905 | 0.081935 | -0.00010963 | 0.17138 | 0.00010963 | west | N | 0.00010963 | 0
80003 | MILHWYS | F | 0 | -0.037245 | south | N | -0.11085 | -0.018009 | -0.10005 | 0.071434 | 0.018009 | south | N | 0.018009 | 0
80010 | EPLVT1 | F | 0 | -0.009932 | south | N | -0.083536 | 0.0093044 | -0.072741 | 0.098747 | 0.0093044 | south | N | 0.0093044 | 0
80012 | LAR | F | 0 | -0.02767 | south | N | -0.10127 | -0.0084336 | -0.090479 | 0.081009 | 0.0084336 | south | N | 0.0084336 | 0
80051 | FORPVCM0 | 8 | 28 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
80053 | FOR69CG0 | 10 | 74 | -0.043936 | south | N | -0.11754 | -0.0247 | -0.10674 | 0.064743 | 0.0247 | south | N | 0.0247 | 0
80080 | GWINDT11 | 1 | 94 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80080 | GWINDT11 | 2 | 41 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80080 | GWINDT11 | 3 | 38 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80080 | GWINDT11 | 4 | 19 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80081 | GWINDT21 | 1 | 94 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80081 | GWINDT21 | 2 | 36 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80081 | GWINDT21 | 3 | 43 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80081 | GWINDT21 | 4 | 22 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80137 | CSDR89 | 8 | 39 | -0.041297 | south | N | -0.1149 | -0.022061 | -0.10411 | 0.067382 | 0.022061 | south | N | 0.022061 | 0
80137 | CSDR89 | 9 | 15 | -0.041297 | south | N | -0.1149 | -0.022061 | -0.10411 | 0.067382 | 0.022061 | south | N | 0.022061 | 0
80138 | CSDR7 | 7 | 7 | -0.041297 | south | N | -0.1149 | -0.022061 | -0.10411 | 0.067382 | 0.022061 | south | N | 0.022061 | 0
80139 | CSDR56 | 5 | 15 | -0.041297 | south | N | -0.1149 | -0.022061 | -0.10411 | 0.067382 | 0.022061 | south | N | 0.022061 | 0
80139 | CSDR56 | 6 | 39 | -0.041297 | south | N | -0.1149 | -0.022061 | -0.10411 | 0.067382 | 0.022061 | south | N | 0.022061 | 0
80140 | CSDR11 | 11 | 39 | -0.041297 | south | N | -0.1149 | -0.022061 | -0.10411 | 0.067382 | 0.022061 | south | N | 0.022061 | 0
80180 | PNSCALT1 | 1 | 148 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80180 | PNSCALT1 | 2 | 50 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80181 | PNSCALT2 | 1 | 55 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80181 | PNSCALT2 | 2 | 50 | -0.037362 | south | Y | -0.11097 | -0.018126 | -0.10017 | 0.071317 | 0.018126 | south | N | 0.018126 | 0
80223 | REYSHR G | 1 | 12 | -0.039103 | south | N | -0.11271 | -0.019867 | -0.10191 | 0.069576 | 0.019867 | south | N | 0.019867 | 0
80224 | VISTRONG | 1 | 15 | -0.040465 | south | N | -0.11407 | -0.021229 | -0.10327 | 0.068214 | 0.021229 | south | N | 0.021229 | 0
80225 | VISTRONG | 2 | 23 | -0.040465 | south | N | -0.11407 | -0.021229 | -0.10327 | 0.068214 | 0.021229 | south | N | 0.021229 | 0
80226 | ALCOA G | 1 | 48 | -0.043316 | south | N | -0.11692 | -0.02408 | -0.10612 | 0.065363 | 0.02408 | south | N | 0.02408 | 0
80227 | AIRCO G | 1 | 8 | -0.041044 | south | N | -0.11465 | -0.021808 | -0.10385 | 0.067635 | 0.021808 | south | N | 0.021808 | 0
80261 | NBEC81A | 1 | 180 | -0.03822 | south | Y | -0.11182 | -0.018984 | -0.10103 | 0.070459 | 0.018984 | south | N | 0.018984 | 0
80262 | NBEC91A | 1 | 180 | -0.038246 | south | Y | -0.11185 | -0.01901 | -0.10105 | 0.070433 | 0.01901 | south | N | 0.01901 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.038063 | south | Y | -0.11167 | -0.018827 | -0.10087 | 0.070616 | 0.018827 | south | N | 0.018827 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.038063 | south | Y | -0.11167 | -0.018827 | -0.10087 | 0.070616 | 0.018827 | south | N | 0.018827 | 0
80265 | LARECU40 | 4 | 100 | -0.027667 | south | Y | -0.10127 | -0.0084306 | -0.090476 | 0.081012 | 0.0084306 | south | N | 0.0084306 | 0
80266 | LARECU50 | 5 | 100 | -0.027667 | south | Y | -0.10127 | -0.0084306 | -0.090476 | 0.081012 | 0.0084306 | south | N | 0.0084306 | 0
80291 | PAPALOTE | 1 | 25 | -0.038777 | south | Y | -0.11238 | -0.019541 | -0.10159 | 0.069902 | 0.019541 | south | N | 0.019541 | 0
80291 | PAPALOTE | 2 | 25 | -0.038777 | south | Y | -0.11238 | -0.019541 | -0.10159 | 0.069902 | 0.019541 | south | N | 0.019541 | 0
80291 | PAPALOTE | 3 | 25 | -0.038777 | south | Y | -0.11238 | -0.019541 | -0.10159 | 0.069902 | 0.019541 | south | N | 0.019541 | 0
80291 | PAPALOTE | 4 | 16 | -0.038777 | south | Y | -0.11238 | -0.019541 | -0.10159 | 0.069902 | 0.019541 | south | N | 0.019541 | 0
80294 | PAPALOTE | 5 | 25 | -0.038777 | south | Y | -0.11238 | -0.019541 | -0.10159 | 0.069902 | 0.019541 | south | N | 0.019541 | 0
80294 | PAPALOTE | 6 | 25 | -0.038777 | south | Y | -0.11238 | -0.019541 | -0.10159 | 0.069902 | 0.019541 | south | N | 0.019541 | 0
80294 | PAPALOTE | 7 | 25 | -0.038777 | south | Y | -0.11238 | -0.019541 | -0.10159 | 0.069902 | 0.019541 | south | N | 0.019541 | 0
80294 | PAPALOTE | 8 | 15 | -0.038777 | south | Y | -0.11238 | -0.019541 | -0.10159 | 0.069902 | 0.019541 | south | N | 0.019541 | 0
86104 | CID-138 | EQ | 0 | -0.027667 | south | N | -0.10127 | -0.0084306 | -0.090476 | 0.081012 | 0.0084306 | south | N | 0.0084306 | 0
86105 | CID-230 | EQ | 500 | -0.027667 | south | N | -0.10127 | -0.0084306 | -0.090476 | 0.081012 | 0.0084306 | south | N | 0.0084306 | 0
86106 | CUF-230 | EQ | 500 | -0.027667 | south | N | -0.10127 | -0.0084306 | -0.090476 | 0.081012 | 0.0084306 | south | N | 0.0084306 | 0
86107 | CUF-138 | EQ | 0 | -0.027667 | south | N | -0.10127 | -0.0084306 | -0.090476 | 0.081012 | 0.0084306 | south | N | 0.0084306 | 0
88198 | BEEVILLE | F | 0 | -0.032998 | south | N | -0.1066 | -0.013762 | -0.095807 | 0.075681 | 0.013762 | south | N | 0.013762 | 0
88253 | HAMILTON | F | 0 | -0.000601 | south | N | -0.074205 | 0.018635 | -0.06341 | 0.10808 | 0.018635 | south | N | 0.018635 | 0
88299 | ZAPATA | F | 0 | -0.031422 | south | N | -0.10503 | -0.012186 | -0.094231 | 0.077257 | 0.012186 | south | N | 0.012186 | 0
88508 | FALFURRI | F | 0 | -0.035259 | south | N | -0.10886 | -0.016023 | -0.098068 | 0.07342 | 0.016023 | south | N | 0.016023 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:46290 ROTHWOOD74 - 40900 KING___345 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.10486 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 48.5493 | 463 | 0.21855 | 101.1881 | 463 | 101.1881
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.097791 | north | 7 | N | N | Nnorth | Nnorth | 1 | 3.1293 | 0 | 0.21148 | 0 | 463 | 101.1881
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21127 | 0 | 463 | 101.1881
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21127 | 0 | 463 | 101.1881 | Weighted Shift Factors
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.097579 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6588 | 17 | 0.21127 | 3.5916 | 480 | 104.7797 | North | 0.073604
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21127 | 0 | 480 | 104.7797 | Houston | -0.11369
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21127 | 0 | 480 | 104.7797 |  | 0.18729
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.095389 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.5787 | 48 | 0.20908 | 10.0358 | 528 | 114.8155
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.095389 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3879 | 46 | 0.20908 | 9.6177 | 574 | 124.4332 | Line Rating | 1710
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.095389 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.0158 | 105 | 0.20908 | 21.9534 | 679 | 146.3865 | Conc Gen | 2694.3
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.324 | 855 | 0.2053 | 175.5296 | 1534 | 321.9161 | Weighted Imp. | 560.1231
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.324 | 855 | 0.2053 | 175.5296 | 2389 | 497.4457 | PTDF | 0.20789
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.9517 | 152.3 | 0.2053 | 31.2669 | 2541.3 | 528.7126
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.0159 | 153 | 0.2053 | 31.4106 | 2694.3 | 560.1231 | Concentration | 1.11
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.086419 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 71.4685 | 827 | 0.20011 | 165.4908
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.086419 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 70.7772 | 819 | 0.20011 | 163.8899
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.1582 | 0 | 0.19902 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.3118 | 0 | 0.19902 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.3118 | 0 | 0.19902 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.4262 | 0 | 0.19902 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.078422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 48.2295 | 615 | 0.19211 | 118.1494
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.078422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 46.0337 | 587 | 0.19211 | 112.7702
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.077738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7151 | 150.7 | 0.19143 | 28.8483
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.077738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7384 | 151 | 0.19143 | 28.9057
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.077738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7907 | 177.4 | 0.19143 | 33.9595
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.077609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7578 | 151.5 | 0.1913 | 28.9819
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.077609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8199 | 152.3 | 0.1913 | 29.135
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.077609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7756 | 177.5 | 0.1913 | 33.9557
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.074693 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.5941 | 182 | 0.18838 | 34.2858
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.074693 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 36.1514 | 484 | 0.18838 | 91.1777
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.074654 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.7327 | 50 | 0.18834 | 9.4172
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.074624 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.18831 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.0069 | 0 | 0.18806 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.6682 | 0 | 0.18806 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.7838 | 0 | 0.18806 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | 1 | 29.674 | 0 | 0.18806 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.074082 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 58.1544 | 785 | 0.18777 | 147.4016
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.074082 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 58.8952 | 795 | 0.18777 | 149.2794
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.074082 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 57.784 | 780 | 0.18777 | 146.4628
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.072199 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.1726 | 224 | 0.18589 | 41.6393
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6081 | 161 | 0.18579 | 29.9123
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8244 | 164 | 0.18579 | 30.4697
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8244 | 164 | 0.18579 | 30.4697
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8494 | 414 | 0.18579 | 76.9174
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6802 | 162 | 0.18579 | 30.0981
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6081 | 161 | 0.18579 | 29.9123
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7523 | 163 | 0.18579 | 30.2839
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.4889 | 409 | 0.18579 | 75.9884
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.071665 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 27.806 | 388 | 0.18536 | 71.918
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.071665 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 36.9075 | 515 | 0.18536 | 95.4582
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.071582 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4316 | 20 | 0.18527 | 3.7055
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.071582 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.7895 | 25 | 0.18527 | 4.6318
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.071582 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.9349 | 41 | 0.18527 | 7.5962
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.071533 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.18522 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.071533 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.18522 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.071497 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8599 | 40 | 0.18519 | 7.4075
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.071494 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.648 | 79 | 0.18518 | 14.6296
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.071494 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.5784 | 106 | 0.18518 | 19.6296
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.071494 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.4381 | 146 | 0.18518 | 27.037
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.071494 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.4335 | 76 | 0.18518 | 14.074
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.071422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 39.8535 | 558 | 0.18511 | 103.2929
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.071422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 41.3533 | 579 | 0.18511 | 107.1803
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.071422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 57.709 | 808 | 0.18511 | 149.5711
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.071364 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.3523 | 0 | 0.18505 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.071364 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.6806 | 0 | 0.18505 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.071364 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.3086 | 0 | 0.18505 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.4118 | 160 | 0.18501 | 29.6024
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1265 | 156 | 0.18501 | 28.8623
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.9795 | 196 | 0.18501 | 36.2629
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1265 | 156 | 0.18501 | 28.8623
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1979 | 157 | 0.18501 | 29.0473
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.1222 | 198 | 0.18501 | 36.6329
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.071268 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.3692 | 370 | 0.18496 | 68.4347
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.9775 | 0 | 0.18496 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.0488 | 0 | 0.18496 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.0218 | 0 | 0.18496 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.1913 | 0 | 0.18496 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.2626 | 0 | 0.18496 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.0931 | 0 | 0.18496 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.07114 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.0938 | 170 | 0.18483 | 31.4212
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.07114 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 36.9928 | 520 | 0.18483 | 96.112
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.071038 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.8415 | 0 | 0.18473 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.071038 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.8415 | 0 | 0.18473 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.070901 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.3663 | 118 | 0.18459 | 21.7818
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.070901 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.1536 | 115 | 0.18459 | 21.2281
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.070901 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 39.421 | 556 | 0.18459 | 102.633
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.070879 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.18457 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.070731 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18442 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.070349 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7884 | 196 | 0.18404 | 36.0718
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.070349 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.8087 | 111 | 0.18404 | 20.4284
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.069682 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.1809 | 60 | 0.18337 | 11.0024
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.069682 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.39 | 63 | 0.18337 | 11.5525
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.069043 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 30.0337 | 435 | 0.18273 | 79.4892
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.068988 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.7611 | 112.5 | 0.18268 | 20.5514
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.068902 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.2163 | 395 | 0.18259 | 72.1241
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.068902 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 29.9724 | 435 | 0.18259 | 79.4279
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.0688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.8883 | 216.4 | 0.18249 | 39.491
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.0688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.8677 | 216.1 | 0.18249 | 39.4363
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.068747 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18244 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.068747 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18244 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.068747 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18244 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.2602 | 224 | 0.18182 | 40.727
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.3965 | 226 | 0.18182 | 41.0906
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.4427 | 212 | 0.18182 | 38.5452
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3746 | 211 | 0.18182 | 38.3633
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.068072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.6047 | 288 | 0.18176 | 52.3477
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.068072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.0066 | 147 | 0.18176 | 26.7191
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.068072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.0066 | 147 | 0.18176 | 26.7191
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.067806 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1815 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.067686 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8079 | 204 | 0.18138 | 37.0009
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.067686 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6049 | 201 | 0.18138 | 36.4567
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.067686 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.38 | 242 | 0.18138 | 43.8932
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.067658 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.7021 | 217.3 | 0.18135 | 39.4071
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.067658 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8699 | 205 | 0.18135 | 37.1765
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.067658 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.43 | 272.4 | 0.18135 | 49.3994
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.067492 | north | 3 | N | N | Nnorth | Nnorth | 1 | 78.0882 | 0 | 0.18118 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.067492 | north | 3 | N | N | Nnorth | Nnorth | 1 | 78.1557 | 0 | 0.18118 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.067305 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.2115 | 18 | 0.181 | 3.2579
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.067305 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.2115 | 18 | 0.181 | 3.2579
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.067305 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.5576 | 38 | 0.181 | 6.8778
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.6851 | 70 | 0.18062 | 12.6435
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.6182 | 69 | 0.18062 | 12.4628
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.6182 | 69 | 0.18062 | 12.4628
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.5512 | 68 | 0.18062 | 12.2822
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.3351 | 20 | 0.18045 | 3.6089
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.3351 | 20 | 0.18045 | 3.6089
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.3351 | 20 | 0.18045 | 3.6089
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1348 | 17 | 0.18045 | 3.0676
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.066729 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.80075 | 0 | 0.18042 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.066729 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.80075 | 0 | 0.18042 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.066683 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.406 | 366 | 0.18037 | 66.0168
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.066644 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.9973 | 120 | 0.18033 | 21.6402
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.06651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1737 | 168 | 0.1802 | 30.2737
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.06651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.9859 | 90 | 0.1802 | 16.2181
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.066309 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.0468 | 242 | 0.18 | 43.5599
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.06607 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.8231 | 73 | 0.17976 | 13.1225
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.06607 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.8623 | 119 | 0.17976 | 21.3915
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.06607 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.5443 | 205 | 0.17976 | 36.851
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.06607 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.7391 | 102 | 0.17976 | 18.3356
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.06607 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.3427 | 96 | 0.17976 | 17.257
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.065785 | west | 4 | Y | N | Ywest | Nwest | 1 | 42.7405 | 649.7 | 0.17948 | 116.6054
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.065452 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7996 | 165 | 0.17914 | 29.5586
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.065064 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3551 | 236 | 0.17875 | 42.1861
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.065061 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.0244 | 400 | 0.17875 | 71.5007
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.064395 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8637 | 60 | 0.17809 | 10.6851
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.064014 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.8408 | 60 | 0.1777 | 10.6623
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.063931 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5897 | 150 | 0.17762 | 26.6433
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3578 | 209 | 0.1776 | 37.1192
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.085 | 126.5 | 0.1776 | 22.4669
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9143 | 249 | 0.1776 | 44.2233
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5909 | 197 | 0.1776 | 34.9879
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3949 | 37.5 | 0.17755 | 6.6583
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8653 | 107.5 | 0.17755 | 19.087
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6215 | 135 | 0.17755 | 23.9698
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5997 | 119 | 0.17755 | 21.1289
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7056 | 105 | 0.17755 | 18.6431
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.141 | 80.5 | 0.17755 | 14.2931
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.063682 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9603 | 125 | 0.17737 | 22.1716
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.063682 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9603 | 125 | 0.17737 | 22.1716
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.063613 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5419 | 150 | 0.1773 | 26.5956
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.063613 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4249 | 101 | 0.1773 | 17.9077
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.063568 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3397 | 84 | 0.17726 | 14.8897
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.063486 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.2851 | 99 | 0.17718 | 17.5405
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.063486 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8726 | 61 | 0.17718 | 10.8078
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.063486 | west | 7 | N | N | Nwest | Nwest | 1 | 1.5872 | 0 | 0.17718 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.063486 | west | 7 | N | N | Nwest | Nwest | 1 | 2.9013 | 0 | 0.17718 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.063486 | west | 7 | N | N | Nwest | Nwest | 1 | 2.9013 | 0 | 0.17718 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.063476 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9501 | 141 | 0.17717 | 24.9805
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.063476 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6171 | 120 | 0.17717 | 21.26
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.063451 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9974 | 63 | 0.17714 | 11.1599
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1862 | 66 | 0.17712 | 11.6898
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3765 | 69 | 0.17712 | 12.2211
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3765 | 69 | 0.17712 | 12.2211
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.2496 | 67 | 0.17712 | 11.8669
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.2496 | 67 | 0.17712 | 11.8669
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1228 | 65 | 0.17712 | 11.5127
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5028 | 150 | 0.17704 | 26.5564
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.9374 | 220 | 0.17704 | 38.9494
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6704 | 200 | 0.17704 | 35.4086
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7226 | 121.9 | 0.17704 | 21.5815
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.063252 | west | 8 | N | N | Nwest | Nwest | 1 | 4.4276 | 0 | 0.17694 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.063252 | west | 8 | N | N | Nwest | Nwest | 1 | 4.6427 | 0 | 0.17694 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.063252 | west | 8 | N | N | Nwest | Nwest | 1 | 4.4529 | 0 | 0.17694 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.063246 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3843 | 180 | 0.17694 | 31.8486
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.063246 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3843 | 180 | 0.17694 | 31.8486
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.063214 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.2232 | 225 | 0.1769 | 39.8036
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.063213 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5856 | 120 | 0.1769 | 21.2285
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.063213 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7286 | 233 | 0.1769 | 41.2186
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.063213 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7589 | 170.2 | 0.1769 | 30.109
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.063156 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5787 | 120 | 0.17685 | 21.2216
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.063142 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.577 | 120 | 0.17683 | 21.2199
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.062949 | west | 8 | N | N | Nwest | Nwest | 1 | 1.6241 | 0 | 0.17664 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.06291 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.4753 | 214.2 | 0.1766 | 37.8279
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.062836 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.315 | 100.5 | 0.17653 | 17.7409
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.062829 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4244 | 150 | 0.17652 | 26.478
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.062825 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6439 | 58 | 0.17652 | 10.2379
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3966 | 70 | 0.1765 | 12.3549
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3966 | 70 | 0.1765 | 12.3549
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8286 | 92.8 | 0.1765 | 16.3791
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.0246 | 80 | 0.1765 | 14.1199
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.0246 | 80 | 0.1765 | 14.1199
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.2229 | 115 | 0.1765 | 20.2974
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.0754 | 208.2 | 0.17649 | 36.7458
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.9242 | 142.1 | 0.17649 | 25.0796
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.315 | 132.4 | 0.17649 | 23.3676
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.5411 | 136 | 0.17649 | 24.003
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.2319 | 147 | 0.17649 | 25.9444
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.1884 | 210 | 0.17649 | 37.0635
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.0536 | 112.5 | 0.17639 | 19.8438
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3735 | 149.5 | 0.17639 | 26.3703
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.662 | 186 | 0.17639 | 32.8085
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.4489 | 214.5 | 0.17639 | 37.8356
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.062513 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.41259 | 6.6 | 0.1762 | 1.1629
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.062513 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1442 | 34.3 | 0.1762 | 6.0438
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.062317 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2852 | 149 | 0.17601 | 26.2252
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.062291 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5583 | 169.5 | 0.17598 | 29.8289
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.062211 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1774 | 35 | 0.1759 | 6.1566
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.062211 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8663 | 30 | 0.1759 | 5.2771
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1039 | 66 | 0.17587 | 11.6075
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.0417 | 65 | 0.17587 | 11.4316
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1661 | 67 | 0.17587 | 11.7833
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1661 | 67 | 0.17587 | 11.7833
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1661 | 67 | 0.17587 | 11.7833
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.06218 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17587 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.06218 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17587 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.059895 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.2875 | 0 | 0.17359 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058951 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7161 | 80 | 0.17264 | 13.8113
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058951 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7161 | 80 | 0.17264 | 13.8113
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.058695 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4021 | 75 | 0.17239 | 12.9289
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058695 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6956 | 80 | 0.17239 | 13.7909
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.058695 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3478 | 40 | 0.17239 | 6.8954
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.05864 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6912 | 80 | 0.17233 | 13.7865
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.058632 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6906 | 80 | 0.17232 | 13.7858
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.0586 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.79 | 150 | 0.17229 | 25.8436
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.0586 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.79 | 150 | 0.17229 | 25.8436
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.057669 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.86503 | 0 | 0.17136 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.057669 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.86503 | 0 | 0.17136 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057325 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.586 | 80 | 0.17102 | 13.6813
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.057112 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3691 | 76.5 | 0.1708 | 13.0664
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.056894 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7791 | 84 | 0.17058 | 14.3291
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.055436 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.3154 | 150 | 0.16913 | 25.369
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.055436 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4349 | 80 | 0.16913 | 13.5301
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.054461 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8876 | 255 | 0.16815 | 42.8787
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.054461 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.1147 | 149 | 0.16815 | 25.0546
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.054461 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.3325 | 153 | 0.16815 | 25.7272
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.05334 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16703 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.05334 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 41.9786 | 787 | 0.16703 | 131.4532
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.052588 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16628 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.052588 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16628 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.050032 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.16372 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.045265 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7897 | 150 | 0.15896 | 23.8434
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.015554 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.12924 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.11369 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.11369 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -1.7321 | 100 | 0.09637 | 9.637
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.018966 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 10.7917 | 569 | -0.054638 | -31.0887
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.018966 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.0192 | 581 | -0.054638 | -31.7444
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.007815 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14067 | 0 | -0.065789 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.007815 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14067 | 0 | -0.065789 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.007815 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11722 | 0 | -0.065789 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.006937 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.095037 | 0 | -0.066667 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.003305 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.09254 | 0 | -0.070299 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.003305 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.095845 | 0 | -0.070299 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.003066 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2939 | 422 | -0.070538 | -29.7668
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.002518 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.045324 | 0 | -0.071086 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.002518 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.045324 | 0 | -0.071086 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.001274 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04459 | 0 | -0.07233 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.001274 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.043316 | 0 | -0.07233 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.001274 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04459 | 0 | -0.07233 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04746 | 42 | -0.072474 | -3.0439
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04972 | 44 | -0.072474 | -3.1888
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04972 | 44 | -0.072474 | -3.1888
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.05311 | 47 | -0.072474 | -3.4063
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.000294 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.09114 | 310 | -0.07331 | -22.7259
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.000294 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.12142 | 413 | -0.07331 | -30.2768
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.000275 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0022 | 0 | -0.073329 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.000275 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0022 | 0 | -0.073329 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.073604 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.073604 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.000601 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.019833 | 0 | -0.074205 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.000601 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.015025 | 0 | -0.074205 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.000601 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.074205 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.041209 | 49 | -0.074445 | -3.6478
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.038686 | 46 | -0.074445 | -3.4244
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.038686 | 46 | -0.074445 | -3.4244
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.039527 | 47 | -0.074445 | -3.4989
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.000841 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.12951 | 154 | -0.074445 | -11.4645
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.000841 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.12447 | 148 | -0.074445 | -11.0178
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.040368 | 48 | -0.074445 | -3.5733
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.040368 | 48 | -0.074445 | -3.5733
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.002359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31139 | 132 | -0.075963 | -10.0271
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.002359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31611 | 134 | -0.075963 | -10.179
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.002359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.76196 | 323 | -0.075963 | -24.5359
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.004354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.66399 | 152.5 | -0.077958 | -11.8885
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.004354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.65092 | 149.5 | -0.077958 | -11.6546
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.004354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0127 | 232.6 | -0.077958 | -18.1329
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.00475 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7505 | 158 | -0.078354 | -12.3799
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.00475 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76 | 160 | -0.078354 | -12.5366
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.00475 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83125 | 175 | -0.078354 | -13.7119
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3619 | 50 | -0.080842 | -4.0421
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3619 | 50 | -0.080842 | -4.0421
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3619 | 50 | -0.080842 | -4.0421
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3619 | 50 | -0.080842 | -4.0421
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.008171 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.049026 | 0 | -0.081775 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.009932 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.083536 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.012231 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -7.1429 | 584 | -0.085835 | -50.1274
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.012231 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -7.2774 | 595 | -0.085835 | -51.0715
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.012363 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -5.3532 | 433 | -0.085967 | -37.2235
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01243 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07458 | 0 | -0.086034 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5658 | 223.9 | -0.08953 | -20.0457
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5833 | 225 | -0.08953 | -20.1441
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.577 | 224.6 | -0.08953 | -20.1083
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6104 | 226.7 | -0.08953 | -20.2963
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9746 | 114 | -0.090925 | -10.3654
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8453 | 222 | -0.090925 | -20.1852
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1871 | 184 | -0.090925 | -16.7301
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8799 | 224 | -0.090925 | -20.3671
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9919 | 115 | -0.090925 | -10.4563
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.017816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.042758 | 0 | -0.09142 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.017816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.042758 | 0 | -0.09142 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.017816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.049885 | 0 | -0.09142 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.018327 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.043985 | 0 | -0.091931 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.018327 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.043985 | 0 | -0.091931 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6902 | 142 | -0.092549 | -13.1419
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.747 | 145 | -0.092549 | -13.4195
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8607 | 151 | -0.092549 | -13.9748
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.494 | 290 | -0.092549 | -26.8391
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.019262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.077048 | 0 | -0.092866 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2046 | 147 | -0.095404 | -14.0243
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0084 | 138 | -0.095404 | -13.1657
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.052 | 140 | -0.095404 | -13.3565
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2046 | 147 | -0.095404 | -14.0243
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9676 | 182 | -0.095404 | -17.3634
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3164 | 198 | -0.095404 | -18.8899
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.022486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1518 | 407 | -0.09609 | -39.1084
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.022488 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.2651 | 412 | -0.096092 | -39.5897
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.022488 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.9952 | 400 | -0.096092 | -38.4366
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.022513 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3058 | 58 | -0.096117 | -5.5748
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.022513 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0037 | 89 | -0.096117 | -8.5544
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.99057 | 44 | -0.096117 | -4.2291
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.99057 | 44 | -0.096117 | -4.2291
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.96806 | 43 | -0.096117 | -4.133
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0131 | 45 | -0.096117 | -4.3252
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.022523 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.5498 | 424 | -0.096127 | -40.7576
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.022523 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.5723 | 425 | -0.096127 | -40.8538
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.022567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.7165 | 209 | -0.096171 | -20.0996
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.022567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.8745 | 216 | -0.096171 | -20.7728
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0381 | 46 | -0.096171 | -4.4238
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0606 | 47 | -0.096171 | -4.52
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0381 | 46 | -0.096171 | -4.4238
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0381 | 46 | -0.096171 | -4.4238
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.022611 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.096215 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.022611 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.096215 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.022611 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.096215 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.023191 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.27829 | 0 | -0.096795 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.023266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6062 | 155 | -0.09687 | -15.0148
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.023266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9552 | 170 | -0.09687 | -16.4678
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.023266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6062 | 155 | -0.09687 | -15.0148
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.023671 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.5681 | 24 | -0.097275 | -2.3346
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.023671 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.5681 | 24 | -0.097275 | -2.3346
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.023671 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.54443 | 23 | -0.097275 | -2.2373
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.023846 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.0199 | 546 | -0.09745 | -53.2074
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.023846 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.8845 | 750 | -0.09745 | -73.0871
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.027667 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.7667 | 100 | -0.10127 | -10.1271
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.027667 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.7667 | 100 | -0.10127 | -10.1271
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.027667 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.027667 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.027667 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.027667 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.02767 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.027673 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.9585 | 396 | -0.10128 | -40.1055
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.031422 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10503 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.032998 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1066 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.033909 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.40691 | 0 | -0.10751 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.033909 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.373 | 0 | -0.10751 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.033909 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.40691 | 0 | -0.10751 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.034742 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.8527 | 629 | -0.10835 | -68.1493
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.035259 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10886 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.036509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3486 | 146.5 | -0.11011 | -16.1315
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.036509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3997 | 147.9 | -0.11011 | -16.2856
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.036509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3161 | 173 | -0.11011 | -19.0495
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.036937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.646 | 207 | -0.11054 | -22.8819
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.036937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.0042 | 216.7 | -0.11054 | -23.9541
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.036937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9388 | 242 | -0.11054 | -26.7508
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.03694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3194 | 144 | -0.11054 | -15.9183
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.03694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3194 | 144 | -0.11054 | -15.9183
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.03694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3167 | 171 | -0.11054 | -18.9029
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.037245 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11085 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.037246 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4153 | 38 | -0.11085 | -4.2123
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.037246 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.71885 | 19.3 | -0.11085 | -2.1394
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.037246 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.55869 | 15 | -0.11085 | -1.6627
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.037246 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7506 | 47 | -0.11085 | -5.2099
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.512 | 94 | -0.11097 | -10.4308
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5318 | 41 | -0.11097 | -4.5496
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4198 | 38 | -0.11097 | -4.2167
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.70988 | 19 | -0.11097 | -2.1083
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.512 | 94 | -0.11097 | -10.4308
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.345 | 36 | -0.11097 | -3.9948
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6066 | 43 | -0.11097 | -4.7715
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.82196 | 22 | -0.11097 | -2.4412
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.5296 | 148 | -0.11097 | -16.4229
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8681 | 50 | -0.11097 | -5.5483
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0549 | 55 | -0.11097 | -6.1031
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8681 | 50 | -0.11097 | -5.5483
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.037533 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0885 | 0 | -0.11114 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.037895 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.44 | 0 | -0.1115 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.037938 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4416 | 0 | -0.11154 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.037996 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.9499 | 0 | -0.1116 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.037996 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.9499 | 0 | -0.1116 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.038056 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4801 | 144 | -0.11166 | -16.079
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.038056 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1545 | 188 | -0.11166 | -20.992
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.038063 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.713 | 334 | -0.11167 | -37.2966
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.038063 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.9414 | 340 | -0.11167 | -37.9666
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.038063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8513 | 180 | -0.11167 | -20.1
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.038063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8513 | 180 | -0.11167 | -20.1
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.03822 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8796 | 180 | -0.11182 | -20.1282
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.038236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.6704 | 0 | -0.11184 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.038236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.6819 | 0 | -0.11184 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.038236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.8501 | 0 | -0.11184 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.038246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.8507 | 336 | -0.11185 | -37.5814
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.038246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8843 | 180 | -0.11185 | -20.1329
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 25 | -0.11238 | -2.8095
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 25 | -0.11238 | -2.8095
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 25 | -0.11238 | -2.8095
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.62043 | 16 | -0.11238 | -1.7981
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 25 | -0.11238 | -2.8095
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 25 | -0.11238 | -2.8095
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 25 | -0.11238 | -2.8095
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.58166 | 15 | -0.11238 | -1.6857
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.038924 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8415 | 0 | -0.11253 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8613 | 47.7 | -0.11262 | -5.3721
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4554 | 37.3 | -0.11262 | -4.2009
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.7949 | 46 | -0.11262 | -5.1807
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.873 | 48 | -0.11262 | -5.4059
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.1783 | 0 | -0.11271 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.9828 | 0 | -0.11271 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.9103 | 0 | -0.11271 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.6699 | 0 | -0.11271 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.7481 | 0 | -0.11271 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.9661 | 0 | -0.11271 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.039103 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46924 | 0 | -0.11271 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.039484 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.86865 | 22 | -0.11309 | -2.4879
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.039484 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.43432 | 11 | -0.11309 | -1.244
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.039484 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.43432 | 11 | -0.11309 | -1.244
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.040465 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.60698 | 0 | -0.11407 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.040465 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.9307 | 0 | -0.11407 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.041044 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.32835 | 0 | -0.11465 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1563 | 0 | -0.1149 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28908 | 0 | -0.1149 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6106 | 0 | -0.1149 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.61945 | 0 | -0.1149 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28908 | 0 | -0.1149 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.61945 | 0 | -0.1149 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6106 | 0 | -0.1149 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6106 | 0 | -0.1149 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.043316 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0792 | 0 | -0.11692 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4709 | 0 | -0.11754 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5588 | 0 | -0.11754 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4709 | 0 | -0.11754 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5149 | 0 | -0.11754 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4446 | 0 | -0.11754 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0984 | 0 | -0.11754 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0211 | 0 | -0.11754 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2302 | 0 | -0.11754 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9156 | 0 | -0.11754 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2513 | 0 | -0.11754 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.3786 | 76 | -0.13122 | -9.9725
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.3786 | 76 | -0.13122 | -9.9725
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.0494 | 105 | -0.13122 | -13.7777
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2634 | 74 | -0.13122 | -9.71
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2634 | 74 | -0.13122 | -9.71
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.8765 | 102 | -0.13122 | -13.3841
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.065836 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.3452 | 66 | -0.13944 | -9.203
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.069926 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -93.2114 | 0 | -0.14353 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.069926 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -92.8617 | 0 | -0.14353 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.2676 | 0 | -0.1571 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.2676 | 0 | -0.1571 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.9355 | 0 | -0.1571 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.1424 | 0 | -0.1571 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2006 | 0 | -0.15748 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9891 | 0 | -0.15748 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7746 | 0 | -0.15748 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.472 | 0 | -0.15748 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.2138 | 0 | -0.15748 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3815 | 0 | -0.15748 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.194 | 0 | -0.15748 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5099 | 0 | -0.15748 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.8848 | 0 | -0.15748 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8717 | 0 | -0.15748 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2845 | 0 | -0.15748 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0394 | 0 | -0.15748 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4355 | 0 | -0.15748 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.472 | 0 | -0.15748 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1365 | 0 | -0.15748 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.6397 | 0 | -0.15748 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.375 | 0 | -0.15748 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.7105 | 0 | -0.15748 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.7105 | 0 | -0.15748 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.3437 | 0 | -0.15748 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.084304 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9856 | 0 | -0.15791 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.084304 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84304 | 0 | -0.15791 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.088868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -14.3077 | 161 | -0.16247 | -26.1579
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.088868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -14.7521 | 166 | -0.16247 | -26.9703
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.088868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -22.0393 | 248 | -0.16247 | -40.2929
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.088868 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -48.5219 | 546 | -0.16247 | -88.7094
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.088868 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -57.1421 | 0 | -0.16247 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.088868 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1553 | 13 | -0.16247 | -2.1121
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2852 | 104 | -0.16288 | -16.94
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2852 | 104 | -0.16288 | -16.94
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8212 | 54 | -0.16288 | -8.7958
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.7319 | 53 | -0.16288 | -8.6329
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8212 | 54 | -0.16288 | -8.7958
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.089 | 57 | -0.16288 | -9.2844
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8212 | 54 | -0.16288 | -8.7958
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8212 | 54 | -0.16288 | -8.7958
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.1783 | 58 | -0.16288 | -9.4473
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.1783 | 58 | -0.16288 | -9.4473
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.089959 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0795 | 12 | -0.16356 | -1.9628
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.090811 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -59.118 | 651 | -0.16441 | -107.0338
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.090811 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -51.2174 | 564 | -0.16441 | -92.7298
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.090811 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -54.4866 | 600 | -0.16441 | -98.6487
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.090864 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.8108 | 0 | -0.16447 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.090864 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.8108 | 0 | -0.16447 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.090864 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.2617 | 0 | -0.16447 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.098451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5386 | 0 | -0.17205 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.10067 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3222 | 0 | -0.17428 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.10481 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.2406 | 50 | -0.17842 | -8.9208
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.9773 | 46 | -0.18181 | -8.3631
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.9773 | 46 | -0.18181 | -8.3631
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.9773 | 46 | -0.18181 | -8.3631
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.9511 | 55 | -0.18181 | -9.9993
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.9511 | 55 | -0.18181 | -9.9993
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.8429 | 54 | -0.18181 | -9.8175
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.0688 | 0 | -0.18396 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.2522 | 0 | -0.18396 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3337 | 0 | -0.18396 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2564 | 0 | -0.18396 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.11036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5315 | 0 | -0.18396 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.11036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3107 | 0 | -0.18396 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.8164 | 0 | -0.184 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3637 | 0 | -0.184 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8513 | 0 | -0.184 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.9134 | 0 | -0.184 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.9466 | 0 | -0.184 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.8141 | 0 | -0.184 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.5985 | 0 | -0.184 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.9378 | 0 | -0.184 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.416 | 0 | -0.184 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.234 | 56 | -0.18492 | -10.3558
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5679 | 59 | -0.18492 | -10.9105
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.234 | 56 | -0.18492 | -10.3558
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.234 | 56 | -0.18492 | -10.3558
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5679 | 59 | -0.18492 | -10.9105
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.234 | 56 | -0.18492 | -10.3558
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.11795 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.19155 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9992 | 0 | -0.19447 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5882 | 0 | -0.19447 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5157 | 0 | -0.19447 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5874 | 0 | -0.19447 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4746 | 0 | -0.19447 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9567 | 0 | -0.19601 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3447 | 0 | -0.19601 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9567 | 0 | -0.19601 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9567 | 0 | -0.19601 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.12491 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.7427 | 0 | -0.19851 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.12491 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.9925 | 0 | -0.19851 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.12672 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4352 | 0 | -0.20032 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.12763 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.3573 | 0 | -0.20123 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.12782 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5338 | 12 | -0.20142 | -2.4171
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.12782 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.20142 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.12787 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.6094 | 169 | -0.20147 | -34.0483
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.12794 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.1106 | 165 | -0.20155 | -33.2552
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.12812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -19.0903 | 0 | -0.20173 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.12812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.3408 | 0 | -0.20173 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.12816 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -27.2979 | 213 | -0.20176 | -42.9754
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.12821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.077 | 0 | -0.20181 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2076 | 0 | -0.20185 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.105 | 0 | -0.20185 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.593 | 0 | -0.20185 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4388 | 0 | -0.20185 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.12831 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.2556 | 228 | -0.20192 | -46.0372
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.12844 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.1187 | 0 | -0.20204 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.12844 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.3701 | 0 | -0.20204 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.12844 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.1646 | 0 | -0.20204 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.12872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.2689 | 0 | -0.20233 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.12872 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.3775 | 0 | -0.20233 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.221 | 0 | -0.20348 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3509 | 0 | -0.20348 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.065 | 0 | -0.20348 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8962 | 0 | -0.20348 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.4824 | 0 | -0.2041 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.6129 | 0 | -0.2041 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.1349 | 0 | -0.2041 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2214 | 0 | -0.2041 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0909 | 0 | -0.2041 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.5718 | 0 | -0.2041 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.6994 | 0 | -0.2041 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.13155 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.653 | 0 | -0.20515 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5582 | 42 | -0.20594 | -8.6495
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5582 | 42 | -0.20594 | -8.6495
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.0288 | 38 | -0.20594 | -7.8257
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.0288 | 38 | -0.20594 | -7.8257
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.6452 | 0 | -0.20623 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.8362 | 0 | -0.20623 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.8892 | 0 | -0.20623 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.8229 | 0 | -0.20623 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -35.6775 | 0 | -0.20623 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.13438 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67192 | 0 | -0.20799 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.13438 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8221 | 0 | -0.20799 | 0
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6087 | 0 | -0.20915 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7036 | 0 | -0.20915 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4325 | 0 | -0.20915 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2217 | 0 | -0.20915 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3992 | 0 | -0.20915 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7652 | 0 | -0.20915 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6974 | 0 | -0.20915 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7443 | 0 | -0.20915 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4399 | 0 | -0.20915 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.576 | 0 | -0.20915 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -20.0614 | 0 | -0.20915 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.13647 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -54.3143 | 398 | -0.21007 | -83.6085
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.13777 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -1.6532 | 12 | -0.21137 | -2.5365
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.138 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -101.4263 | 735 | -0.2116 | -155.5249
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.14147 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -105.1137 | 743 | -0.21508 | -159.8011
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.14647 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -25.1934 | 172 | -0.22008 | -37.8532
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.14647 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -25.1934 | 172 | -0.22008 | -37.8532
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.14647 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -25.1934 | 172 | -0.22008 | -37.8532
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.6565 | 0 | -0.22506 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.4445 | 0 | -0.22506 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.0659 | 0 | -0.22506 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -40.7711 | 0 | -0.22506 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -31.7785 | 0 | -0.25729 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.6558 | 0 | -0.25729 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.2884 | 0 | -0.25729 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.2884 | 0 | -0.25729 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.18369 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.7579 | 0 | -0.25729 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:46290 ROTHWOOD74 - 40900 KING___345 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -31.7785 | 0 | -0.25729 | 0 | 0 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.6558 | 0 | -0.25729 | 0 | 0 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.2884 | 0 | -0.25729 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18369 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.2884 | 0 | -0.25729 | 0 | 0 | 0 | Weighted Shift Factors
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.18369 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.7579 | 0 | -0.25729 | 0 | 0 | 0 | North | 0.073604
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.6565 | 0 | -0.22506 | 0 | 0 | 0 | Houston | -0.11369
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.4445 | 0 | -0.22506 | 0 | 0 | 0 |  | 0.18729
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.0659 | 0 | -0.22506 | 0 | 0 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.15145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -40.7711 | 0 | -0.22506 | 0 | 0 | 0 | Line Rating | 1710
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.14647 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -25.1934 | 172 | -0.22008 | -37.8532 | 172 | 37.8532 | Conc Gen | 3395
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.14647 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -25.1934 | 172 | -0.22008 | -37.8532 | 344 | 75.7063 | Weighted Imp. | 714.5334
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.14647 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -25.1934 | 172 | -0.22008 | -37.8532 | 516 | 113.5595 | PTDF | 0.21047
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.14147 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -105.1137 | 743 | -0.21508 | -159.8011 | 1259 | 273.3606
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.138 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -101.4263 | 735 | -0.2116 | -155.5249 | 1994 | 428.8855 | Concentration | 1.1237
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.13777 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -1.6532 | 0 | -0.21137 | 0 | 1994 | 428.8855
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.13647 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -54.3143 | 398 | -0.21007 | -83.6085 | 2392 | 512.4939
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6087 | 0 | -0.20915 | 0 | 2392 | 512.4939
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7036 | 0 | -0.20915 | 0 | 2392 | 512.4939
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4325 | 0 | -0.20915 | 0 | 2392 | 512.4939
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2217 | 0 | -0.20915 | 0 | 2392 | 512.4939
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3992 | 0 | -0.20915 | 0 | 2392 | 512.4939
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7652 | 0 | -0.20915 | 0 | 2392 | 512.4939
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6974 | 0 | -0.20915 | 0 | 2392 | 512.4939
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7443 | 0 | -0.20915 | 0 | 2392 | 512.4939
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4399 | 0 | -0.20915 | 0 | 2392 | 512.4939
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.576 | 0 | -0.20915 | 0 | 2392 | 512.4939
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.13555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -20.0614 | 0 | -0.20915 | 0 | 2392 | 512.4939
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.13438 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67192 | 0 | -0.20799 | 0 | 2392 | 512.4939
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.13438 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8221 | 0 | -0.20799 | 0 | 2392 | 512.4939
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.6452 | 0 | -0.20623 | 0 | 2392 | 512.4939
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.8362 | 0 | -0.20623 | 0 | 2392 | 512.4939
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.8892 | 0 | -0.20623 | 0 | 2392 | 512.4939
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.8229 | 0 | -0.20623 | 0 | 2392 | 512.4939
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.13263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -35.6775 | 0 | -0.20623 | 0 | 2392 | 512.4939
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5582 | 42 | -0.20594 | -8.6495 | 2434 | 521.1435
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5582 | 42 | -0.20594 | -8.6495 | 2476 | 529.793
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.0288 | 38 | -0.20594 | -7.8257 | 2514 | 537.6187
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.13234 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.0288 | 38 | -0.20594 | -7.8257 | 2552 | 545.4444
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.13155 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.653 | 0 | -0.20515 | 0 | 2552 | 545.4444
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.4824 | 0 | -0.2041 | 0 | 2552 | 545.4444
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.6129 | 0 | -0.2041 | 0 | 2552 | 545.4444
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.1349 | 0 | -0.2041 | 0 | 2552 | 545.4444
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2214 | 0 | -0.2041 | 0 | 2552 | 545.4444
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0909 | 0 | -0.2041 | 0 | 2552 | 545.4444
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.5718 | 0 | -0.2041 | 0 | 2552 | 545.4444
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.1305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.6994 | 0 | -0.2041 | 0 | 2552 | 545.4444
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.221 | 0 | -0.20348 | 0 | 2552 | 545.4444
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3509 | 0 | -0.20348 | 0 | 2552 | 545.4444
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.065 | 0 | -0.20348 | 0 | 2552 | 545.4444
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.12987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8962 | 0 | -0.20348 | 0 | 2552 | 545.4444
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.12872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.2689 | 0 | -0.20233 | 0 | 2552 | 545.4444
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.12872 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.3775 | 0 | -0.20233 | 0 | 2552 | 545.4444
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.12844 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.1187 | 0 | -0.20204 | 0 | 2552 | 545.4444
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.12844 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.3701 | 0 | -0.20204 | 0 | 2552 | 545.4444
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.12844 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.1646 | 0 | -0.20204 | 0 | 2552 | 545.4444
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.12831 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.2556 | 228 | -0.20192 | -46.0372 | 2780 | 591.4816
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2076 | 0 | -0.20185 | 0 | 2780 | 591.4816
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.105 | 0 | -0.20185 | 0 | 2780 | 591.4816
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.593 | 0 | -0.20185 | 0 | 2780 | 591.4816
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.12824 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4388 | 0 | -0.20185 | 0 | 2780 | 591.4816
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.12821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.077 | 0 | -0.20181 | 0 | 2780 | 591.4816
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.12816 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -27.2979 | 213 | -0.20176 | -42.9754 | 2993 | 634.457
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.12812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -19.0903 | 0 | -0.20173 | 0 | 2993 | 634.457
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.12812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.3408 | 0 | -0.20173 | 0 | 2993 | 634.457
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.12794 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.1106 | 165 | -0.20155 | -33.2552 | 3158 | 667.7122
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.12787 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.6094 | 169 | -0.20147 | -34.0483 | 3327 | 701.7606
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.12782 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5338 | 12 | -0.20142 | -2.4171 | 3339 | 704.1776
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.12782 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.20142 | 0 | 3339 | 704.1776
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.12763 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.3573 | 0 | -0.20123 | 0 | 3339 | 704.1776
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.12672 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4352 | 0 | -0.20032 | 0 | 3339 | 704.1776
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.12491 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.7427 | 0 | -0.19851 | 0 | 3339 | 704.1776
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.12491 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.9925 | 0 | -0.19851 | 0 | 3339 | 704.1776
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9567 | 0 | -0.19601 | 0 | 3339 | 704.1776
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3447 | 0 | -0.19601 | 0 | 3339 | 704.1776
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9567 | 0 | -0.19601 | 0 | 3339 | 704.1776
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.12241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9567 | 0 | -0.19601 | 0 | 3339 | 704.1776
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9992 | 0 | -0.19447 | 0 | 3339 | 704.1776
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5882 | 0 | -0.19447 | 0 | 3339 | 704.1776
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5157 | 0 | -0.19447 | 0 | 3339 | 704.1776
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5874 | 0 | -0.19447 | 0 | 3339 | 704.1776
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.12087 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4746 | 0 | -0.19447 | 0 | 3339 | 704.1776
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.11795 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.19155 | 0 | 3339 | 704.1776
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.234 | 56 | -0.18492 | -10.3558 | 3395 | 714.5334
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5679 | 59 | -0.18492 | -10.9105
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.234 | 56 | -0.18492 | -10.3558
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.234 | 56 | -0.18492 | -10.3558
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5679 | 59 | -0.18492 | -10.9105
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.11132 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.234 | 56 | -0.18492 | -10.3558
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.8164 | 0 | -0.184 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3637 | 0 | -0.184 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8513 | 0 | -0.184 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.9134 | 0 | -0.184 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.9466 | 0 | -0.184 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.8141 | 0 | -0.184 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.5985 | 0 | -0.184 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.1104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.9378 | 0 | -0.184 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.1104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.416 | 0 | -0.184 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.11036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5315 | 0 | -0.18396 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.11036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3107 | 0 | -0.18396 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.0688 | 0 | -0.18396 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.2522 | 0 | -0.18396 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3337 | 0 | -0.18396 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.11036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2564 | 0 | -0.18396 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.9773 | 46 | -0.18181 | -8.3631
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.9773 | 46 | -0.18181 | -8.3631
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.9773 | 46 | -0.18181 | -8.3631
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.9511 | 55 | -0.18181 | -9.9993
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.9511 | 55 | -0.18181 | -9.9993
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.1082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.8429 | 54 | -0.18181 | -9.8175
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.10481 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.2406 | 50 | -0.17842 | -8.9208
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.10067 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3222 | 0 | -0.17428 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.098451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5386 | 0 | -0.17205 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.090864 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.8108 | 0 | -0.16447 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.090864 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.8108 | 0 | -0.16447 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.090864 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.2617 | 0 | -0.16447 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.090811 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -59.118 | 0 | -0.16441 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.090811 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -51.2174 | 0 | -0.16441 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.090811 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -54.4866 | 0 | -0.16441 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.089959 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0795 | 12 | -0.16356 | -1.9628
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2852 | 104 | -0.16288 | -16.94
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2852 | 104 | -0.16288 | -16.94
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8212 | 54 | -0.16288 | -8.7958
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.7319 | 53 | -0.16288 | -8.6329
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8212 | 54 | -0.16288 | -8.7958
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.089 | 57 | -0.16288 | -9.2844
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8212 | 54 | -0.16288 | -8.7958
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8212 | 54 | -0.16288 | -8.7958
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.1783 | 58 | -0.16288 | -9.4473
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.089281 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.1783 | 58 | -0.16288 | -9.4473
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.088868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -14.3077 | 161 | -0.16247 | -26.1579
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.088868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -14.7521 | 166 | -0.16247 | -26.9703
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.088868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -22.0393 | 248 | -0.16247 | -40.2929
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.088868 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -48.5219 | 546 | -0.16247 | -88.7094
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.088868 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -57.1421 | 0 | -0.16247 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.088868 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1553 | 13 | -0.16247 | -2.1121
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.084304 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9856 | 0 | -0.15791 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.084304 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84304 | 0 | -0.15791 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2006 | 0 | -0.15748 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9891 | 0 | -0.15748 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7746 | 0 | -0.15748 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.472 | 0 | -0.15748 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.2138 | 0 | -0.15748 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3815 | 0 | -0.15748 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.194 | 0 | -0.15748 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5099 | 0 | -0.15748 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.8848 | 0 | -0.15748 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8717 | 0 | -0.15748 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2845 | 0 | -0.15748 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0394 | 0 | -0.15748 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4355 | 0 | -0.15748 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.472 | 0 | -0.15748 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1365 | 0 | -0.15748 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.6397 | 0 | -0.15748 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.375 | 0 | -0.15748 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.7105 | 0 | -0.15748 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.7105 | 0 | -0.15748 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.083881 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.3437 | 0 | -0.15748 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.2676 | 0 | -0.1571 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.2676 | 0 | -0.1571 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.9355 | 0 | -0.1571 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.083492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.1424 | 0 | -0.1571 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.069926 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -93.2114 | 0 | -0.14353 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.069926 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -92.8617 | 0 | -0.14353 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.065836 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.3452 | 66 | -0.13944 | -9.203
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.3786 | 76 | -0.13122 | -9.9725
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.3786 | 76 | -0.13122 | -9.9725
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.0494 | 105 | -0.13122 | -13.7777
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2634 | 74 | -0.13122 | -9.71
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2634 | 74 | -0.13122 | -9.71
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.057613 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.8765 | 102 | -0.13122 | -13.3841
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4709 | 0 | -0.11754 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5588 | 0 | -0.11754 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4709 | 0 | -0.11754 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5149 | 0 | -0.11754 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4446 | 0 | -0.11754 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0984 | 0 | -0.11754 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0211 | 0 | -0.11754 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2302 | 0 | -0.11754 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9156 | 0 | -0.11754 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.043936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2513 | 0 | -0.11754 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.043316 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0792 | 0 | -0.11692 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1563 | 0 | -0.1149 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28908 | 0 | -0.1149 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6106 | 0 | -0.1149 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.61945 | 0 | -0.1149 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28908 | 0 | -0.1149 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.61945 | 0 | -0.1149 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6106 | 0 | -0.1149 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.041297 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6106 | 0 | -0.1149 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.041044 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.32835 | 0 | -0.11465 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.040465 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.60698 | 0 | -0.11407 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.040465 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.9307 | 0 | -0.11407 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.039484 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.86865 | 22 | -0.11309 | -2.4879
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.039484 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.43432 | 11 | -0.11309 | -1.244
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.039484 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.43432 | 11 | -0.11309 | -1.244
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.1783 | 0 | -0.11271 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.9828 | 0 | -0.11271 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.9103 | 0 | -0.11271 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.6699 | 0 | -0.11271 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.7481 | 0 | -0.11271 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.039103 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.9661 | 0 | -0.11271 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.039103 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46924 | 0 | -0.11271 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8613 | 47.7 | -0.11262 | -5.3721
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4554 | 37.3 | -0.11262 | -4.2009
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.7949 | 46 | -0.11262 | -5.1807
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.03902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.873 | 48 | -0.11262 | -5.4059
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.038924 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8415 | 0 | -0.11253 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 0 | -0.11238 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 0 | -0.11238 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 0 | -0.11238 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.62043 | 0 | -0.11238 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 0 | -0.11238 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 0 | -0.11238 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.96942 | 0 | -0.11238 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.038777 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.58166 | 0 | -0.11238 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.038246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.8507 | 336 | -0.11185 | -37.5814
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.038246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8843 | 180 | -0.11185 | -20.1329
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.038236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.6704 | 0 | -0.11184 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.038236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.6819 | 0 | -0.11184 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.038236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.8501 | 0 | -0.11184 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.03822 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8796 | 180 | -0.11182 | -20.1282
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.038063 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.713 | 334 | -0.11167 | -37.2966
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.038063 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.9414 | 340 | -0.11167 | -37.9666
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.038063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8513 | 180 | -0.11167 | -20.1
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.038063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8513 | 180 | -0.11167 | -20.1
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.038056 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4801 | 144 | -0.11166 | -16.079
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.038056 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1545 | 188 | -0.11166 | -20.992
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.037996 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.9499 | 0 | -0.1116 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.037996 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.9499 | 0 | -0.1116 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.037938 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4416 | 0 | -0.11154 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.037895 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.44 | 0 | -0.1115 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.037533 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0885 | 0 | -0.11114 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.512 | 0 | -0.11097 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5318 | 0 | -0.11097 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4198 | 0 | -0.11097 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.70988 | 0 | -0.11097 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.512 | 0 | -0.11097 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.345 | 0 | -0.11097 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6066 | 0 | -0.11097 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.82196 | 0 | -0.11097 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.5296 | 0 | -0.11097 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8681 | 0 | -0.11097 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0549 | 0 | -0.11097 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.037362 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8681 | 0 | -0.11097 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.037246 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4153 | 38 | -0.11085 | -4.2123
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.037246 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.71885 | 19.3 | -0.11085 | -2.1394
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.037246 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.55869 | 15 | -0.11085 | -1.6627
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.037246 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7506 | 47 | -0.11085 | -5.2099
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.037245 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11085 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.03694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3194 | 144 | -0.11054 | -15.9183
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.03694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3194 | 144 | -0.11054 | -15.9183
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.03694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3167 | 171 | -0.11054 | -18.9029
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.036937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.646 | 207 | -0.11054 | -22.8819
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.036937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.0042 | 216.7 | -0.11054 | -23.9541
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.036937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9388 | 242 | -0.11054 | -26.7508
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.036509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3486 | 146.5 | -0.11011 | -16.1315
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.036509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3997 | 147.9 | -0.11011 | -16.2856
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.036509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3161 | 173 | -0.11011 | -19.0495
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.035259 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10886 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.034742 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.8527 | 0 | -0.10835 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.033909 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.40691 | 0 | -0.10751 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.033909 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.373 | 0 | -0.10751 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.033909 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.40691 | 0 | -0.10751 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.032998 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1066 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.031422 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10503 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.027673 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.9585 | 0 | -0.10128 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.02767 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.027667 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.7667 | 100 | -0.10127 | -10.1271
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.027667 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.7667 | 100 | -0.10127 | -10.1271
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.027667 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.027667 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.027667 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.027667 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10127 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.023846 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.0199 | 0 | -0.09745 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.023846 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.8845 | 0 | -0.09745 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.023671 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.5681 | 24 | -0.097275 | -2.3346
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.023671 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.5681 | 24 | -0.097275 | -2.3346
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.023671 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.54443 | 23 | -0.097275 | -2.2373
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.023266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6062 | 155 | -0.09687 | -15.0148
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.023266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9552 | 170 | -0.09687 | -16.4678
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.023266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6062 | 155 | -0.09687 | -15.0148
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.023191 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.27829 | 0 | -0.096795 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.022803 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.19155 | 8.4 | -0.096407 | -0.80981
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.022611 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.096215 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.022611 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.096215 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.022611 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.096215 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.022567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.7165 | 209 | -0.096171 | -20.0996
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.022567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.8745 | 216 | -0.096171 | -20.7728
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0381 | 46 | -0.096171 | -4.4238
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0606 | 47 | -0.096171 | -4.52
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0381 | 46 | -0.096171 | -4.4238
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.022567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0381 | 46 | -0.096171 | -4.4238
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.022523 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.5498 | 0 | -0.096127 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.022523 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.5723 | 0 | -0.096127 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.022513 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3058 | 58 | -0.096117 | -5.5748
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.022513 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0037 | 89 | -0.096117 | -8.5544
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.99057 | 44 | -0.096117 | -4.2291
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.99057 | 44 | -0.096117 | -4.2291
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.96806 | 43 | -0.096117 | -4.133
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.022513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0131 | 45 | -0.096117 | -4.3252
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.022488 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.2651 | 412 | -0.096092 | -39.5897
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.022488 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.9952 | 400 | -0.096092 | -38.4366
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.022486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1518 | 407 | -0.09609 | -39.1084
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2046 | 147 | -0.095404 | -14.0243
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0084 | 138 | -0.095404 | -13.1657
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.052 | 140 | -0.095404 | -13.3565
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2046 | 147 | -0.095404 | -14.0243
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9676 | 182 | -0.095404 | -17.3634
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.0218 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3164 | 198 | -0.095404 | -18.8899
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.019262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.077048 | 0 | -0.092866 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6902 | 142 | -0.092549 | -13.1419
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.747 | 145 | -0.092549 | -13.4195
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8607 | 151 | -0.092549 | -13.9748
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.018945 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.494 | 290 | -0.092549 | -26.8391
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.018327 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.043985 | 0 | -0.091931 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.018327 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.043985 | 0 | -0.091931 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.017816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.042758 | 0 | -0.09142 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.017816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.042758 | 0 | -0.09142 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.017816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.049885 | 0 | -0.09142 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9746 | 0 | -0.090925 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8453 | 0 | -0.090925 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1871 | 0 | -0.090925 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8799 | 0 | -0.090925 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9919 | 0 | -0.090925 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5658 | 223.9 | -0.08953 | -20.0457
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5833 | 225 | -0.08953 | -20.1441
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.577 | 224.6 | -0.08953 | -20.1083
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.015926 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6104 | 226.7 | -0.08953 | -20.2963
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01243 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07458 | 0 | -0.086034 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.012363 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -5.3532 | 0 | -0.085967 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.012231 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -7.1429 | 0 | -0.085835 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.012231 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -7.2774 | 0 | -0.085835 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.009932 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.083536 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.008171 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.049026 | 0 | -0.081775 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3619 | 50 | -0.080842 | -4.0421
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3619 | 50 | -0.080842 | -4.0421
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3619 | 50 | -0.080842 | -4.0421
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.007238 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3619 | 50 | -0.080842 | -4.0421
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.00475 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7505 | 158 | -0.078354 | -12.3799
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.00475 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76 | 160 | -0.078354 | -12.5366
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.00475 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83125 | 175 | -0.078354 | -13.7119
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.004354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.66399 | 152.5 | -0.077958 | -11.8885
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.004354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.65092 | 149.5 | -0.077958 | -11.6546
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.004354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0127 | 232.6 | -0.077958 | -18.1329
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.002359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31139 | 132 | -0.075963 | -10.0271
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.002359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31611 | 134 | -0.075963 | -10.179
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.002359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.76196 | 323 | -0.075963 | -24.5359
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.041209 | 49 | -0.074445 | -3.6478
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.038686 | 46 | -0.074445 | -3.4244
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.038686 | 46 | -0.074445 | -3.4244
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.039527 | 47 | -0.074445 | -3.4989
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.000841 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.12951 | 154 | -0.074445 | -11.4645
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.000841 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.12447 | 148 | -0.074445 | -11.0178
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.040368 | 48 | -0.074445 | -3.5733
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.000841 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.040368 | 48 | -0.074445 | -3.5733
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.000601 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.019833 | 0 | -0.074205 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.000601 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.015025 | 0 | -0.074205 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.000601 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.074205 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.073604 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.073604 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.073604 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.000275 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0022 | 0 | -0.073329 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.000275 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0022 | 0 | -0.073329 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.000294 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.09114 | 310 | -0.07331 | -22.7259
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.000294 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.12142 | 413 | -0.07331 | -30.2768
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04746 | 42 | -0.072474 | -3.0439
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04972 | 44 | -0.072474 | -3.1888
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04972 | 44 | -0.072474 | -3.1888
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00113 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.05311 | 47 | -0.072474 | -3.4063
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.001274 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04459 | 0 | -0.07233 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.001274 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.043316 | 0 | -0.07233 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.001274 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04459 | 0 | -0.07233 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.002518 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.045324 | 0 | -0.071086 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.002518 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.045324 | 0 | -0.071086 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.003066 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2939 | 422 | -0.070538 | -29.7668
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.003305 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.09254 | 0 | -0.070299 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.003305 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.095845 | 0 | -0.070299 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.006937 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.095037 | 0 | -0.066667 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.007815 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14067 | 0 | -0.065789 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.007815 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14067 | 0 | -0.065789 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.007815 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11722 | 0 | -0.065789 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.018966 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 10.7917 | 0 | -0.054638 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.018966 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.0192 | 0 | -0.054638 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.017321 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -1.7321 | 0 | 0.09637 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.11369 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.11369 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.015554 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.12924 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.045265 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7897 | 0 | 0.15896 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.050032 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.16372 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.052588 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16628 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.052588 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16628 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.05334 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16703 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.05334 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 41.9786 | 787 | 0.16703 | 131.4532
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.054461 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8876 | 255 | 0.16815 | 42.8787
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.054461 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.1147 | 149 | 0.16815 | 25.0546
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.054461 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.3325 | 153 | 0.16815 | 25.7272
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.055436 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.3154 | 150 | 0.16913 | 25.369
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.055436 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4349 | 80 | 0.16913 | 13.5301
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.056894 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7791 | 0 | 0.17058 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.057112 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3691 | 0 | 0.1708 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057325 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.586 | 0 | 0.17102 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.057669 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.86503 | 0 | 0.17136 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.057669 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.86503 | 0 | 0.17136 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.0586 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.79 | 0 | 0.17229 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.0586 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.79 | 0 | 0.17229 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.058632 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6906 | 0 | 0.17232 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.05864 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6912 | 0 | 0.17233 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.058695 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4021 | 0 | 0.17239 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058695 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6956 | 0 | 0.17239 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.058695 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3478 | 0 | 0.17239 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058951 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7161 | 0 | 0.17264 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058951 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7161 | 0 | 0.17264 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.059895 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.2875 | 0 | 0.17359 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1039 | 66 | 0.17587 | 11.6075
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.0417 | 65 | 0.17587 | 11.4316
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1661 | 67 | 0.17587 | 11.7833
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1661 | 67 | 0.17587 | 11.7833
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.06218 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1661 | 67 | 0.17587 | 11.7833
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.06218 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17587 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.06218 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17587 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.062211 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1774 | 0 | 0.1759 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.062211 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8663 | 0 | 0.1759 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.062291 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5583 | 0 | 0.17598 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.062317 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2852 | 0 | 0.17601 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.062513 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.41259 | 0 | 0.1762 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.062513 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1442 | 0 | 0.1762 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.0536 | 0 | 0.17639 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3735 | 0 | 0.17639 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.662 | 0 | 0.17639 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.062699 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.4489 | 0 | 0.17639 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.0754 | 208.2 | 0.17649 | 36.7458
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.9242 | 142.1 | 0.17649 | 25.0796
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.315 | 132.4 | 0.17649 | 23.3676
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.5411 | 136 | 0.17649 | 24.003
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.2319 | 147 | 0.17649 | 25.9444
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.062802 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.1884 | 210 | 0.17649 | 37.0635
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3966 | 70 | 0.1765 | 12.3549
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3966 | 70 | 0.1765 | 12.3549
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8286 | 92.8 | 0.1765 | 16.3791
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.0246 | 80 | 0.1765 | 14.1199
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.0246 | 80 | 0.1765 | 14.1199
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.062808 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.2229 | 115 | 0.1765 | 20.2974
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.062825 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6439 | 0 | 0.17652 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.062829 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4244 | 0 | 0.17652 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.062836 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.315 | 0 | 0.17653 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.06291 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.4753 | 0 | 0.1766 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.062949 | west | 8 | N | N | Nwest | Nwest | 1 | 1.6241 | 0 | 0.17664 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.063142 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.577 | 0 | 0.17683 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.063156 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5787 | 0 | 0.17685 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.063213 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5856 | 0 | 0.1769 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.063213 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7286 | 0 | 0.1769 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.063213 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7589 | 0 | 0.1769 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.063214 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.2232 | 0 | 0.1769 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.063246 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3843 | 0 | 0.17694 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.063246 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3843 | 0 | 0.17694 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.063252 | west | 8 | N | N | Nwest | Nwest | 1 | 4.4276 | 0 | 0.17694 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.063252 | west | 8 | N | N | Nwest | Nwest | 1 | 4.6427 | 0 | 0.17694 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.063252 | west | 8 | N | N | Nwest | Nwest | 1 | 4.4529 | 0 | 0.17694 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5028 | 0 | 0.17704 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.9374 | 0 | 0.17704 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6704 | 0 | 0.17704 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.063352 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7226 | 0 | 0.17704 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1862 | 66 | 0.17712 | 11.6898
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3765 | 69 | 0.17712 | 12.2211
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3765 | 69 | 0.17712 | 12.2211
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.2496 | 67 | 0.17712 | 11.8669
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.2496 | 67 | 0.17712 | 11.8669
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.063427 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1228 | 65 | 0.17712 | 11.5127
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.063451 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9974 | 0 | 0.17714 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.063476 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9501 | 0 | 0.17717 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.063476 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6171 | 0 | 0.17717 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.063486 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.2851 | 0 | 0.17718 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.063486 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8726 | 0 | 0.17718 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.063486 | west | 7 | N | N | Nwest | Nwest | 1 | 1.5872 | 0 | 0.17718 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.063486 | west | 7 | N | N | Nwest | Nwest | 1 | 2.9013 | 0 | 0.17718 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.063486 | west | 7 | N | N | Nwest | Nwest | 1 | 2.9013 | 0 | 0.17718 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.063568 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3397 | 0 | 0.17726 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.063613 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5419 | 0 | 0.1773 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.063613 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4249 | 0 | 0.1773 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.063682 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9603 | 0 | 0.17737 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.063682 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9603 | 0 | 0.17737 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3949 | 0 | 0.17755 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8653 | 0 | 0.17755 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6215 | 0 | 0.17755 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5997 | 0 | 0.17755 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7056 | 0 | 0.17755 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.063863 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.141 | 0 | 0.17755 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3578 | 0 | 0.1776 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.085 | 0 | 0.1776 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9143 | 0 | 0.1776 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.063913 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5909 | 0 | 0.1776 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.063931 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5897 | 0 | 0.17762 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.064014 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.8408 | 0 | 0.1777 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.064395 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8637 | 0 | 0.17809 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.065061 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.0244 | 0 | 0.17875 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.065064 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3551 | 0 | 0.17875 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.065452 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7996 | 0 | 0.17914 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.065785 | west | 4 | Y | N | Ywest | Nwest | 1 | 42.7405 | 0 | 0.17948 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.06607 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.8231 | 73 | 0.17976 | 13.1225
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.06607 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.8623 | 119 | 0.17976 | 21.3915
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.06607 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.5443 | 205 | 0.17976 | 36.851
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.06607 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.7391 | 102 | 0.17976 | 18.3356
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.06607 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.3427 | 96 | 0.17976 | 17.257
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.066309 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.0468 | 242 | 0.18 | 43.5599
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.06651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1737 | 168 | 0.1802 | 30.2737
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.06651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.9859 | 90 | 0.1802 | 16.2181
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.066644 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.9973 | 0 | 0.18033 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.066683 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.406 | 366 | 0.18037 | 66.0168
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.066729 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.80075 | 0 | 0.18042 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.066729 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.80075 | 0 | 0.18042 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.3351 | 20 | 0.18045 | 3.6089
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.3351 | 20 | 0.18045 | 3.6089
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.3351 | 20 | 0.18045 | 3.6089
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.066755 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1348 | 17 | 0.18045 | 3.0676
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.6851 | 70 | 0.18062 | 12.6435
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.6182 | 69 | 0.18062 | 12.4628
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.6182 | 69 | 0.18062 | 12.4628
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.06693 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.5512 | 68 | 0.18062 | 12.2822
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.067305 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.2115 | 18 | 0.181 | 3.2579
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.067305 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.2115 | 18 | 0.181 | 3.2579
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.067305 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.5576 | 38 | 0.181 | 6.8778
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.067492 | north | 3 | N | N | Nnorth | Nnorth | 1 | 78.0882 | 0 | 0.18118 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.067492 | north | 3 | N | N | Nnorth | Nnorth | 1 | 78.1557 | 0 | 0.18118 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.067658 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.7021 | 217.3 | 0.18135 | 39.4071
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.067658 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8699 | 205 | 0.18135 | 37.1765
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.067658 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.43 | 272.4 | 0.18135 | 49.3994
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.067686 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8079 | 204 | 0.18138 | 37.0009
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.067686 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6049 | 201 | 0.18138 | 36.4567
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.067686 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.38 | 242 | 0.18138 | 43.8932
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.067806 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1815 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.068072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.6047 | 288 | 0.18176 | 52.3477
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.068072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.0066 | 147 | 0.18176 | 26.7191
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.068072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.0066 | 147 | 0.18176 | 26.7191
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.2602 | 224 | 0.18182 | 40.727
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.3965 | 226 | 0.18182 | 41.0906
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.4427 | 212 | 0.18182 | 38.5452
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.068126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3746 | 211 | 0.18182 | 38.3633
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.068747 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18244 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.068747 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18244 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.068747 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18244 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.0688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.8883 | 216.4 | 0.18249 | 39.491
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.0688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.8677 | 216.1 | 0.18249 | 39.4363
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.068902 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.2163 | 395 | 0.18259 | 72.1241
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.068902 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 29.9724 | 435 | 0.18259 | 79.4279
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.068988 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.7611 | 0 | 0.18268 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.069043 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 30.0337 | 435 | 0.18273 | 79.4892
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.069682 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.1809 | 60 | 0.18337 | 11.0024
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.069682 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.39 | 63 | 0.18337 | 11.5525
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.070349 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7884 | 196 | 0.18404 | 36.0718
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.070349 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.8087 | 111 | 0.18404 | 20.4284
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.070731 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18442 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.070879 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.18457 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.070901 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.3663 | 118 | 0.18459 | 21.7818
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.070901 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.1536 | 115 | 0.18459 | 21.2281
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.070901 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 39.421 | 556 | 0.18459 | 102.633
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.071038 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.8415 | 0 | 0.18473 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.071038 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.8415 | 0 | 0.18473 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.07114 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.0938 | 170 | 0.18483 | 31.4212
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.07114 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 36.9928 | 520 | 0.18483 | 96.112
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.071268 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.3692 | 370 | 0.18496 | 68.4347
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.9775 | 0 | 0.18496 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.0488 | 0 | 0.18496 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.0218 | 0 | 0.18496 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.1913 | 0 | 0.18496 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.2626 | 0 | 0.18496 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.071268 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.0931 | 0 | 0.18496 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.4118 | 160 | 0.18501 | 29.6024
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1265 | 156 | 0.18501 | 28.8623
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.9795 | 196 | 0.18501 | 36.2629
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1265 | 156 | 0.18501 | 28.8623
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1979 | 157 | 0.18501 | 29.0473
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.071324 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.1222 | 198 | 0.18501 | 36.6329
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.071364 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.3523 | 0 | 0.18505 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.071364 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.6806 | 0 | 0.18505 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.071364 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.3086 | 0 | 0.18505 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.071422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 39.8535 | 0 | 0.18511 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.071422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 41.3533 | 0 | 0.18511 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.071422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 57.709 | 0 | 0.18511 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.071494 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.648 | 79 | 0.18518 | 14.6296
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.071494 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.5784 | 106 | 0.18518 | 19.6296
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.071494 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.4381 | 146 | 0.18518 | 27.037
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.071494 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.4335 | 76 | 0.18518 | 14.074
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.071497 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8599 | 40 | 0.18519 | 7.4075
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.071533 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.18522 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.071533 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.18522 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.071582 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4316 | 20 | 0.18527 | 3.7055
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.071582 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.7895 | 25 | 0.18527 | 4.6318
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.071582 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.9349 | 41 | 0.18527 | 7.5962
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.071665 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 27.806 | 388 | 0.18536 | 71.918
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.071665 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 36.9075 | 515 | 0.18536 | 95.4582
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6081 | 161 | 0.18579 | 29.9123
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8244 | 164 | 0.18579 | 30.4697
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8244 | 164 | 0.18579 | 30.4697
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8494 | 414 | 0.18579 | 76.9174
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6802 | 162 | 0.18579 | 30.0981
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6081 | 161 | 0.18579 | 29.9123
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7523 | 163 | 0.18579 | 30.2839
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.0721 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.4889 | 409 | 0.18579 | 75.9884
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.072199 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.1726 | 224 | 0.18589 | 41.6393
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.074082 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 58.1544 | 0 | 0.18777 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.074082 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 58.8952 | 0 | 0.18777 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.074082 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 57.784 | 0 | 0.18777 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.0069 | 0 | 0.18806 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.6682 | 0 | 0.18806 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.7838 | 0 | 0.18806 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.074371 | north | 1 | N | N | Nnorth | Nnorth | 1 | 29.674 | 0 | 0.18806 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.074624 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.18831 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.074654 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.7327 | 0 | 0.18834 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.074693 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.5941 | 182 | 0.18838 | 34.2858
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.074693 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 36.1514 | 484 | 0.18838 | 91.1777
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.077609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7578 | 151.5 | 0.1913 | 28.9819
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.077609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8199 | 152.3 | 0.1913 | 29.135
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.077609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7756 | 177.5 | 0.1913 | 33.9557
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.077738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7151 | 150.7 | 0.19143 | 28.8483
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.077738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7384 | 151 | 0.19143 | 28.9057
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.077738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7907 | 177.4 | 0.19143 | 33.9595
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.078422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 48.2295 | 0 | 0.19211 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.078422 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 46.0337 | 0 | 0.19211 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.1582 | 0 | 0.19902 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.3118 | 0 | 0.19902 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.3118 | 0 | 0.19902 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.085332 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.4262 | 0 | 0.19902 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.086419 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 71.4685 | 0 | 0.20011 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.086419 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 70.7772 | 0 | 0.20011 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.324 | 0 | 0.2053 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.324 | 0 | 0.2053 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.9517 | 0 | 0.2053 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.091607 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.0159 | 0 | 0.2053 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.095389 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.5787 | 48 | 0.20908 | 10.0358
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.095389 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3879 | 46 | 0.20908 | 9.6177
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.095389 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.0158 | 105 | 0.20908 | 21.9534
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21127 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21127 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.097579 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6588 | 17 | 0.21127 | 3.5916
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21127 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.097579 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21127 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.097791 | north | 7 | N | N | Nnorth | Nnorth | 1 | 3.1293 | 0 | 0.21148 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.10486 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 48.5493 | 0 | 0.21855 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown