## test results
CRE test for: |  | 46500 TOMBAL__ - 45971 KYUDAL74 | [5 empty] | PASS
Line Rating: |  | 1759
Direction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 46500 TOMBAL__ - 45971 KYUDAL74
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.085757
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.020092
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.073398
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.11243
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 46500 TOMBAL__ - 45971 KYUDAL74
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.080681
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.021619
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.073565
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.11684
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 46500 TOMBAL__ - 45971 KYUDAL74
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.10738
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.012191
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.2026
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.093657
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.092334
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.19024
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.2026 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.2026 | 0.10738
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.22632
[6 empty] | Concentration |  | 1.1171 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.22105
[6 empty] | Concentration |  | 1.0911 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 31.1185
| Percent of line rating => | [6 empty] | 1.769% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.6977
[7 empty] | B1(N-S) | 0.046059 | 0.22835 | 0.18229 | 0.046059
[7 empty] | B2 (N-W) | 0.0054351 | 0.026133 | 0.020698 | 0.0054351
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.040286 | -0.19929 | -0.159 | -0.040286
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.03822 | 0.11854 | 0.15676 | -0.03822
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0055068 | 0.31747 | 0.32298 | -0.0055068
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 13.39%
Deployment Error Percent | [6 empty] | B2 | 1.58%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -11.71%
[7 empty] | B5 | -11.11%
[7 empty] | B6 | -1.601%
[7 empty] | Max Abs Error | 13.39% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | n-h
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:46500 TOMBAL__ - 45971 KYUDAL74 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:46500 TOMBAL__ - 45971 KYUDAL74 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.063685 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 16.2397
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.063685 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 9.4891
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.067387 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.0108
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.067387 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.0108
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.063685 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 9.7438
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.064811 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 9.7217
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.064811 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 5.1849
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.077093 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 5.6278
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.077093 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 9.1741
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.077093 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 15.8041
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.077093 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 7.8635
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.077093 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 7.4009
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.077859 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.93431
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.077859 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.93431
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.07759 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 13.0351
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.07759 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 6.9831
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.078514 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.4133
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.078514 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.4133
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.078514 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 2.9835
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.079397 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 22.8663
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.079397 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 11.6714
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.079397 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 11.6714
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.080451 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 9.0507
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.083333 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 3.3333
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.08333 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 6.5831
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.08333 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 8.833
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.08333 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 12.1662
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.08333 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 6.3331
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.081247 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 4.8748
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.081247 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 5.1186
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.08343 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 1.6686
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.08343 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 2.0857
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.08343 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 3.4206
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.12175 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 56.3698
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 4.7971
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 4.7245
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 4.8698
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 4.8698
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 4.8698
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.072684 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 8.286
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.072684 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 37.4323
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 4.8906
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 5.1129
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 5.1129
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 4.9647
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 4.9647
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 4.8165
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.073901 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 5.1731
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.073901 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 5.4243
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.073901 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 5.2026
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 11.1024
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 16.2835
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.074167 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 7.3425
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.074167 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 4.5242
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.074156 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 10.456
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.074167 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 1.8542
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.074167 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 3.3894
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.074167 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 3.3894
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.074156 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 8.8987
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.073556 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 1.8977
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.073429 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 7.3796
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.073775 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 8.853
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.073417 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 4.2582
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.073512 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 15.7463
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.074309 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 11.1463
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.073058 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.48218
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.073058 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 2.5059
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.074309 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 7.5052
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.073791 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 8.8549
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.077814 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 28.4799
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.077383 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 18.7267
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.075963 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 30.3852
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.075966 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 17.928
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.076409 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 12.6075
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.078959 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 16.1076
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.078959 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 15.8708
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.078959 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 19.1081
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.5579
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.5579
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.5579
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 1.3242
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.077761 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 9.3313
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.074733 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 4.484
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.083181 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 6.2386
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.083181 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 6.6212
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.083181 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 7.3532
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 13.3014
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 12.9689
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 16.2943
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 12.9689
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 13.052
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 16.4605
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.082923 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 14.0969
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.082923 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 43.12
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.08307 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 30.7359
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.083246 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 46.4513
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.083246 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 48.1994
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.083246 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 67.2628
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.080172 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 8.9793
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.080172 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 8.0172
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.080172 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 30.305
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.078918 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 17.1489
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.078918 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 16.1782
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.078918 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 21.4973
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.079088 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 60.8978
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 5.4655
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 5.3874
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 5.3874
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 5.3093
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.078727 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 91.0871
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.078727 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 91.1659
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 17.7964
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 17.9552
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.080222 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 17.36
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.080222 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 17.336
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 16.843
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 16.7635
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.080346 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 31.7367
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.080508 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 35.021
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.080346 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 34.9505
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.082452 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 11.3784
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.082646 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 9.7522
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.082646 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 9.5043
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.082646 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 45.9512
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.083526 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 32.4081
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.083526 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 43.0159
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.086307 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 67.751
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.086307 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 68.6141
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.086307 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 67.3195
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.08701 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 15.8358
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.08701 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 42.1128
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.084137 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 18.8467
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.086965 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 4.3483
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.086931 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 3.6511
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.091303 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 56.1513
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.091303 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 53.5949
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.06239 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 33.5034
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.06239 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 49.1009
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.061522 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 4.6142
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.061522 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 13.6579
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.022732 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 12.9345
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.023592 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -4.9307
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.023592 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -5.0959
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.02349 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -9.5604
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0852
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -1.1088
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0852
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0852
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.023533 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -9.978
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.023533 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -10.0015
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.023516 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -1.3639
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.023516 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -2.0929
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.0347
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.0347
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -1.0112
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.0582
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.023502 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -9.6828
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.023502 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -9.4008
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.024973 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -13.6353
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.024973 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -18.7297
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.023635 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -1.4417
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.023635 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -2.2453
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.023635 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -3.5689
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.024341 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.7729
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.024341 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -4.138
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.024341 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.7729
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.042263 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.92979
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.042263 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.46489
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.042263 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.46489
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -1.9925
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -1.5581
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -1.9215
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -2.0051
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.035806 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.42967
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.035806 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.39387
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.02462 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.59088
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.02462 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.59088
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.02462 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.56626
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.029096 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -11.522
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.074209 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -98.9206
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.074209 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -98.5496
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.039454 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -1.4993
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.039454 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.76146
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.039454 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.59181
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.039454 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -1.8543
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.068725 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 5.1544
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.074673 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 11.201
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.0728 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 12.3396
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.05343 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 8.0145
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.074127 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 4.67
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.076788 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 49.8892
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.082805 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 3.3122
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.082805 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 3.3122
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.004787 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 2.0201
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.002613 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -0.34492
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.002613 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -0.35014
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.002613 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -0.844
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.004824 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -0.76219
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.004824 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -0.77184
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.004824 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -0.8442
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.013993 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -8.1719
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.013993 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -8.3258
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.014122 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -6.1148
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -3.6932
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -3.7114
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -3.7048
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -3.7394
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.001266 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.010128
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.001266 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.010128
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.010164 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.18295
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.010164 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.18295
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.010164 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.15246
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.009185 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.12583
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.004092 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.073656
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.004092 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.073656
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.002516 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.08806
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.002516 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.085544
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.002516 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.08806
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.005042 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.14118
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.005042 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.14622
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.072719 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 2.5452
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.072719 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 2.1816
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.47855
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.47855
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.47855
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.47855
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.012682 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.076092
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.018688 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.044851
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.018688 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.044851
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.018688 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.052326
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.020068 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.080272
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.019593 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.047023
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.019593 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.047023
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.3482
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -3.1432
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -3.1888
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.3482
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -4.1454
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -4.5098
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004031 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -0.61473
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004031 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -0.60263
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004031 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -0.93761
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -2.8008
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -2.86
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -2.9783
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -5.72
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.001514 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.049962
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.001514 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.03785
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.035806 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.42967
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.041708 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -3.0447
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -3.7237
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -3.818
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -1.2388
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.30971
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -3.7237
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -3.7709
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -3.6955
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.1784
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -2.1683
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.036963 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -23.2497
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.040777 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -5.8719
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.040777 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -7.6661
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.024987 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.29984
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.007046 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.042276
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.040559 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -13.6278
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.040358 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -13.4796
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.040358 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -13.7217
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.040185 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -1.527
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.040292 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.0073
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.040292 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.0073
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.040226 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -1.5286
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.039775 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -1.1535
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.040548 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -6.0133
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.040548 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -6.0254
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.040548 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -6.2038
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -6.5561
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -6.3486
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -4.1494
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -6.0166
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -6.0996
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -5.2697
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.038649 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -5.6621
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.038649 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -5.7162
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.038649 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -6.6863
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.039117 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -8.0972
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.039117 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -8.4767
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.039117 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -9.4663
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.03912 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -5.6333
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.03912 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -5.6333
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.03912 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -6.6895
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.001245 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 0.38595
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.001245 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 0.51419
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.089754
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.094028
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.094028
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.10044
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.001225
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.00115
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.00115
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.001175
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -2.5e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.00385
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -2.5e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.0037
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.0012
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.0012
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 5.1378
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 5.1378
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 6.8112
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 5.8718
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 5.8718
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 8.4407
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 15.2798
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 10.4287
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 9.7168
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 9.981
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 10.7883
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 15.4119
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 15.6027
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 9.4437
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 18.5888
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 14.7068
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 14.8032
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 9.0226
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.07284 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 10.8532
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.073895 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 13.3011
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.073895 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 13.3011
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.073858 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 16.6181
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.074391 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 9.2989
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.074391 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 9.2989
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 11.6298
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 11.7129
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 25.6686
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 11.879
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 11.9621
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 25.7517
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.082007 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 16.0734
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.082007 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 9.1028
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.082622 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 13.5282
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 13.7803
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 13.7803
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 34.7868
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 13.6122
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 13.5282
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 13.6962
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 34.3666
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.083373 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.083373 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 12.8226
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 11.2631
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 12.5627
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 34.569
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.090515 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 13.6406
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.090515 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 13.6678
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.090515 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 16.0574
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.090367 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 13.6906
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.090367 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 13.7629
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.090367 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 16.0401
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.022732 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 13.2073
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 91.0455
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 91.0455
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.1136 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 3.6353
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.11084 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 5.3202
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.11084 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 5.0985
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 1.3603
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 5.7814
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.11336 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 1.9271
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 2.4939
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 2.834
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.11084 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 11.6379
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.074261 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 6.2379
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.068654 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 5.4923
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.068617 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 10.2926
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.068617 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 10.2926
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -8.0157
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -7.5515
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -6.0004
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -17.3447
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -17.3787
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -17.2428
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -10.8687
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -27.6247
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -4.5286
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -11.3516
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -10.5141
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -11.6232
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -11.544
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.11318 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -3.6217
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.11318 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -3.3953
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -9.9433
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -9.9433
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -10.6599
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -9.8089
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 16.2178
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 16.2924
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.12887 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -17.5256
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.10493 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -3.4627
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -5.5505
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -5.5505
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -5.0219
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -5.0219
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.089558 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -6.3586
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.089558 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.89558
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.096738 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -15.7683
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.096738 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -15.7683
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.096738 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -23.7008
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -8.0768
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -7.4555
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -8.0768
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -8.0768
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.12893 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -19.2107
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.12893 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -8.3934
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -11.1751
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -10.7575
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -10.6839
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -6.6928
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -1.4982
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.13928 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -103.4821
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.13651 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -100.3371
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.14191 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -24.4083
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.14191 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -24.4083
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.14191 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -24.4083
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -28.9552
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.1297 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -22.4383
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.1297 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -17.5096
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -23.6485
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -23.4451
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -23.082
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -39.1043
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -8.2625
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -8.1592
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -10.6638
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -9.5019
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -21.3433
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -20.5455
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -20.5979
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -20.5325
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -35.1798
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.13596 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.6798
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.13596 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -2.8551
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 15.8626
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 16.0477
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 16.0477
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 39.0906
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.13866 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -55.1871
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -5.2585
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -5.2585
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -5.2585
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -6.2873
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -6.2873
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -6.173
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.10051 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 83.1218
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.10051 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 82.3177
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.10294 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -4.7456
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -4.9474
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -4.9474
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -6.8352
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -4.8172
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -4.8172
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -6.6399
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.12912 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -23.2425
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.12912 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -20.4792
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.12912 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -20.2726
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.12776 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -4.4714
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.11997 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -55.0685
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -8.7394
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -8.8738
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -9.4116
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -8.4705
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -8.336
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -13.983
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -7.9327
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -26.1099
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -25.7751
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -25.7751
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -27.1141
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.13519 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -21.2253
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -9.2482
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -9.3785
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -5.08
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -3.9077
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.12664 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -9.878
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.12664 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -10.1313
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.12909 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -2.0912
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.12886 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -21.2619
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.1288 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -21.7667
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.12907 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -27.4921
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.12913 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -29.4412
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.12875 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -1.545
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.12875 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -2.3176
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.11002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -5.501
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -10.4223
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -10.4223
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -5.4116
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -5.3113
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -5.4116
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -5.7122
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -5.4116
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -5.4116
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -5.8124
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -5.8124
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.10417 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -1.2501
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -6.5509
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -6.9019
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -6.5509
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -6.5509
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -6.9019
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -6.5509
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.072199 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -4.7651
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.096086 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -15.4698
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.096086 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -15.9503
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.096086 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -23.8293
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.096086 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -52.463
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.096086 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -61.7833
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.096676 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -62.9361
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.096676 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -54.5253
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.096676 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -58.0056
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.096086 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -1.2491
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.13754 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -1.6505
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -4.6145
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -4.7095
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -4.4381
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -6.2296
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -2.4023
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -2.7687
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -2.7008
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -4.7502
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -2.443
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -11.5906
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -20.0867
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -5.4837
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -6.3151
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -3.9801
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -8.9331
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -7.6064
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -7.7833
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -4.4223
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -1.592
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -8.314
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -6.1913
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -5.5722
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -6.3682
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -5.7314
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -8.9331
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -8.5794
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -9.11
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -6.722
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -7.0758
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -7.0758
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -15.1244
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1986
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.066926 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 5.1198
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.068725 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 5.498
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.068725 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 2.749
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.069015 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 5.5212
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.068662 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 5.493
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.067168 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 5.3734
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.066679 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 5.601
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.069015 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 5.5212
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -2.0379
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.073852 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 8.8622
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.073852 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 17.2075
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.073852 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 12.5696
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -3.9685
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -3.2892
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -4.0042
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -2.0557
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -1.7876
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.075202 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 4.5121
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.01934 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.058885 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.070088 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.33642
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 2.7973
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 8.0191
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 10.0705
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 8.8769
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 7.8326
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 6.005
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.073417 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 11.0125
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 8.2425
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 10.9534
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 13.6277
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 15.7158
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.039454 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.009037 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.028995 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -1.3198
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -2.0551
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -3.4881
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -3.7206
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -1.6228
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -1.5041
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.75204
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -3.7206
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -1.4249
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -1.702
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.87078
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.7255
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.66366
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.30971
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.66366
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.7255
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.7255
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -5.858
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -1.979
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -2.177
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -1.979
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.041494 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.49793
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.043341 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.65011
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.043341 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.99684
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.046459 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -2.23
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.043945 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.35156
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.04053 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -7.2954
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.040559 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -7.3006
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.040358 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -7.2644
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.040358 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -7.2644
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.028992 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -2.8992
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.028992 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -2.8992
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.0283
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.0283
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.0283
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.65811
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.0283
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.0283
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.0283
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.61698
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.028992 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.028992 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -14.496
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.028992 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -14.496
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.028992 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.034987 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.001514 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.033085 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.037301 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:46500 TOMBAL__ - 45971 KYUDAL74 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | [7 empty] | 31.1185
Number of Bus | Name of Bus | ID | Max MW | L:46500 TOMBAL__ - 45971 KYUDAL74 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.063685 | north | Y | -0.022072 | 0.083777 | -0.0097127 | 0.17611 | 0.0097127 | west | Y | 0.022072 | 3.1515
239 | BOSQUESW | 1 | 149 | 0.063685 | north | Y | -0.022072 | 0.083777 | -0.0097127 | 0.17611 | 0.0097127 | west | Y | 0.022072 | 1.8415
244 | WHITNYDM | 1 | 15 | 0.067387 | north | N | -0.01837 | 0.087479 | -0.0060107 | 0.17981 | 0.0060107 | west | Y | 0.01837 | 0
245 | WHITNYDM | 2 | 15 | 0.067387 | north | N | -0.01837 | 0.087479 | -0.0060107 | 0.17981 | 0.0060107 | west | Y | 0.01837 | 0
247 | BOSQUESW | 2 | 153 | 0.063685 | north | Y | -0.022072 | 0.083777 | -0.0097127 | 0.17611 | 0.0097127 | west | Y | 0.022072 | 1.8909
251 | BOSQUESW | 2 | 150 | 0.064811 | north | Y | -0.020946 | 0.084903 | -0.0085867 | 0.17724 | 0.0085867 | west | Y | 0.020946 | 1.8538
253 | BOSQUESW | 2 | 80 | 0.064811 | north | Y | -0.020946 | 0.084903 | -0.0085867 | 0.17724 | 0.0085867 | west | Y | 0.020946 | 0.98872
332 | RWMILLER | 1 | 73 | 0.077093 | north | Y | -0.0086637 | 0.097185 | 0.0036953 | 0.18952 | 0.0036953 | west | Y | 0.0086637 | 0.36269
333 | RWMILLER | 2 | 119 | 0.077093 | north | Y | -0.0086637 | 0.097185 | 0.0036953 | 0.18952 | 0.0036953 | west | Y | 0.0086637 | 0.59123
334 | RWMILLER | 3 | 205 | 0.077093 | north | Y | -0.0086637 | 0.097185 | 0.0036953 | 0.18952 | 0.0036953 | west | Y | 0.0086637 | 1.0185
335 | RWMILLER | 4 | 102 | 0.077093 | north | Y | -0.0086637 | 0.097185 | 0.0036953 | 0.18952 | 0.0036953 | west | Y | 0.0086637 | 0.50677
336 | RWMILLER | 5 | 96 | 0.077093 | north | Y | -0.0086637 | 0.097185 | 0.0036953 | 0.18952 | 0.0036953 | west | Y | 0.0086637 | 0.47696
344 | MRSSHPRD | 1 | 12 | 0.077859 | north | N | -0.0078977 | 0.097951 | 0.0044613 | 0.19028 | 0.0044613 | west | Y | 0.0078977 | 0
345 | MRSSHPRD | 2 | 12 | 0.077859 | north | N | -0.0078977 | 0.097951 | 0.0044613 | 0.19028 | 0.0044613 | west | Y | 0.0078977 | 0
366 | JNSNCNTY | 1 | 168 | 0.07759 | north | Y | -0.0081667 | 0.097682 | 0.0041923 | 0.19002 | 0.0041923 | west | Y | 0.0081667 | 0.66769
367 | JNSNCNTY | 2 | 90 | 0.07759 | north | Y | -0.0081667 | 0.097682 | 0.0041923 | 0.19002 | 0.0041923 | west | Y | 0.0081667 | 0.35769
503 | NTHTEXAS | 1 | 18 | 0.078514 | north | Y | -0.0072427 | 0.098606 | 0.0051163 | 0.19094 | 0.0051163 | west | Y | 0.0072427 | 0.038274
504 | NTHTEXAS | 2 | 18 | 0.078514 | north | Y | -0.0072427 | 0.098606 | 0.0051163 | 0.19094 | 0.0051163 | west | Y | 0.0072427 | 0.038274
505 | NTHTEXAS | 3 | 38 | 0.078514 | north | Y | -0.0072427 | 0.098606 | 0.0051163 | 0.19094 | 0.0051163 | west | Y | 0.0072427 | 0.080801
580 | JCKCNTY8 | 1 | 288 | 0.079397 | north | Y | -0.0063597 | 0.099489 | 0.0059993 | 0.19182 | 0.0059993 | west | Y | 0.0063597 | 0.10378
581 | JCKCNTY8 | 2 | 147 | 0.079397 | north | Y | -0.0063597 | 0.099489 | 0.0059993 | 0.19182 | 0.0059993 | west | Y | 0.0063597 | 0.052971
582 | JCKCNTY8 | 3 | 147 | 0.079397 | north | Y | -0.0063597 | 0.099489 | 0.0059993 | 0.19182 | 0.0059993 | west | Y | 0.0063597 | 0.052971
728 | WOLFRIDG | 1 | 112.5 | 0.080451 | north | Y | -0.0053057 | 0.10054 | 0.0070533 | 0.19288 | 0.0053057 | North | N | 0.0053057 | 0
837 | NEWMAN_G | 1 | 40 | 0.083333 | north | Y | -0.0024237 | 0.10343 | 0.0099353 | 0.19576 | 0.0024237 | North | N | 0.0024237 | 0
842 | OLINGER_ | 1 | 79 | 0.08333 | north | Y | -0.0024267 | 0.10342 | 0.0099323 | 0.19576 | 0.0024267 | North | N | 0.0024267 | 0
843 | OLINGER_ | 1 | 106 | 0.08333 | north | Y | -0.0024267 | 0.10342 | 0.0099323 | 0.19576 | 0.0024267 | North | N | 0.0024267 | 0
844 | OLINGER_ | 1 | 146 | 0.08333 | north | Y | -0.0024267 | 0.10342 | 0.0099323 | 0.19576 | 0.0024267 | North | N | 0.0024267 | 0
845 | OLINGER_ | 1 | 76 | 0.08333 | north | Y | -0.0024267 | 0.10342 | 0.0099323 | 0.19576 | 0.0024267 | North | N | 0.0024267 | 0
923 | SPENCER_ | 1 | 60 | 0.081247 | north | Y | -0.0045097 | 0.10134 | 0.0078493 | 0.19367 | 0.0045097 | North | N | 0.0045097 | 0
924 | SPENCER_ | 1 | 63 | 0.081247 | north | Y | -0.0045097 | 0.10134 | 0.0078493 | 0.19367 | 0.0045097 | North | N | 0.0045097 | 0
948 | STEAM1 | 1 | 20 | 0.08343 | north | Y | -0.0023267 | 0.10352 | 0.010032 | 0.19586 | 0.0023267 | North | N | 0.0023267 | 0
949 | STEAM2 | 1 | 25 | 0.08343 | north | Y | -0.0023267 | 0.10352 | 0.010032 | 0.19586 | 0.0023267 | North | N | 0.0023267 | 0
950 | STEAM3 | 1 | 41 | 0.08343 | north | Y | -0.0023267 | 0.10352 | 0.010032 | 0.19586 | 0.0023267 | North | N | 0.0023267 | 0
990 | GIBN_CRE | 1 | 463 | 0.12175 | north | Y | 0.035992 | 0.14184 | 0.048351 | 0.23417 | 0.035992 | North | N | 0.035992 | 0
1002 | PBCTAGE_ | A | 66 | 0.072684 | west | Y | -0.013073 | 0.092776 | -0.00071369 | 0.18511 | 0.00071369 | west | N | 0.00071369 | 0
1003 | PBCTBGE_ | B | 65 | 0.072684 | west | Y | -0.013073 | 0.092776 | -0.00071369 | 0.18511 | 0.00071369 | west | N | 0.00071369 | 0
1004 | PBCTCGE_ | C | 67 | 0.072684 | west | Y | -0.013073 | 0.092776 | -0.00071369 | 0.18511 | 0.00071369 | west | N | 0.00071369 | 0
1005 | PBCTDGE_ | D | 67 | 0.072684 | west | Y | -0.013073 | 0.092776 | -0.00071369 | 0.18511 | 0.00071369 | west | N | 0.00071369 | 0
1006 | PBCTEGE_ | E | 67 | 0.072684 | west | Y | -0.013073 | 0.092776 | -0.00071369 | 0.18511 | 0.00071369 | west | N | 0.00071369 | 0
1007 | PB5GEN_6 | MB | 114 | 0.072684 | west | Y | -0.013073 | 0.092776 | -0.00071369 | 0.18511 | 0.00071369 | west | N | 0.00071369 | 0
1008 | PB6GEN_7 | MB | 515 | 0.072684 | west | Y | -0.013073 | 0.092776 | -0.00071369 | 0.18511 | 0.00071369 | west | N | 0.00071369 | 0
1039 | MRGNAG_1 | A | 66 | 0.0741 | west | Y | -0.011657 | 0.094192 | 0.00070231 | 0.18653 | 0.00070231 | west | N | 0.00070231 | 0
1040 | MRGNBG_2 | B | 69 | 0.0741 | west | Y | -0.011657 | 0.094192 | 0.00070231 | 0.18653 | 0.00070231 | west | N | 0.00070231 | 0
1041 | MRGNCG_3 | C | 69 | 0.0741 | west | Y | -0.011657 | 0.094192 | 0.00070231 | 0.18653 | 0.00070231 | west | N | 0.00070231 | 0
1042 | MRGNDG_4 | D | 67 | 0.0741 | west | Y | -0.011657 | 0.094192 | 0.00070231 | 0.18653 | 0.00070231 | west | N | 0.00070231 | 0
1043 | MRGNEG_5 | E | 67 | 0.0741 | west | Y | -0.011657 | 0.094192 | 0.00070231 | 0.18653 | 0.00070231 | west | N | 0.00070231 | 0
1044 | MRGNFG_6 | F | 65 | 0.0741 | west | Y | -0.011657 | 0.094192 | 0.00070231 | 0.18653 | 0.00070231 | west | N | 0.00070231 | 0
1045 | CALENG1G | 1 | 70 | 0.073901 | west | N | -0.011856 | 0.093993 | 0.00050331 | 0.18633 | 0.00050331 | west | N | 0.00050331 | 0
1046 | CALENG2G | 2 | 73.4 | 0.073901 | west | N | -0.011856 | 0.093993 | 0.00050331 | 0.18633 | 0.00050331 | west | N | 0.00050331 | 0
1047 | CALENG3G | 3 | 70.4 | 0.073901 | west | N | -0.011856 | 0.093993 | 0.00050331 | 0.18633 | 0.00050331 | west | N | 0.00050331 | 0
1058 | LONGSHOR | 1 | 150 | 0.074016 | west | Y | -0.011741 | 0.094108 | 0.00061831 | 0.18644 | 0.00061831 | west | N | 0.00061831 | 0
1058 | LONGSHOR | 2 | 220 | 0.074016 | west | Y | -0.011741 | 0.094108 | 0.00061831 | 0.18644 | 0.00061831 | west | N | 0.00061831 | 0
1061 | CIELOGEN | 1 | 99 | 0.074167 | west | Y | -0.01159 | 0.094259 | 0.00076931 | 0.18659 | 0.00076931 | west | N | 0.00076931 | 0
1062 | CIELOGEN | 1 | 61 | 0.074167 | west | Y | -0.01159 | 0.094259 | 0.00076931 | 0.18659 | 0.00076931 | west | N | 0.00076931 | 0
1068 | SCURRYCW | 1 | 141 | 0.074156 | west | Y | -0.011601 | 0.094248 | 0.00075831 | 0.18658 | 0.00075831 | west | N | 0.00075831 | 0
1069 | KINDERMG | 1 | 25 | 0.074167 | west | N | -0.01159 | 0.094259 | 0.00076931 | 0.18659 | 0.00076931 | west | N | 0.00076931 | 0
1070 | KINDERMG | 1 | 45.7 | 0.074167 | west | N | -0.01159 | 0.094259 | 0.00076931 | 0.18659 | 0.00076931 | west | N | 0.00076931 | 0
1071 | KINDERMG | 1 | 45.7 | 0.074167 | west | N | -0.01159 | 0.094259 | 0.00076931 | 0.18659 | 0.00076931 | west | N | 0.00076931 | 0
1073 | SCURRYCW | 2 | 120 | 0.074156 | west | Y | -0.011601 | 0.094248 | 0.00075831 | 0.18658 | 0.00075831 | west | N | 0.00075831 | 0
1320 | BSP 1 | 1 | 25.8 | 0.073556 | west | N | -0.012201 | 0.093648 | 0.00015831 | 0.18598 | 0.00015831 | west | N | 0.00015831 | 0
1326 | STANTONW | 1 | 100.5 | 0.073429 | west | Y | -0.012328 | 0.093521 | 3.131e-05 | 0.18585 | 3.131e-05 | west | N | 3.131e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.073775 | west | Y | -0.011982 | 0.093867 | 0.00037731 | 0.1862 | 0.00037731 | west | N | 0.00037731 | 0
1328 | OCOTILLO | 1 | 58 | 0.073417 | west | Y | -0.01234 | 0.093509 | 1.931e-05 | 0.18584 | 1.931e-05 | west | N | 1.931e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.073512 | west | Y | -0.012245 | 0.093604 | 0.00011431 | 0.18594 | 0.00011431 | west | N | 0.00011431 | 0
1343 | TRENTIPP | 1 | 150 | 0.074309 | west | Y | -0.011448 | 0.094401 | 0.00091131 | 0.18673 | 0.00091131 | west | N | 0.00091131 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.073058 | west | Y | -0.012699 | 0.09315 | -0.00033969 | 0.18548 | 0.00033969 | west | N | 0.00033969 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.073058 | west | Y | -0.012699 | 0.09315 | -0.00033969 | 0.18548 | 0.00033969 | west | N | 0.00033969 | 0
1354 | AEPWIND_ | 1 | 101 | 0.074309 | west | Y | -0.011448 | 0.094401 | 0.00091131 | 0.18673 | 0.00091131 | west | N | 0.00091131 | 0
1360 | GUNSIGHT | 1 | 120 | 0.073791 | west | Y | -0.011966 | 0.093883 | 0.00039331 | 0.18622 | 0.00039331 | west | N | 0.00039331 | 0
1432 | GRHAMSES | 2 | 366 | 0.077814 | north | Y | -0.0079427 | 0.097906 | 0.0044163 | 0.19024 | 0.0044163 | west | Y | 0.0079427 | 1.2906
1433 | GRHAMSES | 1 | 242 | 0.077383 | north | Y | -0.0083737 | 0.097475 | 0.0039853 | 0.18981 | 0.0039853 | west | Y | 0.0083737 | 1.062
1437 | MESQUITW | 1 | 400 | 0.075963 | west | Y | -0.0097937 | 0.096055 | 0.0025653 | 0.18839 | 0.0025653 | west | N | 0.0025653 | 0
1438 | MESQUITW | 1 | 236 | 0.075966 | west | Y | -0.0097907 | 0.096058 | 0.0025683 | 0.18839 | 0.0025683 | west | N | 0.0025683 | 0
1442 | COKFIELD | 1 | 165 | 0.076409 | west | Y | -0.0093477 | 0.096501 | 0.0030113 | 0.18883 | 0.0030113 | west | N | 0.0030113 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.078959 | north | Y | -0.0067977 | 0.099051 | 0.0055613 | 0.19138 | 0.0055613 | west | Y | 0.0067977 | 0.25221
1454 | WCPWRCO_ | 2 | 201 | 0.078959 | north | Y | -0.0067977 | 0.099051 | 0.0055613 | 0.19138 | 0.0055613 | west | Y | 0.0067977 | 0.24851
1455 | WCPWRCO_ | 3 | 242 | 0.078959 | north | Y | -0.0067977 | 0.099051 | 0.0055613 | 0.19138 | 0.0055613 | west | Y | 0.0067977 | 0.2992
1479 | WFCOGEN_ | 1 | 20 | 0.077896 | west | Y | -0.0078607 | 0.097988 | 0.0044983 | 0.19032 | 0.0044983 | west | N | 0.0044983 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.077896 | west | Y | -0.0078607 | 0.097988 | 0.0044983 | 0.19032 | 0.0044983 | west | N | 0.0044983 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.077896 | west | Y | -0.0078607 | 0.097988 | 0.0044983 | 0.19032 | 0.0044983 | west | N | 0.0044983 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.077896 | west | Y | -0.0078607 | 0.097988 | 0.0044983 | 0.19032 | 0.0044983 | west | N | 0.0044983 | 0
1600 | BARTNWND | 1 | 120 | 0.077761 | north | Y | -0.0079957 | 0.097853 | 0.0043633 | 0.19019 | 0.0043633 | west | Y | 0.0079957 | 0.43588
1643 | SLSTR1PP | 1 | 60 | 0.074733 | north | Y | -0.011024 | 0.094825 | 0.0013353 | 0.18716 | 0.0013353 | west | Y | 0.011024 | 0.5813
1675 | PEC_1G | 1 | 75 | 0.083181 | north | N | -0.0025757 | 0.10327 | 0.0097833 | 0.19561 | 0.0025757 | North | N | 0.0025757 | 0
1676 | PEC_2G | 2 | 79.6 | 0.083181 | north | N | -0.0025757 | 0.10327 | 0.0097833 | 0.19561 | 0.0025757 | North | N | 0.0025757 | 0
1677 | PEC_3G | 3 | 88.4 | 0.083181 | north | N | -0.0025757 | 0.10327 | 0.0097833 | 0.19561 | 0.0025757 | North | N | 0.0025757 | 0
1678 | LAMARPWR | 1 | 160 | 0.083134 | north | Y | -0.0026227 | 0.10323 | 0.0097363 | 0.19556 | 0.0026227 | North | N | 0.0026227 | 0
1679 | LAMARPWR | 2 | 156 | 0.083134 | north | Y | -0.0026227 | 0.10323 | 0.0097363 | 0.19556 | 0.0026227 | North | N | 0.0026227 | 0
1680 | LAMARPWR | 3 | 196 | 0.083134 | north | Y | -0.0026227 | 0.10323 | 0.0097363 | 0.19556 | 0.0026227 | North | N | 0.0026227 | 0
1681 | LAMARPWR | 4 | 156 | 0.083134 | north | Y | -0.0026227 | 0.10323 | 0.0097363 | 0.19556 | 0.0026227 | North | N | 0.0026227 | 0
1682 | LAMARPWR | 5 | 157 | 0.083134 | north | Y | -0.0026227 | 0.10323 | 0.0097363 | 0.19556 | 0.0026227 | North | N | 0.0026227 | 0
1683 | LAMARPWR | 6 | 198 | 0.083134 | north | Y | -0.0026227 | 0.10323 | 0.0097363 | 0.19556 | 0.0026227 | North | N | 0.0026227 | 0
1687 | VALLEY_1 | 1 | 170 | 0.082923 | north | Y | -0.0028337 | 0.10302 | 0.0095253 | 0.19535 | 0.0028337 | North | N | 0.0028337 | 0
1688 | VALLEY_2 | 2 | 520 | 0.082923 | north | Y | -0.0028337 | 0.10302 | 0.0095253 | 0.19535 | 0.0028337 | North | N | 0.0028337 | 0
1689 | VALLEY_3 | 3 | 370 | 0.08307 | north | Y | -0.0026867 | 0.10316 | 0.0096723 | 0.1955 | 0.0026867 | North | N | 0.0026867 | 0
1701 | MOSES_1G | 1 | 558 | 0.083246 | north | Y | -0.0025107 | 0.10334 | 0.0098483 | 0.19567 | 0.0025107 | North | N | 0.0025107 | 0
1702 | MOSES_2G | 2 | 579 | 0.083246 | north | Y | -0.0025107 | 0.10334 | 0.0098483 | 0.19567 | 0.0025107 | North | N | 0.0025107 | 0
1703 | MOSES_3G | 3 | 808 | 0.083246 | north | Y | -0.0025107 | 0.10334 | 0.0098483 | 0.19567 | 0.0025107 | North | N | 0.0025107 | 0
1861 | EAGLEMNT | MB | 112 | 0.080172 | north | Y | -0.0055847 | 0.10026 | 0.0067743 | 0.1926 | 0.0055847 | North | N | 0.0055847 | 0
1862 | EAGLEMNT | MB | 100 | 0.080172 | north | Y | -0.0055847 | 0.10026 | 0.0067743 | 0.1926 | 0.0055847 | North | N | 0.0055847 | 0
1863 | EAGLEMNT | MB | 378 | 0.080172 | north | Y | -0.0055847 | 0.10026 | 0.0067743 | 0.1926 | 0.0055847 | North | N | 0.0055847 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.078918 | north | Y | -0.0068387 | 0.09901 | 0.0055203 | 0.19134 | 0.0055203 | west | Y | 0.0068387 | 0.28648
1878 | WLFHOLW_ | 2 | 205 | 0.078918 | north | Y | -0.0068387 | 0.09901 | 0.0055203 | 0.19134 | 0.0055203 | west | Y | 0.0068387 | 0.27026
1879 | WLFHOLW_ | 3 | 272.4 | 0.078918 | north | Y | -0.0068387 | 0.09901 | 0.0055203 | 0.19134 | 0.0055203 | west | Y | 0.0068387 | 0.35912
1889 | DECRDOVA | MB | 770 | 0.079088 | north | Y | -0.0066687 | 0.09918 | 0.0056903 | 0.19151 | 0.0056903 | west | Y | 0.0066687 | 0
1892 | DECRDOVA | A | 70 | 0.078078 | north | Y | -0.0076787 | 0.09817 | 0.0046803 | 0.1905 | 0.0046803 | west | Y | 0.0076787 | 0.20988
1893 | DECRDOVA | B | 69 | 0.078078 | north | Y | -0.0076787 | 0.09817 | 0.0046803 | 0.1905 | 0.0046803 | west | Y | 0.0076787 | 0.20689
1894 | DECRDOVA | C | 69 | 0.078078 | north | Y | -0.0076787 | 0.09817 | 0.0046803 | 0.1905 | 0.0046803 | west | Y | 0.0076787 | 0.20689
1895 | DECRDOVA | D | 68 | 0.078078 | north | Y | -0.0076787 | 0.09817 | 0.0046803 | 0.1905 | 0.0046803 | west | Y | 0.0076787 | 0.20389
1898 | COMCHEPK | 1 | 1157 | 0.078727 | north | N | -0.0070297 | 0.098819 | 0.0053293 | 0.19115 | 0.0053293 | west | Y | 0.0070297 | 0
1899 | COMCHEPK | 2 | 1158 | 0.078727 | north | N | -0.0070297 | 0.098819 | 0.0053293 | 0.19115 | 0.0053293 | west | Y | 0.0070297 | 0
1937 | MDLTHELP | 5 | 224 | 0.079448 | north | Y | -0.0063087 | 0.09954 | 0.0060503 | 0.19187 | 0.0060503 | west | Y | 0.0063087 | 0.05787
1938 | MDLTHELP | 6 | 226 | 0.079448 | north | Y | -0.0063087 | 0.09954 | 0.0060503 | 0.19187 | 0.0060503 | west | Y | 0.0063087 | 0.058386
1941 | MDLTHELP | 1 | 216.4 | 0.080222 | north | Y | -0.0055347 | 0.10031 | 0.0068243 | 0.19265 | 0.0055347 | North | N | 0.0055347 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.080222 | north | Y | -0.0055347 | 0.10031 | 0.0068243 | 0.19265 | 0.0055347 | North | N | 0.0055347 | 0
1943 | MDLTHELP | 3 | 212 | 0.079448 | north | Y | -0.0063087 | 0.09954 | 0.0060503 | 0.19187 | 0.0060503 | west | Y | 0.0063087 | 0.05477
1944 | MDLTHELP | 4 | 211 | 0.079448 | north | Y | -0.0063087 | 0.09954 | 0.0060503 | 0.19187 | 0.0060503 | west | Y | 0.0063087 | 0.054511
1947 | HANDLEY_ | 3 | 395 | 0.080346 | north | Y | -0.0054107 | 0.10044 | 0.0069483 | 0.19277 | 0.0054107 | North | N | 0.0054107 | 0
1948 | HANDLEY_ | 4 | 435 | 0.080508 | north | Y | -0.0052487 | 0.1006 | 0.0071103 | 0.19293 | 0.0052487 | North | N | 0.0052487 | 0
1949 | HANDLEY_ | 5 | 435 | 0.080346 | north | Y | -0.0054107 | 0.10044 | 0.0069483 | 0.19277 | 0.0054107 | North | N | 0.0054107 | 0
2371 | COLLIN_1 | MB | 138 | 0.082452 | north | Y | -0.0033047 | 0.10254 | 0.0090543 | 0.19488 | 0.0033047 | North | N | 0.0033047 | 0
2413 | MTCK6_G | 6 | 118 | 0.082646 | north | Y | -0.0031107 | 0.10274 | 0.0092483 | 0.19507 | 0.0031107 | North | N | 0.0031107 | 0
2414 | MTCK7_G | 7 | 115 | 0.082646 | north | Y | -0.0031107 | 0.10274 | 0.0092483 | 0.19507 | 0.0031107 | North | N | 0.0031107 | 0
2417 | MTCK8_G | 8 | 556 | 0.082646 | north | Y | -0.0031107 | 0.10274 | 0.0092483 | 0.19507 | 0.0031107 | North | N | 0.0031107 | 0
2451 | LKHB1_G | 1 | 388 | 0.083526 | north | Y | -0.0022307 | 0.10362 | 0.010128 | 0.19595 | 0.0022307 | North | N | 0.0022307 | 0
2452 | LKHB2_G | 2 | 515 | 0.083526 | north | Y | -0.0022307 | 0.10362 | 0.010128 | 0.19595 | 0.0022307 | North | N | 0.0022307 | 0
3097 | MARTLAKE | 1 | 785 | 0.086307 | north | Y | 0.00055034 | 0.1064 | 0.012909 | 0.19873 | 0.00055034 | North | N | 0.00055034 | 0
3098 | MARTLAKE | 2 | 795 | 0.086307 | north | Y | 0.00055034 | 0.1064 | 0.012909 | 0.19873 | 0.00055034 | North | N | 0.00055034 | 0
3099 | MARTLAKE | 3 | 780 | 0.086307 | north | Y | 0.00055034 | 0.1064 | 0.012909 | 0.19873 | 0.00055034 | North | N | 0.00055034 | 0
3107 | STRYKER_ | 1 | 182 | 0.08701 | north | Y | 0.0012533 | 0.1071 | 0.013612 | 0.19944 | 0.0012533 | North | N | 0.0012533 | 0
3108 | STRYKER_ | 2 | 484 | 0.08701 | north | Y | 0.0012533 | 0.1071 | 0.013612 | 0.19944 | 0.0012533 | North | N | 0.0012533 | 0
3126 | TRINIDAD | 1 | 224 | 0.084137 | north | Y | -0.0016197 | 0.10423 | 0.010739 | 0.19656 | 0.0016197 | North | N | 0.0016197 | 0
3309 | ASPN_G | 1 | 50 | 0.086965 | north | Y | 0.0012083 | 0.10706 | 0.013567 | 0.19939 | 0.0012083 | North | N | 0.0012083 | 0
3348 | CHAMPION | MB | 42 | 0.086931 | north | N | 0.0011743 | 0.10702 | 0.013533 | 0.19936 | 0.0011743 | North | N | 0.0011743 | 0
3381 | BBRN_1G | 1 | 615 | 0.091303 | north | Y | 0.0055463 | 0.1114 | 0.017905 | 0.20373 | 0.0055463 | North | N | 0.0055463 | 0
3382 | BBRN_2G | 2 | 587 | 0.091303 | north | Y | 0.0055463 | 0.1114 | 0.017905 | 0.20373 | 0.0055463 | North | N | 0.0055463 | 0
3403 | THOUSE_1 | MB | 537 | 0.06239 | north | Y | -0.023367 | 0.082482 | -0.011008 | 0.17482 | 0.011008 | west | Y | 0.023367 | 0
3404 | THOUSE_2 | 2 | 787 | 0.06239 | north | Y | -0.023367 | 0.082482 | -0.011008 | 0.17482 | 0.011008 | west | Y | 0.023367 | 9.7265
3416 | LAKE_CRK | MB | 75 | 0.061522 | north | Y | -0.024235 | 0.081614 | -0.011876 | 0.17395 | 0.011876 | west | Y | 0.024235 | 0
3417 | LAKE_CRK | MB | 222 | 0.061522 | north | Y | -0.024235 | 0.081614 | -0.011876 | 0.17395 | 0.011876 | west | Y | 0.024235 | 0
3432 | SANDOW_4 | 4 | 569 | 0.022732 | south | Y | -0.063025 | 0.042824 | -0.050666 | 0.13516 | 0.042824 | south | N | 0.042824 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.023592 | south | Y | -0.10935 | -0.0035 | -0.09699 | 0.088834 | 0.0035 | south | N | 0.0035 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.023592 | south | Y | -0.10935 | -0.0035 | -0.09699 | 0.088834 | 0.0035 | south | N | 0.0035 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.02349 | south | Y | -0.10925 | -0.003398 | -0.096888 | 0.088936 | 0.003398 | south | N | 0.003398 | 0
5031 | BRA_VHBC | 1 | 46 | -0.023592 | south | Y | -0.10935 | -0.0035 | -0.09699 | 0.088834 | 0.0035 | south | N | 0.0035 | 0
5032 | BRA_VHBC | 2 | 47 | -0.023592 | south | Y | -0.10935 | -0.0035 | -0.09699 | 0.088834 | 0.0035 | south | N | 0.0035 | 0
5033 | BRA_VHBC | 3 | 46 | -0.023592 | south | Y | -0.10935 | -0.0035 | -0.09699 | 0.088834 | 0.0035 | south | N | 0.0035 | 0
5034 | BRA_VHBC | 4 | 46 | -0.023592 | south | Y | -0.10935 | -0.0035 | -0.09699 | 0.088834 | 0.0035 | south | N | 0.0035 | 0
5111 | CALAVER_ | 1 | 424 | -0.023533 | south | Y | -0.10929 | -0.003441 | -0.096931 | 0.088893 | 0.003441 | south | N | 0.003441 | 0
5112 | CALAVER_ | 2 | 425 | -0.023533 | south | Y | -0.10929 | -0.003441 | -0.096931 | 0.088893 | 0.003441 | south | N | 0.003441 | 0
5264 | LEON_LCP | 3 | 58 | -0.023516 | south | Y | -0.10927 | -0.003424 | -0.096914 | 0.08891 | 0.003424 | south | N | 0.003424 | 0
5265 | LEON_LCP | 4 | 89 | -0.023516 | south | Y | -0.10927 | -0.003424 | -0.096914 | 0.08891 | 0.003424 | south | N | 0.003424 | 0
5266 | LEON_LCP | 1 | 44 | -0.023516 | south | Y | -0.10927 | -0.003424 | -0.096914 | 0.08891 | 0.003424 | south | N | 0.003424 | 0
5267 | LEON_LCP | 2 | 44 | -0.023516 | south | Y | -0.10927 | -0.003424 | -0.096914 | 0.08891 | 0.003424 | south | N | 0.003424 | 0
5268 | LEON_LCP | 3 | 43 | -0.023516 | south | Y | -0.10927 | -0.003424 | -0.096914 | 0.08891 | 0.003424 | south | N | 0.003424 | 0
5269 | LEON_LCP | 4 | 45 | -0.023516 | south | Y | -0.10927 | -0.003424 | -0.096914 | 0.08891 | 0.003424 | south | N | 0.003424 | 0
5396 | CALAVER_ | 1 | 412 | -0.023502 | south | Y | -0.10926 | -0.00341 | -0.0969 | 0.088924 | 0.00341 | south | N | 0.00341 | 0
5397 | CALAVER_ | 2 | 400 | -0.023502 | south | Y | -0.10926 | -0.00341 | -0.0969 | 0.088924 | 0.00341 | south | N | 0.00341 | 0
5401 | CALAVER_ | 1 | 546 | -0.024973 | south | Y | -0.11073 | -0.004881 | -0.098371 | 0.087453 | 0.004881 | south | N | 0.004881 | 0
5402 | CALAVER_ | 2 | 750 | -0.024973 | south | Y | -0.11073 | -0.004881 | -0.098371 | 0.087453 | 0.004881 | south | N | 0.004881 | 0
5436 | TUTTL_WB | MB | 61 | -0.023635 | south | Y | -0.10939 | -0.003543 | -0.097033 | 0.088791 | 0.003543 | south | N | 0.003543 | 0
5438 | TUTTL_WB | MB | 95 | -0.023635 | south | Y | -0.10939 | -0.003543 | -0.097033 | 0.088791 | 0.003543 | south | N | 0.003543 | 0
5439 | TUTTL_WB | MB | 151 | -0.023635 | south | Y | -0.10939 | -0.003543 | -0.097033 | 0.088791 | 0.003543 | south | N | 0.003543 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.024341 | south | Y | -0.1101 | -0.004249 | -0.097739 | 0.088085 | 0.004249 | south | N | 0.004249 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.024341 | south | Y | -0.1101 | -0.004249 | -0.097739 | 0.088085 | 0.004249 | south | N | 0.004249 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.024341 | south | Y | -0.1101 | -0.004249 | -0.097739 | 0.088085 | 0.004249 | south | N | 0.004249 | 0
5503 | RAYBURNG | 1 | 22 | -0.042263 | south | Y | -0.12802 | -0.022171 | -0.11566 | 0.070163 | 0.022171 | south | N | 0.022171 | 0
5505 | RAYBURNG | 1 | 11 | -0.042263 | south | Y | -0.12802 | -0.022171 | -0.11566 | 0.070163 | 0.022171 | south | N | 0.022171 | 0
5506 | RAYBURNG | 1 | 11 | -0.042263 | south | Y | -0.12802 | -0.022171 | -0.11566 | 0.070163 | 0.022171 | south | N | 0.022171 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.041772 | south | Y | -0.12753 | -0.02168 | -0.11517 | 0.070654 | 0.02168 | south | N | 0.02168 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.041772 | south | Y | -0.12753 | -0.02168 | -0.11517 | 0.070654 | 0.02168 | south | N | 0.02168 | 0
5511 | RAYBURNC | 1 | 46 | -0.041772 | south | Y | -0.12753 | -0.02168 | -0.11517 | 0.070654 | 0.02168 | south | N | 0.02168 | 0
5512 | RAYBURNC | 1 | 48 | -0.041772 | south | Y | -0.12753 | -0.02168 | -0.11517 | 0.070654 | 0.02168 | south | N | 0.02168 | 0
5728 | FALCONHY | 2 | 12 | -0.035806 | south | N | -0.12156 | -0.015714 | -0.1092 | 0.07662 | 0.015714 | south | N | 0.015714 | 0
5729 | FALCONHY | 3 | 11 | -0.035806 | south | N | -0.12156 | -0.015714 | -0.1092 | 0.07662 | 0.015714 | south | N | 0.015714 | 0
5890 | PEARSALL | 1 | 24 | -0.02462 | south | Y | -0.11038 | -0.004528 | -0.098018 | 0.087806 | 0.004528 | south | N | 0.004528 | 0
5891 | PEARSALL | 1 | 24 | -0.02462 | south | Y | -0.11038 | -0.004528 | -0.098018 | 0.087806 | 0.004528 | south | N | 0.004528 | 0
5892 | PEARSALL | 1 | 23 | -0.02462 | south | Y | -0.11038 | -0.004528 | -0.098018 | 0.087806 | 0.004528 | south | N | 0.004528 | 0
5903 | SANMIGUE | 1 | 396 | -0.029096 | south | Y | -0.11485 | -0.009004 | -0.10249 | 0.08333 | 0.009004 | south | N | 0.009004 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.074209 | houston | N | -0.15997 | -0.054117 | -0.14761 | 0.038217 | 0.038217 | houston | N | 0.038217 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.074209 | houston | N | -0.15997 | -0.054117 | -0.14761 | 0.038217 | 0.038217 | houston | N | 0.038217 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | Y | 0.085757 | 0
5932 | SI_RAY9 | 9 | 38 | -0.039454 | south | Y | -0.12521 | -0.019362 | -0.11285 | 0.072972 | 0.019362 | south | N | 0.019362 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.039454 | south | Y | -0.12521 | -0.019362 | -0.11285 | 0.072972 | 0.019362 | south | N | 0.019362 | 0
5934 | SI_RAY5 | 5 | 15 | -0.039454 | south | Y | -0.12521 | -0.019362 | -0.11285 | 0.072972 | 0.019362 | south | N | 0.019362 | 0
5935 | SI_RAY10 | 10 | 47 | -0.039454 | south | Y | -0.12521 | -0.019362 | -0.11285 | 0.072972 | 0.019362 | south | N | 0.019362 | 0
6016 | SWMESA | 1 | 75 | 0.068725 | west | Y | -0.017032 | 0.088817 | -0.0046727 | 0.18115 | 0.0046727 | west | N | 0.0046727 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | Y | 0.073398 | 0
6144 | MCADOO1A | 1 | 150 | 0.074673 | west | Y | -0.011084 | 0.094765 | 0.0012753 | 0.1871 | 0.0012753 | west | N | 0.0012753 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.0728 | west | Y | -0.012957 | 0.092892 | -0.00059769 | 0.18523 | 0.00059769 | west | N | 0.00059769 | 0
6476 | LANGFORD | 1 | 150 | 0.05343 | west | Y | -0.032327 | 0.073522 | -0.019968 | 0.16586 | 0.019968 | west | N | 0.019968 | 0
6637 | SNYDERW1 | 1 | 63 | 0.074127 | west | Y | -0.01163 | 0.094219 | 0.00072931 | 0.18655 | 0.00072931 | west | N | 0.00072931 | 0
6752 | OKLA0A | 1 | 649.7 | 0.076788 | west | Y | -0.0089687 | 0.09688 | 0.0033903 | 0.18921 | 0.0033903 | west | N | 0.0033903 | 0
6948 | DENISNDM | 1 | 40 | 0.082805 | north | N | -0.0029517 | 0.1029 | 0.0094073 | 0.19523 | 0.0029517 | North | N | 0.0029517 | 0
6948 | DENISNDM | 2 | 40 | 0.082805 | north | N | -0.0029517 | 0.1029 | 0.0094073 | 0.19523 | 0.0029517 | North | N | 0.0029517 | 0
7000 | L_FERGUS | 1 | 422 | 0.004787 | south | Y | -0.08097 | 0.024879 | -0.068611 | 0.11721 | 0.024879 | south | N | 0.024879 | 0
7004 | L_SIMGID | 1 | 132 | -0.002613 | south | Y | -0.08837 | 0.017479 | -0.076011 | 0.10981 | 0.017479 | south | N | 0.017479 | 0
7005 | L_SIMGID | 2 | 134 | -0.002613 | south | Y | -0.08837 | 0.017479 | -0.076011 | 0.10981 | 0.017479 | south | N | 0.017479 | 0
7006 | L_SIMGID | 3 | 323 | -0.002613 | south | Y | -0.08837 | 0.017479 | -0.076011 | 0.10981 | 0.017479 | south | N | 0.017479 | 0
7007 | L_LOSTPI | 1 | 158 | -0.004824 | south | Y | -0.090581 | 0.015268 | -0.078222 | 0.1076 | 0.015268 | south | N | 0.015268 | 0
7008 | L_LOSTPI | 2 | 160 | -0.004824 | south | Y | -0.090581 | 0.015268 | -0.078222 | 0.1076 | 0.015268 | south | N | 0.015268 | 0
7009 | L_LOSTPI | 3 | 175 | -0.004824 | south | Y | -0.090581 | 0.015268 | -0.078222 | 0.1076 | 0.015268 | south | N | 0.015268 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.013993 | south | Y | -0.09975 | 0.006099 | -0.087391 | 0.098433 | 0.006099 | south | N | 0.006099 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.013993 | south | Y | -0.09975 | 0.006099 | -0.087391 | 0.098433 | 0.006099 | south | N | 0.006099 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.014122 | south | Y | -0.099879 | 0.00597 | -0.08752 | 0.098304 | 0.00597 | south | N | 0.00597 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.016495 | south | Y | -0.10225 | 0.003597 | -0.089893 | 0.095931 | 0.003597 | south | N | 0.003597 | 0
7015 | L_HAYSEN | 2 | 225 | -0.016495 | south | Y | -0.10225 | 0.003597 | -0.089893 | 0.095931 | 0.003597 | south | N | 0.003597 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.016495 | south | Y | -0.10225 | 0.003597 | -0.089893 | 0.095931 | 0.003597 | south | N | 0.003597 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.016495 | south | Y | -0.10225 | 0.003597 | -0.089893 | 0.095931 | 0.003597 | south | N | 0.003597 | 0
7020 | L_AUSTPL | 1 | 8 | 0.001266 | south | N | -0.084491 | 0.021358 | -0.072132 | 0.11369 | 0.021358 | south | N | 0.021358 | 0
7020 | L_AUSTPL | 2 | 8 | 0.001266 | south | N | -0.084491 | 0.021358 | -0.072132 | 0.11369 | 0.021358 | south | N | 0.021358 | 0
7022 | L_BUCHAN | 1 | 18 | 0.010164 | south | N | -0.075593 | 0.030256 | -0.063234 | 0.12259 | 0.030256 | south | N | 0.030256 | 0
7023 | L_BUCHAN | 2 | 18 | 0.010164 | south | N | -0.075593 | 0.030256 | -0.063234 | 0.12259 | 0.030256 | south | N | 0.030256 | 0
7024 | L_BUCHAN | 3 | 15 | 0.010164 | south | N | -0.075593 | 0.030256 | -0.063234 | 0.12259 | 0.030256 | south | N | 0.030256 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.009185 | south | N | -0.076572 | 0.029277 | -0.064213 | 0.12161 | 0.029277 | south | N | 0.029277 | 0
7028 | L_MARBFA | 1 | 18 | 0.004092 | south | N | -0.081665 | 0.024184 | -0.069306 | 0.11652 | 0.024184 | south | N | 0.024184 | 0
7029 | L_MARBFA | 2 | 18 | 0.004092 | south | N | -0.081665 | 0.024184 | -0.069306 | 0.11652 | 0.024184 | south | N | 0.024184 | 0
7031 | L_MARSFO | 1 | 35 | 0.002516 | south | N | -0.083241 | 0.022608 | -0.070882 | 0.11494 | 0.022608 | south | N | 0.022608 | 0
7032 | L_MARSFO | 2 | 34 | 0.002516 | south | N | -0.083241 | 0.022608 | -0.070882 | 0.11494 | 0.022608 | south | N | 0.022608 | 0
7033 | L_MARSFO | 3 | 35 | 0.002516 | south | N | -0.083241 | 0.022608 | -0.070882 | 0.11494 | 0.022608 | south | N | 0.022608 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.005042 | south | N | -0.080715 | 0.025134 | -0.068356 | 0.11747 | 0.025134 | south | N | 0.025134 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.005042 | south | N | -0.080715 | 0.025134 | -0.068356 | 0.11747 | 0.025134 | south | N | 0.025134 | 0
7038 | L_DELAWA | 1 | 35 | 0.072719 | west | Y | -0.013038 | 0.092811 | -0.00067869 | 0.18514 | 0.00067869 | west | N | 0.00067869 | 0
7038 | L_DELAWA | 2 | 30 | 0.072719 | west | Y | -0.013038 | 0.092811 | -0.00067869 | 0.18514 | 0.00067869 | west | N | 0.00067869 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.009571 | south | Y | -0.095328 | 0.010521 | -0.082969 | 0.10285 | 0.010521 | south | N | 0.010521 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.009571 | south | Y | -0.095328 | 0.010521 | -0.082969 | 0.10285 | 0.010521 | south | N | 0.010521 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.009571 | south | Y | -0.095328 | 0.010521 | -0.082969 | 0.10285 | 0.010521 | south | N | 0.010521 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.009571 | south | Y | -0.095328 | 0.010521 | -0.082969 | 0.10285 | 0.010521 | south | N | 0.010521 | 0
7487 | L_CANYHY | 1 | 6 | -0.012682 | south | N | -0.098439 | 0.00741 | -0.08608 | 0.099744 | 0.00741 | south | N | 0.00741 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.018688 | south | N | -0.10444 | 0.001404 | -0.092086 | 0.093738 | 0.001404 | south | N | 0.001404 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.018688 | south | N | -0.10444 | 0.001404 | -0.092086 | 0.093738 | 0.001404 | south | N | 0.001404 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.018688 | south | N | -0.10444 | 0.001404 | -0.092086 | 0.093738 | 0.001404 | south | N | 0.001404 | 0
7609 | L_SCHUMA | 1 | 4 | -0.020068 | south | N | -0.10582 | 2.4021e-05 | -0.093466 | 0.092358 | 2.4021e-05 | south | N | 2.4021e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.019593 | south | N | -0.10535 | 0.00049902 | -0.092991 | 0.092833 | 0.00049902 | south | N | 0.00049902 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.019593 | south | N | -0.10535 | 0.00049902 | -0.092991 | 0.092833 | 0.00049902 | south | N | 0.00049902 | 0
7800 | L_GUADGE | 1 | 147 | -0.022777 | south | Y | -0.10853 | -0.002685 | -0.096175 | 0.089649 | 0.002685 | south | N | 0.002685 | 0
7801 | L_GUADGE | 2 | 138 | -0.022777 | south | Y | -0.10853 | -0.002685 | -0.096175 | 0.089649 | 0.002685 | south | N | 0.002685 | 0
7802 | L_GUADGE | 3 | 140 | -0.022777 | south | Y | -0.10853 | -0.002685 | -0.096175 | 0.089649 | 0.002685 | south | N | 0.002685 | 0
7803 | L_GUADGE | 4 | 147 | -0.022777 | south | Y | -0.10853 | -0.002685 | -0.096175 | 0.089649 | 0.002685 | south | N | 0.002685 | 0
7804 | L_GUADGE | 5 | 182 | -0.022777 | south | Y | -0.10853 | -0.002685 | -0.096175 | 0.089649 | 0.002685 | south | N | 0.002685 | 0
7805 | L_GUADGE | 6 | 198 | -0.022777 | south | Y | -0.10853 | -0.002685 | -0.096175 | 0.089649 | 0.002685 | south | N | 0.002685 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.004031 | south | Y | -0.089788 | 0.016061 | -0.077429 | 0.10839 | 0.016061 | south | N | 0.016061 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.004031 | south | Y | -0.089788 | 0.016061 | -0.077429 | 0.10839 | 0.016061 | south | N | 0.016061 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.004031 | south | Y | -0.089788 | 0.016061 | -0.077429 | 0.10839 | 0.016061 | south | N | 0.016061 | 0
7810 | L_RIONOG | 1 | 142 | -0.019724 | south | Y | -0.10548 | 0.00036802 | -0.093122 | 0.092702 | 0.00036802 | south | N | 0.00036802 | 0
7811 | L_RIONOG | 2 | 145 | -0.019724 | south | Y | -0.10548 | 0.00036802 | -0.093122 | 0.092702 | 0.00036802 | south | N | 0.00036802 | 0
7812 | L_RIONOG | 3 | 151 | -0.019724 | south | Y | -0.10548 | 0.00036802 | -0.093122 | 0.092702 | 0.00036802 | south | N | 0.00036802 | 0
7813 | L_RIONOG | 4 | 290 | -0.019724 | south | Y | -0.10548 | 0.00036802 | -0.093122 | 0.092702 | 0.00036802 | south | N | 0.00036802 | 0
8032 | AMISTADH | 1 | 33 | 0.001514 | south | N | -0.084243 | 0.021606 | -0.071884 | 0.11394 | 0.021606 | south | N | 0.021606 | 0
8033 | AMISTADH | 2 | 25 | 0.001514 | south | N | -0.084243 | 0.021606 | -0.071884 | 0.11394 | 0.021606 | south | N | 0.021606 | 0
8048 | FALCONHY | 1 | 12 | -0.035806 | south | N | -0.12156 | -0.015714 | -0.1092 | 0.07662 | 0.015714 | south | N | 0.015714 | 0
8066 | DUP1V#1 | 1 | 73 | -0.041708 | south | N | -0.12746 | -0.021616 | -0.11511 | 0.070718 | 0.021616 | south | N | 0.021616 | 0
8134 | FOR69CG0 | 1 | 79 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
8138 | FOR69CG0 | 2 | 81 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | N | 0.020092 | 0
8147 | UCAR #2 | 10 | 28 | -0.044244 | south | N | -0.13 | -0.024152 | -0.11764 | 0.068182 | 0.024152 | south | N | 0.024152 | 0
8148 | UCAR #1 | 2 | 7 | -0.044244 | south | N | -0.13 | -0.024152 | -0.11764 | 0.068182 | 0.024152 | south | N | 0.024152 | 0
8153 | FOR69CG0 | 3 | 79 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
8154 | FOR69CG0 | 4 | 80 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
8156 | FOR69CG0 | 6 | 25 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
8157 | FOR69CG0 | 7 | 46 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
8161 | COLETOU1 | 1 | 629 | -0.036963 | south | Y | -0.12272 | -0.016871 | -0.11036 | 0.075463 | 0.016871 | south | N | 0.016871 | 0
8173 | VICEC51A | 5 | 144 | -0.040777 | south | Y | -0.12653 | -0.020685 | -0.11417 | 0.071649 | 0.020685 | south | N | 0.020685 | 0
8174 | VICEC61A | 6 | 188 | -0.040777 | south | Y | -0.12653 | -0.020685 | -0.11417 | 0.071649 | 0.020685 | south | N | 0.020685 | 0
8189 | CUERO 2 | 1 | 12 | -0.024987 | south | N | -0.11074 | -0.004895 | -0.098385 | 0.087439 | 0.004895 | south | N | 0.004895 | 0
8262 | ELPS | 1 | 6 | -0.007046 | south | N | -0.092803 | 0.013046 | -0.080444 | 0.10538 | 0.013046 | south | N | 0.013046 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | N | 0.020092 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | N | 0.020092 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | N | 0.020092 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | N | 0.020092 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | N | 0.020092 | 0
8442 | NBEC71A | 1 | 336 | -0.040559 | south | Y | -0.12632 | -0.020467 | -0.11396 | 0.071867 | 0.020467 | south | N | 0.020467 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | N | 0.020092 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.085757 | 0.020092 | -0.073398 | 0.11243 | 0.020092 | south | N | 0.020092 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.040358 | south | Y | -0.12611 | -0.020266 | -0.11376 | 0.072068 | 0.020266 | south | N | 0.020266 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.040358 | south | Y | -0.12611 | -0.020266 | -0.11376 | 0.072068 | 0.020266 | south | N | 0.020266 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.040185 | south | N | -0.12594 | -0.020093 | -0.11358 | 0.072241 | 0.020093 | south | N | 0.020093 | 0
8506 | VAL #1 | 1 | 25 | -0.040292 | south | N | -0.12605 | -0.0202 | -0.11369 | 0.072134 | 0.0202 | south | N | 0.0202 | 0
8507 | VAL #2 | 2 | 25 | -0.040292 | south | N | -0.12605 | -0.0202 | -0.11369 | 0.072134 | 0.0202 | south | N | 0.0202 | 0
8511 | OXY_CC0A | 1 | 38 | -0.040226 | south | N | -0.12598 | -0.020134 | -0.11362 | 0.0722 | 0.020134 | south | N | 0.020134 | 0
8517 | CELANEBI | 1 | 29 | -0.039775 | south | N | -0.12553 | -0.019683 | -0.11317 | 0.072651 | 0.019683 | south | N | 0.019683 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.040548 | south | N | -0.1263 | -0.020456 | -0.11395 | 0.071878 | 0.020456 | south | N | 0.020456 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.040548 | south | N | -0.1263 | -0.020456 | -0.11395 | 0.071878 | 0.020456 | south | N | 0.020456 | 0
8562 | CNOPST1 | 3 | 153 | -0.040548 | south | N | -0.1263 | -0.020456 | -0.11395 | 0.071878 | 0.020456 | south | N | 0.020456 | 0
8926 | LGE_GT10 | 1 | 158 | -0.041494 | south | N | -0.12725 | -0.021402 | -0.11489 | 0.070932 | 0.021402 | south | N | 0.021402 | 0
8927 | LGE_GT20 | 2 | 153 | -0.041494 | south | N | -0.12725 | -0.021402 | -0.11489 | 0.070932 | 0.021402 | south | N | 0.021402 | 0
8928 | LGE_STG0 | 3 | 100 | -0.041494 | south | N | -0.12725 | -0.021402 | -0.11489 | 0.070932 | 0.021402 | south | N | 0.021402 | 0
8930 | ICPGN10A | 1 | 145 | -0.041494 | south | N | -0.12725 | -0.021402 | -0.11489 | 0.070932 | 0.021402 | south | N | 0.021402 | 0
8931 | ICPGN20A | 2 | 147 | -0.041494 | south | N | -0.12725 | -0.021402 | -0.11489 | 0.070932 | 0.021402 | south | N | 0.021402 | 0
8932 | ICPGN30A | 3 | 127 | -0.041494 | south | N | -0.12725 | -0.021402 | -0.11489 | 0.070932 | 0.021402 | south | N | 0.021402 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.038649 | south | Y | -0.12441 | -0.018557 | -0.11205 | 0.073777 | 0.018557 | south | N | 0.018557 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.038649 | south | Y | -0.12441 | -0.018557 | -0.11205 | 0.073777 | 0.018557 | south | N | 0.018557 | 0
8935 | FGNTS201 | 3 | 173 | -0.038649 | south | Y | -0.12441 | -0.018557 | -0.11205 | 0.073777 | 0.018557 | south | N | 0.018557 | 0
8936 | MVGN#1 | 1 | 207 | -0.039117 | south | Y | -0.12487 | -0.019025 | -0.11251 | 0.073309 | 0.019025 | south | N | 0.019025 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.039117 | south | Y | -0.12487 | -0.019025 | -0.11251 | 0.073309 | 0.019025 | south | N | 0.019025 | 0
8938 | MVGN#3 | 3 | 242 | -0.039117 | south | Y | -0.12487 | -0.019025 | -0.11251 | 0.073309 | 0.019025 | south | N | 0.019025 | 0
8981 | HECN1 | 1 | 144 | -0.03912 | south | Y | -0.12488 | -0.019028 | -0.11252 | 0.073306 | 0.019028 | south | N | 0.019028 | 0
8982 | HECN2 | 2 | 144 | -0.03912 | south | Y | -0.12488 | -0.019028 | -0.11252 | 0.073306 | 0.019028 | south | N | 0.019028 | 0
8983 | HECN3 | 3 | 171 | -0.03912 | south | Y | -0.12488 | -0.019028 | -0.11252 | 0.073306 | 0.019028 | south | N | 0.019028 | 0
9000 | DECKR_G1 | 1 | 310 | 0.001245 | south | Y | -0.084512 | 0.021337 | -0.072153 | 0.11367 | 0.021337 | south | N | 0.021337 | 0
9001 | DECKR_G2 | 2 | 413 | 0.001245 | south | Y | -0.084512 | 0.021337 | -0.072153 | 0.11367 | 0.021337 | south | N | 0.021337 | 0
9002 | DECKR_G3 | 3 | 42 | 0.002137 | south | Y | -0.08362 | 0.022229 | -0.071261 | 0.11456 | 0.022229 | south | N | 0.022229 | 0
9003 | DECKR_G4 | 4 | 44 | 0.002137 | south | Y | -0.08362 | 0.022229 | -0.071261 | 0.11456 | 0.022229 | south | N | 0.022229 | 0
9004 | DECKR_G5 | 5 | 44 | 0.002137 | south | Y | -0.08362 | 0.022229 | -0.071261 | 0.11456 | 0.022229 | south | N | 0.022229 | 0
9005 | DECKR_G6 | 6 | 47 | 0.002137 | south | Y | -0.08362 | 0.022229 | -0.071261 | 0.11456 | 0.022229 | south | N | 0.022229 | 0
9016 | SANDH_G1 | 1 | 49 | -2.5e-05 | south | Y | -0.085782 | 0.020067 | -0.073423 | 0.1124 | 0.020067 | south | N | 0.020067 | 0
9017 | SANDH_G2 | 2 | 46 | -2.5e-05 | south | Y | -0.085782 | 0.020067 | -0.073423 | 0.1124 | 0.020067 | south | N | 0.020067 | 0
9018 | SANDH_G3 | 3 | 46 | -2.5e-05 | south | Y | -0.085782 | 0.020067 | -0.073423 | 0.1124 | 0.020067 | south | N | 0.020067 | 0
9019 | SANDH_G4 | 4 | 47 | -2.5e-05 | south | Y | -0.085782 | 0.020067 | -0.073423 | 0.1124 | 0.020067 | south | N | 0.020067 | 0
9020 | SANDHG5A | 5A | 154 | -2.5e-05 | south | Y | -0.085782 | 0.020067 | -0.073423 | 0.1124 | 0.020067 | south | N | 0.020067 | 0
9021 | SANDHG5C | 5C | 148 | -2.5e-05 | south | Y | -0.085782 | 0.020067 | -0.073423 | 0.1124 | 0.020067 | south | N | 0.020067 | 0
9022 | SANDH_G6 | 6 | 48 | -2.5e-05 | south | Y | -0.085782 | 0.020067 | -0.073423 | 0.1124 | 0.020067 | south | N | 0.020067 | 0
9023 | SANDH_G7 | 7 | 48 | -2.5e-05 | south | Y | -0.085782 | 0.020067 | -0.073423 | 0.1124 | 0.020067 | south | N | 0.020067 | 0
11001 | NAV1CT | 1 | 70 | 0.073397 | west | Y | -0.01236 | 0.093489 | -6.8989e-07 | 0.18582 | 6.8989e-07 | west | N | 6.8989e-07 | 0
11009 | NAV2CT | 1 | 70 | 0.073397 | west | Y | -0.01236 | 0.093489 | -6.8989e-07 | 0.18582 | 6.8989e-07 | west | N | 6.8989e-07 | 0
11011 | NAV3ST | 1 | 92.8 | 0.073397 | west | Y | -0.01236 | 0.093489 | -6.8989e-07 | 0.18582 | 6.8989e-07 | west | N | 6.8989e-07 | 0
11012 | NAV4CT | 1 | 80 | 0.073397 | west | Y | -0.01236 | 0.093489 | -6.8989e-07 | 0.18582 | 6.8989e-07 | west | N | 6.8989e-07 | 0
11013 | NAV5CT | 1 | 80 | 0.073397 | west | Y | -0.01236 | 0.093489 | -6.8989e-07 | 0.18582 | 6.8989e-07 | west | N | 6.8989e-07 | 0
11014 | NAV6ST | 1 | 115 | 0.073397 | west | Y | -0.01236 | 0.093489 | -6.8989e-07 | 0.18582 | 6.8989e-07 | west | N | 6.8989e-07 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.07339 | west | Y | -0.012367 | 0.093482 | -7.6899e-06 | 0.18582 | 7.6899e-06 | west | N | 7.6899e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.07339 | west | Y | -0.012367 | 0.093482 | -7.6899e-06 | 0.18582 | 7.6899e-06 | west | N | 7.6899e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.07339 | west | Y | -0.012367 | 0.093482 | -7.6899e-06 | 0.18582 | 7.6899e-06 | west | N | 7.6899e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.07339 | west | Y | -0.012367 | 0.093482 | -7.6899e-06 | 0.18582 | 7.6899e-06 | west | N | 7.6899e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.07339 | west | Y | -0.012367 | 0.093482 | -7.6899e-06 | 0.18582 | 7.6899e-06 | west | N | 7.6899e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.07339 | west | Y | -0.012367 | 0.093482 | -7.6899e-06 | 0.18582 | 7.6899e-06 | west | N | 7.6899e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.074654 | west | Y | -0.011103 | 0.094746 | 0.0012563 | 0.18708 | 0.0012563 | west | N | 0.0012563 | 0
11057 | CHAMPION | 1 | 126.5 | 0.074654 | west | Y | -0.011103 | 0.094746 | 0.0012563 | 0.18708 | 0.0012563 | west | N | 0.0012563 | 0
11058 | PYRON_1G | 1 | 249 | 0.074654 | west | Y | -0.011103 | 0.094746 | 0.0012563 | 0.18708 | 0.0012563 | west | N | 0.0012563 | 0
11059 | INADALE_ | 1 | 197 | 0.074654 | west | Y | -0.011103 | 0.094746 | 0.0012563 | 0.18708 | 0.0012563 | west | N | 0.0012563 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.074016 | west | Y | -0.011741 | 0.094108 | 0.00061831 | 0.18644 | 0.00061831 | west | N | 0.00061831 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.074016 | west | Y | -0.011741 | 0.094108 | 0.00061831 | 0.18644 | 0.00061831 | west | N | 0.00061831 | 0
11147 | NOTREES_ | 1 | 149 | 0.07284 | west | Y | -0.012917 | 0.092932 | -0.00055769 | 0.18527 | 0.00055769 | west | N | 0.00055769 | 0
11309 | BULLCREK | 1 | 180 | 0.073895 | west | Y | -0.011862 | 0.093987 | 0.00049731 | 0.18632 | 0.00049731 | west | N | 0.00049731 | 0
11310 | BULLCREK | 1 | 180 | 0.073895 | west | Y | -0.011862 | 0.093987 | 0.00049731 | 0.18632 | 0.00049731 | west | N | 0.00049731 | 0
11320 | COYOTE_1 | 1 | 225 | 0.073858 | west | Y | -0.011899 | 0.09395 | 0.00046031 | 0.18628 | 0.00046031 | west | N | 0.00046031 | 0
11415 | LORAINE_ | 1 | 125 | 0.074391 | west | Y | -0.011366 | 0.094483 | 0.00099331 | 0.18682 | 0.00099331 | west | N | 0.00099331 | 0
11416 | LORAINE_ | 1 | 125 | 0.074391 | west | Y | -0.011366 | 0.094483 | 0.00099331 | 0.18682 | 0.00099331 | west | N | 0.00099331 | 0
11691 | KMICHICT | 1 | 140 | 0.08307 | north | N | -0.0026867 | 0.10316 | 0.0096723 | 0.1955 | 0.0026867 | North | N | 0.0026867 | 0
11692 | KMICHICT | 2 | 141 | 0.08307 | north | N | -0.0026867 | 0.10316 | 0.0096723 | 0.1955 | 0.0026867 | North | N | 0.0026867 | 0
11693 | KMICHIST | 3 | 309 | 0.08307 | north | N | -0.0026867 | 0.10316 | 0.0096723 | 0.1955 | 0.0026867 | North | N | 0.0026867 | 0
11694 | KMICHICT | 4 | 143 | 0.08307 | north | N | -0.0026867 | 0.10316 | 0.0096723 | 0.1955 | 0.0026867 | North | N | 0.0026867 | 0
11695 | KMICHICT | 5 | 144 | 0.08307 | north | N | -0.0026867 | 0.10316 | 0.0096723 | 0.1955 | 0.0026867 | North | N | 0.0026867 | 0
11696 | KMICHIST | 6 | 310 | 0.08307 | north | N | -0.0026867 | 0.10316 | 0.0096723 | 0.1955 | 0.0026867 | North | N | 0.0026867 | 0
12322 | ENNSTRAC | 1 | 196 | 0.082007 | north | Y | -0.0037497 | 0.1021 | 0.0086093 | 0.19443 | 0.0037497 | North | N | 0.0037497 | 0
12323 | ENNSTRAC | 2 | 111 | 0.082007 | north | Y | -0.0037497 | 0.1021 | 0.0086093 | 0.19443 | 0.0037497 | North | N | 0.0037497 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.082622 | north | N | -0.0031347 | 0.10271 | 0.0092243 | 0.19505 | 0.0031347 | North | N | 0.0031347 | 0
12411 | FPLEFR1A | 1 | 161 | 0.084026 | north | Y | -0.0017307 | 0.10412 | 0.010628 | 0.19645 | 0.0017307 | North | N | 0.0017307 | 0
12412 | FPLEFR1B | 2 | 164 | 0.084026 | north | Y | -0.0017307 | 0.10412 | 0.010628 | 0.19645 | 0.0017307 | North | N | 0.0017307 | 0
12413 | FPLEFR1C | 3 | 164 | 0.084026 | north | Y | -0.0017307 | 0.10412 | 0.010628 | 0.19645 | 0.0017307 | North | N | 0.0017307 | 0
12414 | FPLEFR1S | 4 | 414 | 0.084026 | north | Y | -0.0017307 | 0.10412 | 0.010628 | 0.19645 | 0.0017307 | North | N | 0.0017307 | 0
12421 | FPLEFR2A | 1 | 162 | 0.084026 | north | Y | -0.0017307 | 0.10412 | 0.010628 | 0.19645 | 0.0017307 | North | N | 0.0017307 | 0
12422 | FPLEFR2B | 2 | 161 | 0.084026 | north | Y | -0.0017307 | 0.10412 | 0.010628 | 0.19645 | 0.0017307 | North | N | 0.0017307 | 0
12423 | FPLEFR2C | 3 | 163 | 0.084026 | north | Y | -0.0017307 | 0.10412 | 0.010628 | 0.19645 | 0.0017307 | North | N | 0.0017307 | 0
12424 | FPLEFR2S | 4 | 409 | 0.084026 | north | Y | -0.0017307 | 0.10412 | 0.010628 | 0.19645 | 0.0017307 | North | N | 0.0017307 | 0
12440 | PARKD_1S | 1 | 0 | 0.083373 | north | N | -0.0023837 | 0.10347 | 0.0099753 | 0.1958 | 0.0023837 | North | N | 0.0023837 | 0
12449 | PARKD_2S | 1 | 0 | 0.083373 | north | N | -0.0023837 | 0.10347 | 0.0099753 | 0.1958 | 0.0023837 | North | N | 0.0023837 | 0
13116 | TGATEWAY | 1 | 148 | 0.086639 | north | N | 0.00088234 | 0.10673 | 0.013241 | 0.19906 | 0.00088234 | North | N | 0.00088234 | 0
13117 | TGATEWAY | 2 | 130 | 0.086639 | north | N | 0.00088234 | 0.10673 | 0.013241 | 0.19906 | 0.00088234 | North | N | 0.00088234 | 0
13118 | TGATEWAY | 3 | 145 | 0.086639 | north | N | 0.00088234 | 0.10673 | 0.013241 | 0.19906 | 0.00088234 | North | N | 0.00088234 | 0
13119 | TGATEWAY | 4 | 399 | 0.086639 | north | N | 0.00088234 | 0.10673 | 0.013241 | 0.19906 | 0.00088234 | North | N | 0.00088234 | 0
13131 | CALFREST | 1 | 150.7 | 0.090515 | north | Y | 0.0047583 | 0.11061 | 0.017117 | 0.20294 | 0.0047583 | North | N | 0.0047583 | 0
13132 | CALFREST | 2 | 151 | 0.090515 | north | Y | 0.0047583 | 0.11061 | 0.017117 | 0.20294 | 0.0047583 | North | N | 0.0047583 | 0
13133 | CALFREST | 3 | 177.4 | 0.090515 | north | Y | 0.0047583 | 0.11061 | 0.017117 | 0.20294 | 0.0047583 | North | N | 0.0047583 | 0
13134 | CALFREST | 4 | 151.5 | 0.090367 | north | Y | 0.0046103 | 0.11046 | 0.016969 | 0.20279 | 0.0046103 | North | N | 0.0046103 | 0
13135 | CALFREST | 5 | 152.3 | 0.090367 | north | Y | 0.0046103 | 0.11046 | 0.016969 | 0.20279 | 0.0046103 | North | N | 0.0046103 | 0
13136 | CALFREST | 6 | 177.5 | 0.090367 | north | Y | 0.0046103 | 0.11046 | 0.016969 | 0.20279 | 0.0046103 | North | N | 0.0046103 | 0
13432 | SANDOW_5 | 5 | 581 | 0.022732 | south | Y | -0.063025 | 0.042824 | -0.050666 | 0.13516 | 0.042824 | south | N | 0.042824 | 0
13691 | OAKGROVE | 1 | 855 | 0.10649 | north | Y | 0.020729 | 0.12658 | 0.033088 | 0.21891 | 0.020729 | North | N | 0.020729 | 0
13692 | OAKGROVE | 2 | 855 | 0.10649 | north | Y | 0.020729 | 0.12658 | 0.033088 | 0.21891 | 0.020729 | North | N | 0.020729 | 0
32798 | BRYN_TAM | 1 | 32 | 0.1136 | north | N | 0.027847 | 0.1337 | 0.040206 | 0.22603 | 0.027847 | North | N | 0.027847 | 0
32883 | BRYN_DNS | 1 | 48 | 0.11084 | north | Y | 0.02508 | 0.13093 | 0.037439 | 0.22326 | 0.02508 | North | N | 0.02508 | 0
32884 | BRYN_DNS | 1 | 46 | 0.11084 | north | Y | 0.02508 | 0.13093 | 0.037439 | 0.22326 | 0.02508 | North | N | 0.02508 | 0
32886 | BRYN_ATK | MB | 12 | 0.11336 | north | Y | 0.027604 | 0.13345 | 0.039963 | 0.22579 | 0.027604 | North | N | 0.027604 | 0
32887 | BRYN_ATK | MB | 51 | 0.11336 | north | Y | 0.027604 | 0.13345 | 0.039963 | 0.22579 | 0.027604 | North | N | 0.027604 | 0
32888 | BRYN_ATK | 1 | 17 | 0.11336 | north | Y | 0.027604 | 0.13345 | 0.039963 | 0.22579 | 0.027604 | North | N | 0.027604 | 0
32890 | BRYN_ATK | MB | 22 | 0.11336 | north | Y | 0.027604 | 0.13345 | 0.039963 | 0.22579 | 0.027604 | North | N | 0.027604 | 0
32891 | BRYN_ATK | MB | 25 | 0.11336 | north | Y | 0.027604 | 0.13345 | 0.039963 | 0.22579 | 0.027604 | North | N | 0.027604 | 0
32892 | BRYN_DNS | 1 | 105 | 0.11084 | north | Y | 0.02508 | 0.13093 | 0.037439 | 0.22326 | 0.02508 | North | N | 0.02508 | 0
36998 | RDCNYNG1 | 1 | 84 | 0.074261 | west | Y | -0.011496 | 0.094353 | 0.00086331 | 0.18669 | 0.00086331 | west | N | 0.00086331 | 0
38332 | WDWRDU2 | 1 | 80 | 0.068654 | west | Y | -0.017103 | 0.088746 | -0.0047437 | 0.18108 | 0.0047437 | west | N | 0.0047437 | 0
38437 | TNSRBNMS | 1 | 150 | 0.068617 | west | Y | -0.01714 | 0.088709 | -0.0047807 | 0.18104 | 0.0047807 | west | N | 0.0047807 | 0
38438 | TNSRBNMS | 1 | 150 | 0.068617 | west | Y | -0.01714 | 0.088709 | -0.0047807 | 0.18104 | 0.0047807 | west | N | 0.0047807 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.11322 | houston | N | -0.19897 | -0.093124 | -0.18661 | -0.00079018 | 0.00079018 | houston | N | 0.00079018 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.11322 | houston | N | -0.19897 | -0.093124 | -0.18661 | -0.00079018 | 0.00079018 | houston | N | 0.00079018 | 0
38600 | TNBP_CGN | 5 | 53 | -0.11322 | houston | N | -0.19897 | -0.093124 | -0.18661 | -0.00079018 | 0.00079018 | houston | N | 0.00079018 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.11322 | houston | N | -0.19897 | -0.093124 | -0.18661 | -0.00079018 | 0.00079018 | houston | N | 0.00079018 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.11322 | houston | N | -0.19897 | -0.093124 | -0.18661 | -0.00079018 | 0.00079018 | houston | N | 0.00079018 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.11322 | houston | N | -0.19897 | -0.093124 | -0.18661 | -0.00079018 | 0.00079018 | houston | N | 0.00079018 | 0
38614 | TNBPAMCG | 4 | 96 | -0.11322 | houston | N | -0.19897 | -0.093124 | -0.18661 | -0.00079018 | 0.00079018 | houston | N | 0.00079018 | 0
38615 | TNBPAMCG | 1 | 244 | -0.11322 | houston | N | -0.19897 | -0.093124 | -0.18661 | -0.00079018 | 0.00079018 | houston | N | 0.00079018 | 0
38690 | TNBP_CGN | 3 | 40 | -0.11322 | houston | N | -0.19897 | -0.093124 | -0.18661 | -0.00079018 | 0.00079018 | houston | N | 0.00079018 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.11318 | houston | N | -0.19893 | -0.093084 | -0.18657 | -0.00075018 | 0.00075018 | houston | N | 0.00075018 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.11318 | houston | N | -0.19893 | -0.093084 | -0.18657 | -0.00075018 | 0.00075018 | houston | N | 0.00075018 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.11318 | houston | N | -0.19893 | -0.093084 | -0.18657 | -0.00075018 | 0.00075018 | houston | N | 0.00075018 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.11318 | houston | N | -0.19893 | -0.093084 | -0.18657 | -0.00075018 | 0.00075018 | houston | N | 0.00075018 | 0
39470 | TNDOWCGN | 1 | 32 | -0.11318 | houston | N | -0.19893 | -0.093085 | -0.18657 | -0.00075118 | 0.00075118 | houston | N | 0.00075118 | 0
39480 | TNDOWCGN | 1 | 30 | -0.11318 | houston | N | -0.19893 | -0.093085 | -0.18657 | -0.00075118 | 0.00075118 | houston | N | 0.00075118 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.089579 | houston | N | -0.17534 | -0.069487 | -0.16298 | 0.022847 | 0.022847 | houston | N | 0.022847 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.089579 | houston | N | -0.17534 | -0.069487 | -0.16298 | 0.022847 | 0.022847 | houston | N | 0.022847 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.089579 | houston | N | -0.17534 | -0.069487 | -0.16298 | 0.022847 | 0.022847 | houston | N | 0.022847 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.089579 | houston | N | -0.17534 | -0.069487 | -0.16298 | 0.022847 | 0.022847 | houston | N | 0.022847 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.10649 | north | Y | 0.020729 | 0.12658 | 0.033088 | 0.21891 | 0.020729 | North | N | 0.020729 | 0
39970 | TNTNPONE | 1 | 153 | 0.10649 | north | Y | 0.020729 | 0.12658 | 0.033088 | 0.21891 | 0.020729 | North | N | 0.020729 | 0
48500 | APD_GT1_ | 1 | 136 | -0.12887 | houston | N | -0.21462 | -0.10877 | -0.20226 | -0.016439 | 0.016439 | houston | N | 0.016439 | 0
48510 | AK_GT1__ | 1 | 33 | -0.10493 | houston | N | -0.19069 | -0.084839 | -0.17833 | 0.0074948 | 0.0074948 | houston | N | 0.0074948 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.13215 | houston | Y | -0.21791 | -0.11206 | -0.20555 | -0.019729 | 0.019729 | houston | N | 0.019729 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.13215 | houston | Y | -0.21791 | -0.11206 | -0.20555 | -0.019729 | 0.019729 | houston | N | 0.019729 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.13215 | houston | Y | -0.21791 | -0.11206 | -0.20555 | -0.019729 | 0.019729 | houston | N | 0.019729 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.13215 | houston | Y | -0.21791 | -0.11206 | -0.20555 | -0.019729 | 0.019729 | houston | N | 0.019729 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.089558 | houston | N | -0.17531 | -0.069466 | -0.16296 | 0.022868 | 0.022868 | houston | N | 0.022868 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.089558 | houston | N | -0.17531 | -0.069466 | -0.16296 | 0.022868 | 0.022868 | houston | N | 0.022868 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.096738 | houston | N | -0.18249 | -0.076646 | -0.17014 | 0.015688 | 0.015688 | houston | N | 0.015688 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.096738 | houston | N | -0.18249 | -0.076646 | -0.17014 | 0.015688 | 0.015688 | houston | N | 0.015688 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.096738 | houston | N | -0.18249 | -0.076646 | -0.17014 | 0.015688 | 0.015688 | houston | N | 0.015688 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.12426 | houston | N | -0.21002 | -0.10417 | -0.19766 | -0.011833 | 0.011833 | houston | N | 0.011833 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.12426 | houston | N | -0.21002 | -0.10417 | -0.19766 | -0.011833 | 0.011833 | houston | N | 0.011833 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.12426 | houston | N | -0.21002 | -0.10417 | -0.19766 | -0.011833 | 0.011833 | houston | N | 0.011833 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.12426 | houston | N | -0.21002 | -0.10417 | -0.19766 | -0.011833 | 0.011833 | houston | N | 0.011833 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.12893 | houston | N | -0.21469 | -0.10884 | -0.20233 | -0.016505 | 0.016505 | houston | N | 0.016505 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.12893 | houston | N | -0.21469 | -0.10884 | -0.20233 | -0.016505 | 0.016505 | houston | N | 0.016505 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.1228 | houston | N | -0.20856 | -0.10271 | -0.1962 | -0.010377 | 0.010377 | houston | N | 0.010377 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.1228 | houston | N | -0.20856 | -0.10271 | -0.1962 | -0.010377 | 0.010377 | houston | N | 0.010377 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.1228 | houston | N | -0.20856 | -0.10271 | -0.1962 | -0.010377 | 0.010377 | houston | N | 0.010377 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.1228 | houston | N | -0.20856 | -0.10271 | -0.1962 | -0.010377 | 0.010377 | houston | N | 0.010377 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.1228 | houston | N | -0.20856 | -0.10271 | -0.1962 | -0.010377 | 0.010377 | houston | N | 0.010377 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.13928 | houston | Y | -0.22503 | -0.11918 | -0.21267 | -0.02685 | 0.02685 | houston | N | 0.02685 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.13651 | houston | Y | -0.22227 | -0.11642 | -0.20991 | -0.024087 | 0.024087 | houston | N | 0.024087 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.14191 | houston | Y | -0.22767 | -0.12182 | -0.21531 | -0.029483 | 0.029483 | houston | N | 0.029483 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.14191 | houston | Y | -0.22767 | -0.12182 | -0.21531 | -0.029483 | 0.029483 | houston | N | 0.029483 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.14191 | houston | Y | -0.22767 | -0.12182 | -0.21531 | -0.029483 | 0.029483 | houston | N | 0.029483 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.16737 | houston | N | -0.25313 | -0.14728 | -0.24077 | -0.054945 | 0.054945 | houston | N | 0.054945 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.1297 | houston | N | -0.21546 | -0.10961 | -0.2031 | -0.017275 | 0.017275 | houston | N | 0.017275 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.1297 | houston | N | -0.21546 | -0.10961 | -0.2031 | -0.017275 | 0.017275 | houston | N | 0.017275 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.14526 | houston | N | -0.23102 | -0.12517 | -0.21866 | -0.032835 | 0.032835 | houston | N | 0.032835 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.14526 | houston | N | -0.23102 | -0.12517 | -0.21866 | -0.032835 | 0.032835 | houston | N | 0.032835 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.14526 | houston | N | -0.23102 | -0.12517 | -0.21866 | -0.032835 | 0.032835 | houston | N | 0.032835 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.14526 | houston | N | -0.23102 | -0.12517 | -0.21866 | -0.032835 | 0.032835 | houston | N | 0.032835 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.1291 | houston | N | -0.21486 | -0.10901 | -0.2025 | -0.016676 | 0.016676 | houston | N | 0.016676 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.1291 | houston | N | -0.21486 | -0.10901 | -0.2025 | -0.016676 | 0.016676 | houston | N | 0.016676 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.1291 | houston | N | -0.21486 | -0.10901 | -0.2025 | -0.016676 | 0.016676 | houston | N | 0.016676 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.1291 | houston | N | -0.21486 | -0.10901 | -0.2025 | -0.016676 | 0.016676 | houston | N | 0.016676 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.13078 | houston | N | -0.21654 | -0.11069 | -0.20418 | -0.018354 | 0.018354 | houston | N | 0.018354 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.13078 | houston | N | -0.21654 | -0.11069 | -0.20418 | -0.018354 | 0.018354 | houston | N | 0.018354 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.13078 | houston | N | -0.21654 | -0.11069 | -0.20418 | -0.018354 | 0.018354 | houston | N | 0.018354 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.13078 | houston | N | -0.21654 | -0.11069 | -0.20418 | -0.018354 | 0.018354 | houston | N | 0.018354 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.13078 | houston | N | -0.21654 | -0.11069 | -0.20418 | -0.018354 | 0.018354 | houston | N | 0.018354 | 0
48651 | EP_1_2 | 1 | 5 | -0.13596 | houston | N | -0.22172 | -0.11587 | -0.20936 | -0.023533 | 0.023533 | houston | N | 0.023533 | 0
48651 | EP_1_2 | 2 | 21 | -0.13596 | houston | N | -0.22172 | -0.11587 | -0.20936 | -0.023533 | 0.023533 | houston | N | 0.023533 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.10287 | north | N | 0.017113 | 0.12296 | 0.029472 | 0.2153 | 0.017113 | North | N | 0.017113 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.10287 | north | N | 0.017113 | 0.12296 | 0.029472 | 0.2153 | 0.017113 | North | N | 0.017113 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.10287 | north | N | 0.017113 | 0.12296 | 0.029472 | 0.2153 | 0.017113 | North | N | 0.017113 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.10287 | north | N | 0.017113 | 0.12296 | 0.029472 | 0.2153 | 0.017113 | North | N | 0.017113 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.13866 | houston | Y | -0.22442 | -0.11857 | -0.21206 | -0.026235 | 0.026235 | houston | N | 0.026235 | 0
48691 | GBY_7374 | A | 46 | -0.11431 | houston | Y | -0.20007 | -0.094223 | -0.18771 | -0.0018892 | 0.0018892 | houston | N | 0.0018892 | 0
48691 | GBY_7374 | B | 46 | -0.11431 | houston | Y | -0.20007 | -0.094223 | -0.18771 | -0.0018892 | 0.0018892 | houston | N | 0.0018892 | 0
48692 | GBY_8182 | C | 46 | -0.11431 | houston | Y | -0.20007 | -0.094223 | -0.18771 | -0.0018892 | 0.0018892 | houston | N | 0.0018892 | 0
48692 | GBY_8182 | D | 55 | -0.11431 | houston | Y | -0.20007 | -0.094223 | -0.18771 | -0.0018892 | 0.0018892 | houston | N | 0.0018892 | 0
48693 | GBY_8384 | E | 55 | -0.11431 | houston | Y | -0.20007 | -0.094223 | -0.18771 | -0.0018892 | 0.0018892 | houston | N | 0.0018892 | 0
48693 | GBY_8384 | F | 54 | -0.11431 | houston | Y | -0.20007 | -0.094223 | -0.18771 | -0.0018892 | 0.0018892 | houston | N | 0.0018892 | 0
48721 | LEG_1___ | 1 | 827 | 0.10051 | north | Y | 0.014753 | 0.1206 | 0.027112 | 0.21294 | 0.014753 | North | N | 0.014753 | 0
48722 | LEG_2___ | 2 | 819 | 0.10051 | north | Y | 0.014753 | 0.1206 | 0.027112 | 0.21294 | 0.014753 | North | N | 0.014753 | 0
48730 | MNS_GT | 1 | 46.1 | -0.10294 | houston | N | -0.1887 | -0.082849 | -0.17634 | 0.0094848 | 0.0094848 | houston | N | 0.0094848 | 0
48731 | CBE_GT1 | 1 | 76 | -0.065097 | houston | Y | -0.15085 | -0.045005 | -0.13849 | 0.047329 | 0.045005 | south | Y | 0.047329 | 0.17661
48732 | CBE_GT2 | 1 | 76 | -0.065097 | houston | Y | -0.15085 | -0.045005 | -0.13849 | 0.047329 | 0.045005 | south | Y | 0.047329 | 0.17661
48733 | CBE_ST12 | 1 | 105 | -0.065097 | houston | Y | -0.15085 | -0.045005 | -0.13849 | 0.047329 | 0.045005 | south | Y | 0.047329 | 0.244
48734 | CBE_GT3 | 1 | 74 | -0.065097 | houston | Y | -0.15085 | -0.045005 | -0.13849 | 0.047329 | 0.045005 | south | Y | 0.047329 | 0.17196
48735 | CBE_GT4 | 1 | 74 | -0.065097 | houston | Y | -0.15085 | -0.045005 | -0.13849 | 0.047329 | 0.045005 | south | Y | 0.047329 | 0.17196
48736 | CBE_ST34 | 1 | 102 | -0.065097 | houston | Y | -0.15085 | -0.045005 | -0.13849 | 0.047329 | 0.045005 | south | Y | 0.047329 | 0.23703
48740 | PSG_GN2_ | 1 | 180 | -0.12912 | houston | N | -0.21488 | -0.10903 | -0.20252 | -0.016699 | 0.016699 | houston | N | 0.016699 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.12912 | houston | N | -0.21488 | -0.10903 | -0.20252 | -0.016699 | 0.016699 | houston | N | 0.016699 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.12912 | houston | N | -0.21488 | -0.10903 | -0.20252 | -0.016699 | 0.016699 | houston | N | 0.016699 | 0
48761 | PR_GT1__ | 1 | 35 | -0.12776 | houston | N | -0.21351 | -0.10766 | -0.20115 | -0.015329 | 0.015329 | houston | N | 0.015329 | 0
48772 | PHR_GN2_ | MB | 459 | -0.11997 | houston | Y | -0.20573 | -0.099883 | -0.19337 | -0.0075492 | 0.0075492 | houston | N | 0.0075492 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.13445 | houston | N | -0.22021 | -0.11436 | -0.20785 | -0.022026 | 0.022026 | houston | N | 0.022026 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.13445 | houston | N | -0.22021 | -0.11436 | -0.20785 | -0.022026 | 0.022026 | houston | N | 0.022026 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.13445 | houston | N | -0.22021 | -0.11436 | -0.20785 | -0.022026 | 0.022026 | houston | N | 0.022026 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.13445 | houston | N | -0.22021 | -0.11436 | -0.20785 | -0.022026 | 0.022026 | houston | N | 0.022026 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.13445 | houston | N | -0.22021 | -0.11436 | -0.20785 | -0.022026 | 0.022026 | houston | N | 0.022026 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.13445 | houston | N | -0.22021 | -0.11436 | -0.20785 | -0.022026 | 0.022026 | houston | N | 0.022026 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.13445 | houston | N | -0.22021 | -0.11436 | -0.20785 | -0.022026 | 0.022026 | houston | N | 0.022026 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.16737 | houston | N | -0.25313 | -0.14728 | -0.24077 | -0.054945 | 0.054945 | houston | N | 0.054945 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.16737 | houston | N | -0.25313 | -0.14728 | -0.24077 | -0.054945 | 0.054945 | houston | N | 0.054945 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.16737 | houston | N | -0.25313 | -0.14728 | -0.24077 | -0.054945 | 0.054945 | houston | N | 0.054945 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.16737 | houston | N | -0.25313 | -0.14728 | -0.24077 | -0.054945 | 0.054945 | houston | N | 0.054945 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.13519 | houston | N | -0.22095 | -0.1151 | -0.20859 | -0.022767 | 0.022767 | houston | N | 0.022767 | 0
48820 | SHELLG1_ | 1 | 71 | -0.13026 | houston | N | -0.21601 | -0.11016 | -0.20365 | -0.017831 | 0.017831 | houston | N | 0.017831 | 0
48821 | SHELLG2 | 2 | 72 | -0.13026 | houston | N | -0.21601 | -0.11016 | -0.20365 | -0.017831 | 0.017831 | houston | N | 0.017831 | 0
48822 | SHELLG3_ | 1 | 39 | -0.13026 | houston | N | -0.21601 | -0.11016 | -0.20365 | -0.017831 | 0.017831 | houston | N | 0.017831 | 0
48822 | SHELLG3_ | 2 | 30 | -0.13026 | houston | N | -0.21601 | -0.11016 | -0.20365 | -0.017831 | 0.017831 | houston | N | 0.017831 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.12664 | houston | N | -0.2124 | -0.10655 | -0.20004 | -0.014215 | 0.014215 | houston | N | 0.014215 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.12664 | houston | N | -0.2124 | -0.10655 | -0.20004 | -0.014215 | 0.014215 | houston | N | 0.014215 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.12909 | houston | N | -0.21485 | -0.109 | -0.20249 | -0.016663 | 0.016663 | houston | N | 0.016663 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.12886 | houston | Y | -0.21462 | -0.10877 | -0.20226 | -0.016434 | 0.016434 | houston | N | 0.016434 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.1288 | houston | Y | -0.21455 | -0.1087 | -0.20219 | -0.016371 | 0.016371 | houston | N | 0.016371 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.12907 | houston | Y | -0.21483 | -0.10898 | -0.20247 | -0.016645 | 0.016645 | houston | N | 0.016645 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.12913 | houston | Y | -0.21488 | -0.10904 | -0.20253 | -0.016702 | 0.016702 | houston | N | 0.016702 | 0
48855 | SRB_GT21 | B2 | 12 | -0.12875 | houston | Y | -0.21451 | -0.10866 | -0.20215 | -0.016327 | 0.016327 | houston | N | 0.016327 | 0
48855 | SRB_GT21 | MB | 18 | -0.12875 | houston | Y | -0.21451 | -0.10866 | -0.20215 | -0.016327 | 0.016327 | houston | N | 0.016327 | 0
48865 | TECO_GT1 | 1 | 50 | -0.11002 | houston | Y | -0.19578 | -0.089928 | -0.18342 | 0.0024058 | 0.0024058 | houston | N | 0.0024058 | 0
48873 | THW_ST3_ | 3 | 104 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48874 | THW_ST4_ | 4 | 104 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48875 | THW_3132 | A | 54 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48875 | THW_3132 | B | 53 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48877 | THW_3334 | C | 54 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48877 | THW_3334 | D | 57 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48879 | THW_4142 | E | 54 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48879 | THW_4142 | F | 54 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48881 | THW_4344 | G | 58 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48881 | THW_4344 | H | 58 | -0.10021 | houston | Y | -0.18597 | -0.080122 | -0.17361 | 0.012212 | 0.012212 | houston | N | 0.012212 | 0
48883 | THW_GT1_ | B2 | 12 | -0.10417 | houston | Y | -0.18993 | -0.084081 | -0.17757 | 0.0082528 | 0.0082528 | houston | N | 0.0082528 | 0
48885 | THW_5152 | A | 56 | -0.11698 | houston | Y | -0.20274 | -0.096889 | -0.19038 | -0.0045552 | 0.0045552 | houston | N | 0.0045552 | 0
48885 | THW_5152 | B | 59 | -0.11698 | houston | Y | -0.20274 | -0.096889 | -0.19038 | -0.0045552 | 0.0045552 | houston | N | 0.0045552 | 0
48886 | THW_5354 | C | 56 | -0.11698 | houston | Y | -0.20274 | -0.096889 | -0.19038 | -0.0045552 | 0.0045552 | houston | N | 0.0045552 | 0
48886 | THW_5354 | D | 56 | -0.11698 | houston | Y | -0.20274 | -0.096889 | -0.19038 | -0.0045552 | 0.0045552 | houston | N | 0.0045552 | 0
48887 | THW_5556 | E | 59 | -0.11698 | houston | Y | -0.20274 | -0.096889 | -0.19038 | -0.0045552 | 0.0045552 | houston | N | 0.0045552 | 0
48887 | THW_5556 | F | 56 | -0.11698 | houston | Y | -0.20274 | -0.096889 | -0.19038 | -0.0045552 | 0.0045552 | houston | N | 0.0045552 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.072199 | houston | Y | -0.15796 | -0.052107 | -0.1456 | 0.040227 | 0.040227 | houston | N | 0.040227 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.096086 | houston | Y | -0.18184 | -0.075994 | -0.16948 | 0.01634 | 0.01634 | houston | N | 0.01634 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.096086 | houston | Y | -0.18184 | -0.075994 | -0.16948 | 0.01634 | 0.01634 | houston | N | 0.01634 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.096086 | houston | Y | -0.18184 | -0.075994 | -0.16948 | 0.01634 | 0.01634 | houston | N | 0.01634 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.096086 | houston | Y | -0.18184 | -0.075994 | -0.16948 | 0.01634 | 0.01634 | houston | N | 0.01634 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.096086 | houston | N | -0.18184 | -0.075994 | -0.16948 | 0.01634 | 0.01634 | houston | N | 0.01634 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.096676 | houston | Y | -0.18243 | -0.076584 | -0.17007 | 0.01575 | 0.01575 | houston | N | 0.01575 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.096676 | houston | Y | -0.18243 | -0.076584 | -0.17007 | 0.01575 | 0.01575 | houston | N | 0.01575 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.096676 | houston | Y | -0.18243 | -0.076584 | -0.17007 | 0.01575 | 0.01575 | houston | N | 0.01575 | 0
48929 | WAPGT21_ | B1 | 13 | -0.096086 | houston | Y | -0.18184 | -0.075994 | -0.16948 | 0.01634 | 0.01634 | houston | N | 0.01634 | 0
48940 | WARVUE_G | G1 | 12 | -0.13754 | houston | Y | -0.2233 | -0.11745 | -0.21094 | -0.025117 | 0.025117 | houston | N | 0.025117 | 0
49803 | EXN_15GT | 1 | 34 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49826 | EXN938GT | 5 | 45.9 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49828 | EXN941GT | 10 | 17.7 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49829 | EXN942GT | 11 | 20.4 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49830 | EXN943GT | 12 | 19.9 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49831 | EXN944GT | 13 | 35 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49832 | EXN945GT | 9 | 18 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49837 | EXN_GT | 4 | 85.4 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49838 | EXN_14GT | 14 | 148 | -0.13572 | houston | N | -0.22148 | -0.11563 | -0.20912 | -0.023295 | 0.023295 | houston | N | 0.023295 | 0
49851 | DOW17000 | 37 | 62 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49858 | DOW38100 | 31 | 71.4 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49859 | DOW38200 | 33 | 45 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49860 | DOW38300 | 32 | 101 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49862 | DOW39100 | 36 | 86 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49863 | DOW39200 | 35 | 88 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49865 | DOW41000 | 41 | 50 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49866 | DOW42000 | 42 | 18 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49869 | DOW49000 | 45 | 94 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49870 | DOW61000 | 61 | 70 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49871 | DOW62000 | 62 | 63 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49872 | DOW63000 | 63 | 72 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49873 | DOW64000 | 64 | 64.8 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49876 | DOW65000 | 65 | 101 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49877 | DOW66000 | 66 | 97 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49878 | DOW67000 | 67 | 103 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49882 | DOW81000 | 81 | 76 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49884 | DOW82000 | 82 | 80 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49885 | DOW83000 | 83 | 80 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
49886 | DOW84000 | 84 | 171 | -0.088447 | houston | N | -0.1742 | -0.068355 | -0.16184 | 0.023979 | 0.023979 | houston | N | 0.023979 | 0
58909 | PEARSALL | 1 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58909 | PEARSALL | 2 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58909 | PEARSALL | 3 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58909 | PEARSALL | 4 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58909 | PEARSALL | 5 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58909 | PEARSALL | 6 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58919 | PEARSALL | 1 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58919 | PEARSALL | 2 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58919 | PEARSALL | 3 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58919 | PEARSALL | 4 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58919 | PEARSALL | 5 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58919 | PEARSALL | 6 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58929 | PEARSALL | 1 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58929 | PEARSALL | 2 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58929 | PEARSALL | 3 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58929 | PEARSALL | 4 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58929 | PEARSALL | 5 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58929 | PEARSALL | 6 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58949 | PEARSALL | 1 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58949 | PEARSALL | 2 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58949 | PEARSALL | 3 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58949 | PEARSALL | 4 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58949 | PEARSALL | 5 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
58949 | PEARSALL | 6 | 8.4 | -0.023643 | south | Y | -0.1094 | -0.003551 | -0.097041 | 0.088783 | 0.003551 | south | N | 0.003551 | 0
60000 | DSKY2 | 1 | 76.5 | 0.066926 | west | Y | -0.018831 | 0.087018 | -0.0064717 | 0.17935 | 0.0064717 | west | N | 0.0064717 | 0
60003 | KING_NE1 | 1 | 80 | 0.068725 | west | Y | -0.017032 | 0.088817 | -0.0046727 | 0.18115 | 0.0046727 | west | N | 0.0046727 | 0
60005 | KING_SE1 | 1 | 40 | 0.068725 | west | Y | -0.017032 | 0.088817 | -0.0046727 | 0.18115 | 0.0046727 | west | N | 0.0046727 | 0
60007 | KING_SW1 | 1 | 80 | 0.069015 | west | Y | -0.016742 | 0.089107 | -0.0043827 | 0.18144 | 0.0043827 | west | N | 0.0043827 | 0
60016 | WOODWRD1 | 1 | 80 | 0.068662 | west | Y | -0.017095 | 0.088754 | -0.0047357 | 0.18109 | 0.0047357 | west | N | 0.0047357 | 0
60017 | ORNNWP1 | 1 | 80 | 0.067168 | west | Y | -0.018589 | 0.08726 | -0.0062297 | 0.17959 | 0.0062297 | west | N | 0.0062297 | 0
60018 | DSKY1 | 1 | 84 | 0.066679 | west | Y | -0.019078 | 0.086771 | -0.0067187 | 0.1791 | 0.0067187 | west | N | 0.0067187 | 0
60019 | KING_NW1 | 1 | 80 | 0.069015 | west | Y | -0.016742 | 0.089107 | -0.0043827 | 0.18144 | 0.0043827 | west | N | 0.0043827 | 0
60057 | CALLAHAN | 1 | 114 | -0.017876 | south | Y | -0.10363 | 0.002216 | -0.091274 | 0.09455 | 0.002216 | south | N | 0.002216 | 0
60058 | BUFF_GAP | 1 | 120 | 0.073852 | west | Y | -0.011905 | 0.093944 | 0.00045431 | 0.18628 | 0.00045431 | west | N | 0.00045431 | 0
60060 | CIRELLO | 1 | 233 | 0.073852 | west | Y | -0.011905 | 0.093944 | 0.00045431 | 0.18628 | 0.00045431 | west | N | 0.00045431 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.073852 | west | Y | -0.011905 | 0.093944 | 0.00045431 | 0.18628 | 0.00045431 | west | N | 0.00045431 | 0
60066 | H_HOLLOW | 1 | 222 | -0.017876 | south | Y | -0.10363 | 0.002216 | -0.091274 | 0.09455 | 0.002216 | south | N | 0.002216 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.017876 | south | Y | -0.10363 | 0.002216 | -0.091274 | 0.09455 | 0.002216 | south | N | 0.002216 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.017876 | south | Y | -0.10363 | 0.002216 | -0.091274 | 0.09455 | 0.002216 | south | N | 0.002216 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.017876 | south | Y | -0.10363 | 0.002216 | -0.091274 | 0.09455 | 0.002216 | south | N | 0.002216 | 0
60074 | HORSH5 | 1 | 100 | -0.017876 | south | Y | -0.10363 | 0.002216 | -0.091274 | 0.09455 | 0.002216 | south | N | 0.002216 | 0
60081 | WHRLWIND | 1 | 60 | 0.075202 | west | Y | -0.010555 | 0.095294 | 0.0018043 | 0.18763 | 0.0018043 | west | N | 0.0018043 | 0
60201 | RIO DRCS | F | 0 | 0.01934 | south | N | -0.066417 | 0.039432 | -0.054058 | 0.13177 | 0.039432 | south | N | 0.039432 | 0
60202 | FRIEND_R | F | 0 | 0.058885 | west | N | -0.026872 | 0.078977 | -0.014513 | 0.17131 | 0.014513 | west | N | 0.014513 | 0
60203 | PRES0A | BT | 4.8 | 0.070088 | west | N | -0.015669 | 0.09018 | -0.0033097 | 0.18251 | 0.0033097 | west | N | 0.0033097 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.074596 | west | Y | -0.011161 | 0.094688 | 0.0011983 | 0.18702 | 0.0011983 | west | N | 0.0011983 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.074596 | west | Y | -0.011161 | 0.094688 | 0.0011983 | 0.18702 | 0.0011983 | west | N | 0.0011983 | 0
71057 | L_SWEETW | W1 | 135 | 0.074596 | west | Y | -0.011161 | 0.094688 | 0.0011983 | 0.18702 | 0.0011983 | west | N | 0.0011983 | 0
71059 | L_SWEETW | W1 | 119 | 0.074596 | west | Y | -0.011161 | 0.094688 | 0.0011983 | 0.18702 | 0.0011983 | west | N | 0.0011983 | 0
71060 | L_SWEETW | W1 | 105 | 0.074596 | west | Y | -0.011161 | 0.094688 | 0.0011983 | 0.18702 | 0.0011983 | west | N | 0.0011983 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.074596 | west | Y | -0.011161 | 0.094688 | 0.0011983 | 0.18702 | 0.0011983 | west | N | 0.0011983 | 0
76031 | L_GASCCR | W1 | 150 | 0.073417 | west | Y | -0.01234 | 0.093509 | 1.931e-05 | 0.18584 | 1.931e-05 | west | N | 1.931e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.073267 | west | Y | -0.01249 | 0.093359 | -0.00013069 | 0.18569 | 0.00013069 | west | N | 0.00013069 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.073267 | west | Y | -0.01249 | 0.093359 | -0.00013069 | 0.18569 | 0.00013069 | west | N | 0.00013069 | 0
76096 | L_CAPRSI | W1 | 186 | 0.073267 | west | Y | -0.01249 | 0.093359 | -0.00013069 | 0.18569 | 0.00013069 | west | N | 0.00013069 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.073267 | west | Y | -0.01249 | 0.093359 | -0.00013069 | 0.18569 | 0.00013069 | west | N | 0.00013069 | 0
80003 | MILHWYS | F | 0 | -0.039454 | south | N | -0.12521 | -0.019362 | -0.11285 | 0.072972 | 0.019362 | south | N | 0.019362 | 0
80010 | EPLVT1 | F | 0 | -0.009037 | south | N | -0.094794 | 0.011055 | -0.082435 | 0.10339 | 0.011055 | south | N | 0.011055 | 0
80012 | LAR | F | 0 | -0.028995 | south | N | -0.11475 | -0.008903 | -0.10239 | 0.083431 | 0.008903 | south | N | 0.008903 | 0
80051 | FORPVCM0 | 8 | 28 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
80053 | FOR69CG0 | 10 | 74 | -0.047136 | south | N | -0.13289 | -0.027044 | -0.12053 | 0.06529 | 0.027044 | south | N | 0.027044 | 0
80080 | GWINDT11 | 1 | 94 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80080 | GWINDT11 | 2 | 41 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80080 | GWINDT11 | 3 | 38 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80080 | GWINDT11 | 4 | 19 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80081 | GWINDT21 | 1 | 94 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80081 | GWINDT21 | 2 | 36 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80081 | GWINDT21 | 3 | 43 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80081 | GWINDT21 | 4 | 22 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80137 | CSDR89 | 8 | 39 | -0.044244 | south | N | -0.13 | -0.024152 | -0.11764 | 0.068182 | 0.024152 | south | N | 0.024152 | 0
80137 | CSDR89 | 9 | 15 | -0.044244 | south | N | -0.13 | -0.024152 | -0.11764 | 0.068182 | 0.024152 | south | N | 0.024152 | 0
80138 | CSDR7 | 7 | 7 | -0.044244 | south | N | -0.13 | -0.024152 | -0.11764 | 0.068182 | 0.024152 | south | N | 0.024152 | 0
80139 | CSDR56 | 5 | 15 | -0.044244 | south | N | -0.13 | -0.024152 | -0.11764 | 0.068182 | 0.024152 | south | N | 0.024152 | 0
80139 | CSDR56 | 6 | 39 | -0.044244 | south | N | -0.13 | -0.024152 | -0.11764 | 0.068182 | 0.024152 | south | N | 0.024152 | 0
80140 | CSDR11 | 11 | 39 | -0.044244 | south | N | -0.13 | -0.024152 | -0.11764 | 0.068182 | 0.024152 | south | N | 0.024152 | 0
80180 | PNSCALT1 | 1 | 148 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80180 | PNSCALT1 | 2 | 50 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80181 | PNSCALT2 | 1 | 55 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80181 | PNSCALT2 | 2 | 50 | -0.039581 | south | Y | -0.12534 | -0.019489 | -0.11298 | 0.072845 | 0.019489 | south | N | 0.019489 | 0
80223 | REYSHR G | 1 | 12 | -0.041494 | south | N | -0.12725 | -0.021402 | -0.11489 | 0.070932 | 0.021402 | south | N | 0.021402 | 0
80224 | VISTRONG | 1 | 15 | -0.043341 | south | N | -0.1291 | -0.023249 | -0.11674 | 0.069085 | 0.023249 | south | N | 0.023249 | 0
80225 | VISTRONG | 2 | 23 | -0.043341 | south | N | -0.1291 | -0.023249 | -0.11674 | 0.069085 | 0.023249 | south | N | 0.023249 | 0
80226 | ALCOA G | 1 | 48 | -0.046459 | south | N | -0.13222 | -0.026367 | -0.11986 | 0.065967 | 0.026367 | south | N | 0.026367 | 0
80227 | AIRCO G | 1 | 8 | -0.043945 | south | N | -0.1297 | -0.023853 | -0.11734 | 0.068481 | 0.023853 | south | N | 0.023853 | 0
80261 | NBEC81A | 1 | 180 | -0.04053 | south | Y | -0.12629 | -0.020438 | -0.11393 | 0.071896 | 0.020438 | south | N | 0.020438 | 0
80262 | NBEC91A | 1 | 180 | -0.040559 | south | Y | -0.12632 | -0.020467 | -0.11396 | 0.071867 | 0.020467 | south | N | 0.020467 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.040358 | south | Y | -0.12611 | -0.020266 | -0.11376 | 0.072068 | 0.020266 | south | N | 0.020266 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.040358 | south | Y | -0.12611 | -0.020266 | -0.11376 | 0.072068 | 0.020266 | south | N | 0.020266 | 0
80265 | LARECU40 | 4 | 100 | -0.028992 | south | Y | -0.11475 | -0.0089 | -0.10239 | 0.083434 | 0.0089 | south | N | 0.0089 | 0
80266 | LARECU50 | 5 | 100 | -0.028992 | south | Y | -0.11475 | -0.0089 | -0.10239 | 0.083434 | 0.0089 | south | N | 0.0089 | 0
80291 | PAPALOTE | 1 | 25 | -0.041132 | south | Y | -0.12689 | -0.02104 | -0.11453 | 0.071294 | 0.02104 | south | N | 0.02104 | 0
80291 | PAPALOTE | 2 | 25 | -0.041132 | south | Y | -0.12689 | -0.02104 | -0.11453 | 0.071294 | 0.02104 | south | N | 0.02104 | 0
80291 | PAPALOTE | 3 | 25 | -0.041132 | south | Y | -0.12689 | -0.02104 | -0.11453 | 0.071294 | 0.02104 | south | N | 0.02104 | 0
80291 | PAPALOTE | 4 | 16 | -0.041132 | south | Y | -0.12689 | -0.02104 | -0.11453 | 0.071294 | 0.02104 | south | N | 0.02104 | 0
80294 | PAPALOTE | 5 | 25 | -0.041132 | south | Y | -0.12689 | -0.02104 | -0.11453 | 0.071294 | 0.02104 | south | N | 0.02104 | 0
80294 | PAPALOTE | 6 | 25 | -0.041132 | south | Y | -0.12689 | -0.02104 | -0.11453 | 0.071294 | 0.02104 | south | N | 0.02104 | 0
80294 | PAPALOTE | 7 | 25 | -0.041132 | south | Y | -0.12689 | -0.02104 | -0.11453 | 0.071294 | 0.02104 | south | N | 0.02104 | 0
80294 | PAPALOTE | 8 | 15 | -0.041132 | south | Y | -0.12689 | -0.02104 | -0.11453 | 0.071294 | 0.02104 | south | N | 0.02104 | 0
86104 | CID-138 | EQ | 0 | -0.028992 | south | N | -0.11475 | -0.0089 | -0.10239 | 0.083434 | 0.0089 | south | N | 0.0089 | 0
86105 | CID-230 | EQ | 500 | -0.028992 | south | N | -0.11475 | -0.0089 | -0.10239 | 0.083434 | 0.0089 | south | N | 0.0089 | 0
86106 | CUF-230 | EQ | 500 | -0.028992 | south | N | -0.11475 | -0.0089 | -0.10239 | 0.083434 | 0.0089 | south | N | 0.0089 | 0
86107 | CUF-138 | EQ | 0 | -0.028992 | south | N | -0.11475 | -0.0089 | -0.10239 | 0.083434 | 0.0089 | south | N | 0.0089 | 0
88198 | BEEVILLE | F | 0 | -0.034987 | south | N | -0.12074 | -0.014895 | -0.10838 | 0.077439 | 0.014895 | south | N | 0.014895 | 0
88253 | HAMILTON | F | 0 | 0.001514 | south | N | -0.084243 | 0.021606 | -0.071884 | 0.11394 | 0.021606 | south | N | 0.021606 | 0
88299 | ZAPATA | F | 0 | -0.033085 | south | N | -0.11884 | -0.012993 | -0.10648 | 0.079341 | 0.012993 | south | N | 0.012993 | 0
88508 | FALFURRI | F | 0 | -0.037301 | south | N | -0.12306 | -0.017209 | -0.1107 | 0.075125 | 0.017209 | south | N | 0.017209 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:46500 TOMBAL__ - 45971 KYUDAL74 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.12175 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.3698 | 463 | 0.23859 | 110.4685 | 463 | 110.4685
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.1136 | north | 7 | N | N | Nnorth | Nnorth | 1 | 3.6353 | 0 | 0.23045 | 0 | 463 | 110.4685
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2302 | 0 | 463 | 110.4685
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2302 | 0 | 463 | 110.4685 | Weighted Shift Factors
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.11336 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9271 | 17 | 0.2302 | 3.9135 | 480 | 114.382 | North | 0.085757
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2302 | 0 | 480 | 114.382 | Houston | -0.11684
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2302 | 0 | 480 | 114.382 |  | 0.2026
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.11084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3202 | 48 | 0.22768 | 10.9287 | 528 | 125.3107
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.11084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.0985 | 46 | 0.22768 | 10.4733 | 574 | 135.784 | Line Rating | 1759
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.11084 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.6379 | 105 | 0.22768 | 23.9065 | 679 | 159.6905 | Conc Gen | 2694.3
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.0455 | 855 | 0.22333 | 190.9471 | 1534 | 350.6376 | Weighted Imp. | 609.7672
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.0455 | 855 | 0.22333 | 190.9471 | 2389 | 541.5846 | PTDF | 0.22632
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.2178 | 152.3 | 0.22333 | 34.0131 | 2541.3 | 575.5978
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.2924 | 153 | 0.22333 | 34.1695 | 2694.3 | 609.7672 | Concentration | 1.1171
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.8626 | 0 | 0.21971 | 0 | 2694.3 | 609.7672
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.0477 | 0 | 0.21971 | 0 | 2694.3 | 609.7672
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.0477 | 0 | 0.21971 | 0 | 2694.3 | 609.7672
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | 1 | 39.0906 | 0 | 0.21971 | 0 | 2694.3 | 609.7672
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.10051 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.1218 | 827 | 0.21735 | 179.7517
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.10051 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 82.3177 | 819 | 0.21735 | 178.0128
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.091303 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.1513 | 615 | 0.20815 | 128.0103
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.091303 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 53.5949 | 587 | 0.20815 | 122.1822
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.090515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6406 | 150.7 | 0.20736 | 31.249
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.090515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6678 | 151 | 0.20736 | 31.3112
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.090515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.0574 | 177.4 | 0.20736 | 36.7855
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.090367 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6906 | 151.5 | 0.20721 | 31.3925
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.090367 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7629 | 152.3 | 0.20721 | 31.5582
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.090367 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.0401 | 177.5 | 0.20721 | 36.7799
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.08701 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.8358 | 182 | 0.20385 | 37.1014
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.08701 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 42.1128 | 484 | 0.20385 | 98.6653
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.086965 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.3483 | 50 | 0.20381 | 10.1904
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.086931 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.20377 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | 1 | 12.8226 | 0 | 0.20348 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.2631 | 0 | 0.20348 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | 1 | 12.5627 | 0 | 0.20348 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | 1 | 34.569 | 0 | 0.20348 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.086307 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.751 | 785 | 0.20315 | 159.4735
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.086307 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 68.6141 | 795 | 0.20315 | 161.505
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.086307 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.3195 | 780 | 0.20315 | 158.4577
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.084137 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.8467 | 224 | 0.20098 | 45.0197
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5282 | 161 | 0.20087 | 32.3401
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7803 | 164 | 0.20087 | 32.9427
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7803 | 164 | 0.20087 | 32.9427
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7868 | 414 | 0.20087 | 83.1601
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6122 | 162 | 0.20087 | 32.5409
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5282 | 161 | 0.20087 | 32.3401
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6962 | 163 | 0.20087 | 32.7418
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.3666 | 409 | 0.20087 | 82.1558
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.083526 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 32.4081 | 388 | 0.20037 | 77.7435
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.083526 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 43.0159 | 515 | 0.20037 | 103.1905
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.08343 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.6686 | 20 | 0.20027 | 4.0055
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.08343 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0857 | 25 | 0.20027 | 5.0068
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.08343 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.4206 | 41 | 0.20027 | 8.2112
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.083373 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.20022 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.083373 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.20022 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.083333 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.3333 | 40 | 0.20018 | 8.0071
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.08333 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.5831 | 79 | 0.20017 | 15.8137
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.08333 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.833 | 106 | 0.20017 | 21.2184
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.08333 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.1662 | 146 | 0.20017 | 29.2254
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.08333 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.3331 | 76 | 0.20017 | 15.2132
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.083246 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 46.4513 | 558 | 0.20009 | 111.6502
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.083246 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 48.1994 | 579 | 0.20009 | 115.8521
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.083246 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.2628 | 808 | 0.20009 | 161.6726
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.083181 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.2386 | 0 | 0.20002 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.083181 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.6212 | 0 | 0.20002 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.083181 | north | 8 | N | N | Nnorth | Nnorth | 1 | 7.3532 | 0 | 0.20002 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.3014 | 160 | 0.19998 | 31.9965
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9689 | 156 | 0.19998 | 31.1966
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2943 | 196 | 0.19998 | 39.1957
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9689 | 156 | 0.19998 | 31.1966
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.052 | 157 | 0.19998 | 31.3965
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.4605 | 198 | 0.19998 | 39.5956
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.08307 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 30.7359 | 370 | 0.19991 | 73.9681
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.6298 | 0 | 0.19991 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.7129 | 0 | 0.19991 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 25.6686 | 0 | 0.19991 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.879 | 0 | 0.19991 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.9621 | 0 | 0.19991 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 25.7517 | 0 | 0.19991 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.082923 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.0969 | 170 | 0.19977 | 33.9604
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.082923 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 43.12 | 520 | 0.19977 | 103.8788
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.082805 | north | 5 | N | N | Nnorth | Nnorth | 1 | 3.3122 | 0 | 0.19965 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.082805 | north | 5 | N | N | Nnorth | Nnorth | 1 | 3.3122 | 0 | 0.19965 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.082646 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.7522 | 118 | 0.19949 | 23.5398
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.082646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.5043 | 115 | 0.19949 | 22.9413
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.082646 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 45.9512 | 556 | 0.19949 | 110.9164
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.082622 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.19947 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.082452 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1993 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.082007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.0734 | 196 | 0.19885 | 38.9748
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.082007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.1028 | 111 | 0.19885 | 22.0724
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.081247 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8748 | 60 | 0.19809 | 11.8855
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.081247 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.1186 | 63 | 0.19809 | 12.4797
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.080508 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 35.021 | 435 | 0.19735 | 85.8481
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.080451 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 9.0507 | 112.5 | 0.19729 | 22.1957
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.080346 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.7367 | 395 | 0.19719 | 77.89
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.080346 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 34.9505 | 435 | 0.19719 | 85.7776
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.080222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.36 | 216.4 | 0.19707 | 42.6451
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.080222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.336 | 216.1 | 0.19707 | 42.5859
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.080172 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.19702 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.080172 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.19702 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.080172 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.19702 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.7964 | 224 | 0.19629 | 43.9694
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.9552 | 226 | 0.19629 | 44.362
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.843 | 212 | 0.19629 | 41.6139
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7635 | 211 | 0.19629 | 41.4176
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.079397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8663 | 288 | 0.19624 | 56.5174
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.079397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6714 | 147 | 0.19624 | 28.8474
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.079397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6714 | 147 | 0.19624 | 28.8474
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.079088 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.19593 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.078959 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.1076 | 204 | 0.1958 | 39.9438
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.078959 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.8708 | 201 | 0.1958 | 39.3564
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.078959 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.1081 | 242 | 0.1958 | 47.3843
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.078918 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.1489 | 217.3 | 0.19576 | 42.5391
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.078918 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.1782 | 205 | 0.19576 | 40.1312
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.078918 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.4973 | 272.4 | 0.19576 | 53.3255
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.078727 | north | 3 | N | N | Nnorth | Nnorth | 1 | 91.0871 | 0 | 0.19557 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.078727 | north | 3 | N | N | Nnorth | Nnorth | 1 | 91.1659 | 0 | 0.19557 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.078514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.4133 | 18 | 0.19536 | 3.5164
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.078514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.4133 | 18 | 0.19536 | 3.5164
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.078514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.9835 | 38 | 0.19536 | 7.4236
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.4655 | 70 | 0.19492 | 13.6445
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3874 | 69 | 0.19492 | 13.4496
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3874 | 69 | 0.19492 | 13.4496
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3093 | 68 | 0.19492 | 13.2547
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.5579 | 20 | 0.19474 | 3.8948
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.5579 | 20 | 0.19474 | 3.8948
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.5579 | 20 | 0.19474 | 3.8948
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.3242 | 17 | 0.19474 | 3.3106
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.077859 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.93431 | 0 | 0.1947 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.077859 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.93431 | 0 | 0.1947 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.077814 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 28.4799 | 366 | 0.19466 | 71.2448
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.077761 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 9.3313 | 120 | 0.1946 | 23.3526
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.07759 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.0351 | 168 | 0.19443 | 32.6649
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.07759 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9831 | 90 | 0.19443 | 17.4991
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.077383 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.7267 | 242 | 0.19423 | 47.0029
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.077093 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.6278 | 73 | 0.19394 | 14.1574
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.077093 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.1741 | 119 | 0.19394 | 23.0785
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.077093 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.8041 | 205 | 0.19394 | 39.7571
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.077093 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8635 | 102 | 0.19394 | 19.7816
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.077093 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.4009 | 96 | 0.19394 | 18.6179
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.076788 | west | 4 | Y | N | Ywest | Nwest | 1 | 49.8892 | 649.7 | 0.19363 | 125.8026
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.076409 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6075 | 165 | 0.19325 | 31.8867
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.075966 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.928 | 236 | 0.19281 | 45.5031
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.075963 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.3852 | 400 | 0.19281 | 77.1228
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.075202 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5121 | 60 | 0.19205 | 11.5228
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.074733 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.484 | 60 | 0.19158 | 11.4946
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.074673 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.201 | 150 | 0.19152 | 28.7275
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.6027 | 209 | 0.1915 | 40.0231
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4437 | 126.5 | 0.1915 | 24.2245
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5888 | 249 | 0.1915 | 47.683
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7068 | 197 | 0.1915 | 37.7251
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7973 | 37.5 | 0.19144 | 7.179
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0191 | 107.5 | 0.19144 | 20.5798
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.0705 | 135 | 0.19144 | 25.8444
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8769 | 119 | 0.19144 | 22.7813
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8326 | 105 | 0.19144 | 20.1012
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.005 | 80.5 | 0.19144 | 15.4109
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.074391 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2989 | 125 | 0.19123 | 23.9044
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.074391 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2989 | 125 | 0.19123 | 23.9044
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.074309 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1463 | 150 | 0.19115 | 28.6729
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.074309 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5052 | 101 | 0.19115 | 19.3064
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.074261 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.2379 | 84 | 0.1911 | 16.0528
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.074167 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3425 | 99 | 0.19101 | 18.9101
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.074167 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5242 | 61 | 0.19101 | 11.6517
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.074167 | west | 7 | N | N | Nwest | Nwest | 1 | 1.8542 | 0 | 0.19101 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.074167 | west | 7 | N | N | Nwest | Nwest | 1 | 3.3894 | 0 | 0.19101 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.074167 | west | 7 | N | N | Nwest | Nwest | 1 | 3.3894 | 0 | 0.19101 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.074156 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.456 | 141 | 0.191 | 26.931
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.074156 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8987 | 120 | 0.191 | 22.92
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.074127 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.67 | 63 | 0.19097 | 12.0312
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8906 | 66 | 0.19094 | 12.6023
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 5.1129 | 69 | 0.19094 | 13.1751
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 5.1129 | 69 | 0.19094 | 13.1751
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.9647 | 67 | 0.19094 | 12.7932
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.9647 | 67 | 0.19094 | 12.7932
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8165 | 65 | 0.19094 | 12.4114
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1024 | 150 | 0.19086 | 28.629
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2835 | 220 | 0.19086 | 41.9892
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8032 | 200 | 0.19086 | 38.172
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0226 | 121.9 | 0.19086 | 23.2658
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.073901 | west | 8 | N | N | Nwest | Nwest | 1 | 5.1731 | 0 | 0.19074 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.073901 | west | 8 | N | N | Nwest | Nwest | 1 | 5.4243 | 0 | 0.19074 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.073901 | west | 8 | N | N | Nwest | Nwest | 1 | 5.2026 | 0 | 0.19074 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.073895 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3011 | 180 | 0.19074 | 34.333
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.073895 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3011 | 180 | 0.19074 | 34.333
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.073858 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.6181 | 225 | 0.1907 | 42.9079
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.073852 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8622 | 120 | 0.1907 | 22.8835
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.073852 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2075 | 233 | 0.1907 | 44.4321
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.073852 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5696 | 170.2 | 0.1907 | 32.4564
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.073791 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8549 | 120 | 0.19063 | 22.8762
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.073775 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.853 | 120 | 0.19062 | 22.8743
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.073556 | west | 8 | N | N | Nwest | Nwest | 1 | 1.8977 | 0 | 0.1904 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.073512 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7463 | 214.2 | 0.19036 | 40.7742
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.073429 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3796 | 100.5 | 0.19027 | 19.1224
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.073417 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2582 | 58 | 0.19026 | 11.0351
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.073417 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.0125 | 150 | 0.19026 | 28.5391
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.1378 | 70 | 0.19024 | 13.3169
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.1378 | 70 | 0.19024 | 13.3169
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.8112 | 92.8 | 0.19024 | 17.6544
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8718 | 80 | 0.19024 | 15.2193
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8718 | 80 | 0.19024 | 15.2193
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.4407 | 115 | 0.19024 | 21.8777
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.2798 | 208.2 | 0.19023 | 39.6067
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.4287 | 142.1 | 0.19023 | 27.0322
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.7168 | 132.4 | 0.19023 | 25.187
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.981 | 136 | 0.19023 | 25.8718
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.7883 | 147 | 0.19023 | 27.9644
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.4119 | 210 | 0.19023 | 39.9491
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2425 | 112.5 | 0.19011 | 21.3875
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.9534 | 149.5 | 0.19011 | 28.4216
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6277 | 186 | 0.19011 | 35.3606
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7158 | 214.5 | 0.19011 | 40.7788
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.073058 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.48218 | 6.6 | 0.1899 | 1.2534
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.073058 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5059 | 34.3 | 0.1899 | 6.5136
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.07284 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8532 | 149 | 0.18968 | 28.2629
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.0728 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3396 | 169.5 | 0.18964 | 32.1446
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.072719 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5452 | 35 | 0.18956 | 6.6347
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.072719 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1816 | 30 | 0.18956 | 5.6869
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.7971 | 66 | 0.18953 | 12.5088
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.7245 | 65 | 0.18953 | 12.3193
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8698 | 67 | 0.18953 | 12.6984
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8698 | 67 | 0.18953 | 12.6984
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8698 | 67 | 0.18953 | 12.6984
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.072684 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18953 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.072684 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18953 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.070088 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.33642 | 0 | 0.18693 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.069015 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5212 | 80 | 0.18586 | 14.8687
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.069015 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5212 | 80 | 0.18586 | 14.8687
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.068725 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1544 | 75 | 0.18557 | 13.9177
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.068725 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.498 | 80 | 0.18557 | 14.8455
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.068725 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.749 | 40 | 0.18557 | 7.4228
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.068662 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.493 | 80 | 0.18551 | 14.8405
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.068654 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4923 | 80 | 0.1855 | 14.8398
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.068617 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.2926 | 150 | 0.18546 | 27.8191
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.068617 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.2926 | 150 | 0.18546 | 27.8191
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.067387 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0108 | 0 | 0.18423 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.067387 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0108 | 0 | 0.18423 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.067168 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3734 | 80 | 0.18401 | 14.721
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.066926 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1198 | 76.5 | 0.18377 | 14.0584
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.066679 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.601 | 84 | 0.18352 | 15.4159
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.064811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.7217 | 150 | 0.18165 | 27.2482
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.064811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.1849 | 80 | 0.18165 | 14.5324
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.063685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2397 | 255 | 0.18053 | 46.0349
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.063685 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.4891 | 149 | 0.18053 | 26.8988
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.063685 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.7438 | 153 | 0.18053 | 27.6209
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.06239 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17923 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.06239 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 49.1009 | 787 | 0.17923 | 141.0571
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.061522 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17837 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.061522 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17837 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.058885 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17573 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.05343 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0145 | 150 | 0.17027 | 25.5411
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.01934 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.13618 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.11684 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.11684 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -1.7876 | 100 | 0.098968 | 9.8968
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.022732 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 12.9345 | 569 | -0.063025 | -35.861
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.022732 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 13.2073 | 581 | -0.063025 | -36.6173
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.010164 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18295 | 0 | -0.075593 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.010164 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18295 | 0 | -0.075593 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.010164 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15246 | 0 | -0.075593 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.009185 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.12583 | 0 | -0.076572 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.005042 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14118 | 0 | -0.080715 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.005042 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14622 | 0 | -0.080715 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.004787 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.0201 | 422 | -0.08097 | -34.1692
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.004092 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.073656 | 0 | -0.081665 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.004092 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.073656 | 0 | -0.081665 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.002516 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08806 | 0 | -0.083241 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.002516 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.085544 | 0 | -0.083241 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.002516 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08806 | 0 | -0.083241 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.089754 | 42 | -0.08362 | -3.512
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.094028 | 44 | -0.08362 | -3.6793
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.094028 | 44 | -0.08362 | -3.6793
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.10044 | 47 | -0.08362 | -3.9301
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.001514 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.049962 | 0 | -0.084243 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.001514 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03785 | 0 | -0.084243 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.001514 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.084243 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.001266 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010128 | 0 | -0.084491 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.001266 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010128 | 0 | -0.084491 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.001245 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.38595 | 310 | -0.084512 | -26.1986
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.001245 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.51419 | 413 | -0.084512 | -34.9033
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.085757 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.085757 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.001225 | 49 | -0.085782 | -4.2033
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00115 | 46 | -0.085782 | -3.946
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00115 | 46 | -0.085782 | -3.946
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.001175 | 47 | -0.085782 | -4.0317
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -2.5e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.00385 | 154 | -0.085782 | -13.2104
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -2.5e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0037 | 148 | -0.085782 | -12.6957
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0012 | 48 | -0.085782 | -4.1175
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0012 | 48 | -0.085782 | -4.1175
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.002613 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.34492 | 132 | -0.08837 | -11.6648
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.002613 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.35014 | 134 | -0.08837 | -11.8415
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.002613 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.844 | 323 | -0.08837 | -28.5434
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.004031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.61473 | 152.5 | -0.089788 | -13.6926
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.004031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60263 | 149.5 | -0.089788 | -13.4233
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.004031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.93761 | 232.6 | -0.089788 | -20.8846
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.004824 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76219 | 158 | -0.090581 | -14.3117
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.004824 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.77184 | 160 | -0.090581 | -14.4929
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.004824 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.8442 | 175 | -0.090581 | -15.8516
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.007046 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.042276 | 0 | -0.092803 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.009037 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.094794 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.47855 | 50 | -0.095328 | -4.7664
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.47855 | 50 | -0.095328 | -4.7664
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.47855 | 50 | -0.095328 | -4.7664
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.47855 | 50 | -0.095328 | -4.7664
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.012682 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076092 | 0 | -0.098439 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.013993 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.1719 | 584 | -0.09975 | -58.2538
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.013993 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.3258 | 595 | -0.09975 | -59.351
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.014122 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -6.1148 | 433 | -0.099879 | -43.2475
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6932 | 223.9 | -0.10225 | -22.8941
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7114 | 225 | -0.10225 | -23.0066
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7048 | 224.6 | -0.10225 | -22.9657
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7394 | 226.7 | -0.10225 | -23.1805
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0379 | 114 | -0.10363 | -11.8141
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.9685 | 222 | -0.10363 | -23.0064
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2892 | 184 | -0.10363 | -19.0684
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0042 | 224 | -0.10363 | -23.2137
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0557 | 115 | -0.10363 | -11.9178
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.018688 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.044851 | 0 | -0.10444 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.018688 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.044851 | 0 | -0.10444 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.018688 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.052326 | 0 | -0.10444 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019593 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.047023 | 0 | -0.10535 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019593 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.047023 | 0 | -0.10535 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8008 | 142 | -0.10548 | -14.9783
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.86 | 145 | -0.10548 | -15.2947
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9783 | 151 | -0.10548 | -15.9276
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.72 | 290 | -0.10548 | -30.5894
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.020068 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.080272 | 0 | -0.10582 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3482 | 147 | -0.10853 | -15.9544
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1432 | 138 | -0.10853 | -14.9776
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1888 | 140 | -0.10853 | -15.1947
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3482 | 147 | -0.10853 | -15.9544
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1454 | 182 | -0.10853 | -19.7531
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5098 | 198 | -0.10853 | -21.4897
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.02349 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.5604 | 407 | -0.10925 | -44.4634
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.023502 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.6828 | 412 | -0.10926 | -45.0146
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.023502 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.4008 | 400 | -0.10926 | -43.7035
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.023516 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3639 | 58 | -0.10927 | -6.3378
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.023516 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0929 | 89 | -0.10927 | -9.7253
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0347 | 44 | -0.10927 | -4.808
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0347 | 44 | -0.10927 | -4.808
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0112 | 43 | -0.10927 | -4.6987
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0582 | 45 | -0.10927 | -4.9173
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.023533 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.978 | 424 | -0.10929 | -46.3388
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.023533 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.0015 | 425 | -0.10929 | -46.4481
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.023592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.9307 | 209 | -0.10935 | -22.8539
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.023592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0959 | 216 | -0.10935 | -23.6193
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0852 | 46 | -0.10935 | -5.03
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1088 | 47 | -0.10935 | -5.1394
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0852 | 46 | -0.10935 | -5.03
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0852 | 46 | -0.10935 | -5.03
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.023635 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10939 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.023635 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10939 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.023635 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10939 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.024341 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7729 | 155 | -0.1101 | -17.0651
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.024341 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.138 | 170 | -0.1101 | -18.7166
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.024341 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7729 | 155 | -0.1101 | -17.0651
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.02462 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.59088 | 24 | -0.11038 | -2.649
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.02462 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.59088 | 24 | -0.11038 | -2.649
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.02462 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.56626 | 23 | -0.11038 | -2.5387
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.024973 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.6353 | 546 | -0.11073 | -60.4584
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.024973 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.7297 | 750 | -0.11073 | -83.0472
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.024987 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29984 | 0 | -0.11074 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.028992 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.8992 | 100 | -0.11475 | -11.4749
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.028992 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.8992 | 100 | -0.11475 | -11.4749
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.028992 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.028992 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.028992 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.028992 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.028995 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.029096 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -11.522 | 396 | -0.11485 | -45.4817
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.033085 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11884 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.034987 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12074 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.035806 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.42967 | 0 | -0.12156 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.035806 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39387 | 0 | -0.12156 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.035806 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.42967 | 0 | -0.12156 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.036963 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -23.2497 | 629 | -0.12272 | -77.1907
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.037301 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12306 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.038649 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6621 | 146.5 | -0.12441 | -18.2254
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.038649 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7162 | 147.9 | -0.12441 | -18.3996
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.038649 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6863 | 173 | -0.12441 | -21.5222
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.039117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.0972 | 207 | -0.12487 | -25.8488
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.039117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.4767 | 216.7 | -0.12487 | -27.0601
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.039117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4663 | 242 | -0.12487 | -30.2194
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.03912 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6333 | 144 | -0.12488 | -17.9822
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.03912 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6333 | 144 | -0.12488 | -17.9822
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.03912 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6895 | 171 | -0.12488 | -21.3539
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.039454 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12521 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.039454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4993 | 38 | -0.12521 | -4.758
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.039454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.76146 | 19.3 | -0.12521 | -2.4166
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.039454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.59181 | 15 | -0.12521 | -1.8782
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.039454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8543 | 47 | -0.12521 | -5.8849
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7206 | 94 | -0.12534 | -11.7817
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6228 | 41 | -0.12534 | -5.1388
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5041 | 38 | -0.12534 | -4.7628
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.75204 | 19 | -0.12534 | -2.3814
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7206 | 94 | -0.12534 | -11.7817
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4249 | 36 | -0.12534 | -4.5122
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.702 | 43 | -0.12534 | -5.3895
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.87078 | 22 | -0.12534 | -2.7574
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.858 | 148 | -0.12534 | -18.55
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.979 | 50 | -0.12534 | -6.2669
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.177 | 55 | -0.12534 | -6.8936
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.979 | 50 | -0.12534 | -6.2669
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.039775 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1535 | 0 | -0.12553 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.040185 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.527 | 0 | -0.12594 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.040226 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5286 | 0 | -0.12598 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.040292 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0073 | 0 | -0.12605 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.040292 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0073 | 0 | -0.12605 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.040358 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.4796 | 334 | -0.12611 | -42.1223
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.040358 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.7217 | 340 | -0.12611 | -42.879
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.040358 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2644 | 180 | -0.12611 | -22.7006
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.040358 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2644 | 180 | -0.12611 | -22.7006
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.04053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2954 | 180 | -0.12629 | -22.7316
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.040548 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.0133 | 0 | -0.1263 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.040548 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.0254 | 0 | -0.1263 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.040548 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.2038 | 0 | -0.1263 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.040559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6278 | 336 | -0.12632 | -42.4421
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.040559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.3006 | 180 | -0.12632 | -22.7368
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.040777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8719 | 144 | -0.12653 | -18.2208
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.040777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6661 | 188 | -0.12653 | -23.7883
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 25 | -0.12689 | -3.1722
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 25 | -0.12689 | -3.1722
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 25 | -0.12689 | -3.1722
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.65811 | 16 | -0.12689 | -2.0302
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 25 | -0.12689 | -3.1722
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 25 | -0.12689 | -3.1722
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 25 | -0.12689 | -3.1722
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.61698 | 15 | -0.12689 | -1.9033
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.5561 | 0 | -0.12725 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.3486 | 0 | -0.12725 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.1494 | 0 | -0.12725 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.0166 | 0 | -0.12725 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.0996 | 0 | -0.12725 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.2697 | 0 | -0.12725 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.041494 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.49793 | 0 | -0.12725 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.041708 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0447 | 0 | -0.12746 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9925 | 47.7 | -0.12753 | -6.0831
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.5581 | 37.3 | -0.12753 | -4.7568
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9215 | 46 | -0.12753 | -5.8663
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.0051 | 48 | -0.12753 | -6.1214
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.042263 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.92979 | 22 | -0.12802 | -2.8164
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.042263 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.46489 | 11 | -0.12802 | -1.4082
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.042263 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.46489 | 11 | -0.12802 | -1.4082
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.043341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.65011 | 0 | -0.1291 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.043341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.99684 | 0 | -0.1291 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.043945 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.35156 | 0 | -0.1297 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2388 | 0 | -0.13 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30971 | 0 | -0.13 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7255 | 0 | -0.13 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.66366 | 0 | -0.13 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30971 | 0 | -0.13 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.66366 | 0 | -0.13 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7255 | 0 | -0.13 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7255 | 0 | -0.13 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.046459 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.23 | 0 | -0.13222 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7237 | 0 | -0.13289 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.818 | 0 | -0.13289 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7237 | 0 | -0.13289 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7709 | 0 | -0.13289 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6955 | 0 | -0.13289 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1784 | 0 | -0.13289 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1683 | 0 | -0.13289 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3198 | 0 | -0.13289 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0551 | 0 | -0.13289 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4881 | 0 | -0.13289 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.9474 | 76 | -0.15085 | -11.4649
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.9474 | 76 | -0.15085 | -11.4649
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.8352 | 105 | -0.15085 | -15.8396
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8172 | 74 | -0.15085 | -11.1632
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8172 | 74 | -0.15085 | -11.1632
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6399 | 102 | -0.15085 | -15.3871
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.072199 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.7651 | 66 | -0.15796 | -10.4251
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.074209 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -98.9206 | 0 | -0.15997 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.074209 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -98.5496 | 0 | -0.15997 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4837 | 0 | -0.1742 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3151 | 0 | -0.1742 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9801 | 0 | -0.1742 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.9331 | 0 | -0.1742 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.6064 | 0 | -0.1742 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.7833 | 0 | -0.1742 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4223 | 0 | -0.1742 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.592 | 0 | -0.1742 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.314 | 0 | -0.1742 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1913 | 0 | -0.1742 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5722 | 0 | -0.1742 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3682 | 0 | -0.1742 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.7314 | 0 | -0.1742 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.9331 | 0 | -0.1742 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.5794 | 0 | -0.1742 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.11 | 0 | -0.1742 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.722 | 0 | -0.1742 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0758 | 0 | -0.1742 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0758 | 0 | -0.1742 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.1244 | 0 | -0.1742 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.089558 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3586 | 0 | -0.17531 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.089558 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89558 | 0 | -0.17531 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.9433 | 0 | -0.17534 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.9433 | 0 | -0.17534 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.6599 | 0 | -0.17534 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.8089 | 0 | -0.17534 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.096086 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -15.4698 | 161 | -0.18184 | -29.2767
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.096086 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -15.9503 | 166 | -0.18184 | -30.1859
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.096086 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -23.8293 | 248 | -0.18184 | -45.097
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.096086 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -52.463 | 546 | -0.18184 | -99.2861
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.096086 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -61.7833 | 0 | -0.18184 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.096086 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2491 | 13 | -0.18184 | -2.364
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.096676 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -62.9361 | 651 | -0.18243 | -118.7637
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.096676 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -54.5253 | 564 | -0.18243 | -102.892
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.096676 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -58.0056 | 600 | -0.18243 | -109.4596
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.096738 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.7683 | 0 | -0.18249 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.096738 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.7683 | 0 | -0.18249 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.096738 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.7008 | 0 | -0.18249 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.4223 | 104 | -0.18597 | -19.3409
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.4223 | 104 | -0.18597 | -19.3409
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.4116 | 54 | -0.18597 | -10.0424
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.3113 | 53 | -0.18597 | -9.8564
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.4116 | 54 | -0.18597 | -10.0424
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.7122 | 57 | -0.18597 | -10.6003
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.4116 | 54 | -0.18597 | -10.0424
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.4116 | 54 | -0.18597 | -10.0424
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.8124 | 58 | -0.18597 | -10.7863
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.8124 | 58 | -0.18597 | -10.7863
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.10294 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7456 | 0 | -0.1887 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.10417 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2501 | 12 | -0.18993 | -2.2792
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.10493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4627 | 0 | -0.19069 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.11002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.501 | 50 | -0.19578 | -9.7888
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3516 | 0 | -0.19893 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.5141 | 0 | -0.19893 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6232 | 0 | -0.19893 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.544 | 0 | -0.19893 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.11318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6217 | 0 | -0.19893 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.11318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3953 | 0 | -0.19893 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0157 | 0 | -0.19897 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5515 | 0 | -0.19897 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0004 | 0 | -0.19897 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.3447 | 0 | -0.19897 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.3787 | 0 | -0.19897 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.2428 | 0 | -0.19897 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.8687 | 0 | -0.19897 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.6247 | 0 | -0.19897 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5286 | 0 | -0.19897 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.2585 | 46 | -0.20007 | -9.2033
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.2585 | 46 | -0.20007 | -9.2033
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.2585 | 46 | -0.20007 | -9.2033
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.2873 | 55 | -0.20007 | -11.0039
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.2873 | 55 | -0.20007 | -11.0039
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.173 | 54 | -0.20007 | -10.8039
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5509 | 56 | -0.20274 | -11.3533
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.9019 | 59 | -0.20274 | -11.9615
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5509 | 56 | -0.20274 | -11.3533
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5509 | 56 | -0.20274 | -11.3533
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.9019 | 59 | -0.20274 | -11.9615
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5509 | 56 | -0.20274 | -11.3533
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.11997 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.20573 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.1751 | 0 | -0.20856 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.7575 | 0 | -0.20856 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6839 | 0 | -0.20856 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6928 | 0 | -0.20856 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4982 | 0 | -0.20856 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0768 | 0 | -0.21002 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.4555 | 0 | -0.21002 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0768 | 0 | -0.21002 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0768 | 0 | -0.21002 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.12664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.878 | 0 | -0.2124 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.12664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1313 | 0 | -0.2124 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.12776 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4714 | 0 | -0.21351 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.12875 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.545 | 12 | -0.21451 | -2.5741
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.12875 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.21451 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.1288 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.7667 | 169 | -0.21455 | -36.2596
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.12886 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.2619 | 165 | -0.21462 | -35.4117
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.12887 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.5256 | 0 | -0.21462 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.12893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -19.2107 | 0 | -0.21469 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.12893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.3934 | 0 | -0.21469 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.12907 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -27.4921 | 213 | -0.21483 | -45.7583
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.12909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0912 | 0 | -0.21485 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2625 | 0 | -0.21486 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1592 | 0 | -0.21486 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6638 | 0 | -0.21486 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5019 | 0 | -0.21486 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.12912 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.2425 | 0 | -0.21488 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.12912 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.4792 | 0 | -0.21488 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.12912 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.2726 | 0 | -0.21488 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.12913 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.4412 | 228 | -0.21488 | -48.9937
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.1297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.4383 | 0 | -0.21546 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.1297 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.5096 | 0 | -0.21546 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.2482 | 0 | -0.21601 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3785 | 0 | -0.21601 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.08 | 0 | -0.21601 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9077 | 0 | -0.21601 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.3433 | 0 | -0.21654 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.5455 | 0 | -0.21654 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.5979 | 0 | -0.21654 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.5325 | 0 | -0.21654 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -35.1798 | 0 | -0.21654 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5505 | 42 | -0.21791 | -9.1523
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5505 | 42 | -0.21791 | -9.1523
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.0219 | 38 | -0.21791 | -8.2806
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.0219 | 38 | -0.21791 | -8.2806
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.7394 | 0 | -0.22021 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8738 | 0 | -0.22021 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4116 | 0 | -0.22021 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.4705 | 0 | -0.22021 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.336 | 0 | -0.22021 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.983 | 0 | -0.22021 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.9327 | 0 | -0.22021 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.13519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.2253 | 0 | -0.22095 | 0
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6145 | 0 | -0.22148 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7095 | 0 | -0.22148 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4381 | 0 | -0.22148 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2296 | 0 | -0.22148 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4023 | 0 | -0.22148 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7687 | 0 | -0.22148 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7008 | 0 | -0.22148 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7502 | 0 | -0.22148 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.443 | 0 | -0.22148 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5906 | 0 | -0.22148 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -20.0867 | 0 | -0.22148 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.13596 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6798 | 0 | -0.22172 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.13596 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8551 | 0 | -0.22172 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.13651 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -100.3371 | 735 | -0.22227 | -163.3682
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.13754 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -1.6505 | 12 | -0.2233 | -2.6796
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.13866 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -55.1871 | 398 | -0.22442 | -89.3182
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.13928 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -103.4821 | 743 | -0.22503 | -167.1993
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.14191 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -24.4083 | 172 | -0.22767 | -39.1585
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.14191 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -24.4083 | 172 | -0.22767 | -39.1585
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.14191 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -24.4083 | 172 | -0.22767 | -39.1585
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.6485 | 0 | -0.23102 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.4451 | 0 | -0.23102 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.082 | 0 | -0.23102 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -39.1043 | 0 | -0.23102 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.9552 | 0 | -0.25313 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.1099 | 0 | -0.25313 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.7751 | 0 | -0.25313 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.7751 | 0 | -0.25313 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.1141 | 0 | -0.25313 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:46500 TOMBAL__ - 45971 KYUDAL74 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.9552 | 0 | -0.25313 | 0 | 0 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.1099 | 0 | -0.25313 | 0 | 0 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.7751 | 0 | -0.25313 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.16737 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.7751 | 0 | -0.25313 | 0 | 0 | 0 | Weighted Shift Factors
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.1141 | 0 | -0.25313 | 0 | 0 | 0 | North | 0.085757
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.6485 | 0 | -0.23102 | 0 | 0 | 0 | Houston | -0.11684
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.4451 | 0 | -0.23102 | 0 | 0 | 0 |  | 0.2026
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.082 | 0 | -0.23102 | 0 | 0 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.14526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -39.1043 | 0 | -0.23102 | 0 | 0 | 0 | Line Rating | 1759
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.14191 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -24.4083 | 172 | -0.22767 | -39.1585 | 172 | 39.1585 | Conc Gen | 3510
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.14191 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -24.4083 | 172 | -0.22767 | -39.1585 | 344 | 78.317 | Weighted Imp. | 775.8926
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.14191 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -24.4083 | 172 | -0.22767 | -39.1585 | 516 | 117.4755 | PTDF | 0.22105
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.13928 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -103.4821 | 743 | -0.22503 | -167.1993 | 1259 | 284.6747
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.13866 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -55.1871 | 398 | -0.22442 | -89.3182 | 1657 | 373.993 | Concentration | 1.0911
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.13754 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -1.6505 | 0 | -0.2233 | 0 | 1657 | 373.993
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.13651 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -100.3371 | 735 | -0.22227 | -163.3682 | 2392 | 537.3612
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.13596 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6798 | 0 | -0.22172 | 0 | 2392 | 537.3612
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.13596 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8551 | 0 | -0.22172 | 0 | 2392 | 537.3612
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6145 | 0 | -0.22148 | 0 | 2392 | 537.3612
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7095 | 0 | -0.22148 | 0 | 2392 | 537.3612
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4381 | 0 | -0.22148 | 0 | 2392 | 537.3612
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2296 | 0 | -0.22148 | 0 | 2392 | 537.3612
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4023 | 0 | -0.22148 | 0 | 2392 | 537.3612
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7687 | 0 | -0.22148 | 0 | 2392 | 537.3612
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7008 | 0 | -0.22148 | 0 | 2392 | 537.3612
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7502 | 0 | -0.22148 | 0 | 2392 | 537.3612
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.443 | 0 | -0.22148 | 0 | 2392 | 537.3612
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5906 | 0 | -0.22148 | 0 | 2392 | 537.3612
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.13572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -20.0867 | 0 | -0.22148 | 0 | 2392 | 537.3612
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.13519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.2253 | 0 | -0.22095 | 0 | 2392 | 537.3612
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.7394 | 0 | -0.22021 | 0 | 2392 | 537.3612
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8738 | 0 | -0.22021 | 0 | 2392 | 537.3612
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4116 | 0 | -0.22021 | 0 | 2392 | 537.3612
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.4705 | 0 | -0.22021 | 0 | 2392 | 537.3612
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.336 | 0 | -0.22021 | 0 | 2392 | 537.3612
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.983 | 0 | -0.22021 | 0 | 2392 | 537.3612
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.13445 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.9327 | 0 | -0.22021 | 0 | 2392 | 537.3612
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5505 | 42 | -0.21791 | -9.1523 | 2434 | 546.5135
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5505 | 42 | -0.21791 | -9.1523 | 2476 | 555.6657
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.0219 | 38 | -0.21791 | -8.2806 | 2514 | 563.9464
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.13215 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.0219 | 38 | -0.21791 | -8.2806 | 2552 | 572.227
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.3433 | 0 | -0.21654 | 0 | 2552 | 572.227
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.5455 | 0 | -0.21654 | 0 | 2552 | 572.227
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.5979 | 0 | -0.21654 | 0 | 2552 | 572.227
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.5325 | 0 | -0.21654 | 0 | 2552 | 572.227
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.13078 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -35.1798 | 0 | -0.21654 | 0 | 2552 | 572.227
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.2482 | 0 | -0.21601 | 0 | 2552 | 572.227
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3785 | 0 | -0.21601 | 0 | 2552 | 572.227
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.08 | 0 | -0.21601 | 0 | 2552 | 572.227
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.13026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9077 | 0 | -0.21601 | 0 | 2552 | 572.227
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.1297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.4383 | 0 | -0.21546 | 0 | 2552 | 572.227
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.1297 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.5096 | 0 | -0.21546 | 0 | 2552 | 572.227
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.12913 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.4412 | 228 | -0.21488 | -48.9937 | 2780 | 621.2207
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.12912 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.2425 | 0 | -0.21488 | 0 | 2780 | 621.2207
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.12912 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.4792 | 0 | -0.21488 | 0 | 2780 | 621.2207
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.12912 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.2726 | 0 | -0.21488 | 0 | 2780 | 621.2207
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2625 | 0 | -0.21486 | 0 | 2780 | 621.2207
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1592 | 0 | -0.21486 | 0 | 2780 | 621.2207
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6638 | 0 | -0.21486 | 0 | 2780 | 621.2207
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.1291 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5019 | 0 | -0.21486 | 0 | 2780 | 621.2207
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.12909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0912 | 0 | -0.21485 | 0 | 2780 | 621.2207
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.12907 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -27.4921 | 213 | -0.21483 | -45.7583 | 2993 | 666.979
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.12893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -19.2107 | 0 | -0.21469 | 0 | 2993 | 666.979
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.12893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.3934 | 0 | -0.21469 | 0 | 2993 | 666.979
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.12887 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.5256 | 0 | -0.21462 | 0 | 2993 | 666.979
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.12886 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.2619 | 165 | -0.21462 | -35.4117 | 3158 | 702.3908
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.1288 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.7667 | 169 | -0.21455 | -36.2596 | 3327 | 738.6503
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.12875 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.545 | 12 | -0.21451 | -2.5741 | 3339 | 741.2245
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.12875 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.21451 | 0 | 3339 | 741.2245
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.12776 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4714 | 0 | -0.21351 | 0 | 3339 | 741.2245
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.12664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.878 | 0 | -0.2124 | 0 | 3339 | 741.2245
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.12664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1313 | 0 | -0.2124 | 0 | 3339 | 741.2245
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0768 | 0 | -0.21002 | 0 | 3339 | 741.2245
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.4555 | 0 | -0.21002 | 0 | 3339 | 741.2245
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0768 | 0 | -0.21002 | 0 | 3339 | 741.2245
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.12426 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0768 | 0 | -0.21002 | 0 | 3339 | 741.2245
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.1751 | 0 | -0.20856 | 0 | 3339 | 741.2245
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.7575 | 0 | -0.20856 | 0 | 3339 | 741.2245
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6839 | 0 | -0.20856 | 0 | 3339 | 741.2245
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6928 | 0 | -0.20856 | 0 | 3339 | 741.2245
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.1228 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4982 | 0 | -0.20856 | 0 | 3339 | 741.2245
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.11997 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.20573 | 0 | 3339 | 741.2245
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5509 | 56 | -0.20274 | -11.3533 | 3395 | 752.5778
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.9019 | 59 | -0.20274 | -11.9615 | 3454 | 764.5393
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5509 | 56 | -0.20274 | -11.3533 | 3510 | 775.8926
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5509 | 56 | -0.20274 | -11.3533
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.9019 | 59 | -0.20274 | -11.9615
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.11698 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.5509 | 56 | -0.20274 | -11.3533
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.2585 | 46 | -0.20007 | -9.2033
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.2585 | 46 | -0.20007 | -9.2033
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.2585 | 46 | -0.20007 | -9.2033
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.2873 | 55 | -0.20007 | -11.0039
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.2873 | 55 | -0.20007 | -11.0039
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.11431 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.173 | 54 | -0.20007 | -10.8039
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0157 | 0 | -0.19897 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5515 | 0 | -0.19897 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0004 | 0 | -0.19897 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.3447 | 0 | -0.19897 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.3787 | 0 | -0.19897 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.2428 | 0 | -0.19897 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.8687 | 0 | -0.19897 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.11322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.6247 | 0 | -0.19897 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.11322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5286 | 0 | -0.19897 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.11318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6217 | 0 | -0.19893 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.11318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3953 | 0 | -0.19893 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3516 | 0 | -0.19893 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.5141 | 0 | -0.19893 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6232 | 0 | -0.19893 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.11318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.544 | 0 | -0.19893 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.11002 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.501 | 50 | -0.19578 | -9.7888
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.10493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4627 | 0 | -0.19069 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.10417 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2501 | 12 | -0.18993 | -2.2792
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.10294 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7456 | 0 | -0.1887 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.4223 | 104 | -0.18597 | -19.3409
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.4223 | 104 | -0.18597 | -19.3409
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.4116 | 54 | -0.18597 | -10.0424
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.3113 | 53 | -0.18597 | -9.8564
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.4116 | 54 | -0.18597 | -10.0424
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.7122 | 57 | -0.18597 | -10.6003
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.4116 | 54 | -0.18597 | -10.0424
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.4116 | 54 | -0.18597 | -10.0424
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.8124 | 58 | -0.18597 | -10.7863
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.10021 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.8124 | 58 | -0.18597 | -10.7863
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.096738 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.7683 | 0 | -0.18249 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.096738 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.7683 | 0 | -0.18249 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.096738 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.7008 | 0 | -0.18249 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.096676 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -62.9361 | 0 | -0.18243 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.096676 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -54.5253 | 0 | -0.18243 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.096676 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -58.0056 | 0 | -0.18243 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.096086 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -15.4698 | 161 | -0.18184 | -29.2767
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.096086 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -15.9503 | 166 | -0.18184 | -30.1859
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.096086 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -23.8293 | 248 | -0.18184 | -45.097
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.096086 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -52.463 | 546 | -0.18184 | -99.2861
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.096086 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -61.7833 | 0 | -0.18184 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.096086 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2491 | 13 | -0.18184 | -2.364
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.9433 | 0 | -0.17534 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.9433 | 0 | -0.17534 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.6599 | 0 | -0.17534 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.089579 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.8089 | 0 | -0.17534 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.089558 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3586 | 0 | -0.17531 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.089558 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89558 | 0 | -0.17531 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4837 | 0 | -0.1742 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3151 | 0 | -0.1742 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9801 | 0 | -0.1742 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.9331 | 0 | -0.1742 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.6064 | 0 | -0.1742 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.7833 | 0 | -0.1742 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4223 | 0 | -0.1742 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.592 | 0 | -0.1742 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.314 | 0 | -0.1742 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1913 | 0 | -0.1742 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5722 | 0 | -0.1742 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3682 | 0 | -0.1742 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.7314 | 0 | -0.1742 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.9331 | 0 | -0.1742 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.5794 | 0 | -0.1742 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.11 | 0 | -0.1742 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.722 | 0 | -0.1742 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0758 | 0 | -0.1742 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0758 | 0 | -0.1742 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.088447 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.1244 | 0 | -0.1742 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.074209 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -98.9206 | 0 | -0.15997 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.074209 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -98.5496 | 0 | -0.15997 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.072199 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -4.7651 | 66 | -0.15796 | -10.4251
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.9474 | 76 | -0.15085 | -11.4649
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.9474 | 76 | -0.15085 | -11.4649
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.8352 | 105 | -0.15085 | -15.8396
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8172 | 74 | -0.15085 | -11.1632
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.8172 | 74 | -0.15085 | -11.1632
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.065097 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6399 | 102 | -0.15085 | -15.3871
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7237 | 0 | -0.13289 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.818 | 0 | -0.13289 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7237 | 0 | -0.13289 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7709 | 0 | -0.13289 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6955 | 0 | -0.13289 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1784 | 0 | -0.13289 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1683 | 0 | -0.13289 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3198 | 0 | -0.13289 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0551 | 0 | -0.13289 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.047136 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4881 | 0 | -0.13289 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.046459 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.23 | 0 | -0.13222 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2388 | 0 | -0.13 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30971 | 0 | -0.13 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7255 | 0 | -0.13 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.66366 | 0 | -0.13 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30971 | 0 | -0.13 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.66366 | 0 | -0.13 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7255 | 0 | -0.13 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.044244 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7255 | 0 | -0.13 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.043945 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.35156 | 0 | -0.1297 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.043341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.65011 | 0 | -0.1291 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.043341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.99684 | 0 | -0.1291 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.042263 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.92979 | 22 | -0.12802 | -2.8164
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.042263 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.46489 | 11 | -0.12802 | -1.4082
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.042263 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.46489 | 11 | -0.12802 | -1.4082
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9925 | 47.7 | -0.12753 | -6.0831
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.5581 | 37.3 | -0.12753 | -4.7568
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9215 | 46 | -0.12753 | -5.8663
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.041772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.0051 | 48 | -0.12753 | -6.1214
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.041708 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0447 | 0 | -0.12746 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.5561 | 0 | -0.12725 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.3486 | 0 | -0.12725 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.1494 | 0 | -0.12725 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.0166 | 0 | -0.12725 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.0996 | 0 | -0.12725 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.041494 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.2697 | 0 | -0.12725 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.041494 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.49793 | 0 | -0.12725 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 0 | -0.12689 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 0 | -0.12689 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 0 | -0.12689 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.65811 | 0 | -0.12689 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 0 | -0.12689 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 0 | -0.12689 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0283 | 0 | -0.12689 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.041132 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.61698 | 0 | -0.12689 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.040777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8719 | 144 | -0.12653 | -18.2208
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.040777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6661 | 188 | -0.12653 | -23.7883
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.040559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6278 | 336 | -0.12632 | -42.4421
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.040559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.3006 | 180 | -0.12632 | -22.7368
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.040548 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.0133 | 0 | -0.1263 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.040548 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.0254 | 0 | -0.1263 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.040548 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.2038 | 0 | -0.1263 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.04053 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2954 | 180 | -0.12629 | -22.7316
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.040358 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.4796 | 334 | -0.12611 | -42.1223
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.040358 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.7217 | 340 | -0.12611 | -42.879
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.040358 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2644 | 180 | -0.12611 | -22.7006
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.040358 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2644 | 180 | -0.12611 | -22.7006
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.040292 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0073 | 0 | -0.12605 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.040292 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0073 | 0 | -0.12605 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.040226 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5286 | 0 | -0.12598 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.040185 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.527 | 0 | -0.12594 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.039775 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1535 | 0 | -0.12553 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7206 | 0 | -0.12534 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6228 | 0 | -0.12534 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5041 | 0 | -0.12534 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.75204 | 0 | -0.12534 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7206 | 0 | -0.12534 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4249 | 0 | -0.12534 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.702 | 0 | -0.12534 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.87078 | 0 | -0.12534 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.858 | 0 | -0.12534 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.979 | 0 | -0.12534 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.177 | 0 | -0.12534 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.039581 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.979 | 0 | -0.12534 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.039454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4993 | 38 | -0.12521 | -4.758
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.039454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.76146 | 19.3 | -0.12521 | -2.4166
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.039454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.59181 | 15 | -0.12521 | -1.8782
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.039454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8543 | 47 | -0.12521 | -5.8849
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.039454 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12521 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.03912 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6333 | 144 | -0.12488 | -17.9822
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.03912 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6333 | 144 | -0.12488 | -17.9822
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.03912 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6895 | 171 | -0.12488 | -21.3539
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.039117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.0972 | 207 | -0.12487 | -25.8488
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.039117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.4767 | 216.7 | -0.12487 | -27.0601
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.039117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4663 | 242 | -0.12487 | -30.2194
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.038649 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6621 | 146.5 | -0.12441 | -18.2254
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.038649 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7162 | 147.9 | -0.12441 | -18.3996
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.038649 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6863 | 173 | -0.12441 | -21.5222
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.037301 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12306 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.036963 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -23.2497 | 0 | -0.12272 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.035806 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.42967 | 0 | -0.12156 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.035806 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39387 | 0 | -0.12156 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.035806 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.42967 | 0 | -0.12156 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.034987 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12074 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.033085 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11884 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.029096 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -11.522 | 0 | -0.11485 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.028995 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.028992 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.8992 | 100 | -0.11475 | -11.4749
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.028992 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.8992 | 100 | -0.11475 | -11.4749
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.028992 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.028992 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.028992 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.028992 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11475 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.024987 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29984 | 0 | -0.11074 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.024973 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.6353 | 0 | -0.11073 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.024973 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.7297 | 0 | -0.11073 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.02462 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.59088 | 24 | -0.11038 | -2.649
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.02462 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.59088 | 24 | -0.11038 | -2.649
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.02462 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.56626 | 23 | -0.11038 | -2.5387
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.024341 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7729 | 155 | -0.1101 | -17.0651
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.024341 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.138 | 170 | -0.1101 | -18.7166
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.024341 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7729 | 155 | -0.1101 | -17.0651
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.023643 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1986 | 8.4 | -0.1094 | -0.91896
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.023635 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10939 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.023635 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10939 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.023635 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10939 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.023592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.9307 | 209 | -0.10935 | -22.8539
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.023592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0959 | 216 | -0.10935 | -23.6193
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0852 | 46 | -0.10935 | -5.03
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1088 | 47 | -0.10935 | -5.1394
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0852 | 46 | -0.10935 | -5.03
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.023592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0852 | 46 | -0.10935 | -5.03
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.023533 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.978 | 0 | -0.10929 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.023533 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.0015 | 0 | -0.10929 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.023516 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3639 | 58 | -0.10927 | -6.3378
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.023516 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0929 | 89 | -0.10927 | -9.7253
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0347 | 44 | -0.10927 | -4.808
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0347 | 44 | -0.10927 | -4.808
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0112 | 43 | -0.10927 | -4.6987
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.023516 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0582 | 45 | -0.10927 | -4.9173
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.023502 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.6828 | 412 | -0.10926 | -45.0146
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.023502 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.4008 | 400 | -0.10926 | -43.7035
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.02349 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.5604 | 407 | -0.10925 | -44.4634
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3482 | 147 | -0.10853 | -15.9544
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1432 | 138 | -0.10853 | -14.9776
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1888 | 140 | -0.10853 | -15.1947
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3482 | 147 | -0.10853 | -15.9544
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1454 | 182 | -0.10853 | -19.7531
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.022777 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5098 | 198 | -0.10853 | -21.4897
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.020068 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.080272 | 0 | -0.10582 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8008 | 142 | -0.10548 | -14.9783
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.86 | 145 | -0.10548 | -15.2947
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9783 | 151 | -0.10548 | -15.9276
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019724 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.72 | 290 | -0.10548 | -30.5894
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019593 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.047023 | 0 | -0.10535 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019593 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.047023 | 0 | -0.10535 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.018688 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.044851 | 0 | -0.10444 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.018688 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.044851 | 0 | -0.10444 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.018688 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.052326 | 0 | -0.10444 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0379 | 0 | -0.10363 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.9685 | 0 | -0.10363 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2892 | 0 | -0.10363 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0042 | 0 | -0.10363 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0557 | 0 | -0.10363 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6932 | 223.9 | -0.10225 | -22.8941
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7114 | 225 | -0.10225 | -23.0066
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7048 | 224.6 | -0.10225 | -22.9657
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.016495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7394 | 226.7 | -0.10225 | -23.1805
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.014122 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -6.1148 | 0 | -0.099879 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.013993 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.1719 | 0 | -0.09975 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.013993 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.3258 | 0 | -0.09975 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.012682 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076092 | 0 | -0.098439 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.47855 | 50 | -0.095328 | -4.7664
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.47855 | 50 | -0.095328 | -4.7664
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.47855 | 50 | -0.095328 | -4.7664
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.009571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.47855 | 50 | -0.095328 | -4.7664
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.009037 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.094794 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.007046 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.042276 | 0 | -0.092803 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.004824 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76219 | 158 | -0.090581 | -14.3117
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.004824 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.77184 | 160 | -0.090581 | -14.4929
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.004824 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.8442 | 175 | -0.090581 | -15.8516
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.004031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.61473 | 152.5 | -0.089788 | -13.6926
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.004031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60263 | 149.5 | -0.089788 | -13.4233
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.004031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.93761 | 232.6 | -0.089788 | -20.8846
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.002613 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.34492 | 132 | -0.08837 | -11.6648
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.002613 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.35014 | 134 | -0.08837 | -11.8415
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.002613 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.844 | 323 | -0.08837 | -28.5434
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.001225 | 49 | -0.085782 | -4.2033
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00115 | 46 | -0.085782 | -3.946
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00115 | 46 | -0.085782 | -3.946
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.001175 | 47 | -0.085782 | -4.0317
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -2.5e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.00385 | 154 | -0.085782 | -13.2104
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -2.5e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0037 | 148 | -0.085782 | -12.6957
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0012 | 48 | -0.085782 | -4.1175
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -2.5e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0012 | 48 | -0.085782 | -4.1175
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.085757 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.085757 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.085757 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.001245 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.38595 | 310 | -0.084512 | -26.1986
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.001245 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.51419 | 413 | -0.084512 | -34.9033
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.001266 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010128 | 0 | -0.084491 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.001266 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010128 | 0 | -0.084491 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.001514 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.049962 | 0 | -0.084243 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.001514 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03785 | 0 | -0.084243 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.001514 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.084243 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.089754 | 42 | -0.08362 | -3.512
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.094028 | 44 | -0.08362 | -3.6793
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.094028 | 44 | -0.08362 | -3.6793
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.002137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.10044 | 47 | -0.08362 | -3.9301
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.002516 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08806 | 0 | -0.083241 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.002516 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.085544 | 0 | -0.083241 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.002516 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08806 | 0 | -0.083241 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.004092 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.073656 | 0 | -0.081665 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.004092 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.073656 | 0 | -0.081665 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.004787 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.0201 | 422 | -0.08097 | -34.1692
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.005042 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14118 | 0 | -0.080715 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.005042 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14622 | 0 | -0.080715 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.009185 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.12583 | 0 | -0.076572 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.010164 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18295 | 0 | -0.075593 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.010164 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18295 | 0 | -0.075593 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.010164 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15246 | 0 | -0.075593 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.022732 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 12.9345 | 0 | -0.063025 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.022732 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 13.2073 | 0 | -0.063025 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.017876 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -1.7876 | 0 | 0.098968 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.11684 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.11684 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.01934 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.13618 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.05343 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0145 | 0 | 0.17027 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.058885 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17573 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.061522 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17837 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.061522 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17837 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.06239 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17923 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.06239 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 49.1009 | 787 | 0.17923 | 141.0571
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.063685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2397 | 255 | 0.18053 | 46.0349
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.063685 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.4891 | 149 | 0.18053 | 26.8988
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.063685 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.7438 | 153 | 0.18053 | 27.6209
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.064811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.7217 | 150 | 0.18165 | 27.2482
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.064811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.1849 | 80 | 0.18165 | 14.5324
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.066679 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.601 | 0 | 0.18352 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.066926 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1198 | 0 | 0.18377 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.067168 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3734 | 0 | 0.18401 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.067387 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0108 | 0 | 0.18423 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.067387 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0108 | 0 | 0.18423 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.068617 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.2926 | 0 | 0.18546 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.068617 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.2926 | 0 | 0.18546 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.068654 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4923 | 0 | 0.1855 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.068662 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.493 | 0 | 0.18551 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.068725 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1544 | 0 | 0.18557 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.068725 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.498 | 0 | 0.18557 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.068725 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.749 | 0 | 0.18557 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.069015 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5212 | 0 | 0.18586 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.069015 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5212 | 0 | 0.18586 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.070088 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.33642 | 0 | 0.18693 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.7971 | 66 | 0.18953 | 12.5088
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.7245 | 65 | 0.18953 | 12.3193
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8698 | 67 | 0.18953 | 12.6984
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8698 | 67 | 0.18953 | 12.6984
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.072684 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8698 | 67 | 0.18953 | 12.6984
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.072684 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18953 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.072684 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18953 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.072719 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5452 | 0 | 0.18956 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.072719 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1816 | 0 | 0.18956 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.0728 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3396 | 0 | 0.18964 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.07284 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8532 | 0 | 0.18968 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.073058 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.48218 | 0 | 0.1899 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.073058 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5059 | 0 | 0.1899 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2425 | 0 | 0.19011 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.9534 | 0 | 0.19011 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6277 | 0 | 0.19011 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.073267 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7158 | 0 | 0.19011 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.2798 | 208.2 | 0.19023 | 39.6067
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.4287 | 142.1 | 0.19023 | 27.0322
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.7168 | 132.4 | 0.19023 | 25.187
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.981 | 136 | 0.19023 | 25.8718
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.7883 | 147 | 0.19023 | 27.9644
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.07339 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.4119 | 210 | 0.19023 | 39.9491
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.1378 | 70 | 0.19024 | 13.3169
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.1378 | 70 | 0.19024 | 13.3169
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.8112 | 92.8 | 0.19024 | 17.6544
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8718 | 80 | 0.19024 | 15.2193
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8718 | 80 | 0.19024 | 15.2193
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.073397 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.4407 | 115 | 0.19024 | 21.8777
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.073417 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.0125 | 0 | 0.19026 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.073417 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2582 | 0 | 0.19026 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.073429 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3796 | 0 | 0.19027 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.073512 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7463 | 0 | 0.19036 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.073556 | west | 8 | N | N | Nwest | Nwest | 1 | 1.8977 | 0 | 0.1904 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.073775 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.853 | 0 | 0.19062 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.073791 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8549 | 0 | 0.19063 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.073852 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8622 | 0 | 0.1907 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.073852 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2075 | 0 | 0.1907 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.073852 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5696 | 0 | 0.1907 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.073858 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.6181 | 0 | 0.1907 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.073895 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3011 | 0 | 0.19074 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.073895 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3011 | 0 | 0.19074 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.073901 | west | 8 | N | N | Nwest | Nwest | 1 | 5.1731 | 0 | 0.19074 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.073901 | west | 8 | N | N | Nwest | Nwest | 1 | 5.4243 | 0 | 0.19074 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.073901 | west | 8 | N | N | Nwest | Nwest | 1 | 5.2026 | 0 | 0.19074 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1024 | 0 | 0.19086 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2835 | 0 | 0.19086 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8032 | 0 | 0.19086 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.074016 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0226 | 0 | 0.19086 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8906 | 66 | 0.19094 | 12.6023
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 5.1129 | 69 | 0.19094 | 13.1751
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 5.1129 | 69 | 0.19094 | 13.1751
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.9647 | 67 | 0.19094 | 12.7932
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.9647 | 67 | 0.19094 | 12.7932
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.0741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.8165 | 65 | 0.19094 | 12.4114
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.074127 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.67 | 0 | 0.19097 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.074156 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.456 | 0 | 0.191 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.074156 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8987 | 0 | 0.191 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.074167 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3425 | 0 | 0.19101 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.074167 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5242 | 0 | 0.19101 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.074167 | west | 7 | N | N | Nwest | Nwest | 1 | 1.8542 | 0 | 0.19101 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.074167 | west | 7 | N | N | Nwest | Nwest | 1 | 3.3894 | 0 | 0.19101 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.074167 | west | 7 | N | N | Nwest | Nwest | 1 | 3.3894 | 0 | 0.19101 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.074261 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.2379 | 0 | 0.1911 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.074309 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1463 | 0 | 0.19115 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.074309 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5052 | 0 | 0.19115 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.074391 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2989 | 0 | 0.19123 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.074391 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2989 | 0 | 0.19123 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7973 | 0 | 0.19144 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0191 | 0 | 0.19144 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.0705 | 0 | 0.19144 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8769 | 0 | 0.19144 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8326 | 0 | 0.19144 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.074596 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.005 | 0 | 0.19144 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.6027 | 0 | 0.1915 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4437 | 0 | 0.1915 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5888 | 0 | 0.1915 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.074654 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7068 | 0 | 0.1915 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.074673 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.201 | 0 | 0.19152 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.074733 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.484 | 0 | 0.19158 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.075202 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5121 | 0 | 0.19205 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.075963 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.3852 | 0 | 0.19281 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.075966 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.928 | 0 | 0.19281 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.076409 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6075 | 0 | 0.19325 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.076788 | west | 4 | Y | N | Ywest | Nwest | 1 | 49.8892 | 0 | 0.19363 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.077093 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.6278 | 73 | 0.19394 | 14.1574
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.077093 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.1741 | 119 | 0.19394 | 23.0785
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.077093 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.8041 | 205 | 0.19394 | 39.7571
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.077093 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8635 | 102 | 0.19394 | 19.7816
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.077093 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.4009 | 96 | 0.19394 | 18.6179
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.077383 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.7267 | 242 | 0.19423 | 47.0029
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.07759 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.0351 | 168 | 0.19443 | 32.6649
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.07759 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9831 | 90 | 0.19443 | 17.4991
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.077761 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 9.3313 | 0 | 0.1946 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.077814 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 28.4799 | 366 | 0.19466 | 71.2448
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.077859 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.93431 | 0 | 0.1947 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.077859 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.93431 | 0 | 0.1947 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.5579 | 20 | 0.19474 | 3.8948
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.5579 | 20 | 0.19474 | 3.8948
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.5579 | 20 | 0.19474 | 3.8948
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.077896 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.3242 | 17 | 0.19474 | 3.3106
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.4655 | 70 | 0.19492 | 13.6445
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3874 | 69 | 0.19492 | 13.4496
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3874 | 69 | 0.19492 | 13.4496
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.078078 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3093 | 68 | 0.19492 | 13.2547
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.078514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.4133 | 18 | 0.19536 | 3.5164
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.078514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.4133 | 18 | 0.19536 | 3.5164
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.078514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.9835 | 38 | 0.19536 | 7.4236
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.078727 | north | 3 | N | N | Nnorth | Nnorth | 1 | 91.0871 | 0 | 0.19557 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.078727 | north | 3 | N | N | Nnorth | Nnorth | 1 | 91.1659 | 0 | 0.19557 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.078918 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.1489 | 217.3 | 0.19576 | 42.5391
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.078918 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.1782 | 205 | 0.19576 | 40.1312
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.078918 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.4973 | 272.4 | 0.19576 | 53.3255
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.078959 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.1076 | 204 | 0.1958 | 39.9438
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.078959 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.8708 | 201 | 0.1958 | 39.3564
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.078959 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.1081 | 242 | 0.1958 | 47.3843
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.079088 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.19593 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.079397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8663 | 288 | 0.19624 | 56.5174
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.079397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6714 | 147 | 0.19624 | 28.8474
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.079397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6714 | 147 | 0.19624 | 28.8474
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.7964 | 224 | 0.19629 | 43.9694
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.9552 | 226 | 0.19629 | 44.362
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.843 | 212 | 0.19629 | 41.6139
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.079448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7635 | 211 | 0.19629 | 41.4176
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.080172 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.19702 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.080172 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.19702 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.080172 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.19702 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.080222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.36 | 216.4 | 0.19707 | 42.6451
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.080222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.336 | 216.1 | 0.19707 | 42.5859
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.080346 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.7367 | 395 | 0.19719 | 77.89
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.080346 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 34.9505 | 435 | 0.19719 | 85.7776
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.080451 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 9.0507 | 0 | 0.19729 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.080508 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 35.021 | 435 | 0.19735 | 85.8481
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.081247 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8748 | 60 | 0.19809 | 11.8855
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.081247 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.1186 | 63 | 0.19809 | 12.4797
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.082007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.0734 | 196 | 0.19885 | 38.9748
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.082007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.1028 | 111 | 0.19885 | 22.0724
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.082452 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1993 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.082622 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.19947 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.082646 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.7522 | 118 | 0.19949 | 23.5398
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.082646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.5043 | 115 | 0.19949 | 22.9413
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.082646 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 45.9512 | 556 | 0.19949 | 110.9164
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.082805 | north | 5 | N | N | Nnorth | Nnorth | 1 | 3.3122 | 0 | 0.19965 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.082805 | north | 5 | N | N | Nnorth | Nnorth | 1 | 3.3122 | 0 | 0.19965 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.082923 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.0969 | 170 | 0.19977 | 33.9604
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.082923 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 43.12 | 520 | 0.19977 | 103.8788
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.08307 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 30.7359 | 370 | 0.19991 | 73.9681
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.6298 | 0 | 0.19991 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.7129 | 0 | 0.19991 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 25.6686 | 0 | 0.19991 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.879 | 0 | 0.19991 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.9621 | 0 | 0.19991 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.08307 | north | 1 | N | N | Nnorth | Nnorth | 1 | 25.7517 | 0 | 0.19991 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.3014 | 160 | 0.19998 | 31.9965
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9689 | 156 | 0.19998 | 31.1966
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2943 | 196 | 0.19998 | 39.1957
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9689 | 156 | 0.19998 | 31.1966
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.052 | 157 | 0.19998 | 31.3965
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.083134 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.4605 | 198 | 0.19998 | 39.5956
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.083181 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.2386 | 0 | 0.20002 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.083181 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.6212 | 0 | 0.20002 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.083181 | north | 8 | N | N | Nnorth | Nnorth | 1 | 7.3532 | 0 | 0.20002 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.083246 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 46.4513 | 0 | 0.20009 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.083246 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 48.1994 | 0 | 0.20009 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.083246 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.2628 | 0 | 0.20009 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.08333 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.5831 | 79 | 0.20017 | 15.8137
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.08333 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.833 | 106 | 0.20017 | 21.2184
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.08333 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.1662 | 146 | 0.20017 | 29.2254
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.08333 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.3331 | 76 | 0.20017 | 15.2132
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.083333 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.3333 | 40 | 0.20018 | 8.0071
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.083373 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.20022 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.083373 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.20022 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.08343 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.6686 | 20 | 0.20027 | 4.0055
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.08343 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0857 | 25 | 0.20027 | 5.0068
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.08343 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.4206 | 41 | 0.20027 | 8.2112
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.083526 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 32.4081 | 388 | 0.20037 | 77.7435
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.083526 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 43.0159 | 515 | 0.20037 | 103.1905
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5282 | 161 | 0.20087 | 32.3401
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7803 | 164 | 0.20087 | 32.9427
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7803 | 164 | 0.20087 | 32.9427
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7868 | 414 | 0.20087 | 83.1601
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6122 | 162 | 0.20087 | 32.5409
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5282 | 161 | 0.20087 | 32.3401
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6962 | 163 | 0.20087 | 32.7418
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.084026 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.3666 | 409 | 0.20087 | 82.1558
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.084137 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.8467 | 224 | 0.20098 | 45.0197
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.086307 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.751 | 0 | 0.20315 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.086307 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 68.6141 | 0 | 0.20315 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.086307 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.3195 | 0 | 0.20315 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | 1 | 12.8226 | 0 | 0.20348 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.2631 | 0 | 0.20348 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | 1 | 12.5627 | 0 | 0.20348 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.086639 | north | 1 | N | N | Nnorth | Nnorth | 1 | 34.569 | 0 | 0.20348 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.086931 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.20377 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.086965 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.3483 | 0 | 0.20381 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.08701 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.8358 | 182 | 0.20385 | 37.1014
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.08701 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 42.1128 | 484 | 0.20385 | 98.6653
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.090367 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6906 | 151.5 | 0.20721 | 31.3925
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.090367 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7629 | 152.3 | 0.20721 | 31.5582
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.090367 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.0401 | 177.5 | 0.20721 | 36.7799
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.090515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6406 | 150.7 | 0.20736 | 31.249
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.090515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6678 | 151 | 0.20736 | 31.3112
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.090515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.0574 | 177.4 | 0.20736 | 36.7855
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.091303 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.1513 | 0 | 0.20815 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.091303 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 53.5949 | 0 | 0.20815 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.10051 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.1218 | 0 | 0.21735 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.10051 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 82.3177 | 0 | 0.21735 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.8626 | 0 | 0.21971 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.0477 | 0 | 0.21971 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.0477 | 0 | 0.21971 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.10287 | north | 1 | N | N | Nnorth | Nnorth | 1 | 39.0906 | 0 | 0.21971 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.0455 | 0 | 0.22333 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.0455 | 0 | 0.22333 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.2178 | 0 | 0.22333 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.10649 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.2924 | 0 | 0.22333 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.11084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3202 | 48 | 0.22768 | 10.9287
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.11084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.0985 | 46 | 0.22768 | 10.4733
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.11084 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.6379 | 105 | 0.22768 | 23.9065
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2302 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2302 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.11336 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9271 | 17 | 0.2302 | 3.9135
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2302 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.11336 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2302 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.1136 | north | 7 | N | N | Nnorth | Nnorth | 1 | 3.6353 | 0 | 0.23045 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.12175 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.3698 | 0 | 0.23859 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown