## test results
CRE test for: |  | 3391 Jewett 44645 SNGLTN_3_ctg2 | [5 empty] | PASS
Line Rating: |  | 1290.45
Direction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3391 Jewett 44645 SNGLTN_3_ctg2
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.14958
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.044882
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.12541
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.16788
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3391 Jewett 44645 SNGLTN_3_ctg2
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.13878
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.047178
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.12572
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.17018
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3391 Jewett 44645 SNGLTN_3_ctg2
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.19676
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.023864
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.31976
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.1706
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.123
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.29559
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.31976 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.31976 | 0.19676
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.36522
[6 empty] | Concentration |  | 1.1422 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.32939
[6 empty] | Concentration |  | 1.0301 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 67.5674
| Percent of line rating => | [6 empty] | 5.236% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.0757
[7 empty] | B1(N-S) | 0.0167 | 0.22835 | 0.21165 | 0.0167
[7 empty] | B2 (N-W) | 0.00046239 | 0.026133 | 0.02567 | 0.00046239
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.015776 | -0.19929 | -0.18351 | -0.015776
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.013769 | 0.11854 | 0.13231 | -0.013769
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.00048941 | 0.31747 | 0.31796 | -0.00048941
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 4.855%
Deployment Error Percent | [6 empty] | B2 | 0.1344%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -4.587%
[7 empty] | B5 | -4.003%
[7 empty] | B6 | -0.1423%
[7 empty] | Max Abs Error | 4.855% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-H
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3391 Jewett 44645 SNGLTN_3_ctg2 C:967 GIBN_CRE - 44645 SNGLTN_3 75 C:967 GIBN_CRE - 44645 SNGLTN_3 99 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3391 Jewett 44645 SNGLTN_3_ctg2 C:967 GIBN_CRE - 44645 SNGLTN_3 75 C:967 GIBN_CRE - 44645 SNGLTN_3 99
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.09863 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 25.1506
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.09863 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 14.6959
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.10822 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.6233
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.10822 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.6233
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.09863 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 15.0904
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.10215 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 15.3222
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.10215 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 8.1718
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13149 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 9.5988
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13149 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 15.6473
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13149 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 26.9554
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13149 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 13.412
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13149 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 12.623
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.13342 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.6011
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.13342 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.6011
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.13203 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 22.1815
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.13203 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 11.883
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.13457 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.4223
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.13457 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.4223
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.13457 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 5.1138
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13654 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 39.3238
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13654 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 20.0715
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13654 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 20.0715
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.1389 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 15.6258
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 5.8115
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 11.4782
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 15.4012
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 21.2129
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14529 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 11.0423
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14058 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 8.4345
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14058 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 8.8562
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14555 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.9111
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14555 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.6388
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14555 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 5.9676
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.19262 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 89.1844
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 8.1917
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 8.0676
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.3158
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.3158
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.3158
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12412 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 14.1493
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12412 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 63.9203
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 8.3609
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.7409
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.7409
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.4876
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.4876
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 8.2342
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12632 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 8.8427
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12632 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 9.2722
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12632 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 8.8932
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 18.9798
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 27.837
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.1268 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 12.5531
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.1268 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 7.7347
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 17.8758
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.1268 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 3.17
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.1268 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.7947
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.1268 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.7947
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 15.2135
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.12568 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 3.2426
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 12.609
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.12609 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 15.1304
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.12544 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 7.2756
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.12562 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 26.9067
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12701 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 19.0523
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12476 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.8234
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12476 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 4.2792
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12701 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 12.8285
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.12612 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 15.1338
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.1336 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 48.8965
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.13267 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 32.1066
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.13014 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 52.0544
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.13014 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 30.7133
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.13097 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 21.6101
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13577 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 27.6973
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13577 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 27.29
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13577 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 32.8566
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.6751
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.6751
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.6751
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 2.2738
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.13322 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 15.9859
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.12666 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 7.5995
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.145 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 10.8751
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.145 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 11.5421
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.145 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 12.8181
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 23.1798
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.6003
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 28.3953
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.6003
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 22.7452
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 28.6851
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14438 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 24.5453
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14438 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 75.0797
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14472 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 53.5449
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14514 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 80.9892
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14514 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 84.0372
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14514 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 117.2747
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13809 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 15.4666
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13809 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 13.8095
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13809 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 52.1999
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.13528 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 29.397
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.13528 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 27.733
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.13528 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 36.8511
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.13562 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 104.4297
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 9.3365
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 9.2032
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 9.2032
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 9.0698
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.13491 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 156.0909
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.13491 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 156.2258
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 30.4297
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 30.7014
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.13749 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 29.7537
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.13749 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 29.7125
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 28.7996
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 28.6637
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.13825 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 54.6076
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.13862 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 60.298
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.13825 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 60.1374
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.14325 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 19.7688
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14346 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 16.9283
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14346 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 16.4979
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14346 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 79.7638
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14567 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 56.5215
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14567 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 75.0221
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.15289 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 120.0171
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.15289 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 121.546
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.15289 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 119.2526
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.15601 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 28.3931
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.15601 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 75.5069
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.14989 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 33.5747
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.15473 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 7.7367
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.15469 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 6.497
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.16249 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 99.9338
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.16249 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 95.384
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.094263 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 50.6192
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.094263 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 74.185
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.094431 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 7.0823
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.094431 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 20.9637
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.026412 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 15.0284
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.04985 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -10.4186
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.04985 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -10.7676
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.049632 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -20.2002
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -2.2931
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -2.343
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -2.2931
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -2.2931
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.049722 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -21.0821
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.049722 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -21.1319
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.049642 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -2.8792
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.049642 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -4.4181
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -2.1842
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -2.1842
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -2.1346
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -2.2339
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.049696 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -20.4748
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.049696 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -19.8784
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.051978 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -28.38
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.051978 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -38.9835
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.049918 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -3.045
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.049918 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -4.7422
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.049918 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -7.5376
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.05099 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -7.9035
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.05099 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -8.6683
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.05099 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -7.9035
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.079768 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.7549
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.079768 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.87745
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.079768 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.87745
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -3.7713
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -2.949
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -3.6369
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -3.795
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.068268 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.81922
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.068268 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.75095
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.050446 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.2107
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.050446 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.2107
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.050446 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -1.1603
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.058198 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -23.0464
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.12539 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -167.1422
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.12539 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -166.5153
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.07409 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -2.8154
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.07409 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -1.4299
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.07409 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -1.1114
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.07409 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -3.4822
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11695 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 8.7712
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 19.1569
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.12423 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 21.057
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.089005 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 13.3507
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 7.9837
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.13168 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 85.5551
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14411 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.7644
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14411 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.7644
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.003465 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -1.4622
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.021073 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -2.7816
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.021073 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -2.8238
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.021073 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -6.8066
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.023174 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -3.6615
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.023174 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -3.7078
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.023174 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -4.0555
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.04108 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -23.9907
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.04108 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -24.4426
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.041221 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -17.8487
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -8.8196
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -8.863
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -8.8472
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -8.9299
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.011394 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.091152
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.011394 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.091152
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.005824 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.10483
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.005824 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.10483
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.005824 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.08736
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.004259 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.058348
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.005063 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.091134
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.005063 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.091134
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.30397
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.29529
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.30397
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.003109 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.087052
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.003109 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.090161
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12418 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 4.3463
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12418 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.7254
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.8895
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.8895
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.8895
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.8895
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.033402 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.20041
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.043263 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.10383
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.043263 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.10383
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.043263 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.12114
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.044693 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.17877
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.045917 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.1102
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.045917 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.1102
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -7.1617
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -6.7232
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -6.8207
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -7.1617
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -8.8669
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -9.6464
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.020618 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -3.1442
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.020618 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -3.0824
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.020618 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -4.7957
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -6.2744
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -6.407
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -6.6721
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -12.8139
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.00367 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.12111
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.00367 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.09175
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.068268 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.81922
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.079114 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -5.7753
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -6.9088
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -7.0837
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -2.3208
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.5802
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -6.9088
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -6.9962
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -6.8563
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -2.1863
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -4.0228
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.071055 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -44.6936
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.077717 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -11.1912
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.077717 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -14.6108
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.054635 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.65562
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.018914 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.11348
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.075872 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -25.493
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.075554 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -25.235
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.075554 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -25.6884
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.075318 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -2.8621
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.075477 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.8869
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.075477 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.8869
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.075362 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -2.8638
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.074622 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -2.164
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.075855 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -11.2493
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.075855 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -11.2721
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.075855 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -11.6058
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -12.2199
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -11.8332
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -7.7341
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -11.2144
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -11.3691
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -9.8223
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.072808 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -10.6664
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.072808 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -10.7683
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.072808 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -12.5958
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.073555 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -15.2259
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.073555 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -15.9394
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.073555 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -17.8003
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.07356 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -10.5926
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.07356 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -10.5926
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.07356 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -12.5788
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.011591 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -3.5932
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.011591 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -4.7871
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.43189
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.45245
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.45245
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.4833
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.67047
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.62942
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.62942
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.6431
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013683 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -2.1072
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013683 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -2.0251
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.65678
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.65678
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.7787
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.7787
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 11.638
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 10.0328
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 10.0328
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 14.4222
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 26.1077
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 17.8189
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 16.6026
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 17.054
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 18.4334
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 26.3334
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 26.692
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 16.1557
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 31.8005
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 25.1595
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 25.3064
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 15.4243
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.1244 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 18.5355
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12631 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.7351
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12631 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.7351
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.12624 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 28.4038
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12722 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.9026
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12722 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.9026
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 20.2602
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 20.405
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 44.7172
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 20.6944
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 20.8391
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 44.862
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14277 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 27.9833
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14277 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 15.8477
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.14361 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 23.6523
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 24.0931
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 24.0931
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 60.8203
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 23.7993
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 23.6523
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 23.9462
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 60.0858
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14525 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14525 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 22.7248
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 19.961
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 22.2642
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 61.2649
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.16086 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 24.2416
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.16086 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 24.2899
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.16086 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 28.5366
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.16059 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 24.3292
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.16059 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 24.4577
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.16059 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 28.5045
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.026412 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 15.3454
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 167.5578
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 167.5578
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.18548 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 5.9354
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.1826 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 8.7649
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.1826 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 8.3997
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 2.2244
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 9.4535
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.18536 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 3.1512
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 4.078
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 4.6341
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.1826 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 19.1732
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.12697 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 10.6653
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.11682 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 9.3456
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.11675 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 17.513
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.11675 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 17.513
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -11.7619
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -11.0808
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -8.8048
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -25.451
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -25.5008
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -25.3014
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -15.9484
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -40.5355
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -6.6452
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -16.6601
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -15.431
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -17.0588
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -16.9425
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.1661 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -5.3153
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.1661 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -4.9831
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -16.6351
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -16.6351
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -17.8341
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -16.4103
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 29.8468
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 29.984
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.176 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -23.9365
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.16071 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -5.3035
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -7.3942
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -7.3942
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.69
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.69
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.14723 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -10.4531
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.14723 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -1.4723
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.15979 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -26.0451
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.15979 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -26.0451
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.15979 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -39.1476
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -11.2003
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -10.3387
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -11.2003
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -11.2003
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.17472 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -26.0327
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.17472 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -11.374
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -15.6146
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -15.0312
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -14.9282
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -9.3516
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -2.0934
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.17906 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -133.0431
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.17784 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -130.7131
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.17943 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -30.8618
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.17943 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -30.8618
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.17943 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -30.8618
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -32.2143
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.17625 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -30.4906
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.17625 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -23.7932
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -29.3517
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -29.0993
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -28.6486
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -48.5349
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -11.1869
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -11.0471
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -14.4381
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -12.865
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -28.4002
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -27.3387
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -27.4083
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -27.3213
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -46.8116
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.179 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.895
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.179 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -3.759
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -36.0631
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -36.484
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -36.484
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -88.8714
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.1806 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -71.8792
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -7.9768
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -7.9768
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -7.9768
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.5375
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.5375
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -9.3641
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.1826 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 151.011
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.1826 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 149.5502
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.1593 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -7.3439
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -9.5832
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -9.5832
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -13.24
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -9.331
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -9.331
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -12.8617
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.17482 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -31.4676
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.17482 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -27.7265
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.17482 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -27.4467
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.17433 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -6.1016
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.16974 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -77.9111
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -11.6357
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -11.8147
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -12.5308
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -11.2777
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -11.0987
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -18.6171
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -10.5616
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -29.0488
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -28.6763
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -28.6763
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18621 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -30.166
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.17929 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -28.1487
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -12.4445
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -12.6197
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -6.8357
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -5.2582
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.17366 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -13.5452
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.17366 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -13.8926
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.17479 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -2.8316
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.1747 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -28.8248
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.17467 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -29.5194
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.17478 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -37.2286
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.17481 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -39.8562
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.17465 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -2.0958
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.17465 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -3.1438
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.16819 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -8.4094
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -18.4515
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -18.4515
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -9.5806
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -9.4032
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -9.5806
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -10.1128
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -9.5806
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -9.5806
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -10.2902
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -10.2902
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.17854 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -2.1424
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -10.1433
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -10.6867
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -10.1433
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -10.1433
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -10.6867
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -10.1433
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.1302 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -8.5934
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16123 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -25.9585
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16123 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -26.7647
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16123 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -39.9858
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16123 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -88.0332
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16123 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -103.6728
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.15971 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -103.9693
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.15971 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -90.0747
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.15971 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -95.8242
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16123 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -2.096
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.17903 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -2.1484
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -6.0567
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -6.1814
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -5.8251
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -8.1766
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -3.1531
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -3.634
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -3.545
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -6.2349
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -3.2065
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -15.2131
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -26.3646
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -8.9226
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -10.2754
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -6.4761
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -14.5352
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -12.3765
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -12.6643
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -7.1956
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -2.5904
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -13.5278
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -10.0739
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -9.0665
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -10.3617
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -9.3256
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -14.5352
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -13.9596
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -14.823
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -10.9374
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -11.513
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -11.513
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -24.6091
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.40936
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.11369 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 8.6974
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11695 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 9.3559
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11695 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 4.678
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11747 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 9.3979
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.11683 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 9.3468
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.11413 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 9.1306
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.11325 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 9.5127
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11747 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 9.3979
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -4.6627
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12617 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 15.1408
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12617 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 29.3983
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12617 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 21.4746
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -9.08
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -7.5258
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -9.1618
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -4.7036
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -4.0901
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.12869 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.7212
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.025271 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.099146 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.11942 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.57321
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.7846
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 13.7159
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 17.2247
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 15.1832
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 13.397
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 10.271
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.12539 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 18.8085
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 14.0748
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 18.7038
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 23.2703
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 26.8359
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.07409 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.02246 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.057465 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -2.4487
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -3.813
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -6.4715
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.9834
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -3.046
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -2.8231
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -1.4115
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.9834
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -2.6745
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -3.1946
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.6344
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -3.2326
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.2433
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.5802
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.2433
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -3.2326
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -3.2326
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -10.9952
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.7146
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -4.0861
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.7146
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.077341 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.92809
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.081495 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.2224
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.081495 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.8744
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.086393 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -4.1469
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.082337 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.6587
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.075828 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -13.649
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.075872 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -13.657
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.075554 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -13.5997
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.075554 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -13.5997
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.057461 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -5.7461
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.057461 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -5.7461
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.9188
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.9188
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.9188
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -1.228
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.9188
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.9188
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.9188
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -1.1513
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.057461 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.057461 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -28.7305
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.057461 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -28.7305
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.057461 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.067676 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.00367 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.063925 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.070743 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:3391 Jewett 44645 SNGLTN_3_ctg2 C:967 GIBN_CRE - 44645 SNGLTN_3 75 C:967 GIBN_CRE - 44645 SNGLTN_3 99 | [7 empty] | 67.5674
Number of Bus | Name of Bus | ID | Max MW | L:3391 Jewett 44645 SNGLTN_3_ctg2 C:967 GIBN_CRE - 44645 SNGLTN_3 75 C:967 GIBN_CRE - 44645 SNGLTN_3 99 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.09863 | north | Y | -0.050955 | 0.14351 | -0.026784 | 0.26651 | 0.026784 | west | Y | 0.050955 | 6.1634
239 | BOSQUESW | 1 | 149 | 0.09863 | north | Y | -0.050955 | 0.14351 | -0.026784 | 0.26651 | 0.026784 | west | Y | 0.050955 | 3.6014
244 | WHITNYDM | 1 | 15 | 0.10822 | north | N | -0.041366 | 0.1531 | -0.017195 | 0.2761 | 0.017195 | west | Y | 0.041366 | 0
245 | WHITNYDM | 2 | 15 | 0.10822 | north | N | -0.041366 | 0.1531 | -0.017195 | 0.2761 | 0.017195 | west | Y | 0.041366 | 0
247 | BOSQUESW | 2 | 153 | 0.09863 | north | Y | -0.050955 | 0.14351 | -0.026784 | 0.26651 | 0.026784 | west | Y | 0.050955 | 3.6981
251 | BOSQUESW | 2 | 150 | 0.10215 | north | Y | -0.047437 | 0.14703 | -0.023266 | 0.27003 | 0.023266 | west | Y | 0.047437 | 3.6256
253 | BOSQUESW | 2 | 80 | 0.10215 | north | Y | -0.047437 | 0.14703 | -0.023266 | 0.27003 | 0.023266 | west | Y | 0.047437 | 1.9336
332 | RWMILLER | 1 | 73 | 0.13149 | north | Y | -0.018095 | 0.17637 | 0.0060757 | 0.29937 | 0.0060757 | west | Y | 0.018095 | 0.87738
333 | RWMILLER | 2 | 119 | 0.13149 | north | Y | -0.018095 | 0.17637 | 0.0060757 | 0.29937 | 0.0060757 | west | Y | 0.018095 | 1.4303
334 | RWMILLER | 3 | 205 | 0.13149 | north | Y | -0.018095 | 0.17637 | 0.0060757 | 0.29937 | 0.0060757 | west | Y | 0.018095 | 2.4639
335 | RWMILLER | 4 | 102 | 0.13149 | north | Y | -0.018095 | 0.17637 | 0.0060757 | 0.29937 | 0.0060757 | west | Y | 0.018095 | 1.2259
336 | RWMILLER | 5 | 96 | 0.13149 | north | Y | -0.018095 | 0.17637 | 0.0060757 | 0.29937 | 0.0060757 | west | Y | 0.018095 | 1.1538
344 | MRSSHPRD | 1 | 12 | 0.13342 | north | N | -0.016164 | 0.1783 | 0.0080067 | 0.3013 | 0.0080067 | west | Y | 0.016164 | 0
345 | MRSSHPRD | 2 | 12 | 0.13342 | north | N | -0.016164 | 0.1783 | 0.0080067 | 0.3013 | 0.0080067 | west | Y | 0.016164 | 0
366 | JNSNCNTY | 1 | 168 | 0.13203 | north | Y | -0.017552 | 0.17692 | 0.0066187 | 0.29991 | 0.0066187 | west | Y | 0.017552 | 1.8367
367 | JNSNCNTY | 2 | 90 | 0.13203 | north | Y | -0.017552 | 0.17692 | 0.0066187 | 0.29991 | 0.0066187 | west | Y | 0.017552 | 0.98397
503 | NTHTEXAS | 1 | 18 | 0.13457 | north | Y | -0.015011 | 0.17946 | 0.0091597 | 0.30245 | 0.0091597 | west | Y | 0.015011 | 0.10532
504 | NTHTEXAS | 2 | 18 | 0.13457 | north | Y | -0.015011 | 0.17946 | 0.0091597 | 0.30245 | 0.0091597 | west | Y | 0.015011 | 0.10532
505 | NTHTEXAS | 3 | 38 | 0.13457 | north | Y | -0.015011 | 0.17946 | 0.0091597 | 0.30245 | 0.0091597 | west | Y | 0.015011 | 0.22234
580 | JCKCNTY8 | 1 | 288 | 0.13654 | north | Y | -0.013044 | 0.18142 | 0.011127 | 0.30442 | 0.011127 | west | Y | 0.013044 | 0.55208
581 | JCKCNTY8 | 2 | 147 | 0.13654 | north | Y | -0.013044 | 0.18142 | 0.011127 | 0.30442 | 0.011127 | west | Y | 0.013044 | 0.28179
582 | JCKCNTY8 | 3 | 147 | 0.13654 | north | Y | -0.013044 | 0.18142 | 0.011127 | 0.30442 | 0.011127 | west | Y | 0.013044 | 0.28179
728 | WOLFRIDG | 1 | 112.5 | 0.1389 | north | Y | -0.010689 | 0.18378 | 0.013482 | 0.30678 | 0.010689 | North | N | 0.010689 | 0
837 | NEWMAN_G | 1 | 40 | 0.14529 | north | Y | -0.0042967 | 0.19017 | 0.019874 | 0.31317 | 0.0042967 | North | N | 0.0042967 | 0
842 | OLINGER_ | 1 | 79 | 0.14529 | north | Y | -0.0042907 | 0.19018 | 0.01988 | 0.31317 | 0.0042907 | North | N | 0.0042907 | 0
843 | OLINGER_ | 1 | 106 | 0.14529 | north | Y | -0.0042907 | 0.19018 | 0.01988 | 0.31317 | 0.0042907 | North | N | 0.0042907 | 0
844 | OLINGER_ | 1 | 146 | 0.14529 | north | Y | -0.0042907 | 0.19018 | 0.01988 | 0.31317 | 0.0042907 | North | N | 0.0042907 | 0
845 | OLINGER_ | 1 | 76 | 0.14529 | north | Y | -0.0042907 | 0.19018 | 0.01988 | 0.31317 | 0.0042907 | North | N | 0.0042907 | 0
923 | SPENCER_ | 1 | 60 | 0.14058 | north | Y | -0.0090097 | 0.18546 | 0.015161 | 0.30845 | 0.0090097 | North | N | 0.0090097 | 0
924 | SPENCER_ | 1 | 63 | 0.14058 | north | Y | -0.0090097 | 0.18546 | 0.015161 | 0.30845 | 0.0090097 | North | N | 0.0090097 | 0
948 | STEAM1 | 1 | 20 | 0.14555 | north | Y | -0.0040317 | 0.19044 | 0.020139 | 0.31343 | 0.0040317 | North | N | 0.0040317 | 0
949 | STEAM2 | 1 | 25 | 0.14555 | north | Y | -0.0040327 | 0.19043 | 0.020138 | 0.31343 | 0.0040327 | North | N | 0.0040327 | 0
950 | STEAM3 | 1 | 41 | 0.14555 | north | Y | -0.0040327 | 0.19043 | 0.020138 | 0.31343 | 0.0040327 | North | N | 0.0040327 | 0
990 | GIBN_CRE | 1 | 463 | 0.19262 | north | Y | 0.043038 | 0.23751 | 0.067209 | 0.3605 | 0.043038 | North | N | 0.043038 | 0
1002 | PBCTAGE_ | A | 66 | 0.12412 | west | Y | -0.025468 | 0.169 | -0.0012973 | 0.292 | 0.0012973 | west | N | 0.0012973 | 0
1003 | PBCTBGE_ | B | 65 | 0.12412 | west | Y | -0.025468 | 0.169 | -0.0012973 | 0.292 | 0.0012973 | west | N | 0.0012973 | 0
1004 | PBCTCGE_ | C | 67 | 0.12412 | west | Y | -0.025468 | 0.169 | -0.0012973 | 0.292 | 0.0012973 | west | N | 0.0012973 | 0
1005 | PBCTDGE_ | D | 67 | 0.12412 | west | Y | -0.025468 | 0.169 | -0.0012973 | 0.292 | 0.0012973 | west | N | 0.0012973 | 0
1006 | PBCTEGE_ | E | 67 | 0.12412 | west | Y | -0.025468 | 0.169 | -0.0012973 | 0.292 | 0.0012973 | west | N | 0.0012973 | 0
1007 | PB5GEN_6 | MB | 114 | 0.12412 | west | Y | -0.025468 | 0.169 | -0.0012973 | 0.292 | 0.0012973 | west | N | 0.0012973 | 0
1008 | PB6GEN_7 | MB | 515 | 0.12412 | west | Y | -0.025468 | 0.169 | -0.0012973 | 0.292 | 0.0012973 | west | N | 0.0012973 | 0
1039 | MRGNAG_1 | A | 66 | 0.12668 | west | Y | -0.022905 | 0.17156 | 0.0012657 | 0.29456 | 0.0012657 | west | N | 0.0012657 | 0
1040 | MRGNBG_2 | B | 69 | 0.12668 | west | Y | -0.022905 | 0.17156 | 0.0012657 | 0.29456 | 0.0012657 | west | N | 0.0012657 | 0
1041 | MRGNCG_3 | C | 69 | 0.12668 | west | Y | -0.022905 | 0.17156 | 0.0012657 | 0.29456 | 0.0012657 | west | N | 0.0012657 | 0
1042 | MRGNDG_4 | D | 67 | 0.12668 | west | Y | -0.022905 | 0.17156 | 0.0012657 | 0.29456 | 0.0012657 | west | N | 0.0012657 | 0
1043 | MRGNEG_5 | E | 67 | 0.12668 | west | Y | -0.022905 | 0.17156 | 0.0012657 | 0.29456 | 0.0012657 | west | N | 0.0012657 | 0
1044 | MRGNFG_6 | F | 65 | 0.12668 | west | Y | -0.022905 | 0.17156 | 0.0012657 | 0.29456 | 0.0012657 | west | N | 0.0012657 | 0
1045 | CALENG1G | 1 | 70 | 0.12632 | west | N | -0.023261 | 0.17121 | 0.00090969 | 0.2942 | 0.00090969 | west | N | 0.00090969 | 0
1046 | CALENG2G | 2 | 73.4 | 0.12632 | west | N | -0.023261 | 0.17121 | 0.00090969 | 0.2942 | 0.00090969 | west | N | 0.00090969 | 0
1047 | CALENG3G | 3 | 70.4 | 0.12632 | west | N | -0.023261 | 0.17121 | 0.00090969 | 0.2942 | 0.00090969 | west | N | 0.00090969 | 0
1058 | LONGSHOR | 1 | 150 | 0.12653 | west | Y | -0.023053 | 0.17141 | 0.0011177 | 0.29441 | 0.0011177 | west | N | 0.0011177 | 0
1058 | LONGSHOR | 2 | 220 | 0.12653 | west | Y | -0.023053 | 0.17141 | 0.0011177 | 0.29441 | 0.0011177 | west | N | 0.0011177 | 0
1061 | CIELOGEN | 1 | 99 | 0.1268 | west | Y | -0.022786 | 0.17168 | 0.0013847 | 0.29468 | 0.0013847 | west | N | 0.0013847 | 0
1062 | CIELOGEN | 1 | 61 | 0.1268 | west | Y | -0.022786 | 0.17168 | 0.0013847 | 0.29468 | 0.0013847 | west | N | 0.0013847 | 0
1068 | SCURRYCW | 1 | 141 | 0.12678 | west | Y | -0.022806 | 0.17166 | 0.0013647 | 0.29466 | 0.0013647 | west | N | 0.0013647 | 0
1069 | KINDERMG | 1 | 25 | 0.1268 | west | N | -0.022786 | 0.17168 | 0.0013847 | 0.29468 | 0.0013847 | west | N | 0.0013847 | 0
1070 | KINDERMG | 1 | 45.7 | 0.1268 | west | N | -0.022786 | 0.17168 | 0.0013847 | 0.29468 | 0.0013847 | west | N | 0.0013847 | 0
1071 | KINDERMG | 1 | 45.7 | 0.1268 | west | N | -0.022786 | 0.17168 | 0.0013847 | 0.29468 | 0.0013847 | west | N | 0.0013847 | 0
1073 | SCURRYCW | 2 | 120 | 0.12678 | west | Y | -0.022806 | 0.17166 | 0.0013647 | 0.29466 | 0.0013647 | west | N | 0.0013647 | 0
1320 | BSP 1 | 1 | 25.8 | 0.12568 | west | N | -0.023903 | 0.17056 | 0.00026769 | 0.29356 | 0.00026769 | west | N | 0.00026769 | 0
1326 | STANTONW | 1 | 100.5 | 0.12546 | west | Y | -0.024122 | 0.17035 | 4.8695e-05 | 0.29334 | 4.8695e-05 | west | N | 4.8695e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.12609 | west | Y | -0.023498 | 0.17097 | 0.00067269 | 0.29397 | 0.00067269 | west | N | 0.00067269 | 0
1328 | OCOTILLO | 1 | 58 | 0.12544 | west | Y | -0.024143 | 0.17032 | 2.7695e-05 | 0.29332 | 2.7695e-05 | west | N | 2.7695e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.12562 | west | Y | -0.02397 | 0.1705 | 0.00020069 | 0.29349 | 0.00020069 | west | N | 0.00020069 | 0
1343 | TRENTIPP | 1 | 150 | 0.12701 | west | Y | -0.02257 | 0.1719 | 0.0016007 | 0.29489 | 0.0016007 | west | N | 0.0016007 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.12476 | west | Y | -0.024828 | 0.16964 | -0.00065731 | 0.29264 | 0.00065731 | west | N | 0.00065731 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.12476 | west | Y | -0.024828 | 0.16964 | -0.00065731 | 0.29264 | 0.00065731 | west | N | 0.00065731 | 0
1354 | AEPWIND_ | 1 | 101 | 0.12701 | west | Y | -0.02257 | 0.1719 | 0.0016007 | 0.29489 | 0.0016007 | west | N | 0.0016007 | 0
1360 | GUNSIGHT | 1 | 120 | 0.12612 | west | Y | -0.02347 | 0.171 | 0.00070069 | 0.29399 | 0.00070069 | west | N | 0.00070069 | 0
1432 | GRHAMSES | 2 | 366 | 0.1336 | north | Y | -0.015988 | 0.17848 | 0.0081827 | 0.30148 | 0.0081827 | west | Y | 0.015988 | 2.8566
1433 | GRHAMSES | 1 | 242 | 0.13267 | north | Y | -0.016913 | 0.17755 | 0.0072577 | 0.30055 | 0.0072577 | west | Y | 0.016913 | 2.3365
1437 | MESQUITW | 1 | 400 | 0.13014 | west | Y | -0.019449 | 0.17502 | 0.0047217 | 0.29802 | 0.0047217 | west | N | 0.0047217 | 0
1438 | MESQUITW | 1 | 236 | 0.13014 | west | Y | -0.019444 | 0.17502 | 0.0047267 | 0.29802 | 0.0047267 | west | N | 0.0047267 | 0
1442 | COKFIELD | 1 | 165 | 0.13097 | west | Y | -0.018615 | 0.17585 | 0.0055557 | 0.29885 | 0.0055557 | west | N | 0.0055557 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.13577 | north | Y | -0.013814 | 0.18065 | 0.010357 | 0.30365 | 0.010357 | west | Y | 0.013814 | 0.70522
1454 | WCPWRCO_ | 2 | 201 | 0.13577 | north | Y | -0.013814 | 0.18065 | 0.010357 | 0.30365 | 0.010357 | west | Y | 0.013814 | 0.69485
1455 | WCPWRCO_ | 3 | 242 | 0.13577 | north | Y | -0.013814 | 0.18065 | 0.010357 | 0.30365 | 0.010357 | west | Y | 0.013814 | 0.83658
1479 | WFCOGEN_ | 1 | 20 | 0.13375 | west | Y | -0.015832 | 0.17864 | 0.0083387 | 0.30163 | 0.0083387 | west | N | 0.0083387 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.13375 | west | Y | -0.015832 | 0.17864 | 0.0083387 | 0.30163 | 0.0083387 | west | N | 0.0083387 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.13375 | west | Y | -0.015832 | 0.17864 | 0.0083387 | 0.30163 | 0.0083387 | west | N | 0.0083387 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.13375 | west | Y | -0.015832 | 0.17864 | 0.0083387 | 0.30163 | 0.0083387 | west | N | 0.0083387 | 0
1600 | BARTNWND | 1 | 120 | 0.13322 | north | Y | -0.016369 | 0.1781 | 0.0078017 | 0.3011 | 0.0078017 | west | Y | 0.016369 | 1.028
1643 | SLSTR1PP | 1 | 60 | 0.12666 | north | Y | -0.022926 | 0.17154 | 0.0012447 | 0.29454 | 0.0012447 | west | Y | 0.022926 | 1.3009
1675 | PEC_1G | 1 | 75 | 0.145 | north | N | -0.0045837 | 0.18988 | 0.019587 | 0.31288 | 0.0045837 | North | N | 0.0045837 | 0
1676 | PEC_2G | 2 | 79.6 | 0.145 | north | N | -0.0045837 | 0.18988 | 0.019587 | 0.31288 | 0.0045837 | North | N | 0.0045837 | 0
1677 | PEC_3G | 3 | 88.4 | 0.145 | north | N | -0.0045837 | 0.18988 | 0.019587 | 0.31288 | 0.0045837 | North | N | 0.0045837 | 0
1678 | LAMARPWR | 1 | 160 | 0.14487 | north | Y | -0.0047107 | 0.18976 | 0.01946 | 0.31275 | 0.0047107 | North | N | 0.0047107 | 0
1679 | LAMARPWR | 2 | 156 | 0.14487 | north | Y | -0.0047107 | 0.18976 | 0.01946 | 0.31275 | 0.0047107 | North | N | 0.0047107 | 0
1680 | LAMARPWR | 3 | 196 | 0.14487 | north | Y | -0.0047107 | 0.18976 | 0.01946 | 0.31275 | 0.0047107 | North | N | 0.0047107 | 0
1681 | LAMARPWR | 4 | 156 | 0.14487 | north | Y | -0.0047107 | 0.18976 | 0.01946 | 0.31275 | 0.0047107 | North | N | 0.0047107 | 0
1682 | LAMARPWR | 5 | 157 | 0.14487 | north | Y | -0.0047107 | 0.18976 | 0.01946 | 0.31275 | 0.0047107 | North | N | 0.0047107 | 0
1683 | LAMARPWR | 6 | 198 | 0.14487 | north | Y | -0.0047107 | 0.18976 | 0.01946 | 0.31275 | 0.0047107 | North | N | 0.0047107 | 0
1687 | VALLEY_1 | 1 | 170 | 0.14438 | north | Y | -0.0052007 | 0.18927 | 0.01897 | 0.31226 | 0.0052007 | North | N | 0.0052007 | 0
1688 | VALLEY_2 | 2 | 520 | 0.14438 | north | Y | -0.0052007 | 0.18927 | 0.01897 | 0.31226 | 0.0052007 | North | N | 0.0052007 | 0
1689 | VALLEY_3 | 3 | 370 | 0.14472 | north | Y | -0.0048687 | 0.1896 | 0.019302 | 0.3126 | 0.0048687 | North | N | 0.0048687 | 0
1701 | MOSES_1G | 1 | 558 | 0.14514 | north | Y | -0.0044427 | 0.19002 | 0.019728 | 0.31302 | 0.0044427 | North | N | 0.0044427 | 0
1702 | MOSES_2G | 2 | 579 | 0.14514 | north | Y | -0.0044427 | 0.19002 | 0.019728 | 0.31302 | 0.0044427 | North | N | 0.0044427 | 0
1703 | MOSES_3G | 3 | 808 | 0.14514 | north | Y | -0.0044427 | 0.19002 | 0.019728 | 0.31302 | 0.0044427 | North | N | 0.0044427 | 0
1861 | EAGLEMNT | MB | 112 | 0.13809 | north | Y | -0.01149 | 0.18298 | 0.012681 | 0.30597 | 0.01149 | North | N | 0.01149 | 0
1862 | EAGLEMNT | MB | 100 | 0.13809 | north | Y | -0.01149 | 0.18298 | 0.012681 | 0.30597 | 0.01149 | North | N | 0.01149 | 0
1863 | EAGLEMNT | MB | 378 | 0.13809 | north | Y | -0.01149 | 0.18298 | 0.012681 | 0.30597 | 0.01149 | North | N | 0.01149 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.13528 | north | Y | -0.014302 | 0.18017 | 0.0098687 | 0.30316 | 0.0098687 | west | Y | 0.014302 | 0.96328
1878 | WLFHOLW_ | 2 | 205 | 0.13528 | north | Y | -0.014302 | 0.18017 | 0.0098687 | 0.30316 | 0.0098687 | west | Y | 0.014302 | 0.90876
1879 | WLFHOLW_ | 3 | 272.4 | 0.13528 | north | Y | -0.014302 | 0.18017 | 0.0098687 | 0.30316 | 0.0098687 | west | Y | 0.014302 | 1.2075
1889 | DECRDOVA | MB | 770 | 0.13562 | north | Y | -0.013962 | 0.18051 | 0.010209 | 0.3035 | 0.010209 | west | Y | 0.013962 | 0
1892 | DECRDOVA | A | 70 | 0.13338 | north | Y | -0.016206 | 0.17826 | 0.0079647 | 0.30126 | 0.0079647 | west | Y | 0.016206 | 0.57687
1893 | DECRDOVA | B | 69 | 0.13338 | north | Y | -0.016206 | 0.17826 | 0.0079647 | 0.30126 | 0.0079647 | west | Y | 0.016206 | 0.56863
1894 | DECRDOVA | C | 69 | 0.13338 | north | Y | -0.016206 | 0.17826 | 0.0079647 | 0.30126 | 0.0079647 | west | Y | 0.016206 | 0.56863
1895 | DECRDOVA | D | 68 | 0.13338 | north | Y | -0.016206 | 0.17826 | 0.0079647 | 0.30126 | 0.0079647 | west | Y | 0.016206 | 0.56038
1898 | COMCHEPK | 1 | 1157 | 0.13491 | north | N | -0.014675 | 0.17979 | 0.0094957 | 0.30279 | 0.0094957 | west | Y | 0.014675 | 0
1899 | COMCHEPK | 2 | 1158 | 0.13491 | north | N | -0.014675 | 0.17979 | 0.0094957 | 0.30279 | 0.0094957 | west | Y | 0.014675 | 0
1937 | MDLTHELP | 5 | 224 | 0.13585 | north | Y | -0.013738 | 0.18073 | 0.010433 | 0.30373 | 0.010433 | west | Y | 0.013738 | 0.74031
1938 | MDLTHELP | 6 | 226 | 0.13585 | north | Y | -0.013738 | 0.18073 | 0.010433 | 0.30373 | 0.010433 | west | Y | 0.013738 | 0.74692
1941 | MDLTHELP | 1 | 216.4 | 0.13749 | north | Y | -0.012091 | 0.18238 | 0.01208 | 0.30537 | 0.01208 | west | Y | 0.012091 | 0.0023708
1942 | MDLTHELP | 2 | 216.1 | 0.13749 | north | Y | -0.012091 | 0.18238 | 0.01208 | 0.30537 | 0.01208 | west | Y | 0.012091 | 0.0023675
1943 | MDLTHELP | 3 | 212 | 0.13585 | north | Y | -0.013738 | 0.18073 | 0.010433 | 0.30373 | 0.010433 | west | Y | 0.013738 | 0.70065
1944 | MDLTHELP | 4 | 211 | 0.13585 | north | Y | -0.013738 | 0.18073 | 0.010433 | 0.30373 | 0.010433 | west | Y | 0.013738 | 0.69735
1947 | HANDLEY_ | 3 | 395 | 0.13825 | north | Y | -0.011338 | 0.18313 | 0.012833 | 0.30613 | 0.011338 | North | N | 0.011338 | 0
1948 | HANDLEY_ | 4 | 435 | 0.13862 | north | Y | -0.010969 | 0.1835 | 0.013202 | 0.3065 | 0.010969 | North | N | 0.010969 | 0
1949 | HANDLEY_ | 5 | 435 | 0.13825 | north | Y | -0.011338 | 0.18313 | 0.012833 | 0.30613 | 0.011338 | North | N | 0.011338 | 0
2371 | COLLIN_1 | MB | 138 | 0.14325 | north | Y | -0.0063327 | 0.18813 | 0.017838 | 0.31113 | 0.0063327 | North | N | 0.0063327 | 0
2413 | MTCK6_G | 6 | 118 | 0.14346 | north | Y | -0.0061247 | 0.18834 | 0.018046 | 0.31134 | 0.0061247 | North | N | 0.0061247 | 0
2414 | MTCK7_G | 7 | 115 | 0.14346 | north | Y | -0.0061247 | 0.18834 | 0.018046 | 0.31134 | 0.0061247 | North | N | 0.0061247 | 0
2417 | MTCK8_G | 8 | 556 | 0.14346 | north | Y | -0.0061247 | 0.18834 | 0.018046 | 0.31134 | 0.0061247 | North | N | 0.0061247 | 0
2451 | LKHB1_G | 1 | 388 | 0.14567 | north | Y | -0.0039107 | 0.19056 | 0.02026 | 0.31355 | 0.0039107 | North | N | 0.0039107 | 0
2452 | LKHB2_G | 2 | 515 | 0.14567 | north | Y | -0.0039107 | 0.19056 | 0.02026 | 0.31355 | 0.0039107 | North | N | 0.0039107 | 0
3097 | MARTLAKE | 1 | 785 | 0.15289 | north | Y | 0.0033033 | 0.19777 | 0.027474 | 0.32077 | 0.0033033 | North | N | 0.0033033 | 0
3098 | MARTLAKE | 2 | 795 | 0.15289 | north | Y | 0.0033033 | 0.19777 | 0.027474 | 0.32077 | 0.0033033 | North | N | 0.0033033 | 0
3099 | MARTLAKE | 3 | 780 | 0.15289 | north | Y | 0.0033033 | 0.19777 | 0.027474 | 0.32077 | 0.0033033 | North | N | 0.0033033 | 0
3107 | STRYKER_ | 1 | 182 | 0.15601 | north | Y | 0.0064213 | 0.20089 | 0.030592 | 0.32389 | 0.0064213 | North | N | 0.0064213 | 0
3108 | STRYKER_ | 2 | 484 | 0.15601 | north | Y | 0.0064213 | 0.20089 | 0.030592 | 0.32389 | 0.0064213 | North | N | 0.0064213 | 0
3126 | TRINIDAD | 1 | 224 | 0.14989 | north | Y | 0.00030235 | 0.19477 | 0.024473 | 0.31777 | 0.00030235 | North | N | 0.00030235 | 0
3309 | ASPN_G | 1 | 50 | 0.15473 | north | Y | 0.0051493 | 0.19962 | 0.02932 | 0.32261 | 0.0051493 | North | N | 0.0051493 | 0
3348 | CHAMPION | MB | 42 | 0.15469 | north | N | 0.0051063 | 0.19957 | 0.029277 | 0.32257 | 0.0051063 | North | N | 0.0051063 | 0
3381 | BBRN_1G | 1 | 615 | 0.16249 | north | Y | 0.012909 | 0.20738 | 0.03708 | 0.33037 | 0.012909 | North | N | 0.012909 | 0
3382 | BBRN_2G | 2 | 587 | 0.16249 | north | Y | 0.012909 | 0.20738 | 0.03708 | 0.33037 | 0.012909 | North | N | 0.012909 | 0
3403 | THOUSE_1 | MB | 537 | 0.094263 | north | Y | -0.055322 | 0.13915 | -0.031151 | 0.26214 | 0.031151 | west | Y | 0.055322 | 0
3404 | THOUSE_2 | 2 | 787 | 0.094263 | north | Y | -0.055322 | 0.13915 | -0.031151 | 0.26214 | 0.031151 | west | Y | 0.055322 | 19.0221
3416 | LAKE_CRK | MB | 75 | 0.094431 | north | Y | -0.055154 | 0.13931 | -0.030983 | 0.26231 | 0.030983 | west | Y | 0.055154 | 0
3417 | LAKE_CRK | MB | 222 | 0.094431 | north | Y | -0.055154 | 0.13931 | -0.030983 | 0.26231 | 0.030983 | west | Y | 0.055154 | 0
3432 | SANDOW_4 | 4 | 569 | 0.026412 | south | Y | -0.12317 | 0.071294 | -0.099002 | 0.19429 | 0.071294 | south | N | 0.071294 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.04985 | south | Y | -0.19943 | -0.0049675 | -0.17526 | 0.11803 | 0.0049675 | south | N | 0.0049675 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.04985 | south | Y | -0.19943 | -0.0049675 | -0.17526 | 0.11803 | 0.0049675 | south | N | 0.0049675 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.049632 | south | Y | -0.19922 | -0.0047495 | -0.17505 | 0.11825 | 0.0047495 | south | N | 0.0047495 | 0
5031 | BRA_VHBC | 1 | 46 | -0.04985 | south | Y | -0.19943 | -0.0049675 | -0.17526 | 0.11803 | 0.0049675 | south | N | 0.0049675 | 0
5032 | BRA_VHBC | 2 | 47 | -0.04985 | south | Y | -0.19943 | -0.0049675 | -0.17526 | 0.11803 | 0.0049675 | south | N | 0.0049675 | 0
5033 | BRA_VHBC | 3 | 46 | -0.04985 | south | Y | -0.19943 | -0.0049675 | -0.17526 | 0.11803 | 0.0049675 | south | N | 0.0049675 | 0
5034 | BRA_VHBC | 4 | 46 | -0.04985 | south | Y | -0.19943 | -0.0049675 | -0.17526 | 0.11803 | 0.0049675 | south | N | 0.0049675 | 0
5111 | CALAVER_ | 1 | 424 | -0.049722 | south | Y | -0.19931 | -0.0048395 | -0.17514 | 0.11816 | 0.0048395 | south | N | 0.0048395 | 0
5112 | CALAVER_ | 2 | 425 | -0.049722 | south | Y | -0.19931 | -0.0048395 | -0.17514 | 0.11816 | 0.0048395 | south | N | 0.0048395 | 0
5264 | LEON_LCP | 3 | 58 | -0.049642 | south | Y | -0.19923 | -0.0047595 | -0.17506 | 0.11824 | 0.0047595 | south | N | 0.0047595 | 0
5265 | LEON_LCP | 4 | 89 | -0.049642 | south | Y | -0.19923 | -0.0047595 | -0.17506 | 0.11824 | 0.0047595 | south | N | 0.0047595 | 0
5266 | LEON_LCP | 1 | 44 | -0.049642 | south | Y | -0.19923 | -0.0047595 | -0.17506 | 0.11824 | 0.0047595 | south | N | 0.0047595 | 0
5267 | LEON_LCP | 2 | 44 | -0.049642 | south | Y | -0.19923 | -0.0047595 | -0.17506 | 0.11824 | 0.0047595 | south | N | 0.0047595 | 0
5268 | LEON_LCP | 3 | 43 | -0.049642 | south | Y | -0.19923 | -0.0047595 | -0.17506 | 0.11824 | 0.0047595 | south | N | 0.0047595 | 0
5269 | LEON_LCP | 4 | 45 | -0.049642 | south | Y | -0.19923 | -0.0047595 | -0.17506 | 0.11824 | 0.0047595 | south | N | 0.0047595 | 0
5396 | CALAVER_ | 1 | 412 | -0.049696 | south | Y | -0.19928 | -0.0048135 | -0.17511 | 0.11818 | 0.0048135 | south | N | 0.0048135 | 0
5397 | CALAVER_ | 2 | 400 | -0.049696 | south | Y | -0.19928 | -0.0048135 | -0.17511 | 0.11818 | 0.0048135 | south | N | 0.0048135 | 0
5401 | CALAVER_ | 1 | 546 | -0.051978 | south | Y | -0.20156 | -0.0070955 | -0.17739 | 0.1159 | 0.0070955 | south | N | 0.0070955 | 0
5402 | CALAVER_ | 2 | 750 | -0.051978 | south | Y | -0.20156 | -0.0070955 | -0.17739 | 0.1159 | 0.0070955 | south | N | 0.0070955 | 0
5436 | TUTTL_WB | MB | 61 | -0.049918 | south | Y | -0.1995 | -0.0050355 | -0.17533 | 0.11796 | 0.0050355 | south | N | 0.0050355 | 0
5438 | TUTTL_WB | MB | 95 | -0.049918 | south | Y | -0.1995 | -0.0050355 | -0.17533 | 0.11796 | 0.0050355 | south | N | 0.0050355 | 0
5439 | TUTTL_WB | MB | 151 | -0.049918 | south | Y | -0.1995 | -0.0050355 | -0.17533 | 0.11796 | 0.0050355 | south | N | 0.0050355 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.05099 | south | Y | -0.20057 | -0.0061075 | -0.1764 | 0.11689 | 0.0061075 | south | N | 0.0061075 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.05099 | south | Y | -0.20057 | -0.0061075 | -0.1764 | 0.11689 | 0.0061075 | south | N | 0.0061075 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.05099 | south | Y | -0.20057 | -0.0061075 | -0.1764 | 0.11689 | 0.0061075 | south | N | 0.0061075 | 0
5503 | RAYBURNG | 1 | 22 | -0.079768 | south | Y | -0.22935 | -0.034886 | -0.20518 | 0.088112 | 0.034886 | south | N | 0.034886 | 0
5505 | RAYBURNG | 1 | 11 | -0.079768 | south | Y | -0.22935 | -0.034886 | -0.20518 | 0.088112 | 0.034886 | south | N | 0.034886 | 0
5506 | RAYBURNG | 1 | 11 | -0.079768 | south | Y | -0.22935 | -0.034886 | -0.20518 | 0.088112 | 0.034886 | south | N | 0.034886 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.079062 | south | Y | -0.22865 | -0.03418 | -0.20448 | 0.088818 | 0.03418 | south | N | 0.03418 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.079062 | south | Y | -0.22865 | -0.03418 | -0.20448 | 0.088818 | 0.03418 | south | N | 0.03418 | 0
5511 | RAYBURNC | 1 | 46 | -0.079062 | south | Y | -0.22865 | -0.03418 | -0.20448 | 0.088818 | 0.03418 | south | N | 0.03418 | 0
5512 | RAYBURNC | 1 | 48 | -0.079062 | south | Y | -0.22865 | -0.03418 | -0.20448 | 0.088818 | 0.03418 | south | N | 0.03418 | 0
5728 | FALCONHY | 2 | 12 | -0.068268 | south | N | -0.21785 | -0.023386 | -0.19368 | 0.099612 | 0.023386 | south | N | 0.023386 | 0
5729 | FALCONHY | 3 | 11 | -0.068268 | south | N | -0.21785 | -0.023386 | -0.19368 | 0.099612 | 0.023386 | south | N | 0.023386 | 0
5890 | PEARSALL | 1 | 24 | -0.050446 | south | Y | -0.20003 | -0.0055635 | -0.17586 | 0.11743 | 0.0055635 | south | N | 0.0055635 | 0
5891 | PEARSALL | 1 | 24 | -0.050446 | south | Y | -0.20003 | -0.0055635 | -0.17586 | 0.11743 | 0.0055635 | south | N | 0.0055635 | 0
5892 | PEARSALL | 1 | 23 | -0.050446 | south | Y | -0.20003 | -0.0055635 | -0.17586 | 0.11743 | 0.0055635 | south | N | 0.0055635 | 0
5903 | SANMIGUE | 1 | 396 | -0.058198 | south | Y | -0.20778 | -0.013316 | -0.18361 | 0.10968 | 0.013316 | south | N | 0.013316 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.12539 | houston | N | -0.27497 | -0.080506 | -0.2508 | 0.042492 | 0.042492 | houston | N | 0.042492 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.12539 | houston | N | -0.27497 | -0.080506 | -0.2508 | 0.042492 | 0.042492 | houston | N | 0.042492 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | Y | 0.14958 | 0
5932 | SI_RAY9 | 9 | 38 | -0.07409 | south | Y | -0.22367 | -0.029208 | -0.1995 | 0.09379 | 0.029208 | south | N | 0.029208 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.07409 | south | Y | -0.22367 | -0.029208 | -0.1995 | 0.09379 | 0.029208 | south | N | 0.029208 | 0
5934 | SI_RAY5 | 5 | 15 | -0.07409 | south | Y | -0.22367 | -0.029208 | -0.1995 | 0.09379 | 0.029208 | south | N | 0.029208 | 0
5935 | SI_RAY10 | 10 | 47 | -0.07409 | south | Y | -0.22367 | -0.029208 | -0.1995 | 0.09379 | 0.029208 | south | N | 0.029208 | 0
6016 | SWMESA | 1 | 75 | 0.11695 | west | Y | -0.032636 | 0.16183 | -0.0084653 | 0.28483 | 0.0084653 | west | N | 0.0084653 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | Y | 0.12541 | 0
6144 | MCADOO1A | 1 | 150 | 0.12771 | west | Y | -0.021872 | 0.1726 | 0.0022987 | 0.29559 | 0.0022987 | west | N | 0.0022987 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.12423 | west | Y | -0.025355 | 0.16911 | -0.0011843 | 0.29211 | 0.0011843 | west | N | 0.0011843 | 0
6476 | LANGFORD | 1 | 150 | 0.089005 | west | Y | -0.06058 | 0.13389 | -0.036409 | 0.25688 | 0.036409 | west | N | 0.036409 | 0
6637 | SNYDERW1 | 1 | 63 | 0.12673 | west | Y | -0.02286 | 0.17161 | 0.0013107 | 0.2946 | 0.0013107 | west | N | 0.0013107 | 0
6752 | OKLA0A | 1 | 649.7 | 0.13168 | west | Y | -0.017901 | 0.17657 | 0.0062697 | 0.29956 | 0.0062697 | west | N | 0.0062697 | 0
6948 | DENISNDM | 1 | 40 | 0.14411 | north | N | -0.0054737 | 0.18899 | 0.018697 | 0.31199 | 0.0054737 | North | N | 0.0054737 | 0
6948 | DENISNDM | 2 | 40 | 0.14411 | north | N | -0.0054737 | 0.18899 | 0.018697 | 0.31199 | 0.0054737 | North | N | 0.0054737 | 0
7000 | L_FERGUS | 1 | 422 | -0.003465 | south | Y | -0.15305 | 0.041417 | -0.12888 | 0.16441 | 0.041417 | south | N | 0.041417 | 0
7004 | L_SIMGID | 1 | 132 | -0.021073 | south | Y | -0.17066 | 0.023809 | -0.14649 | 0.14681 | 0.023809 | south | N | 0.023809 | 0
7005 | L_SIMGID | 2 | 134 | -0.021073 | south | Y | -0.17066 | 0.023809 | -0.14649 | 0.14681 | 0.023809 | south | N | 0.023809 | 0
7006 | L_SIMGID | 3 | 323 | -0.021073 | south | Y | -0.17066 | 0.023809 | -0.14649 | 0.14681 | 0.023809 | south | N | 0.023809 | 0
7007 | L_LOSTPI | 1 | 158 | -0.023174 | south | Y | -0.17276 | 0.021708 | -0.14859 | 0.14471 | 0.021708 | south | N | 0.021708 | 0
7008 | L_LOSTPI | 2 | 160 | -0.023174 | south | Y | -0.17276 | 0.021708 | -0.14859 | 0.14471 | 0.021708 | south | N | 0.021708 | 0
7009 | L_LOSTPI | 3 | 175 | -0.023174 | south | Y | -0.17276 | 0.021708 | -0.14859 | 0.14471 | 0.021708 | south | N | 0.021708 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.04108 | south | Y | -0.19066 | 0.0038025 | -0.16649 | 0.1268 | 0.0038025 | south | N | 0.0038025 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.04108 | south | Y | -0.19066 | 0.0038025 | -0.16649 | 0.1268 | 0.0038025 | south | N | 0.0038025 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.041221 | south | Y | -0.19081 | 0.0036615 | -0.16664 | 0.12666 | 0.0036615 | south | N | 0.0036615 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.039391 | south | Y | -0.18898 | 0.0054915 | -0.16481 | 0.12849 | 0.0054915 | south | N | 0.0054915 | 0
7015 | L_HAYSEN | 2 | 225 | -0.039391 | south | Y | -0.18898 | 0.0054915 | -0.16481 | 0.12849 | 0.0054915 | south | N | 0.0054915 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.039391 | south | Y | -0.18898 | 0.0054915 | -0.16481 | 0.12849 | 0.0054915 | south | N | 0.0054915 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.039391 | south | Y | -0.18898 | 0.0054915 | -0.16481 | 0.12849 | 0.0054915 | south | N | 0.0054915 | 0
7020 | L_AUSTPL | 1 | 8 | -0.011394 | south | N | -0.16098 | 0.033488 | -0.13681 | 0.15649 | 0.033488 | south | N | 0.033488 | 0
7020 | L_AUSTPL | 2 | 8 | -0.011394 | south | N | -0.16098 | 0.033488 | -0.13681 | 0.15649 | 0.033488 | south | N | 0.033488 | 0
7022 | L_BUCHAN | 1 | 18 | 0.005824 | south | N | -0.14376 | 0.050706 | -0.11959 | 0.1737 | 0.050706 | south | N | 0.050706 | 0
7023 | L_BUCHAN | 2 | 18 | 0.005824 | south | N | -0.14376 | 0.050706 | -0.11959 | 0.1737 | 0.050706 | south | N | 0.050706 | 0
7024 | L_BUCHAN | 3 | 15 | 0.005824 | south | N | -0.14376 | 0.050706 | -0.11959 | 0.1737 | 0.050706 | south | N | 0.050706 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.004259 | south | N | -0.14533 | 0.049141 | -0.12116 | 0.17214 | 0.049141 | south | N | 0.049141 | 0
7028 | L_MARBFA | 1 | 18 | -0.005063 | south | N | -0.15465 | 0.039819 | -0.13048 | 0.16282 | 0.039819 | south | N | 0.039819 | 0
7029 | L_MARBFA | 2 | 18 | -0.005063 | south | N | -0.15465 | 0.039819 | -0.13048 | 0.16282 | 0.039819 | south | N | 0.039819 | 0
7031 | L_MARSFO | 1 | 35 | -0.008685 | south | N | -0.15827 | 0.036197 | -0.1341 | 0.15919 | 0.036197 | south | N | 0.036197 | 0
7032 | L_MARSFO | 2 | 34 | -0.008685 | south | N | -0.15827 | 0.036197 | -0.1341 | 0.15919 | 0.036197 | south | N | 0.036197 | 0
7033 | L_MARSFO | 3 | 35 | -0.008685 | south | N | -0.15827 | 0.036197 | -0.1341 | 0.15919 | 0.036197 | south | N | 0.036197 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.003109 | south | N | -0.15269 | 0.041773 | -0.12852 | 0.16477 | 0.041773 | south | N | 0.041773 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.003109 | south | N | -0.15269 | 0.041773 | -0.12852 | 0.16477 | 0.041773 | south | N | 0.041773 | 0
7038 | L_DELAWA | 1 | 35 | 0.12418 | west | Y | -0.025404 | 0.16906 | -0.0012333 | 0.29206 | 0.0012333 | west | N | 0.0012333 | 0
7038 | L_DELAWA | 2 | 30 | 0.12418 | west | Y | -0.025404 | 0.16906 | -0.0012333 | 0.29206 | 0.0012333 | west | N | 0.0012333 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.037789 | south | Y | -0.18737 | 0.0070935 | -0.1632 | 0.13009 | 0.0070935 | south | N | 0.0070935 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.037789 | south | Y | -0.18737 | 0.0070935 | -0.1632 | 0.13009 | 0.0070935 | south | N | 0.0070935 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.037789 | south | Y | -0.18737 | 0.0070935 | -0.1632 | 0.13009 | 0.0070935 | south | N | 0.0070935 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.037789 | south | Y | -0.18737 | 0.0070935 | -0.1632 | 0.13009 | 0.0070935 | south | N | 0.0070935 | 0
7487 | L_CANYHY | 1 | 6 | -0.033402 | south | N | -0.18299 | 0.01148 | -0.15882 | 0.13448 | 0.01148 | south | N | 0.01148 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.043263 | south | N | -0.19285 | 0.0016195 | -0.16868 | 0.12462 | 0.0016195 | south | N | 0.0016195 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.043263 | south | N | -0.19285 | 0.0016195 | -0.16868 | 0.12462 | 0.0016195 | south | N | 0.0016195 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.043263 | south | N | -0.19285 | 0.0016195 | -0.16868 | 0.12462 | 0.0016195 | south | N | 0.0016195 | 0
7609 | L_SCHUMA | 1 | 4 | -0.044693 | south | N | -0.19428 | 0.00018948 | -0.17011 | 0.12319 | 0.00018948 | south | N | 0.00018948 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.045917 | south | N | -0.1955 | -0.0010345 | -0.17133 | 0.12196 | 0.0010345 | south | N | 0.0010345 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.045917 | south | N | -0.1955 | -0.0010345 | -0.17133 | 0.12196 | 0.0010345 | south | N | 0.0010345 | 0
7800 | L_GUADGE | 1 | 147 | -0.048719 | south | Y | -0.1983 | -0.0038365 | -0.17413 | 0.11916 | 0.0038365 | south | N | 0.0038365 | 0
7801 | L_GUADGE | 2 | 138 | -0.048719 | south | Y | -0.1983 | -0.0038365 | -0.17413 | 0.11916 | 0.0038365 | south | N | 0.0038365 | 0
7802 | L_GUADGE | 3 | 140 | -0.048719 | south | Y | -0.1983 | -0.0038365 | -0.17413 | 0.11916 | 0.0038365 | south | N | 0.0038365 | 0
7803 | L_GUADGE | 4 | 147 | -0.048719 | south | Y | -0.1983 | -0.0038365 | -0.17413 | 0.11916 | 0.0038365 | south | N | 0.0038365 | 0
7804 | L_GUADGE | 5 | 182 | -0.048719 | south | Y | -0.1983 | -0.0038365 | -0.17413 | 0.11916 | 0.0038365 | south | N | 0.0038365 | 0
7805 | L_GUADGE | 6 | 198 | -0.048719 | south | Y | -0.1983 | -0.0038365 | -0.17413 | 0.11916 | 0.0038365 | south | N | 0.0038365 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.020618 | south | Y | -0.1702 | 0.024264 | -0.14603 | 0.14726 | 0.024264 | south | N | 0.024264 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.020618 | south | Y | -0.1702 | 0.024264 | -0.14603 | 0.14726 | 0.024264 | south | N | 0.024264 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.020618 | south | Y | -0.1702 | 0.024264 | -0.14603 | 0.14726 | 0.024264 | south | N | 0.024264 | 0
7810 | L_RIONOG | 1 | 142 | -0.044186 | south | Y | -0.19377 | 0.00069648 | -0.1696 | 0.12369 | 0.00069648 | south | N | 0.00069648 | 0
7811 | L_RIONOG | 2 | 145 | -0.044186 | south | Y | -0.19377 | 0.00069648 | -0.1696 | 0.12369 | 0.00069648 | south | N | 0.00069648 | 0
7812 | L_RIONOG | 3 | 151 | -0.044186 | south | Y | -0.19377 | 0.00069648 | -0.1696 | 0.12369 | 0.00069648 | south | N | 0.00069648 | 0
7813 | L_RIONOG | 4 | 290 | -0.044186 | south | Y | -0.19377 | 0.00069648 | -0.1696 | 0.12369 | 0.00069648 | south | N | 0.00069648 | 0
8032 | AMISTADH | 1 | 33 | -0.00367 | south | N | -0.15325 | 0.041212 | -0.12908 | 0.16421 | 0.041212 | south | N | 0.041212 | 0
8033 | AMISTADH | 2 | 25 | -0.00367 | south | N | -0.15325 | 0.041212 | -0.12908 | 0.16421 | 0.041212 | south | N | 0.041212 | 0
8048 | FALCONHY | 1 | 12 | -0.068268 | south | N | -0.21785 | -0.023386 | -0.19368 | 0.099612 | 0.023386 | south | N | 0.023386 | 0
8066 | DUP1V#1 | 1 | 73 | -0.079114 | south | N | -0.2287 | -0.034232 | -0.20453 | 0.088766 | 0.034232 | south | N | 0.034232 | 0
8134 | FOR69CG0 | 1 | 79 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
8138 | FOR69CG0 | 2 | 81 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | N | 0.044882 | 0
8147 | UCAR #2 | 10 | 28 | -0.082886 | south | N | -0.23247 | -0.038004 | -0.2083 | 0.084994 | 0.038004 | south | N | 0.038004 | 0
8148 | UCAR #1 | 2 | 7 | -0.082886 | south | N | -0.23247 | -0.038004 | -0.2083 | 0.084994 | 0.038004 | south | N | 0.038004 | 0
8153 | FOR69CG0 | 3 | 79 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
8154 | FOR69CG0 | 4 | 80 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
8156 | FOR69CG0 | 6 | 25 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
8157 | FOR69CG0 | 7 | 46 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
8161 | COLETOU1 | 1 | 629 | -0.071055 | south | Y | -0.22064 | -0.026173 | -0.19647 | 0.096825 | 0.026173 | south | N | 0.026173 | 0
8173 | VICEC51A | 5 | 144 | -0.077717 | south | Y | -0.2273 | -0.032835 | -0.20313 | 0.090163 | 0.032835 | south | N | 0.032835 | 0
8174 | VICEC61A | 6 | 188 | -0.077717 | south | Y | -0.2273 | -0.032835 | -0.20313 | 0.090163 | 0.032835 | south | N | 0.032835 | 0
8189 | CUERO 2 | 1 | 12 | -0.054635 | south | N | -0.20422 | -0.0097525 | -0.18005 | 0.11324 | 0.0097525 | south | N | 0.0097525 | 0
8262 | ELPS | 1 | 6 | -0.018914 | south | N | -0.1685 | 0.025968 | -0.14433 | 0.14897 | 0.025968 | south | N | 0.025968 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | N | 0.044882 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | N | 0.044882 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | N | 0.044882 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | N | 0.044882 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | N | 0.044882 | 0
8442 | NBEC71A | 1 | 336 | -0.075872 | south | Y | -0.22546 | -0.03099 | -0.20129 | 0.092008 | 0.03099 | south | N | 0.03099 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | N | 0.044882 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.14958 | 0.044882 | -0.12541 | 0.16788 | 0.044882 | south | N | 0.044882 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.075554 | south | Y | -0.22514 | -0.030672 | -0.20097 | 0.092326 | 0.030672 | south | N | 0.030672 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.075554 | south | Y | -0.22514 | -0.030672 | -0.20097 | 0.092326 | 0.030672 | south | N | 0.030672 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.075318 | south | N | -0.2249 | -0.030436 | -0.20073 | 0.092562 | 0.030436 | south | N | 0.030436 | 0
8506 | VAL #1 | 1 | 25 | -0.075477 | south | N | -0.22506 | -0.030595 | -0.20089 | 0.092403 | 0.030595 | south | N | 0.030595 | 0
8507 | VAL #2 | 2 | 25 | -0.075477 | south | N | -0.22506 | -0.030595 | -0.20089 | 0.092403 | 0.030595 | south | N | 0.030595 | 0
8511 | OXY_CC0A | 1 | 38 | -0.075362 | south | N | -0.22495 | -0.03048 | -0.20078 | 0.092518 | 0.03048 | south | N | 0.03048 | 0
8517 | CELANEBI | 1 | 29 | -0.074622 | south | N | -0.22421 | -0.02974 | -0.20004 | 0.093258 | 0.02974 | south | N | 0.02974 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.075855 | south | N | -0.22544 | -0.030973 | -0.20127 | 0.092025 | 0.030973 | south | N | 0.030973 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.075855 | south | N | -0.22544 | -0.030973 | -0.20127 | 0.092025 | 0.030973 | south | N | 0.030973 | 0
8562 | CNOPST1 | 3 | 153 | -0.075855 | south | N | -0.22544 | -0.030973 | -0.20127 | 0.092025 | 0.030973 | south | N | 0.030973 | 0
8926 | LGE_GT10 | 1 | 158 | -0.077341 | south | N | -0.22693 | -0.032459 | -0.20276 | 0.090539 | 0.032459 | south | N | 0.032459 | 0
8927 | LGE_GT20 | 2 | 153 | -0.077341 | south | N | -0.22693 | -0.032459 | -0.20276 | 0.090539 | 0.032459 | south | N | 0.032459 | 0
8928 | LGE_STG0 | 3 | 100 | -0.077341 | south | N | -0.22693 | -0.032459 | -0.20276 | 0.090539 | 0.032459 | south | N | 0.032459 | 0
8930 | ICPGN10A | 1 | 145 | -0.077341 | south | N | -0.22693 | -0.032459 | -0.20276 | 0.090539 | 0.032459 | south | N | 0.032459 | 0
8931 | ICPGN20A | 2 | 147 | -0.077341 | south | N | -0.22693 | -0.032459 | -0.20276 | 0.090539 | 0.032459 | south | N | 0.032459 | 0
8932 | ICPGN30A | 3 | 127 | -0.077341 | south | N | -0.22693 | -0.032459 | -0.20276 | 0.090539 | 0.032459 | south | N | 0.032459 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.072808 | south | Y | -0.22239 | -0.027926 | -0.19822 | 0.095072 | 0.027926 | south | N | 0.027926 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.072808 | south | Y | -0.22239 | -0.027926 | -0.19822 | 0.095072 | 0.027926 | south | N | 0.027926 | 0
8935 | FGNTS201 | 3 | 173 | -0.072808 | south | Y | -0.22239 | -0.027926 | -0.19822 | 0.095072 | 0.027926 | south | N | 0.027926 | 0
8936 | MVGN#1 | 1 | 207 | -0.073555 | south | Y | -0.22314 | -0.028673 | -0.19897 | 0.094325 | 0.028673 | south | N | 0.028673 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.073555 | south | Y | -0.22314 | -0.028673 | -0.19897 | 0.094325 | 0.028673 | south | N | 0.028673 | 0
8938 | MVGN#3 | 3 | 242 | -0.073555 | south | Y | -0.22314 | -0.028673 | -0.19897 | 0.094325 | 0.028673 | south | N | 0.028673 | 0
8981 | HECN1 | 1 | 144 | -0.07356 | south | Y | -0.22314 | -0.028678 | -0.19897 | 0.09432 | 0.028678 | south | N | 0.028678 | 0
8982 | HECN2 | 2 | 144 | -0.07356 | south | Y | -0.22314 | -0.028678 | -0.19897 | 0.09432 | 0.028678 | south | N | 0.028678 | 0
8983 | HECN3 | 3 | 171 | -0.07356 | south | Y | -0.22314 | -0.028678 | -0.19897 | 0.09432 | 0.028678 | south | N | 0.028678 | 0
9000 | DECKR_G1 | 1 | 310 | -0.011591 | south | Y | -0.16118 | 0.033291 | -0.13701 | 0.15629 | 0.033291 | south | N | 0.033291 | 0
9001 | DECKR_G2 | 2 | 413 | -0.011591 | south | Y | -0.16118 | 0.033291 | -0.13701 | 0.15629 | 0.033291 | south | N | 0.033291 | 0
9002 | DECKR_G3 | 3 | 42 | -0.010283 | south | Y | -0.15987 | 0.034599 | -0.1357 | 0.1576 | 0.034599 | south | N | 0.034599 | 0
9003 | DECKR_G4 | 4 | 44 | -0.010283 | south | Y | -0.15987 | 0.034599 | -0.1357 | 0.1576 | 0.034599 | south | N | 0.034599 | 0
9004 | DECKR_G5 | 5 | 44 | -0.010283 | south | Y | -0.15987 | 0.034599 | -0.1357 | 0.1576 | 0.034599 | south | N | 0.034599 | 0
9005 | DECKR_G6 | 6 | 47 | -0.010283 | south | Y | -0.15987 | 0.034599 | -0.1357 | 0.1576 | 0.034599 | south | N | 0.034599 | 0
9016 | SANDH_G1 | 1 | 49 | -0.013683 | south | Y | -0.16327 | 0.031199 | -0.1391 | 0.1542 | 0.031199 | south | N | 0.031199 | 0
9017 | SANDH_G2 | 2 | 46 | -0.013683 | south | Y | -0.16327 | 0.031199 | -0.1391 | 0.1542 | 0.031199 | south | N | 0.031199 | 0
9018 | SANDH_G3 | 3 | 46 | -0.013683 | south | Y | -0.16327 | 0.031199 | -0.1391 | 0.1542 | 0.031199 | south | N | 0.031199 | 0
9019 | SANDH_G4 | 4 | 47 | -0.013683 | south | Y | -0.16327 | 0.031199 | -0.1391 | 0.1542 | 0.031199 | south | N | 0.031199 | 0
9020 | SANDHG5A | 5A | 154 | -0.013683 | south | Y | -0.16327 | 0.031199 | -0.1391 | 0.1542 | 0.031199 | south | N | 0.031199 | 0
9021 | SANDHG5C | 5C | 148 | -0.013683 | south | Y | -0.16327 | 0.031199 | -0.1391 | 0.1542 | 0.031199 | south | N | 0.031199 | 0
9022 | SANDH_G6 | 6 | 48 | -0.013683 | south | Y | -0.16327 | 0.031199 | -0.1391 | 0.1542 | 0.031199 | south | N | 0.031199 | 0
9023 | SANDH_G7 | 7 | 48 | -0.013683 | south | Y | -0.16327 | 0.031199 | -0.1391 | 0.1542 | 0.031199 | south | N | 0.031199 | 0
11001 | NAV1CT | 1 | 70 | 0.12541 | west | Y | -0.024175 | 0.17029 | -4.3051e-06 | 0.29329 | 4.3051e-06 | west | N | 4.3051e-06 | 0
11009 | NAV2CT | 1 | 70 | 0.12541 | west | Y | -0.024175 | 0.17029 | -4.3051e-06 | 0.29329 | 4.3051e-06 | west | N | 4.3051e-06 | 0
11011 | NAV3ST | 1 | 92.8 | 0.12541 | west | Y | -0.024175 | 0.17029 | -4.3051e-06 | 0.29329 | 4.3051e-06 | west | N | 4.3051e-06 | 0
11012 | NAV4CT | 1 | 80 | 0.12541 | west | Y | -0.024175 | 0.17029 | -4.3051e-06 | 0.29329 | 4.3051e-06 | west | N | 4.3051e-06 | 0
11013 | NAV5CT | 1 | 80 | 0.12541 | west | Y | -0.024175 | 0.17029 | -4.3051e-06 | 0.29329 | 4.3051e-06 | west | N | 4.3051e-06 | 0
11014 | NAV6ST | 1 | 115 | 0.12541 | west | Y | -0.024175 | 0.17029 | -4.3051e-06 | 0.29329 | 4.3051e-06 | west | N | 4.3051e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.1254 | west | Y | -0.024188 | 0.17028 | -1.7305e-05 | 0.29328 | 1.7305e-05 | west | N | 1.7305e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.1254 | west | Y | -0.024188 | 0.17028 | -1.7305e-05 | 0.29328 | 1.7305e-05 | west | N | 1.7305e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.1254 | west | Y | -0.024188 | 0.17028 | -1.7305e-05 | 0.29328 | 1.7305e-05 | west | N | 1.7305e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.1254 | west | Y | -0.024188 | 0.17028 | -1.7305e-05 | 0.29328 | 1.7305e-05 | west | N | 1.7305e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.1254 | west | Y | -0.024188 | 0.17028 | -1.7305e-05 | 0.29328 | 1.7305e-05 | west | N | 1.7305e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.1254 | west | Y | -0.024188 | 0.17028 | -1.7305e-05 | 0.29328 | 1.7305e-05 | west | N | 1.7305e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.12771 | west | Y | -0.021872 | 0.1726 | 0.0022987 | 0.29559 | 0.0022987 | west | N | 0.0022987 | 0
11057 | CHAMPION | 1 | 126.5 | 0.12771 | west | Y | -0.021872 | 0.1726 | 0.0022987 | 0.29559 | 0.0022987 | west | N | 0.0022987 | 0
11058 | PYRON_1G | 1 | 249 | 0.12771 | west | Y | -0.021872 | 0.1726 | 0.0022987 | 0.29559 | 0.0022987 | west | N | 0.0022987 | 0
11059 | INADALE_ | 1 | 197 | 0.12771 | west | Y | -0.021872 | 0.1726 | 0.0022987 | 0.29559 | 0.0022987 | west | N | 0.0022987 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.12653 | west | Y | -0.023053 | 0.17141 | 0.0011177 | 0.29441 | 0.0011177 | west | N | 0.0011177 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.12653 | west | Y | -0.023053 | 0.17141 | 0.0011177 | 0.29441 | 0.0011177 | west | N | 0.0011177 | 0
11147 | NOTREES_ | 1 | 149 | 0.1244 | west | Y | -0.025186 | 0.16928 | -0.0010153 | 0.29228 | 0.0010153 | west | N | 0.0010153 | 0
11309 | BULLCREK | 1 | 180 | 0.12631 | west | Y | -0.023279 | 0.17119 | 0.00089169 | 0.29419 | 0.00089169 | west | N | 0.00089169 | 0
11310 | BULLCREK | 1 | 180 | 0.12631 | west | Y | -0.023279 | 0.17119 | 0.00089169 | 0.29419 | 0.00089169 | west | N | 0.00089169 | 0
11320 | COYOTE_1 | 1 | 225 | 0.12624 | west | Y | -0.023346 | 0.17112 | 0.00082469 | 0.29412 | 0.00082469 | west | N | 0.00082469 | 0
11415 | LORAINE_ | 1 | 125 | 0.12722 | west | Y | -0.022364 | 0.1721 | 0.0018067 | 0.2951 | 0.0018067 | west | N | 0.0018067 | 0
11416 | LORAINE_ | 1 | 125 | 0.12722 | west | Y | -0.022364 | 0.1721 | 0.0018067 | 0.2951 | 0.0018067 | west | N | 0.0018067 | 0
11691 | KMICHICT | 1 | 140 | 0.14472 | north | N | -0.0048687 | 0.1896 | 0.019302 | 0.3126 | 0.0048687 | North | N | 0.0048687 | 0
11692 | KMICHICT | 2 | 141 | 0.14472 | north | N | -0.0048687 | 0.1896 | 0.019302 | 0.3126 | 0.0048687 | North | N | 0.0048687 | 0
11693 | KMICHIST | 3 | 309 | 0.14472 | north | N | -0.0048687 | 0.1896 | 0.019302 | 0.3126 | 0.0048687 | North | N | 0.0048687 | 0
11694 | KMICHICT | 4 | 143 | 0.14472 | north | N | -0.0048687 | 0.1896 | 0.019302 | 0.3126 | 0.0048687 | North | N | 0.0048687 | 0
11695 | KMICHICT | 5 | 144 | 0.14472 | north | N | -0.0048687 | 0.1896 | 0.019302 | 0.3126 | 0.0048687 | North | N | 0.0048687 | 0
11696 | KMICHIST | 6 | 310 | 0.14472 | north | N | -0.0048687 | 0.1896 | 0.019302 | 0.3126 | 0.0048687 | North | N | 0.0048687 | 0
12322 | ENNSTRAC | 1 | 196 | 0.14277 | north | Y | -0.0068127 | 0.18765 | 0.017358 | 0.31065 | 0.0068127 | North | N | 0.0068127 | 0
12323 | ENNSTRAC | 2 | 111 | 0.14277 | north | Y | -0.0068127 | 0.18765 | 0.017358 | 0.31065 | 0.0068127 | North | N | 0.0068127 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.14361 | north | N | -0.0059747 | 0.18849 | 0.018196 | 0.31149 | 0.0059747 | North | N | 0.0059747 | 0
12411 | FPLEFR1A | 1 | 161 | 0.14691 | north | Y | -0.0026757 | 0.19179 | 0.021495 | 0.31479 | 0.0026757 | North | N | 0.0026757 | 0
12412 | FPLEFR1B | 2 | 164 | 0.14691 | north | Y | -0.0026757 | 0.19179 | 0.021495 | 0.31479 | 0.0026757 | North | N | 0.0026757 | 0
12413 | FPLEFR1C | 3 | 164 | 0.14691 | north | Y | -0.0026757 | 0.19179 | 0.021495 | 0.31479 | 0.0026757 | North | N | 0.0026757 | 0
12414 | FPLEFR1S | 4 | 414 | 0.14691 | north | Y | -0.0026757 | 0.19179 | 0.021495 | 0.31479 | 0.0026757 | North | N | 0.0026757 | 0
12421 | FPLEFR2A | 1 | 162 | 0.14691 | north | Y | -0.0026757 | 0.19179 | 0.021495 | 0.31479 | 0.0026757 | North | N | 0.0026757 | 0
12422 | FPLEFR2B | 2 | 161 | 0.14691 | north | Y | -0.0026757 | 0.19179 | 0.021495 | 0.31479 | 0.0026757 | North | N | 0.0026757 | 0
12423 | FPLEFR2C | 3 | 163 | 0.14691 | north | Y | -0.0026757 | 0.19179 | 0.021495 | 0.31479 | 0.0026757 | North | N | 0.0026757 | 0
12424 | FPLEFR2S | 4 | 409 | 0.14691 | north | Y | -0.0026757 | 0.19179 | 0.021495 | 0.31479 | 0.0026757 | North | N | 0.0026757 | 0
12440 | PARKD_1S | 1 | 0 | 0.14525 | north | N | -0.0043397 | 0.19013 | 0.019831 | 0.31312 | 0.0043397 | North | N | 0.0043397 | 0
12449 | PARKD_2S | 1 | 0 | 0.14525 | north | N | -0.0043397 | 0.19013 | 0.019831 | 0.31312 | 0.0043397 | North | N | 0.0043397 | 0
13116 | TGATEWAY | 1 | 148 | 0.15355 | north | N | 0.0039613 | 0.19843 | 0.028132 | 0.32143 | 0.0039613 | North | N | 0.0039613 | 0
13117 | TGATEWAY | 2 | 130 | 0.15355 | north | N | 0.0039613 | 0.19843 | 0.028132 | 0.32143 | 0.0039613 | North | N | 0.0039613 | 0
13118 | TGATEWAY | 3 | 145 | 0.15355 | north | N | 0.0039613 | 0.19843 | 0.028132 | 0.32143 | 0.0039613 | North | N | 0.0039613 | 0
13119 | TGATEWAY | 4 | 399 | 0.15355 | north | N | 0.0039613 | 0.19843 | 0.028132 | 0.32143 | 0.0039613 | North | N | 0.0039613 | 0
13131 | CALFREST | 1 | 150.7 | 0.16086 | north | Y | 0.011275 | 0.20574 | 0.035446 | 0.32874 | 0.011275 | North | N | 0.011275 | 0
13132 | CALFREST | 2 | 151 | 0.16086 | north | Y | 0.011275 | 0.20574 | 0.035446 | 0.32874 | 0.011275 | North | N | 0.011275 | 0
13133 | CALFREST | 3 | 177.4 | 0.16086 | north | Y | 0.011275 | 0.20574 | 0.035446 | 0.32874 | 0.011275 | North | N | 0.011275 | 0
13134 | CALFREST | 4 | 151.5 | 0.16059 | north | Y | 0.011004 | 0.20547 | 0.035175 | 0.32847 | 0.011004 | North | N | 0.011004 | 0
13135 | CALFREST | 5 | 152.3 | 0.16059 | north | Y | 0.011004 | 0.20547 | 0.035175 | 0.32847 | 0.011004 | North | N | 0.011004 | 0
13136 | CALFREST | 6 | 177.5 | 0.16059 | north | Y | 0.011004 | 0.20547 | 0.035175 | 0.32847 | 0.011004 | North | N | 0.011004 | 0
13432 | SANDOW_5 | 5 | 581 | 0.026412 | south | Y | -0.12317 | 0.071294 | -0.099002 | 0.19429 | 0.071294 | south | N | 0.071294 | 0
13691 | OAKGROVE | 1 | 855 | 0.19597 | north | Y | 0.046389 | 0.24086 | 0.07056 | 0.36385 | 0.046389 | North | N | 0.046389 | 0
13692 | OAKGROVE | 2 | 855 | 0.19597 | north | Y | 0.046389 | 0.24086 | 0.07056 | 0.36385 | 0.046389 | North | N | 0.046389 | 0
32798 | BRYN_TAM | 1 | 32 | 0.18548 | north | N | 0.035896 | 0.23036 | 0.060067 | 0.35336 | 0.035896 | North | N | 0.035896 | 0
32883 | BRYN_DNS | 1 | 48 | 0.1826 | north | Y | 0.033017 | 0.22748 | 0.057188 | 0.35048 | 0.033017 | North | N | 0.033017 | 0
32884 | BRYN_DNS | 1 | 46 | 0.1826 | north | Y | 0.033017 | 0.22748 | 0.057188 | 0.35048 | 0.033017 | North | N | 0.033017 | 0
32886 | BRYN_ATK | MB | 12 | 0.18536 | north | Y | 0.035778 | 0.23025 | 0.059949 | 0.35324 | 0.035778 | North | N | 0.035778 | 0
32887 | BRYN_ATK | MB | 51 | 0.18536 | north | Y | 0.035778 | 0.23025 | 0.059949 | 0.35324 | 0.035778 | North | N | 0.035778 | 0
32888 | BRYN_ATK | 1 | 17 | 0.18536 | north | Y | 0.035778 | 0.23025 | 0.059949 | 0.35324 | 0.035778 | North | N | 0.035778 | 0
32890 | BRYN_ATK | MB | 22 | 0.18536 | north | Y | 0.035778 | 0.23025 | 0.059949 | 0.35324 | 0.035778 | North | N | 0.035778 | 0
32891 | BRYN_ATK | MB | 25 | 0.18536 | north | Y | 0.035778 | 0.23025 | 0.059949 | 0.35324 | 0.035778 | North | N | 0.035778 | 0
32892 | BRYN_DNS | 1 | 105 | 0.1826 | north | Y | 0.033017 | 0.22748 | 0.057188 | 0.35048 | 0.033017 | North | N | 0.033017 | 0
36998 | RDCNYNG1 | 1 | 84 | 0.12697 | west | Y | -0.022617 | 0.17185 | 0.0015537 | 0.29485 | 0.0015537 | west | N | 0.0015537 | 0
38332 | WDWRDU2 | 1 | 80 | 0.11682 | west | Y | -0.032765 | 0.1617 | -0.0085943 | 0.2847 | 0.0085943 | west | N | 0.0085943 | 0
38437 | TNSRBNMS | 1 | 150 | 0.11675 | west | Y | -0.032832 | 0.16164 | -0.0086613 | 0.28463 | 0.0086613 | west | N | 0.0086613 | 0
38438 | TNSRBNMS | 1 | 150 | 0.11675 | west | Y | -0.032832 | 0.16164 | -0.0086613 | 0.28463 | 0.0086613 | west | N | 0.0086613 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.16613 | houston | N | -0.31571 | -0.12125 | -0.29154 | 0.0017507 | 0.0017507 | houston | N | 0.0017507 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.16613 | houston | N | -0.31571 | -0.12125 | -0.29154 | 0.0017507 | 0.0017507 | houston | N | 0.0017507 | 0
38600 | TNBP_CGN | 5 | 53 | -0.16613 | houston | N | -0.31571 | -0.12125 | -0.29154 | 0.0017507 | 0.0017507 | houston | N | 0.0017507 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.16613 | houston | N | -0.31571 | -0.12125 | -0.29154 | 0.0017507 | 0.0017507 | houston | N | 0.0017507 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.16613 | houston | N | -0.31571 | -0.12125 | -0.29154 | 0.0017507 | 0.0017507 | houston | N | 0.0017507 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.16613 | houston | N | -0.31571 | -0.12125 | -0.29154 | 0.0017507 | 0.0017507 | houston | N | 0.0017507 | 0
38614 | TNBPAMCG | 4 | 96 | -0.16613 | houston | N | -0.31571 | -0.12125 | -0.29154 | 0.0017507 | 0.0017507 | houston | N | 0.0017507 | 0
38615 | TNBPAMCG | 1 | 244 | -0.16613 | houston | N | -0.31571 | -0.12125 | -0.29154 | 0.0017507 | 0.0017507 | houston | N | 0.0017507 | 0
38690 | TNBP_CGN | 3 | 40 | -0.16613 | houston | N | -0.31571 | -0.12125 | -0.29154 | 0.0017507 | 0.0017507 | houston | N | 0.0017507 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.1661 | houston | N | -0.31569 | -0.12122 | -0.29152 | 0.0017767 | 0.0017767 | houston | N | 0.0017767 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.1661 | houston | N | -0.31569 | -0.12122 | -0.29152 | 0.0017767 | 0.0017767 | houston | N | 0.0017767 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.1661 | houston | N | -0.31569 | -0.12122 | -0.29152 | 0.0017767 | 0.0017767 | houston | N | 0.0017767 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.1661 | houston | N | -0.31569 | -0.12122 | -0.29152 | 0.0017767 | 0.0017767 | houston | N | 0.0017767 | 0
39470 | TNDOWCGN | 1 | 32 | -0.1661 | houston | N | -0.31569 | -0.12122 | -0.29152 | 0.0017757 | 0.0017757 | houston | N | 0.0017757 | 0
39480 | TNDOWCGN | 1 | 30 | -0.1661 | houston | N | -0.31569 | -0.12122 | -0.29152 | 0.0017757 | 0.0017757 | houston | N | 0.0017757 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.14987 | houston | N | -0.29945 | -0.10498 | -0.27528 | 0.018014 | 0.018014 | houston | N | 0.018014 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.14987 | houston | N | -0.29945 | -0.10498 | -0.27528 | 0.018014 | 0.018014 | houston | N | 0.018014 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.14987 | houston | N | -0.29945 | -0.10498 | -0.27528 | 0.018014 | 0.018014 | houston | N | 0.018014 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.14987 | houston | N | -0.29945 | -0.10498 | -0.27528 | 0.018014 | 0.018014 | houston | N | 0.018014 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.19597 | north | Y | 0.046389 | 0.24086 | 0.07056 | 0.36385 | 0.046389 | North | N | 0.046389 | 0
39970 | TNTNPONE | 1 | 153 | 0.19597 | north | Y | 0.046389 | 0.24086 | 0.07056 | 0.36385 | 0.046389 | North | N | 0.046389 | 0
48500 | APD_GT1_ | 1 | 136 | -0.176 | houston | N | -0.32559 | -0.13112 | -0.30142 | -0.0081243 | 0.0081243 | houston | N | 0.0081243 | 0
48510 | AK_GT1__ | 1 | 33 | -0.16071 | houston | N | -0.3103 | -0.11583 | -0.28613 | 0.0071677 | 0.0071677 | houston | N | 0.0071677 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.17605 | houston | Y | -0.32564 | -0.13117 | -0.30147 | -0.0081733 | 0.0081733 | houston | N | 0.0081733 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.17605 | houston | Y | -0.32564 | -0.13117 | -0.30147 | -0.0081733 | 0.0081733 | houston | N | 0.0081733 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.17605 | houston | Y | -0.32564 | -0.13117 | -0.30147 | -0.0081733 | 0.0081733 | houston | N | 0.0081733 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.17605 | houston | Y | -0.32564 | -0.13117 | -0.30147 | -0.0081733 | 0.0081733 | houston | N | 0.0081733 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.14723 | houston | N | -0.29681 | -0.10234 | -0.27264 | 0.020653 | 0.020653 | houston | N | 0.020653 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.14723 | houston | N | -0.29681 | -0.10234 | -0.27264 | 0.020653 | 0.020653 | houston | N | 0.020653 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.15979 | houston | N | -0.30937 | -0.1149 | -0.2852 | 0.0080937 | 0.0080937 | houston | N | 0.0080937 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.15979 | houston | N | -0.30937 | -0.1149 | -0.2852 | 0.0080937 | 0.0080937 | houston | N | 0.0080937 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.15979 | houston | N | -0.30937 | -0.1149 | -0.2852 | 0.0080937 | 0.0080937 | houston | N | 0.0080937 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.17231 | houston | N | -0.3219 | -0.12743 | -0.29773 | -0.0044323 | 0.0044323 | houston | N | 0.0044323 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.17231 | houston | N | -0.3219 | -0.12743 | -0.29773 | -0.0044323 | 0.0044323 | houston | N | 0.0044323 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.17231 | houston | N | -0.3219 | -0.12743 | -0.29773 | -0.0044323 | 0.0044323 | houston | N | 0.0044323 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.17231 | houston | N | -0.3219 | -0.12743 | -0.29773 | -0.0044323 | 0.0044323 | houston | N | 0.0044323 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.17472 | houston | N | -0.3243 | -0.12983 | -0.30013 | -0.0068363 | 0.0068363 | houston | N | 0.0068363 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.17472 | houston | N | -0.3243 | -0.12983 | -0.30013 | -0.0068363 | 0.0068363 | houston | N | 0.0068363 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.17159 | houston | N | -0.32117 | -0.12671 | -0.297 | -0.0037093 | 0.0037093 | houston | N | 0.0037093 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.17159 | houston | N | -0.32117 | -0.12671 | -0.297 | -0.0037093 | 0.0037093 | houston | N | 0.0037093 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.17159 | houston | N | -0.32117 | -0.12671 | -0.297 | -0.0037093 | 0.0037093 | houston | N | 0.0037093 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.17159 | houston | N | -0.32117 | -0.12671 | -0.297 | -0.0037093 | 0.0037093 | houston | N | 0.0037093 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.17159 | houston | N | -0.32117 | -0.12671 | -0.297 | -0.0037093 | 0.0037093 | houston | N | 0.0037093 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.17906 | houston | Y | -0.32865 | -0.13418 | -0.30448 | -0.011182 | 0.011182 | houston | N | 0.011182 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.17784 | houston | Y | -0.32743 | -0.13296 | -0.30326 | -0.0099613 | 0.0099613 | houston | N | 0.0099613 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.17943 | houston | Y | -0.32901 | -0.13455 | -0.30484 | -0.011549 | 0.011549 | houston | N | 0.011549 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.17943 | houston | Y | -0.32901 | -0.13455 | -0.30484 | -0.011549 | 0.011549 | houston | N | 0.011549 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.17943 | houston | Y | -0.32901 | -0.13455 | -0.30484 | -0.011549 | 0.011549 | houston | N | 0.011549 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.18621 | houston | N | -0.33579 | -0.14133 | -0.31162 | -0.01833 | 0.01833 | houston | N | 0.01833 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.17625 | houston | N | -0.32583 | -0.13136 | -0.30166 | -0.0083663 | 0.0083663 | houston | N | 0.0083663 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.17625 | houston | N | -0.32583 | -0.13136 | -0.30166 | -0.0083663 | 0.0083663 | houston | N | 0.0083663 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.18029 | houston | N | -0.32988 | -0.13541 | -0.30571 | -0.012413 | 0.012413 | houston | N | 0.012413 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.18029 | houston | N | -0.32988 | -0.13541 | -0.30571 | -0.012413 | 0.012413 | houston | N | 0.012413 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.18029 | houston | N | -0.32988 | -0.13541 | -0.30571 | -0.012413 | 0.012413 | houston | N | 0.012413 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.18029 | houston | N | -0.32988 | -0.13541 | -0.30571 | -0.012413 | 0.012413 | houston | N | 0.012413 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.1748 | houston | N | -0.32438 | -0.12991 | -0.30021 | -0.0069163 | 0.0069163 | houston | N | 0.0069163 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.1748 | houston | N | -0.32438 | -0.12991 | -0.30021 | -0.0069163 | 0.0069163 | houston | N | 0.0069163 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.1748 | houston | N | -0.32438 | -0.12991 | -0.30021 | -0.0069163 | 0.0069163 | houston | N | 0.0069163 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.1748 | houston | N | -0.32438 | -0.12991 | -0.30021 | -0.0069163 | 0.0069163 | houston | N | 0.0069163 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.17402 | houston | N | -0.32361 | -0.12914 | -0.29944 | -0.0061413 | 0.0061413 | houston | N | 0.0061413 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.17402 | houston | N | -0.32361 | -0.12914 | -0.29944 | -0.0061413 | 0.0061413 | houston | N | 0.0061413 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.17402 | houston | N | -0.32361 | -0.12914 | -0.29944 | -0.0061413 | 0.0061413 | houston | N | 0.0061413 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.17402 | houston | N | -0.32361 | -0.12914 | -0.29944 | -0.0061413 | 0.0061413 | houston | N | 0.0061413 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.17402 | houston | N | -0.32361 | -0.12914 | -0.29944 | -0.0061413 | 0.0061413 | houston | N | 0.0061413 | 0
48651 | EP_1_2 | 1 | 5 | -0.179 | houston | N | -0.32858 | -0.13412 | -0.30441 | -0.01112 | 0.01112 | houston | N | 0.01112 | 0
48651 | EP_1_2 | 2 | 21 | -0.179 | houston | N | -0.32858 | -0.13412 | -0.30441 | -0.01112 | 0.01112 | houston | N | 0.01112 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.23387 | north | N | -0.38346 | -0.18899 | -0.35929 | -0.065992 | 0.065992 | houston | Y | 0.38346 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.23387 | north | N | -0.38346 | -0.18899 | -0.35929 | -0.065992 | 0.065992 | houston | Y | 0.38346 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.23387 | north | N | -0.38346 | -0.18899 | -0.35929 | -0.065992 | 0.065992 | houston | Y | 0.38346 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.23387 | north | N | -0.38346 | -0.18899 | -0.35929 | -0.065992 | 0.065992 | houston | Y | 0.38346 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.1806 | houston | Y | -0.33019 | -0.13572 | -0.30602 | -0.012721 | 0.012721 | houston | N | 0.012721 | 0
48691 | GBY_7374 | A | 46 | -0.17341 | houston | Y | -0.32299 | -0.12853 | -0.29882 | -0.0055293 | 0.0055293 | houston | N | 0.0055293 | 0
48691 | GBY_7374 | B | 46 | -0.17341 | houston | Y | -0.32299 | -0.12853 | -0.29882 | -0.0055293 | 0.0055293 | houston | N | 0.0055293 | 0
48692 | GBY_8182 | C | 46 | -0.17341 | houston | Y | -0.32299 | -0.12853 | -0.29882 | -0.0055293 | 0.0055293 | houston | N | 0.0055293 | 0
48692 | GBY_8182 | D | 55 | -0.17341 | houston | Y | -0.32299 | -0.12853 | -0.29882 | -0.0055293 | 0.0055293 | houston | N | 0.0055293 | 0
48693 | GBY_8384 | E | 55 | -0.17341 | houston | Y | -0.32299 | -0.12853 | -0.29882 | -0.0055293 | 0.0055293 | houston | N | 0.0055293 | 0
48693 | GBY_8384 | F | 54 | -0.17341 | houston | Y | -0.32299 | -0.12853 | -0.29882 | -0.0055293 | 0.0055293 | houston | N | 0.0055293 | 0
48721 | LEG_1___ | 1 | 827 | 0.1826 | north | Y | 0.033016 | 0.22748 | 0.057187 | 0.35048 | 0.033016 | North | N | 0.033016 | 0
48722 | LEG_2___ | 2 | 819 | 0.1826 | north | Y | 0.033016 | 0.22748 | 0.057187 | 0.35048 | 0.033016 | North | N | 0.033016 | 0
48730 | MNS_GT | 1 | 46.1 | -0.1593 | houston | N | -0.30889 | -0.11442 | -0.28472 | 0.0085767 | 0.0085767 | houston | N | 0.0085767 | 0
48731 | CBE_GT1 | 1 | 76 | -0.1261 | houston | Y | -0.27568 | -0.081213 | -0.25151 | 0.041785 | 0.041785 | houston | N | 0.041785 | 0
48732 | CBE_GT2 | 1 | 76 | -0.1261 | houston | Y | -0.27568 | -0.081213 | -0.25151 | 0.041785 | 0.041785 | houston | N | 0.041785 | 0
48733 | CBE_ST12 | 1 | 105 | -0.1261 | houston | Y | -0.27568 | -0.081213 | -0.25151 | 0.041785 | 0.041785 | houston | N | 0.041785 | 0
48734 | CBE_GT3 | 1 | 74 | -0.1261 | houston | Y | -0.27568 | -0.081213 | -0.25151 | 0.041785 | 0.041785 | houston | N | 0.041785 | 0
48735 | CBE_GT4 | 1 | 74 | -0.1261 | houston | Y | -0.27568 | -0.081213 | -0.25151 | 0.041785 | 0.041785 | houston | N | 0.041785 | 0
48736 | CBE_ST34 | 1 | 102 | -0.1261 | houston | Y | -0.27568 | -0.081213 | -0.25151 | 0.041785 | 0.041785 | houston | N | 0.041785 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.17482 | houston | N | -0.3244 | -0.12994 | -0.30023 | -0.0069403 | 0.0069403 | houston | N | 0.0069403 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.17482 | houston | N | -0.3244 | -0.12994 | -0.30023 | -0.0069403 | 0.0069403 | houston | N | 0.0069403 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.17482 | houston | N | -0.3244 | -0.12994 | -0.30023 | -0.0069403 | 0.0069403 | houston | N | 0.0069403 | 0
48761 | PR_GT1__ | 1 | 35 | -0.17433 | houston | N | -0.32392 | -0.12945 | -0.29975 | -0.0064523 | 0.0064523 | houston | N | 0.0064523 | 0
48772 | PHR_GN2_ | MB | 459 | -0.16974 | houston | Y | -0.31933 | -0.12486 | -0.29516 | -0.0018613 | 0.0018613 | houston | N | 0.0018613 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.17901 | houston | N | -0.3286 | -0.13413 | -0.30443 | -0.011131 | 0.011131 | houston | N | 0.011131 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.17901 | houston | N | -0.3286 | -0.13413 | -0.30443 | -0.011131 | 0.011131 | houston | N | 0.011131 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.17901 | houston | N | -0.3286 | -0.13413 | -0.30443 | -0.011131 | 0.011131 | houston | N | 0.011131 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.17901 | houston | N | -0.3286 | -0.13413 | -0.30443 | -0.011131 | 0.011131 | houston | N | 0.011131 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.17901 | houston | N | -0.3286 | -0.13413 | -0.30443 | -0.011131 | 0.011131 | houston | N | 0.011131 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.17901 | houston | N | -0.3286 | -0.13413 | -0.30443 | -0.011131 | 0.011131 | houston | N | 0.011131 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.17901 | houston | N | -0.3286 | -0.13413 | -0.30443 | -0.011131 | 0.011131 | houston | N | 0.011131 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.18621 | houston | N | -0.33579 | -0.14133 | -0.31162 | -0.01833 | 0.01833 | houston | N | 0.01833 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.18621 | houston | N | -0.33579 | -0.14133 | -0.31162 | -0.01833 | 0.01833 | houston | N | 0.01833 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.18621 | houston | N | -0.33579 | -0.14133 | -0.31162 | -0.01833 | 0.01833 | houston | N | 0.01833 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.18621 | houston | N | -0.33579 | -0.14133 | -0.31162 | -0.01833 | 0.01833 | houston | N | 0.01833 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.17929 | houston | N | -0.32888 | -0.13441 | -0.30471 | -0.011411 | 0.011411 | houston | N | 0.011411 | 0
48820 | SHELLG1_ | 1 | 71 | -0.17527 | houston | N | -0.32486 | -0.13039 | -0.30069 | -0.0073943 | 0.0073943 | houston | N | 0.0073943 | 0
48821 | SHELLG2 | 2 | 72 | -0.17527 | houston | N | -0.32486 | -0.13039 | -0.30069 | -0.0073943 | 0.0073943 | houston | N | 0.0073943 | 0
48822 | SHELLG3_ | 1 | 39 | -0.17527 | houston | N | -0.32486 | -0.13039 | -0.30069 | -0.0073943 | 0.0073943 | houston | N | 0.0073943 | 0
48822 | SHELLG3_ | 2 | 30 | -0.17527 | houston | N | -0.32486 | -0.13039 | -0.30069 | -0.0073943 | 0.0073943 | houston | N | 0.0073943 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.17366 | houston | N | -0.32324 | -0.12877 | -0.29907 | -0.0057773 | 0.0057773 | houston | N | 0.0057773 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.17366 | houston | N | -0.32324 | -0.12877 | -0.29907 | -0.0057773 | 0.0057773 | houston | N | 0.0057773 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.17479 | houston | N | -0.32437 | -0.12991 | -0.3002 | -0.0069103 | 0.0069103 | houston | N | 0.0069103 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.1747 | houston | Y | -0.32428 | -0.12981 | -0.30011 | -0.0068163 | 0.0068163 | houston | N | 0.0068163 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.17467 | houston | Y | -0.32426 | -0.12979 | -0.30009 | -0.0067913 | 0.0067913 | houston | N | 0.0067913 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.17478 | houston | Y | -0.32437 | -0.1299 | -0.3002 | -0.0069023 | 0.0069023 | houston | N | 0.0069023 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.17481 | houston | Y | -0.32439 | -0.12993 | -0.30022 | -0.0069283 | 0.0069283 | houston | N | 0.0069283 | 0
48855 | SRB_GT21 | B2 | 12 | -0.17465 | houston | Y | -0.32424 | -0.12977 | -0.30007 | -0.0067733 | 0.0067733 | houston | N | 0.0067733 | 0
48855 | SRB_GT21 | MB | 18 | -0.17465 | houston | Y | -0.32424 | -0.12977 | -0.30007 | -0.0067733 | 0.0067733 | houston | N | 0.0067733 | 0
48865 | TECO_GT1 | 1 | 50 | -0.16819 | houston | Y | -0.31777 | -0.12331 | -0.2936 | -0.0003093 | 0.0003093 | houston | N | 0.0003093 | 0
48873 | THW_ST3_ | 3 | 104 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48874 | THW_ST4_ | 4 | 104 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48875 | THW_3132 | A | 54 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48875 | THW_3132 | B | 53 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48877 | THW_3334 | C | 54 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48877 | THW_3334 | D | 57 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48879 | THW_4142 | E | 54 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48879 | THW_4142 | F | 54 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48881 | THW_4344 | G | 58 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48881 | THW_4344 | H | 58 | -0.17742 | houston | Y | -0.327 | -0.13254 | -0.30283 | -0.0095383 | 0.0095383 | houston | N | 0.0095383 | 0
48883 | THW_GT1_ | B2 | 12 | -0.17854 | houston | Y | -0.32812 | -0.13365 | -0.30395 | -0.010656 | 0.010656 | houston | N | 0.010656 | 0
48885 | THW_5152 | A | 56 | -0.18113 | houston | Y | -0.33071 | -0.13625 | -0.30654 | -0.01325 | 0.01325 | houston | N | 0.01325 | 0
48885 | THW_5152 | B | 59 | -0.18113 | houston | Y | -0.33071 | -0.13625 | -0.30654 | -0.01325 | 0.01325 | houston | N | 0.01325 | 0
48886 | THW_5354 | C | 56 | -0.18113 | houston | Y | -0.33071 | -0.13625 | -0.30654 | -0.01325 | 0.01325 | houston | N | 0.01325 | 0
48886 | THW_5354 | D | 56 | -0.18113 | houston | Y | -0.33071 | -0.13625 | -0.30654 | -0.01325 | 0.01325 | houston | N | 0.01325 | 0
48887 | THW_5556 | E | 59 | -0.18113 | houston | Y | -0.33071 | -0.13625 | -0.30654 | -0.01325 | 0.01325 | houston | N | 0.01325 | 0
48887 | THW_5556 | F | 56 | -0.18113 | houston | Y | -0.33071 | -0.13625 | -0.30654 | -0.01325 | 0.01325 | houston | N | 0.01325 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.1302 | houston | Y | -0.27979 | -0.085321 | -0.25562 | 0.037677 | 0.037677 | houston | N | 0.037677 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.16123 | houston | Y | -0.31082 | -0.11635 | -0.28665 | 0.0066467 | 0.0066467 | houston | N | 0.0066467 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.16123 | houston | Y | -0.31082 | -0.11635 | -0.28665 | 0.0066467 | 0.0066467 | houston | N | 0.0066467 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.16123 | houston | Y | -0.31082 | -0.11635 | -0.28665 | 0.0066467 | 0.0066467 | houston | N | 0.0066467 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.16123 | houston | Y | -0.31082 | -0.11635 | -0.28665 | 0.0066467 | 0.0066467 | houston | N | 0.0066467 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.16123 | houston | N | -0.31082 | -0.11635 | -0.28665 | 0.0066467 | 0.0066467 | houston | N | 0.0066467 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.15971 | houston | Y | -0.30929 | -0.11482 | -0.28512 | 0.0081727 | 0.0081727 | houston | N | 0.0081727 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.15971 | houston | Y | -0.30929 | -0.11482 | -0.28512 | 0.0081727 | 0.0081727 | houston | N | 0.0081727 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.15971 | houston | Y | -0.30929 | -0.11482 | -0.28512 | 0.0081727 | 0.0081727 | houston | N | 0.0081727 | 0
48929 | WAPGT21_ | B1 | 13 | -0.16123 | houston | Y | -0.31082 | -0.11635 | -0.28665 | 0.0066467 | 0.0066467 | houston | N | 0.0066467 | 0
48940 | WARVUE_G | G1 | 12 | -0.17903 | houston | Y | -0.32861 | -0.13415 | -0.30444 | -0.01115 | 0.01115 | houston | N | 0.01115 | 0
49803 | EXN_15GT | 1 | 34 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49826 | EXN938GT | 5 | 45.9 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49828 | EXN941GT | 10 | 17.7 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49829 | EXN942GT | 11 | 20.4 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49830 | EXN943GT | 12 | 19.9 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49831 | EXN944GT | 13 | 35 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49832 | EXN945GT | 9 | 18 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49837 | EXN_GT | 4 | 85.4 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49838 | EXN_14GT | 14 | 148 | -0.17814 | houston | N | -0.32772 | -0.13326 | -0.30355 | -0.010259 | 0.010259 | houston | N | 0.010259 | 0
49851 | DOW17000 | 37 | 62 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49858 | DOW38100 | 31 | 71.4 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49859 | DOW38200 | 33 | 45 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49860 | DOW38300 | 32 | 101 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49862 | DOW39100 | 36 | 86 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49863 | DOW39200 | 35 | 88 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49865 | DOW41000 | 41 | 50 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49866 | DOW42000 | 42 | 18 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49869 | DOW49000 | 45 | 94 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49870 | DOW61000 | 61 | 70 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49871 | DOW62000 | 62 | 63 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49872 | DOW63000 | 63 | 72 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49873 | DOW64000 | 64 | 64.8 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49876 | DOW65000 | 65 | 101 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49877 | DOW66000 | 66 | 97 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49878 | DOW67000 | 67 | 103 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49882 | DOW81000 | 81 | 76 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49884 | DOW82000 | 82 | 80 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49885 | DOW83000 | 83 | 80 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
49886 | DOW84000 | 84 | 171 | -0.14391 | houston | N | -0.2935 | -0.099031 | -0.26933 | 0.023967 | 0.023967 | houston | N | 0.023967 | 0
58909 | PEARSALL | 1 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58909 | PEARSALL | 2 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58909 | PEARSALL | 3 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58909 | PEARSALL | 4 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58909 | PEARSALL | 5 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58909 | PEARSALL | 6 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58919 | PEARSALL | 1 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58919 | PEARSALL | 2 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58919 | PEARSALL | 3 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58919 | PEARSALL | 4 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58919 | PEARSALL | 5 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58919 | PEARSALL | 6 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58929 | PEARSALL | 1 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58929 | PEARSALL | 2 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58929 | PEARSALL | 3 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58929 | PEARSALL | 4 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58929 | PEARSALL | 5 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58929 | PEARSALL | 6 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58949 | PEARSALL | 1 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58949 | PEARSALL | 2 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58949 | PEARSALL | 3 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58949 | PEARSALL | 4 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58949 | PEARSALL | 5 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
58949 | PEARSALL | 6 | 8.4 | -0.048733 | south | Y | -0.19832 | -0.0038505 | -0.17415 | 0.11915 | 0.0038505 | south | N | 0.0038505 | 0
60000 | DSKY2 | 1 | 76.5 | 0.11369 | west | Y | -0.035894 | 0.15857 | -0.011723 | 0.28157 | 0.011723 | west | N | 0.011723 | 0
60003 | KING_NE1 | 1 | 80 | 0.11695 | west | Y | -0.032636 | 0.16183 | -0.0084653 | 0.28483 | 0.0084653 | west | N | 0.0084653 | 0
60005 | KING_SE1 | 1 | 40 | 0.11695 | west | Y | -0.032636 | 0.16183 | -0.0084653 | 0.28483 | 0.0084653 | west | N | 0.0084653 | 0
60007 | KING_SW1 | 1 | 80 | 0.11747 | west | Y | -0.032111 | 0.16236 | -0.0079403 | 0.28535 | 0.0079403 | west | N | 0.0079403 | 0
60016 | WOODWRD1 | 1 | 80 | 0.11683 | west | Y | -0.03275 | 0.16172 | -0.0085793 | 0.28471 | 0.0085793 | west | N | 0.0085793 | 0
60017 | ORNNWP1 | 1 | 80 | 0.11413 | west | Y | -0.035453 | 0.15901 | -0.011282 | 0.28201 | 0.011282 | west | N | 0.011282 | 0
60018 | DSKY1 | 1 | 84 | 0.11325 | west | Y | -0.036338 | 0.15813 | -0.012167 | 0.28113 | 0.012167 | west | N | 0.012167 | 0
60019 | KING_NW1 | 1 | 80 | 0.11747 | west | Y | -0.032111 | 0.16236 | -0.0079403 | 0.28535 | 0.0079403 | west | N | 0.0079403 | 0
60057 | CALLAHAN | 1 | 114 | -0.040901 | south | Y | -0.19049 | 0.0039815 | -0.16632 | 0.12698 | 0.0039815 | south | N | 0.0039815 | 0
60058 | BUFF_GAP | 1 | 120 | 0.12617 | west | Y | -0.023412 | 0.17106 | 0.00075869 | 0.29405 | 0.00075869 | west | N | 0.00075869 | 0
60060 | CIRELLO | 1 | 233 | 0.12617 | west | Y | -0.023412 | 0.17106 | 0.00075869 | 0.29405 | 0.00075869 | west | N | 0.00075869 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.12617 | west | Y | -0.023412 | 0.17106 | 0.00075869 | 0.29405 | 0.00075869 | west | N | 0.00075869 | 0
60066 | H_HOLLOW | 1 | 222 | -0.040901 | south | Y | -0.19049 | 0.0039815 | -0.16632 | 0.12698 | 0.0039815 | south | N | 0.0039815 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.040901 | south | Y | -0.19049 | 0.0039815 | -0.16632 | 0.12698 | 0.0039815 | south | N | 0.0039815 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.040901 | south | Y | -0.19049 | 0.0039815 | -0.16632 | 0.12698 | 0.0039815 | south | N | 0.0039815 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.040901 | south | Y | -0.19049 | 0.0039815 | -0.16632 | 0.12698 | 0.0039815 | south | N | 0.0039815 | 0
60074 | HORSH5 | 1 | 100 | -0.040901 | south | Y | -0.19049 | 0.0039815 | -0.16632 | 0.12698 | 0.0039815 | south | N | 0.0039815 | 0
60081 | WHRLWIND | 1 | 60 | 0.12869 | west | Y | -0.020899 | 0.17357 | 0.0032717 | 0.29657 | 0.0032717 | west | N | 0.0032717 | 0
60201 | RIO DRCS | F | 0 | 0.025271 | south | N | -0.12431 | 0.070153 | -0.10014 | 0.19315 | 0.070153 | south | N | 0.070153 | 0
60202 | FRIEND_R | F | 0 | 0.099146 | west | N | -0.050439 | 0.14403 | -0.026268 | 0.26703 | 0.026268 | west | N | 0.026268 | 0
60203 | PRES0A | BT | 4.8 | 0.11942 | west | N | -0.030167 | 0.1643 | -0.0059963 | 0.2873 | 0.0059963 | west | N | 0.0059963 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.12759 | west | Y | -0.021995 | 0.17247 | 0.0021757 | 0.29547 | 0.0021757 | west | N | 0.0021757 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.12759 | west | Y | -0.021995 | 0.17247 | 0.0021757 | 0.29547 | 0.0021757 | west | N | 0.0021757 | 0
71057 | L_SWEETW | W1 | 135 | 0.12759 | west | Y | -0.021995 | 0.17247 | 0.0021757 | 0.29547 | 0.0021757 | west | N | 0.0021757 | 0
71059 | L_SWEETW | W1 | 119 | 0.12759 | west | Y | -0.021995 | 0.17247 | 0.0021757 | 0.29547 | 0.0021757 | west | N | 0.0021757 | 0
71060 | L_SWEETW | W1 | 105 | 0.12759 | west | Y | -0.021995 | 0.17247 | 0.0021757 | 0.29547 | 0.0021757 | west | N | 0.0021757 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.12759 | west | Y | -0.021995 | 0.17247 | 0.0021757 | 0.29547 | 0.0021757 | west | N | 0.0021757 | 0
76031 | L_GASCCR | W1 | 150 | 0.12539 | west | Y | -0.024195 | 0.17027 | -2.4305e-05 | 0.29327 | 2.4305e-05 | west | N | 2.4305e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.12511 | west | Y | -0.024476 | 0.16999 | -0.00030531 | 0.29299 | 0.00030531 | west | N | 0.00030531 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.12511 | west | Y | -0.024476 | 0.16999 | -0.00030531 | 0.29299 | 0.00030531 | west | N | 0.00030531 | 0
76096 | L_CAPRSI | W1 | 186 | 0.12511 | west | Y | -0.024476 | 0.16999 | -0.00030531 | 0.29299 | 0.00030531 | west | N | 0.00030531 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.12511 | west | Y | -0.024476 | 0.16999 | -0.00030531 | 0.29299 | 0.00030531 | west | N | 0.00030531 | 0
80003 | MILHWYS | F | 0 | -0.07409 | south | N | -0.22367 | -0.029208 | -0.1995 | 0.09379 | 0.029208 | south | N | 0.029208 | 0
80010 | EPLVT1 | F | 0 | -0.02246 | south | N | -0.17204 | 0.022422 | -0.14787 | 0.14542 | 0.022422 | south | N | 0.022422 | 0
80012 | LAR | F | 0 | -0.057465 | south | N | -0.20705 | -0.012583 | -0.18288 | 0.11041 | 0.012583 | south | N | 0.012583 | 0
80051 | FORPVCM0 | 8 | 28 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
80053 | FOR69CG0 | 10 | 74 | -0.087453 | south | N | -0.23704 | -0.042571 | -0.21287 | 0.080427 | 0.042571 | south | N | 0.042571 | 0
80080 | GWINDT11 | 1 | 94 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80080 | GWINDT11 | 2 | 41 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80080 | GWINDT11 | 3 | 38 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80080 | GWINDT11 | 4 | 19 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80081 | GWINDT21 | 1 | 94 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80081 | GWINDT21 | 2 | 36 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80081 | GWINDT21 | 3 | 43 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80081 | GWINDT21 | 4 | 22 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80137 | CSDR89 | 8 | 39 | -0.082886 | south | N | -0.23247 | -0.038004 | -0.2083 | 0.084994 | 0.038004 | south | N | 0.038004 | 0
80137 | CSDR89 | 9 | 15 | -0.082886 | south | N | -0.23247 | -0.038004 | -0.2083 | 0.084994 | 0.038004 | south | N | 0.038004 | 0
80138 | CSDR7 | 7 | 7 | -0.082886 | south | N | -0.23247 | -0.038004 | -0.2083 | 0.084994 | 0.038004 | south | N | 0.038004 | 0
80139 | CSDR56 | 5 | 15 | -0.082886 | south | N | -0.23247 | -0.038004 | -0.2083 | 0.084994 | 0.038004 | south | N | 0.038004 | 0
80139 | CSDR56 | 6 | 39 | -0.082886 | south | N | -0.23247 | -0.038004 | -0.2083 | 0.084994 | 0.038004 | south | N | 0.038004 | 0
80140 | CSDR11 | 11 | 39 | -0.082886 | south | N | -0.23247 | -0.038004 | -0.2083 | 0.084994 | 0.038004 | south | N | 0.038004 | 0
80180 | PNSCALT1 | 1 | 148 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80180 | PNSCALT1 | 2 | 50 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80181 | PNSCALT2 | 1 | 55 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80181 | PNSCALT2 | 2 | 50 | -0.074292 | south | Y | -0.22388 | -0.02941 | -0.19971 | 0.093588 | 0.02941 | south | N | 0.02941 | 0
80223 | REYSHR G | 1 | 12 | -0.077341 | south | N | -0.22693 | -0.032459 | -0.20276 | 0.090539 | 0.032459 | south | N | 0.032459 | 0
80224 | VISTRONG | 1 | 15 | -0.081495 | south | N | -0.23108 | -0.036613 | -0.20691 | 0.086385 | 0.036613 | south | N | 0.036613 | 0
80225 | VISTRONG | 2 | 23 | -0.081495 | south | N | -0.23108 | -0.036613 | -0.20691 | 0.086385 | 0.036613 | south | N | 0.036613 | 0
80226 | ALCOA G | 1 | 48 | -0.086393 | south | N | -0.23598 | -0.041511 | -0.21181 | 0.081487 | 0.041511 | south | N | 0.041511 | 0
80227 | AIRCO G | 1 | 8 | -0.082337 | south | N | -0.23192 | -0.037455 | -0.20775 | 0.085543 | 0.037455 | south | N | 0.037455 | 0
80261 | NBEC81A | 1 | 180 | -0.075828 | south | Y | -0.22541 | -0.030946 | -0.20124 | 0.092052 | 0.030946 | south | N | 0.030946 | 0
80262 | NBEC91A | 1 | 180 | -0.075872 | south | Y | -0.22546 | -0.03099 | -0.20129 | 0.092008 | 0.03099 | south | N | 0.03099 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.075554 | south | Y | -0.22514 | -0.030672 | -0.20097 | 0.092326 | 0.030672 | south | N | 0.030672 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.075554 | south | Y | -0.22514 | -0.030672 | -0.20097 | 0.092326 | 0.030672 | south | N | 0.030672 | 0
80265 | LARECU40 | 4 | 100 | -0.057461 | south | Y | -0.20705 | -0.012579 | -0.18288 | 0.11042 | 0.012579 | south | N | 0.012579 | 0
80266 | LARECU50 | 5 | 100 | -0.057461 | south | Y | -0.20705 | -0.012579 | -0.18288 | 0.11042 | 0.012579 | south | N | 0.012579 | 0
80291 | PAPALOTE | 1 | 25 | -0.076752 | south | Y | -0.22634 | -0.03187 | -0.20217 | 0.091128 | 0.03187 | south | N | 0.03187 | 0
80291 | PAPALOTE | 2 | 25 | -0.076752 | south | Y | -0.22634 | -0.03187 | -0.20217 | 0.091128 | 0.03187 | south | N | 0.03187 | 0
80291 | PAPALOTE | 3 | 25 | -0.076752 | south | Y | -0.22634 | -0.03187 | -0.20217 | 0.091128 | 0.03187 | south | N | 0.03187 | 0
80291 | PAPALOTE | 4 | 16 | -0.076752 | south | Y | -0.22634 | -0.03187 | -0.20217 | 0.091128 | 0.03187 | south | N | 0.03187 | 0
80294 | PAPALOTE | 5 | 25 | -0.076752 | south | Y | -0.22634 | -0.03187 | -0.20217 | 0.091128 | 0.03187 | south | N | 0.03187 | 0
80294 | PAPALOTE | 6 | 25 | -0.076752 | south | Y | -0.22634 | -0.03187 | -0.20217 | 0.091128 | 0.03187 | south | N | 0.03187 | 0
80294 | PAPALOTE | 7 | 25 | -0.076752 | south | Y | -0.22634 | -0.03187 | -0.20217 | 0.091128 | 0.03187 | south | N | 0.03187 | 0
80294 | PAPALOTE | 8 | 15 | -0.076752 | south | Y | -0.22634 | -0.03187 | -0.20217 | 0.091128 | 0.03187 | south | N | 0.03187 | 0
86104 | CID-138 | EQ | 0 | -0.057461 | south | N | -0.20705 | -0.012579 | -0.18288 | 0.11042 | 0.012579 | south | N | 0.012579 | 0
86105 | CID-230 | EQ | 500 | -0.057461 | south | N | -0.20705 | -0.012579 | -0.18288 | 0.11042 | 0.012579 | south | N | 0.012579 | 0
86106 | CUF-230 | EQ | 500 | -0.057461 | south | N | -0.20705 | -0.012579 | -0.18288 | 0.11042 | 0.012579 | south | N | 0.012579 | 0
86107 | CUF-138 | EQ | 0 | -0.057461 | south | N | -0.20705 | -0.012579 | -0.18288 | 0.11042 | 0.012579 | south | N | 0.012579 | 0
88198 | BEEVILLE | F | 0 | -0.067676 | south | N | -0.21726 | -0.022794 | -0.19309 | 0.1002 | 0.022794 | south | N | 0.022794 | 0
88253 | HAMILTON | F | 0 | -0.00367 | south | N | -0.15325 | 0.041212 | -0.12908 | 0.16421 | 0.041212 | south | N | 0.041212 | 0
88299 | ZAPATA | F | 0 | -0.063925 | south | N | -0.21351 | -0.019043 | -0.18934 | 0.10395 | 0.019043 | south | N | 0.019043 | 0
88508 | FALFURRI | F | 0 | -0.070743 | south | N | -0.22033 | -0.025861 | -0.19616 | 0.097137 | 0.025861 | south | N | 0.025861 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3391 Jewett 44645 SNGLTN_3_ctg2 C:967 GIBN_CRE - 44645 SNGLTN_3 75 C:967 GIBN_CRE - 44645 SNGLTN_3 99 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 167.5578 | 855 | 0.36615 | 313.0581 | 855 | 313.0581
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 167.5578 | 855 | 0.36615 | 313.0581 | 1710 | 626.1162
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 29.8468 | 152.3 | 0.36615 | 55.7646 | 1862.3 | 681.8808
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 29.984 | 153 | 0.36615 | 56.0209 | 2015.3 | 737.9017 | Weighted Shift Factors
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.19262 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 89.1844 | 463 | 0.3628 | 167.9758 | 2478.3 | 905.8775 | North | 0.14958
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.18548 | north | 7 | N | N | Nnorth | Nnorth | 1 | 5.9354 | 0 | 0.35566 | 0 | 2478.3 | 905.8775 | Houston | -0.17018
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.35554 | 0 | 2478.3 | 905.8775 |  | 0.31976
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.35554 | 0 | 2478.3 | 905.8775
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.18536 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.1512 | 17 | 0.35554 | 6.0442 | 2495.3 | 911.9217 | Line Rating | 1290.45
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.35554 | 0 | 2495.3 | 911.9217 | Conc Gen | 2543.3
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.35554 | 0 | 2495.3 | 911.9217 | Weighted Imp. | 928.855
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.1826 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.7649 | 48 | 0.35278 | 16.9333 | 2543.3 | 928.855 | PTDF | 0.36522
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.1826 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.3997 | 46 | 0.35278 | 16.2278
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.1826 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 19.1732 | 105 | 0.35278 | 37.0417 |  |  | Concentration | 1.1422
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.1826 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 151.011 | 827 | 0.35278 | 291.7464
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.1826 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 149.5502 | 819 | 0.35278 | 288.9242
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.16249 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 99.9338 | 615 | 0.33267 | 204.5919
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.16249 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 95.384 | 587 | 0.33267 | 195.2772
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.16086 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2416 | 150.7 | 0.33104 | 49.8871
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.16086 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2899 | 151 | 0.33104 | 49.9864
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.16086 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.5366 | 177.4 | 0.33104 | 58.7258
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.16059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.3292 | 151.5 | 0.33076 | 50.1109
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.16059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.4577 | 152.3 | 0.33076 | 50.3755
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.16059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.5045 | 177.5 | 0.33076 | 58.7108
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.15601 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 28.3931 | 182 | 0.32618 | 59.3651
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.15601 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.5069 | 484 | 0.32618 | 157.872
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.15473 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.7367 | 50 | 0.32491 | 16.2455
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.15469 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.32487 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.7248 | 0 | 0.32372 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.961 | 0 | 0.32372 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.2642 | 0 | 0.32372 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 61.2649 | 0 | 0.32372 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.15289 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 120.0171 | 785 | 0.32306 | 253.6051
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.15289 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 121.546 | 795 | 0.32306 | 256.8357
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.15289 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 119.2526 | 780 | 0.32306 | 251.9898
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.14989 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.5747 | 224 | 0.32006 | 71.6941
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6523 | 161 | 0.31708 | 51.0507
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.0931 | 164 | 0.31708 | 52.0019
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.0931 | 164 | 0.31708 | 52.0019
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 60.8203 | 414 | 0.31708 | 131.2731
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.7993 | 162 | 0.31708 | 51.3677
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6523 | 161 | 0.31708 | 51.0507
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.9462 | 163 | 0.31708 | 51.6848
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 60.0858 | 409 | 0.31708 | 129.6877
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14567 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 56.5215 | 388 | 0.31585 | 122.5497
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14567 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.0221 | 515 | 0.31585 | 162.6626
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.14555 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.9111 | 20 | 0.31573 | 6.3146
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.14555 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.6388 | 25 | 0.31573 | 7.8932
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.14555 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.9676 | 41 | 0.31573 | 12.9448
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.4782 | 79 | 0.31547 | 24.9221
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.4012 | 106 | 0.31547 | 33.4398
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 21.2129 | 146 | 0.31547 | 46.0586
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.0423 | 76 | 0.31547 | 23.9757
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.8115 | 40 | 0.31546 | 12.6186
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14525 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31542 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14525 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31542 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14514 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.9892 | 558 | 0.31532 | 175.9473
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14514 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 84.0372 | 579 | 0.31532 | 182.569
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14514 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 117.2747 | 808 | 0.31532 | 254.7768
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.145 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.8751 | 0 | 0.31518 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.145 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.5421 | 0 | 0.31518 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.145 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.8181 | 0 | 0.31518 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1798 | 160 | 0.31505 | 50.408
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.6003 | 156 | 0.31505 | 49.1478
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.3953 | 196 | 0.31505 | 61.7498
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.6003 | 156 | 0.31505 | 49.1478
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7452 | 157 | 0.31505 | 49.4628
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.6851 | 198 | 0.31505 | 62.3799
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14472 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 53.5449 | 370 | 0.31489 | 116.51
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.2602 | 0 | 0.31489 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.405 | 0 | 0.31489 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.7172 | 0 | 0.31489 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.6944 | 0 | 0.31489 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.8391 | 0 | 0.31489 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.862 | 0 | 0.31489 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14438 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 24.5453 | 170 | 0.31456 | 53.4752
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14438 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.0797 | 520 | 0.31456 | 163.5711
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14411 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.7644 | 0 | 0.31429 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14411 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.7644 | 0 | 0.31429 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14361 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31379 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14346 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.9283 | 118 | 0.31364 | 37.009
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14346 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.4979 | 115 | 0.31364 | 36.0681
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14346 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 79.7638 | 556 | 0.31364 | 174.3815
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14325 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31343 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.9833 | 196 | 0.31295 | 61.3378
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.8477 | 111 | 0.31295 | 34.7372
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14058 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4345 | 60 | 0.31075 | 18.645
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14058 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.8562 | 63 | 0.31075 | 19.5773
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.1389 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.6258 | 112.5 | 0.30907 | 34.7706
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.13862 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 60.298 | 435 | 0.30879 | 134.3244
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.13825 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.6076 | 395 | 0.30842 | 121.827
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.13825 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 60.1374 | 435 | 0.30842 | 134.1639
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.13809 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30827 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.13809 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30827 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.13809 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30827 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.13749 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.7537 | 216.4 | 0.30767 | 66.5797
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.13749 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.7125 | 216.1 | 0.30767 | 66.4874
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.13654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 39.3238 | 288 | 0.30672 | 88.3344
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.13654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.0715 | 147 | 0.30672 | 45.0874
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.13654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.0715 | 147 | 0.30672 | 45.0874
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.4297 | 224 | 0.30602 | 68.5491
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.7014 | 226 | 0.30602 | 69.1612
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.7996 | 212 | 0.30602 | 64.8768
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.6637 | 211 | 0.30602 | 64.5708
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.13577 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.6973 | 204 | 0.30595 | 62.4131
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.13577 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.29 | 201 | 0.30595 | 61.4953
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.13577 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.8566 | 242 | 0.30595 | 74.0391
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.13562 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3058 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.13528 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.397 | 217.3 | 0.30546 | 66.3762
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.13528 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.733 | 205 | 0.30546 | 62.6191
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.13528 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 36.8511 | 272.4 | 0.30546 | 83.207
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.13491 | north | 3 | N | N | Nnorth | Nnorth | 1 | 156.0909 | 0 | 0.30509 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.13491 | north | 3 | N | N | Nnorth | Nnorth | 1 | 156.2258 | 0 | 0.30509 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.13457 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4223 | 18 | 0.30475 | 5.4855
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.13457 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4223 | 18 | 0.30475 | 5.4855
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.13457 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.1138 | 38 | 0.30475 | 11.5805
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6751 | 20 | 0.30393 | 6.0786
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6751 | 20 | 0.30393 | 6.0786
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6751 | 20 | 0.30393 | 6.0786
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2738 | 17 | 0.30393 | 5.1668
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.1336 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.8965 | 366 | 0.30377 | 111.1808
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13342 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6011 | 0 | 0.3036 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13342 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6011 | 0 | 0.3036 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.3365 | 70 | 0.30355 | 21.2488
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.2032 | 69 | 0.30355 | 20.9453
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.2032 | 69 | 0.30355 | 20.9453
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.0698 | 68 | 0.30355 | 20.6417
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.13322 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.9859 | 120 | 0.30339 | 36.407
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.13267 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 32.1066 | 242 | 0.30285 | 73.2892
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.13203 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1815 | 168 | 0.30221 | 50.7711
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.13203 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.883 | 90 | 0.30221 | 27.1988
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13168 | west | 4 | Y | N | Ywest | Nwest | 1 | 85.5551 | 649.7 | 0.30186 | 196.1183
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.13149 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.5988 | 73 | 0.30167 | 22.0216
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.13149 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.6473 | 119 | 0.30167 | 35.8982
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.13149 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.9554 | 205 | 0.30167 | 61.8415
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.13149 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.412 | 102 | 0.30167 | 30.7699
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.13149 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.623 | 96 | 0.30167 | 28.9599
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13097 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.6101 | 165 | 0.30115 | 49.6891
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13014 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.7133 | 236 | 0.30032 | 70.8748
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13014 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.0544 | 400 | 0.30031 | 120.1247
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.12869 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7212 | 60 | 0.29886 | 17.9317
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1569 | 150 | 0.29789 | 44.6833
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.692 | 209 | 0.29789 | 62.2588
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1557 | 126.5 | 0.29789 | 37.6829
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.8005 | 249 | 0.29789 | 74.1743
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.1595 | 197 | 0.29789 | 58.6841
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7846 | 37.5 | 0.29777 | 11.1662
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7159 | 107.5 | 0.29777 | 32.0098
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2247 | 135 | 0.29777 | 40.1984
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1832 | 119 | 0.29777 | 35.4341
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.397 | 105 | 0.29777 | 31.2654
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.271 | 80.5 | 0.29777 | 23.9701
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12722 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9026 | 125 | 0.2974 | 37.1746
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12722 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9026 | 125 | 0.2974 | 37.1746
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12701 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0523 | 150 | 0.29719 | 44.5786
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12701 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8285 | 101 | 0.29719 | 30.0163
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12697 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6653 | 84 | 0.29714 | 24.9601
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.1268 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5531 | 99 | 0.29697 | 29.4005
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.1268 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7347 | 61 | 0.29697 | 18.1155
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.1268 | west | 7 | N | N | Nwest | Nwest | 1 | 3.17 | 0 | 0.29697 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.1268 | west | 7 | N | N | Nwest | Nwest | 1 | 5.7947 | 0 | 0.29697 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.1268 | west | 7 | N | N | Nwest | Nwest | 1 | 5.7947 | 0 | 0.29697 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8758 | 141 | 0.29695 | 41.8706
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2135 | 120 | 0.29695 | 35.6346
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9837 | 63 | 0.2969 | 18.7048
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3609 | 66 | 0.29686 | 19.5925
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7409 | 69 | 0.29686 | 20.483
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7409 | 69 | 0.29686 | 20.483
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4876 | 67 | 0.29686 | 19.8893
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4876 | 67 | 0.29686 | 19.8893
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2342 | 65 | 0.29686 | 19.2956
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.12666 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.5995 | 60 | 0.29683 | 17.8101
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9798 | 150 | 0.29671 | 44.5062
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.837 | 220 | 0.29671 | 65.2757
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.3064 | 200 | 0.29671 | 59.3416
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4243 | 121.9 | 0.29671 | 36.1687
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12632 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8427 | 0 | 0.2965 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12632 | west | 8 | N | N | Nwest | Nwest | 1 | 9.2722 | 0 | 0.2965 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12632 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8932 | 0 | 0.2965 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12631 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7351 | 180 | 0.29648 | 53.3667
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12631 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7351 | 180 | 0.29648 | 53.3667
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12624 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.4038 | 225 | 0.29641 | 66.6933
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12617 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1408 | 120 | 0.29635 | 35.5619
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12617 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.3983 | 233 | 0.29635 | 69.0493
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12617 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.4746 | 170.2 | 0.29635 | 50.4386
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12612 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1338 | 120 | 0.29629 | 35.5549
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12609 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1304 | 120 | 0.29626 | 35.5515
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12568 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2426 | 0 | 0.29586 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12562 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.9067 | 214.2 | 0.29579 | 63.3584
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.609 | 100.5 | 0.29564 | 29.7117
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12544 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2756 | 58 | 0.29562 | 17.1458
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7787 | 70 | 0.29559 | 20.691
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7787 | 70 | 0.29559 | 20.691
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.638 | 92.8 | 0.29559 | 27.4304
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0328 | 80 | 0.29559 | 23.6469
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0328 | 80 | 0.29559 | 23.6469
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.4222 | 115 | 0.29559 | 33.9924
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.1077 | 208.2 | 0.29557 | 61.5383
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.8189 | 142.1 | 0.29557 | 42.0009
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.6026 | 132.4 | 0.29557 | 39.1338
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.054 | 136 | 0.29557 | 40.1979
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.4334 | 147 | 0.29557 | 43.4492
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.3334 | 210 | 0.29557 | 62.0703
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12539 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.8085 | 150 | 0.29557 | 44.3349
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0748 | 112.5 | 0.29528 | 33.2195
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.7038 | 149.5 | 0.29528 | 44.1451
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.2703 | 186 | 0.29528 | 54.923
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.8359 | 214.5 | 0.29528 | 63.3386
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12476 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8234 | 6.6 | 0.29493 | 1.9466
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12476 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2792 | 34.3 | 0.29493 | 10.1162
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.1244 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5355 | 149 | 0.29457 | 43.8916
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12423 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.057 | 169.5 | 0.29441 | 49.9018
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12418 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3463 | 35 | 0.29436 | 10.3025
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12418 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7254 | 30 | 0.29436 | 8.8307
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1917 | 66 | 0.29429 | 19.4233
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0676 | 65 | 0.29429 | 19.129
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3158 | 67 | 0.29429 | 19.7176
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3158 | 67 | 0.29429 | 19.7176
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3158 | 67 | 0.29429 | 19.7176
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12412 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29429 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12412 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29429 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11942 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.57321 | 0 | 0.28959 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11747 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3979 | 80 | 0.28765 | 23.012
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11747 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3979 | 80 | 0.28765 | 23.012
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11695 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7712 | 75 | 0.28712 | 21.5344
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11695 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3559 | 80 | 0.28712 | 22.97
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11695 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.678 | 40 | 0.28712 | 11.485
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11683 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3468 | 80 | 0.28701 | 22.9609
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11682 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3456 | 80 | 0.287 | 22.9597
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.11675 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.513 | 150 | 0.28693 | 43.0393
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.11675 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.513 | 150 | 0.28693 | 43.0393
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11413 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1306 | 80 | 0.28431 | 22.7446
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.11369 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6974 | 76.5 | 0.28387 | 21.7158
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.11325 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5127 | 84 | 0.28342 | 23.8075
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.10822 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6233 | 0 | 0.27839 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.10822 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6233 | 0 | 0.27839 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.10215 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.3222 | 150 | 0.27232 | 40.8486
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.10215 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.1718 | 80 | 0.27232 | 21.7859
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.099146 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.26932 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.09863 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.1506 | 255 | 0.26881 | 68.5455
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.09863 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.6959 | 149 | 0.26881 | 40.0521
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.09863 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 15.0904 | 153 | 0.26881 | 41.1273
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.094431 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26461 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.094431 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26461 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.094263 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26444 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.094263 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 74.185 | 787 | 0.26444 | 208.1133
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.089005 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3507 | 150 | 0.25918 | 38.8771
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.025271 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.19545 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17018 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17018 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -4.0901 | 100 | 0.12927 | 12.9275
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | 1 | -36.0631 | 0 | -0.063696 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | 1 | -36.484 | 0 | -0.063696 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | 1 | -36.484 | 0 | -0.063696 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | 1 | -88.8714 | 0 | -0.063696 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.026412 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.0284 | 569 | -0.12317 | -70.0852
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.026412 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.3454 | 581 | -0.12317 | -71.5633
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.005824 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10483 | 0 | -0.14376 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.005824 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10483 | 0 | -0.14376 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.005824 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08736 | 0 | -0.14376 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.004259 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.058348 | 0 | -0.14533 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14958 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14958 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.003109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.087052 | 0 | -0.15269 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.003109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.090161 | 0 | -0.15269 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.003465 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4622 | 422 | -0.15305 | -64.587
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.00367 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.12111 | 0 | -0.15325 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.00367 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.09175 | 0 | -0.15325 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.00367 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.15325 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.005063 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091134 | 0 | -0.15465 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.005063 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091134 | 0 | -0.15465 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.30397 | 0 | -0.15827 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29529 | 0 | -0.15827 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.30397 | 0 | -0.15827 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.43189 | 42 | -0.15987 | -6.7144
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.45245 | 44 | -0.15987 | -7.0342
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.45245 | 44 | -0.15987 | -7.0342
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4833 | 47 | -0.15987 | -7.5138
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.011394 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091152 | 0 | -0.16098 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.011394 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091152 | 0 | -0.16098 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.011591 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.5932 | 310 | -0.16118 | -49.9645
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.011591 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.7871 | 413 | -0.16118 | -66.5655
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.67047 | 49 | -0.16327 | -8.0001
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.62942 | 46 | -0.16327 | -7.5103
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.62942 | 46 | -0.16327 | -7.5103
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.6431 | 47 | -0.16327 | -7.6736
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.013683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1072 | 154 | -0.16327 | -25.1432
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.013683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.0251 | 148 | -0.16327 | -24.1636
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.65678 | 48 | -0.16327 | -7.8368
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.65678 | 48 | -0.16327 | -7.8368
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.018914 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11348 | 0 | -0.1685 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.020618 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1442 | 152.5 | -0.1702 | -25.9559
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.020618 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0824 | 149.5 | -0.1702 | -25.4453
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.020618 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.7957 | 232.6 | -0.1702 | -39.5891
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.021073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7816 | 132 | -0.17066 | -22.5268
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.021073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8238 | 134 | -0.17066 | -22.8681
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.021073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.8066 | 323 | -0.17066 | -55.1224
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.02246 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17204 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.023174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6615 | 158 | -0.17276 | -27.2959
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.023174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7078 | 160 | -0.17276 | -27.6414
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.023174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.0555 | 175 | -0.17276 | -30.2328
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.033402 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.20041 | 0 | -0.18299 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8895 | 50 | -0.18737 | -9.3687
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8895 | 50 | -0.18737 | -9.3687
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8895 | 50 | -0.18737 | -9.3687
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8895 | 50 | -0.18737 | -9.3687
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8196 | 223.9 | -0.18898 | -42.3116
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.863 | 225 | -0.18898 | -42.5195
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8472 | 224.6 | -0.18898 | -42.4439
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9299 | 226.7 | -0.18898 | -42.8408
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.6627 | 114 | -0.19049 | -21.7154
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.08 | 222 | -0.19049 | -42.2878
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.5258 | 184 | -0.19049 | -35.0494
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.1618 | 224 | -0.19049 | -42.6688
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7036 | 115 | -0.19049 | -21.9058
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.04108 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -23.9907 | 584 | -0.19066 | -111.3482
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.04108 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.4426 | 595 | -0.19066 | -113.4455
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.041221 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.8487 | 433 | -0.19081 | -82.6188
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.043263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10383 | 0 | -0.19285 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.043263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10383 | 0 | -0.19285 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.043263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.12114 | 0 | -0.19285 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.2744 | 142 | -0.19377 | -27.5154
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.407 | 145 | -0.19377 | -28.0967
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6721 | 151 | -0.19377 | -29.2594
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.8139 | 290 | -0.19377 | -56.1935
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.044693 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17877 | 0 | -0.19428 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.045917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1102 | 0 | -0.1955 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.045917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1102 | 0 | -0.1955 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1617 | 147 | -0.1983 | -29.1506
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7232 | 138 | -0.1983 | -27.3659
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8207 | 140 | -0.1983 | -27.7625
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1617 | 147 | -0.1983 | -29.1506
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8669 | 182 | -0.1983 | -36.0913
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.6464 | 198 | -0.1983 | -39.2641
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.049632 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -20.2002 | 407 | -0.19922 | -81.0812
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.049642 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8792 | 58 | -0.19923 | -11.5551
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.049642 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.4181 | 89 | -0.19923 | -17.7312
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1842 | 44 | -0.19923 | -8.766
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1842 | 44 | -0.19923 | -8.766
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1346 | 43 | -0.19923 | -8.5667
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2339 | 45 | -0.19923 | -8.9652
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.049696 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -20.4748 | 412 | -0.19928 | -82.1036
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.049696 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.8784 | 400 | -0.19928 | -79.7123
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.049722 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.0821 | 424 | -0.19931 | -84.506
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.049722 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.1319 | 425 | -0.19931 | -84.7053
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.04985 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.4186 | 209 | -0.19943 | -41.6818
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.04985 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.7676 | 216 | -0.19943 | -43.0779
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2931 | 46 | -0.19943 | -9.174
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.343 | 47 | -0.19943 | -9.3734
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2931 | 46 | -0.19943 | -9.174
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2931 | 46 | -0.19943 | -9.174
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.049918 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1995 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.049918 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1995 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.049918 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1995 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.050446 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2107 | 24 | -0.20003 | -4.8007
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.050446 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.2107 | 24 | -0.20003 | -4.8007
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.050446 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 23 | -0.20003 | -4.6007
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.05099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.9035 | 155 | -0.20057 | -31.0891
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.05099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.6683 | 170 | -0.20057 | -34.0977
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.05099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.9035 | 155 | -0.20057 | -31.0891
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.051978 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -28.38 | 546 | -0.20156 | -110.0532
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.051978 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -38.9835 | 750 | -0.20156 | -151.172
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.054635 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.65562 | 0 | -0.20422 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.057461 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.7461 | 100 | -0.20705 | -20.7046
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.057461 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.7461 | 100 | -0.20705 | -20.7046
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.057461 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.057461 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.057461 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.057461 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.057465 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.058198 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -23.0464 | 396 | -0.20778 | -82.2819
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.063925 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21351 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.067676 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21726 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.068268 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81922 | 0 | -0.21785 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.068268 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.75095 | 0 | -0.21785 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.068268 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81922 | 0 | -0.21785 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.070743 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.22033 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.071055 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -44.6936 | 629 | -0.22064 | -138.7823
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.072808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.6664 | 146.5 | -0.22239 | -32.5805
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.072808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7683 | 147.9 | -0.22239 | -32.8919
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.072808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5958 | 173 | -0.22239 | -38.4739
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.073555 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.2259 | 207 | -0.22314 | -46.1899
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.073555 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.9394 | 216.7 | -0.22314 | -48.3544
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.073555 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8003 | 242 | -0.22314 | -53.9998
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.07356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5926 | 144 | -0.22314 | -32.1328
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.07356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5926 | 144 | -0.22314 | -32.1328
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.07356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5788 | 171 | -0.22314 | -38.1577
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.07409 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.22367 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.07409 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8154 | 38 | -0.22367 | -8.4996
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.07409 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4299 | 19.3 | -0.22367 | -4.3169
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.07409 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.1114 | 15 | -0.22367 | -3.3551
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.07409 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4822 | 47 | -0.22367 | -10.5127
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9834 | 94 | -0.22388 | -21.0444
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.046 | 41 | -0.22388 | -9.1789
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8231 | 38 | -0.22388 | -8.5073
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4115 | 19 | -0.22388 | -4.2537
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9834 | 94 | -0.22388 | -21.0444
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6745 | 36 | -0.22388 | -8.0596
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1946 | 43 | -0.22388 | -9.6267
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6344 | 22 | -0.22388 | -4.9253
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.9952 | 148 | -0.22388 | -33.1337
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7146 | 50 | -0.22388 | -11.1938
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0861 | 55 | -0.22388 | -12.3132
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7146 | 50 | -0.22388 | -11.1938
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.074622 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.164 | 0 | -0.22421 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.075318 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8621 | 0 | -0.2249 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.075362 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8638 | 0 | -0.22495 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.075477 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8869 | 0 | -0.22506 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.075477 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8869 | 0 | -0.22506 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.075554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.235 | 334 | -0.22514 | -75.1963
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.075554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.6884 | 340 | -0.22514 | -76.5471
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.075554 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.5997 | 180 | -0.22514 | -40.525
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.075554 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.5997 | 180 | -0.22514 | -40.525
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.075828 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.649 | 180 | -0.22541 | -40.5743
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.075855 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2493 | 0 | -0.22544 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.075855 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2721 | 0 | -0.22544 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.075855 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.6058 | 0 | -0.22544 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.075872 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.493 | 336 | -0.22546 | -75.7534
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.075872 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.657 | 180 | -0.22546 | -40.5822
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 25 | -0.22634 | -5.6584
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 25 | -0.22634 | -5.6584
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 25 | -0.22634 | -5.6584
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.228 | 16 | -0.22634 | -3.6214
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 25 | -0.22634 | -5.6584
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 25 | -0.22634 | -5.6584
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 25 | -0.22634 | -5.6584
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1513 | 15 | -0.22634 | -3.395
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -12.2199 | 0 | -0.22693 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.8332 | 0 | -0.22693 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.7341 | 0 | -0.22693 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2144 | 0 | -0.22693 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.3691 | 0 | -0.22693 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.8223 | 0 | -0.22693 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.077341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.92809 | 0 | -0.22693 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.077717 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.1912 | 144 | -0.2273 | -32.7314
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.077717 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.6108 | 188 | -0.2273 | -42.7327
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7713 | 47.7 | -0.22865 | -10.9064
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.949 | 37.3 | -0.22865 | -8.5285
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6369 | 46 | -0.22865 | -10.5177
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.795 | 48 | -0.22865 | -10.975
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.079114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7753 | 0 | -0.2287 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.079768 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.7549 | 22 | -0.22935 | -5.0458
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.079768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.87745 | 11 | -0.22935 | -2.5229
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.079768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.87745 | 11 | -0.22935 | -2.5229
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.081495 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2224 | 0 | -0.23108 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.081495 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8744 | 0 | -0.23108 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.082337 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.6587 | 0 | -0.23192 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.3208 | 0 | -0.23247 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5802 | 0 | -0.23247 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2326 | 0 | -0.23247 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2433 | 0 | -0.23247 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5802 | 0 | -0.23247 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2433 | 0 | -0.23247 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2326 | 0 | -0.23247 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2326 | 0 | -0.23247 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.086393 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.1469 | 0 | -0.23598 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.9088 | 0 | -0.23704 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -7.0837 | 0 | -0.23704 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.9088 | 0 | -0.23704 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.9962 | 0 | -0.23704 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.8563 | 0 | -0.23704 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1863 | 0 | -0.23704 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.0228 | 0 | -0.23704 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4487 | 0 | -0.23704 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.813 | 0 | -0.23704 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.4715 | 0 | -0.23704 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.12539 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -167.1422 | 0 | -0.27497 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.12539 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -166.5153 | 0 | -0.27497 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5832 | 76 | -0.27568 | -20.9517
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5832 | 76 | -0.27568 | -20.9517
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -13.24 | 105 | -0.27568 | -28.9464
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.331 | 74 | -0.27568 | -20.4003
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.331 | 74 | -0.27568 | -20.4003
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -12.8617 | 102 | -0.27568 | -28.1193
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.1302 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.5934 | 66 | -0.27979 | -18.466
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.9226 | 0 | -0.2935 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2754 | 0 | -0.2935 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4761 | 0 | -0.2935 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.5352 | 0 | -0.2935 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.3765 | 0 | -0.2935 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6643 | 0 | -0.2935 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1956 | 0 | -0.2935 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5904 | 0 | -0.2935 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.5278 | 0 | -0.2935 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0739 | 0 | -0.2935 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0665 | 0 | -0.2935 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.3617 | 0 | -0.2935 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3256 | 0 | -0.2935 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.5352 | 0 | -0.2935 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.9596 | 0 | -0.2935 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.823 | 0 | -0.2935 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9374 | 0 | -0.2935 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.513 | 0 | -0.2935 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.513 | 0 | -0.2935 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.6091 | 0 | -0.2935 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.14723 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4531 | 0 | -0.29681 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.14723 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4723 | 0 | -0.29681 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.6351 | 0 | -0.29945 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.6351 | 0 | -0.29945 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.8341 | 0 | -0.29945 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.4103 | 0 | -0.29945 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.1593 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3439 | 0 | -0.30889 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.15971 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -103.9693 | 651 | -0.30929 | -201.3489
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.15971 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -90.0747 | 564 | -0.30929 | -174.4405
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.15971 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -95.8242 | 600 | -0.30929 | -185.575
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.15979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.0451 | 0 | -0.30937 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.15979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.0451 | 0 | -0.30937 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.15979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -39.1476 | 0 | -0.30937 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.16071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3035 | 0 | -0.3103 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.16123 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.9585 | 161 | -0.31082 | -50.0416
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.16123 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.7647 | 166 | -0.31082 | -51.5957
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.16123 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -39.9858 | 248 | -0.31082 | -77.0828
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.16123 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -88.0332 | 546 | -0.31082 | -169.7064
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.16123 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -103.6728 | 0 | -0.31082 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.16123 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.096 | 13 | -0.31082 | -4.0406
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.6601 | 0 | -0.31569 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.431 | 0 | -0.31569 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.0588 | 0 | -0.31569 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.9425 | 0 | -0.31569 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.1661 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3153 | 0 | -0.31569 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.1661 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9831 | 0 | -0.31569 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7619 | 0 | -0.31571 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0808 | 0 | -0.31571 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8048 | 0 | -0.31571 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.451 | 0 | -0.31571 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.5008 | 0 | -0.31571 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.3014 | 0 | -0.31571 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.9484 | 0 | -0.31571 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -40.5355 | 0 | -0.31571 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6452 | 0 | -0.31571 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.16819 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.4094 | 50 | -0.31777 | -15.8887
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.16974 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.31933 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.6146 | 0 | -0.32117 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.0312 | 0 | -0.32117 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.9282 | 0 | -0.32117 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3516 | 0 | -0.32117 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0934 | 0 | -0.32117 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2003 | 0 | -0.3219 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3387 | 0 | -0.3219 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2003 | 0 | -0.3219 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2003 | 0 | -0.3219 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.9768 | 46 | -0.32299 | -14.8577
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.9768 | 46 | -0.32299 | -14.8577
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.9768 | 46 | -0.32299 | -14.8577
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.5375 | 55 | -0.32299 | -17.7647
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.5375 | 55 | -0.32299 | -17.7647
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.3641 | 54 | -0.32299 | -17.4417
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.17366 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.5452 | 0 | -0.32324 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.17366 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.8926 | 0 | -0.32324 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.4002 | 0 | -0.32361 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.3387 | 0 | -0.32361 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.4083 | 0 | -0.32361 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.3213 | 0 | -0.32361 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -46.8116 | 0 | -0.32361 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.17433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1016 | 0 | -0.32392 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.17465 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0958 | 12 | -0.32424 | -3.8909
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.17465 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32424 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.17467 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.5194 | 169 | -0.32426 | -54.7992
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.1747 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -28.8248 | 165 | -0.32428 | -53.5063
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.17472 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.0327 | 0 | -0.3243 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.17472 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.374 | 0 | -0.3243 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.17478 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -37.2286 | 213 | -0.32437 | -69.0901
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.17479 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8316 | 0 | -0.32437 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.1869 | 0 | -0.32438 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0471 | 0 | -0.32438 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.4381 | 0 | -0.32438 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.865 | 0 | -0.32438 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.17481 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -39.8562 | 228 | -0.32439 | -73.9615
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.17482 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -31.4676 | 0 | -0.3244 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.17482 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.7265 | 0 | -0.3244 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.17482 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.4467 | 0 | -0.3244 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.4445 | 0 | -0.32486 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6197 | 0 | -0.32486 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8357 | 0 | -0.32486 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2582 | 0 | -0.32486 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.9365 | 0 | -0.32559 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.3942 | 42 | -0.32564 | -13.6768
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.3942 | 42 | -0.32564 | -13.6768
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.69 | 38 | -0.32564 | -12.3742
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.69 | 38 | -0.32564 | -12.3742
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.17625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.4906 | 0 | -0.32583 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.17625 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.7932 | 0 | -0.32583 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -18.4515 | 104 | -0.327 | -34.0083
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -18.4515 | 104 | -0.327 | -34.0083
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5806 | 54 | -0.327 | -17.6581
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4032 | 53 | -0.327 | -17.3311
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5806 | 54 | -0.327 | -17.6581
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.1128 | 57 | -0.327 | -18.6392
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5806 | 54 | -0.327 | -17.6581
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5806 | 54 | -0.327 | -17.6581
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.2902 | 58 | -0.327 | -18.9662
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.2902 | 58 | -0.327 | -18.9662
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.17784 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -130.7131 | 735 | -0.32743 | -240.6579
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0567 | 0 | -0.32772 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1814 | 0 | -0.32772 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8251 | 0 | -0.32772 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1766 | 0 | -0.32772 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1531 | 0 | -0.32772 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.634 | 0 | -0.32772 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.545 | 0 | -0.32772 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2349 | 0 | -0.32772 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2065 | 0 | -0.32772 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.2131 | 0 | -0.32772 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.3646 | 0 | -0.32772 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.17854 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1424 | 12 | -0.32812 | -3.9374
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.179 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.895 | 0 | -0.32858 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.179 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.759 | 0 | -0.32858 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.6357 | 0 | -0.3286 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.8147 | 0 | -0.3286 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5308 | 0 | -0.3286 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.2777 | 0 | -0.3286 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0987 | 0 | -0.3286 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -18.6171 | 0 | -0.3286 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5616 | 0 | -0.3286 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.17903 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -2.1484 | 12 | -0.32861 | -3.9434
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.17906 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -133.0431 | 743 | -0.32865 | -244.1845
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.17929 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.1487 | 0 | -0.32888 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.17943 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -30.8618 | 172 | -0.32901 | -56.5903
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.17943 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -30.8618 | 172 | -0.32901 | -56.5903
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.17943 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -30.8618 | 172 | -0.32901 | -56.5903
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.3517 | 0 | -0.32988 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.0993 | 0 | -0.32988 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.6486 | 0 | -0.32988 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -48.5349 | 0 | -0.32988 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.1806 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -71.8792 | 398 | -0.33019 | -131.4139
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.1433 | 56 | -0.33071 | -18.52
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.6867 | 59 | -0.33071 | -19.5122
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.1433 | 56 | -0.33071 | -18.52
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.1433 | 56 | -0.33071 | -18.52
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.6867 | 59 | -0.33071 | -19.5122
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.1433 | 56 | -0.33071 | -18.52
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.2143 | 0 | -0.33579 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.0488 | 0 | -0.33579 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.6763 | 0 | -0.33579 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.6763 | 0 | -0.33579 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.18621 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.166 | 0 | -0.33579 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3391 Jewett 44645 SNGLTN_3_ctg2 C:967 GIBN_CRE - 44645 SNGLTN_3 75 C:967 GIBN_CRE - 44645 SNGLTN_3 99 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.2143 | 0 | -0.33579 | 0 | 0 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.0488 | 0 | -0.33579 | 0 | 0 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.6763 | 0 | -0.33579 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18621 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.6763 | 0 | -0.33579 | 0 | 0 | 0 | Weighted Shift Factors
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.18621 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.166 | 0 | -0.33579 | 0 | 0 | 0 | North | 0.14958
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.1433 | 56 | -0.33071 | -18.52 | 56 | 18.52 | Houston | -0.17018
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.6867 | 59 | -0.33071 | -19.5122 | 115 | 38.0322 |  | 0.31976
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.1433 | 56 | -0.33071 | -18.52 | 171 | 56.5522
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.1433 | 56 | -0.33071 | -18.52 | 227 | 75.0722 | Line Rating | 1290.45
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.6867 | 59 | -0.33071 | -19.5122 | 286 | 94.5844 | Conc Gen | 2011
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.18113 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.1433 | 56 | -0.33071 | -18.52 | 342 | 113.1044 | Weighted Imp. | 662.4113
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.1806 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -71.8792 | 398 | -0.33019 | -131.4139 | 740 | 244.5183 | PTDF | 0.32939
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.3517 | 0 | -0.32988 | 0 | 740 | 244.5183
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.0993 | 0 | -0.32988 | 0 | 740 | 244.5183 | Concentration | 1.0301
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.6486 | 0 | -0.32988 | 0 | 740 | 244.5183
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.18029 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -48.5349 | 0 | -0.32988 | 0 | 740 | 244.5183
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.17943 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -30.8618 | 172 | -0.32901 | -56.5903 | 912 | 301.1086
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.17943 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -30.8618 | 172 | -0.32901 | -56.5903 | 1084 | 357.699
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.17943 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -30.8618 | 172 | -0.32901 | -56.5903 | 1256 | 414.2893
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.17929 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.1487 | 0 | -0.32888 | 0 | 1256 | 414.2893
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.17906 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -133.0431 | 743 | -0.32865 | -244.1845 | 1999 | 658.4738
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.17903 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -2.1484 | 0 | -0.32861 | 0 | 1999 | 658.4738
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.6357 | 0 | -0.3286 | 0 | 1999 | 658.4738
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.8147 | 0 | -0.3286 | 0 | 1999 | 658.4738
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5308 | 0 | -0.3286 | 0 | 1999 | 658.4738
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.2777 | 0 | -0.3286 | 0 | 1999 | 658.4738
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0987 | 0 | -0.3286 | 0 | 1999 | 658.4738
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -18.6171 | 0 | -0.3286 | 0 | 1999 | 658.4738
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.17901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5616 | 0 | -0.3286 | 0 | 1999 | 658.4738
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.179 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.895 | 0 | -0.32858 | 0 | 1999 | 658.4738
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.179 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.759 | 0 | -0.32858 | 0 | 1999 | 658.4738
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.17854 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1424 | 12 | -0.32812 | -3.9374 | 2011 | 662.4113
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0567 | 0 | -0.32772 | 0 | 2011 | 662.4113
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1814 | 0 | -0.32772 | 0 | 2011 | 662.4113
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8251 | 0 | -0.32772 | 0 | 2011 | 662.4113
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1766 | 0 | -0.32772 | 0 | 2011 | 662.4113
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1531 | 0 | -0.32772 | 0 | 2011 | 662.4113
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.634 | 0 | -0.32772 | 0 | 2011 | 662.4113
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.545 | 0 | -0.32772 | 0 | 2011 | 662.4113
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2349 | 0 | -0.32772 | 0 | 2011 | 662.4113
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2065 | 0 | -0.32772 | 0 | 2011 | 662.4113
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.2131 | 0 | -0.32772 | 0 | 2011 | 662.4113
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.17814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.3646 | 0 | -0.32772 | 0 | 2011 | 662.4113
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.17784 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -130.7131 | 735 | -0.32743 | -240.6579
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -18.4515 | 104 | -0.327 | -34.0083
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -18.4515 | 104 | -0.327 | -34.0083
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5806 | 54 | -0.327 | -17.6581
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4032 | 53 | -0.327 | -17.3311
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5806 | 54 | -0.327 | -17.6581
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.1128 | 57 | -0.327 | -18.6392
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5806 | 54 | -0.327 | -17.6581
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5806 | 54 | -0.327 | -17.6581
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.2902 | 58 | -0.327 | -18.9662
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.17742 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.2902 | 58 | -0.327 | -18.9662
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.17625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.4906 | 0 | -0.32583 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.17625 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.7932 | 0 | -0.32583 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.3942 | 42 | -0.32564 | -13.6768
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.3942 | 42 | -0.32564 | -13.6768
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.69 | 38 | -0.32564 | -12.3742
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.17605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.69 | 38 | -0.32564 | -12.3742
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.9365 | 0 | -0.32559 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.4445 | 0 | -0.32486 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6197 | 0 | -0.32486 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8357 | 0 | -0.32486 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.17527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2582 | 0 | -0.32486 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.17482 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -31.4676 | 0 | -0.3244 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.17482 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.7265 | 0 | -0.3244 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.17482 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.4467 | 0 | -0.3244 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.17481 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -39.8562 | 228 | -0.32439 | -73.9615
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.1869 | 0 | -0.32438 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0471 | 0 | -0.32438 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.4381 | 0 | -0.32438 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.1748 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.865 | 0 | -0.32438 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.17479 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8316 | 0 | -0.32437 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.17478 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -37.2286 | 213 | -0.32437 | -69.0901
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.17472 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.0327 | 0 | -0.3243 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.17472 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.374 | 0 | -0.3243 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.1747 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -28.8248 | 165 | -0.32428 | -53.5063
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.17467 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.5194 | 169 | -0.32426 | -54.7992
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.17465 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0958 | 12 | -0.32424 | -3.8909
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.17465 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32424 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.17433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1016 | 0 | -0.32392 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.4002 | 0 | -0.32361 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.3387 | 0 | -0.32361 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.4083 | 0 | -0.32361 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.3213 | 0 | -0.32361 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.17402 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -46.8116 | 0 | -0.32361 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.17366 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.5452 | 0 | -0.32324 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.17366 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.8926 | 0 | -0.32324 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.9768 | 46 | -0.32299 | -14.8577
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.9768 | 46 | -0.32299 | -14.8577
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.9768 | 46 | -0.32299 | -14.8577
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.5375 | 55 | -0.32299 | -17.7647
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.5375 | 55 | -0.32299 | -17.7647
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.17341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.3641 | 54 | -0.32299 | -17.4417
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2003 | 0 | -0.3219 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3387 | 0 | -0.3219 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2003 | 0 | -0.3219 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.17231 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2003 | 0 | -0.3219 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.6146 | 0 | -0.32117 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.0312 | 0 | -0.32117 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.9282 | 0 | -0.32117 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3516 | 0 | -0.32117 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.17159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0934 | 0 | -0.32117 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.16974 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.31933 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.16819 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.4094 | 50 | -0.31777 | -15.8887
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7619 | 0 | -0.31571 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0808 | 0 | -0.31571 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8048 | 0 | -0.31571 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.451 | 0 | -0.31571 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.5008 | 0 | -0.31571 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.3014 | 0 | -0.31571 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.9484 | 0 | -0.31571 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.16613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -40.5355 | 0 | -0.31571 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.16613 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6452 | 0 | -0.31571 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.1661 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3153 | 0 | -0.31569 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.1661 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9831 | 0 | -0.31569 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.6601 | 0 | -0.31569 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.431 | 0 | -0.31569 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.0588 | 0 | -0.31569 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.1661 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.9425 | 0 | -0.31569 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.16123 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.9585 | 161 | -0.31082 | -50.0416
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.16123 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.7647 | 166 | -0.31082 | -51.5957
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.16123 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -39.9858 | 248 | -0.31082 | -77.0828
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.16123 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -88.0332 | 546 | -0.31082 | -169.7064
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.16123 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -103.6728 | 0 | -0.31082 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.16123 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.096 | 13 | -0.31082 | -4.0406
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.16071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3035 | 0 | -0.3103 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.15979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.0451 | 0 | -0.30937 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.15979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.0451 | 0 | -0.30937 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.15979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -39.1476 | 0 | -0.30937 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.15971 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -103.9693 | 0 | -0.30929 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.15971 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -90.0747 | 0 | -0.30929 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.15971 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -95.8242 | 0 | -0.30929 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.1593 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3439 | 0 | -0.30889 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.6351 | 0 | -0.29945 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.6351 | 0 | -0.29945 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.8341 | 0 | -0.29945 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.14987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.4103 | 0 | -0.29945 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.14723 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4531 | 0 | -0.29681 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.14723 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4723 | 0 | -0.29681 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.9226 | 0 | -0.2935 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2754 | 0 | -0.2935 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4761 | 0 | -0.2935 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.5352 | 0 | -0.2935 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.3765 | 0 | -0.2935 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6643 | 0 | -0.2935 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1956 | 0 | -0.2935 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5904 | 0 | -0.2935 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.5278 | 0 | -0.2935 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0739 | 0 | -0.2935 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0665 | 0 | -0.2935 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.3617 | 0 | -0.2935 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3256 | 0 | -0.2935 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.5352 | 0 | -0.2935 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.9596 | 0 | -0.2935 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.823 | 0 | -0.2935 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9374 | 0 | -0.2935 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.513 | 0 | -0.2935 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.513 | 0 | -0.2935 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.14391 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.6091 | 0 | -0.2935 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.1302 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.5934 | 66 | -0.27979 | -18.466
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5832 | 76 | -0.27568 | -20.9517
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5832 | 76 | -0.27568 | -20.9517
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -13.24 | 105 | -0.27568 | -28.9464
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.331 | 74 | -0.27568 | -20.4003
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.331 | 74 | -0.27568 | -20.4003
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.1261 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -12.8617 | 102 | -0.27568 | -28.1193
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.12539 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -167.1422 | 0 | -0.27497 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.12539 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -166.5153 | 0 | -0.27497 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.9088 | 0 | -0.23704 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -7.0837 | 0 | -0.23704 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.9088 | 0 | -0.23704 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.9962 | 0 | -0.23704 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.8563 | 0 | -0.23704 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1863 | 0 | -0.23704 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.0228 | 0 | -0.23704 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4487 | 0 | -0.23704 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.813 | 0 | -0.23704 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.087453 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.4715 | 0 | -0.23704 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.086393 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.1469 | 0 | -0.23598 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.3208 | 0 | -0.23247 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5802 | 0 | -0.23247 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2326 | 0 | -0.23247 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2433 | 0 | -0.23247 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5802 | 0 | -0.23247 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2433 | 0 | -0.23247 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2326 | 0 | -0.23247 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.082886 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2326 | 0 | -0.23247 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.082337 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.6587 | 0 | -0.23192 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.081495 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2224 | 0 | -0.23108 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.081495 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8744 | 0 | -0.23108 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.079768 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.7549 | 22 | -0.22935 | -5.0458
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.079768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.87745 | 11 | -0.22935 | -2.5229
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.079768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.87745 | 11 | -0.22935 | -2.5229
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.079114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7753 | 0 | -0.2287 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7713 | 47.7 | -0.22865 | -10.9064
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.949 | 37.3 | -0.22865 | -8.5285
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6369 | 46 | -0.22865 | -10.5177
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.079062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.795 | 48 | -0.22865 | -10.975
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.077717 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.1912 | 144 | -0.2273 | -32.7314
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.077717 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.6108 | 188 | -0.2273 | -42.7327
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -12.2199 | 0 | -0.22693 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.8332 | 0 | -0.22693 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.7341 | 0 | -0.22693 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2144 | 0 | -0.22693 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.3691 | 0 | -0.22693 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.077341 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.8223 | 0 | -0.22693 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.077341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.92809 | 0 | -0.22693 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 0 | -0.22634 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 0 | -0.22634 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 0 | -0.22634 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.228 | 0 | -0.22634 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 0 | -0.22634 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 0 | -0.22634 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9188 | 0 | -0.22634 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.076752 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1513 | 0 | -0.22634 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.075872 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.493 | 336 | -0.22546 | -75.7534
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.075872 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.657 | 180 | -0.22546 | -40.5822
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.075855 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2493 | 0 | -0.22544 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.075855 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2721 | 0 | -0.22544 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.075855 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.6058 | 0 | -0.22544 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.075828 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.649 | 180 | -0.22541 | -40.5743
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.075554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.235 | 334 | -0.22514 | -75.1963
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.075554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.6884 | 340 | -0.22514 | -76.5471
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.075554 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.5997 | 180 | -0.22514 | -40.525
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.075554 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.5997 | 180 | -0.22514 | -40.525
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.075477 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8869 | 0 | -0.22506 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.075477 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8869 | 0 | -0.22506 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.075362 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8638 | 0 | -0.22495 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.075318 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8621 | 0 | -0.2249 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.074622 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.164 | 0 | -0.22421 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9834 | 0 | -0.22388 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.046 | 0 | -0.22388 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8231 | 0 | -0.22388 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4115 | 0 | -0.22388 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9834 | 0 | -0.22388 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6745 | 0 | -0.22388 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1946 | 0 | -0.22388 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6344 | 0 | -0.22388 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.9952 | 0 | -0.22388 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7146 | 0 | -0.22388 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0861 | 0 | -0.22388 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.074292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7146 | 0 | -0.22388 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.07409 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8154 | 38 | -0.22367 | -8.4996
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.07409 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4299 | 19.3 | -0.22367 | -4.3169
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.07409 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.1114 | 15 | -0.22367 | -3.3551
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.07409 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4822 | 47 | -0.22367 | -10.5127
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.07409 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.22367 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.07356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5926 | 144 | -0.22314 | -32.1328
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.07356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5926 | 144 | -0.22314 | -32.1328
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.07356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5788 | 171 | -0.22314 | -38.1577
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.073555 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.2259 | 207 | -0.22314 | -46.1899
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.073555 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.9394 | 216.7 | -0.22314 | -48.3544
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.073555 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8003 | 242 | -0.22314 | -53.9998
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.072808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.6664 | 146.5 | -0.22239 | -32.5805
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.072808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7683 | 147.9 | -0.22239 | -32.8919
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.072808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5958 | 173 | -0.22239 | -38.4739
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.071055 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -44.6936 | 0 | -0.22064 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.070743 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.22033 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.068268 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81922 | 0 | -0.21785 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.068268 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.75095 | 0 | -0.21785 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.068268 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81922 | 0 | -0.21785 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.067676 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21726 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.063925 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21351 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.058198 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -23.0464 | 0 | -0.20778 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.057465 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.057461 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.7461 | 100 | -0.20705 | -20.7046
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.057461 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.7461 | 100 | -0.20705 | -20.7046
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.057461 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.057461 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.057461 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.057461 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20705 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.054635 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.65562 | 0 | -0.20422 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.051978 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -28.38 | 0 | -0.20156 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.051978 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -38.9835 | 0 | -0.20156 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.05099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.9035 | 155 | -0.20057 | -31.0891
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.05099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.6683 | 170 | -0.20057 | -34.0977
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.05099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.9035 | 155 | -0.20057 | -31.0891
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.050446 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2107 | 24 | -0.20003 | -4.8007
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.050446 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.2107 | 24 | -0.20003 | -4.8007
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.050446 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 23 | -0.20003 | -4.6007
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.049918 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1995 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.049918 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1995 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.049918 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1995 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.04985 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.4186 | 209 | -0.19943 | -41.6818
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.04985 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.7676 | 216 | -0.19943 | -43.0779
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2931 | 46 | -0.19943 | -9.174
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.343 | 47 | -0.19943 | -9.3734
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2931 | 46 | -0.19943 | -9.174
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.04985 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2931 | 46 | -0.19943 | -9.174
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.049722 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.0821 | 0 | -0.19931 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.049722 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.1319 | 0 | -0.19931 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.049696 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -20.4748 | 412 | -0.19928 | -82.1036
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.049696 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.8784 | 400 | -0.19928 | -79.7123
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.049642 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8792 | 58 | -0.19923 | -11.5551
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.049642 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.4181 | 89 | -0.19923 | -17.7312
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1842 | 44 | -0.19923 | -8.766
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1842 | 44 | -0.19923 | -8.766
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1346 | 43 | -0.19923 | -8.5667
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.049642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2339 | 45 | -0.19923 | -8.9652
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.049632 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -20.2002 | 407 | -0.19922 | -81.0812
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.048733 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.40936 | 8.4 | -0.19832 | -1.6659
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1617 | 147 | -0.1983 | -29.1506
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7232 | 138 | -0.1983 | -27.3659
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8207 | 140 | -0.1983 | -27.7625
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1617 | 147 | -0.1983 | -29.1506
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8669 | 182 | -0.1983 | -36.0913
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.048719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.6464 | 198 | -0.1983 | -39.2641
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.045917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1102 | 0 | -0.1955 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.045917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1102 | 0 | -0.1955 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.044693 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17877 | 0 | -0.19428 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.2744 | 142 | -0.19377 | -27.5154
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.407 | 145 | -0.19377 | -28.0967
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6721 | 151 | -0.19377 | -29.2594
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.044186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.8139 | 290 | -0.19377 | -56.1935
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.043263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10383 | 0 | -0.19285 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.043263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10383 | 0 | -0.19285 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.043263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.12114 | 0 | -0.19285 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.041221 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.8487 | 0 | -0.19081 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.04108 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -23.9907 | 0 | -0.19066 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.04108 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.4426 | 0 | -0.19066 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.6627 | 0 | -0.19049 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.08 | 0 | -0.19049 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.5258 | 0 | -0.19049 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.1618 | 0 | -0.19049 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7036 | 0 | -0.19049 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8196 | 223.9 | -0.18898 | -42.3116
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.863 | 225 | -0.18898 | -42.5195
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8472 | 224.6 | -0.18898 | -42.4439
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.039391 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9299 | 226.7 | -0.18898 | -42.8408
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8895 | 50 | -0.18737 | -9.3687
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8895 | 50 | -0.18737 | -9.3687
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8895 | 50 | -0.18737 | -9.3687
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.037789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8895 | 50 | -0.18737 | -9.3687
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.033402 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.20041 | 0 | -0.18299 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.023174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6615 | 158 | -0.17276 | -27.2959
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.023174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7078 | 160 | -0.17276 | -27.6414
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.023174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.0555 | 175 | -0.17276 | -30.2328
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.02246 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17204 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.021073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7816 | 132 | -0.17066 | -22.5268
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.021073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8238 | 134 | -0.17066 | -22.8681
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.021073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.8066 | 323 | -0.17066 | -55.1224
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.020618 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1442 | 152.5 | -0.1702 | -25.9559
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.020618 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0824 | 149.5 | -0.1702 | -25.4453
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.020618 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.7957 | 232.6 | -0.1702 | -39.5891
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.018914 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11348 | 0 | -0.1685 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.67047 | 49 | -0.16327 | -8.0001
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.62942 | 46 | -0.16327 | -7.5103
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.62942 | 46 | -0.16327 | -7.5103
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.6431 | 47 | -0.16327 | -7.6736
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.013683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1072 | 154 | -0.16327 | -25.1432
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.013683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.0251 | 148 | -0.16327 | -24.1636
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.65678 | 48 | -0.16327 | -7.8368
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.013683 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.65678 | 48 | -0.16327 | -7.8368
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.011591 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.5932 | 310 | -0.16118 | -49.9645
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.011591 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.7871 | 413 | -0.16118 | -66.5655
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.011394 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091152 | 0 | -0.16098 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.011394 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091152 | 0 | -0.16098 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.43189 | 42 | -0.15987 | -6.7144
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.45245 | 44 | -0.15987 | -7.0342
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.45245 | 44 | -0.15987 | -7.0342
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.010283 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4833 | 47 | -0.15987 | -7.5138
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.30397 | 0 | -0.15827 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29529 | 0 | -0.15827 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.30397 | 0 | -0.15827 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.005063 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091134 | 0 | -0.15465 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.005063 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091134 | 0 | -0.15465 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.00367 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.12111 | 0 | -0.15325 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.00367 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.09175 | 0 | -0.15325 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.00367 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.15325 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.003465 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4622 | 422 | -0.15305 | -64.587
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.003109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.087052 | 0 | -0.15269 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.003109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.090161 | 0 | -0.15269 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14958 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14958 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14958 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.004259 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.058348 | 0 | -0.14533 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.005824 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10483 | 0 | -0.14376 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.005824 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10483 | 0 | -0.14376 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.005824 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08736 | 0 | -0.14376 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.026412 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.0284 | 0 | -0.12317 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.026412 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.3454 | 0 | -0.12317 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | 1 | -36.0631 | 0 | -0.063696 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | 1 | -36.484 | 0 | -0.063696 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | 1 | -36.484 | 0 | -0.063696 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.23387 | north | 1 | N | N | Nnorth | Nnorth | 1 | -88.8714 | 0 | -0.063696 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.040901 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -4.0901 | 0 | 0.12927 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17018 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17018 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.025271 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.19545 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.089005 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3507 | 0 | 0.25918 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.094263 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26444 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.094263 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 74.185 | 787 | 0.26444 | 208.1133
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.094431 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26461 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.094431 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26461 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.09863 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.1506 | 255 | 0.26881 | 68.5455
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.09863 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.6959 | 149 | 0.26881 | 40.0521
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.09863 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 15.0904 | 153 | 0.26881 | 41.1273
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.099146 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.26932 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.10215 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.3222 | 150 | 0.27232 | 40.8486
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.10215 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.1718 | 80 | 0.27232 | 21.7859
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.10822 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6233 | 0 | 0.27839 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.10822 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6233 | 0 | 0.27839 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.11325 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5127 | 0 | 0.28342 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.11369 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6974 | 0 | 0.28387 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11413 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1306 | 0 | 0.28431 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.11675 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.513 | 0 | 0.28693 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.11675 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.513 | 0 | 0.28693 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11682 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3456 | 0 | 0.287 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11683 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3468 | 0 | 0.28701 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11695 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7712 | 0 | 0.28712 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11695 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3559 | 0 | 0.28712 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11695 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.678 | 0 | 0.28712 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11747 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3979 | 0 | 0.28765 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11747 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3979 | 0 | 0.28765 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11942 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.57321 | 0 | 0.28959 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1917 | 66 | 0.29429 | 19.4233
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0676 | 65 | 0.29429 | 19.129
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3158 | 67 | 0.29429 | 19.7176
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3158 | 67 | 0.29429 | 19.7176
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12412 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3158 | 67 | 0.29429 | 19.7176
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12412 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29429 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12412 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29429 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12418 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3463 | 0 | 0.29436 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12418 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7254 | 0 | 0.29436 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12423 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.057 | 0 | 0.29441 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.1244 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5355 | 0 | 0.29457 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12476 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8234 | 0 | 0.29493 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12476 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2792 | 0 | 0.29493 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0748 | 0 | 0.29528 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.7038 | 0 | 0.29528 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.2703 | 0 | 0.29528 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12511 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.8359 | 0 | 0.29528 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12539 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.8085 | 0 | 0.29557 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.1077 | 208.2 | 0.29557 | 61.5383
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.8189 | 142.1 | 0.29557 | 42.0009
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.6026 | 132.4 | 0.29557 | 39.1338
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.054 | 136 | 0.29557 | 40.1979
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.4334 | 147 | 0.29557 | 43.4492
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.1254 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.3334 | 210 | 0.29557 | 62.0703
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7787 | 70 | 0.29559 | 20.691
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7787 | 70 | 0.29559 | 20.691
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.638 | 92.8 | 0.29559 | 27.4304
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0328 | 80 | 0.29559 | 23.6469
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0328 | 80 | 0.29559 | 23.6469
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12541 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.4222 | 115 | 0.29559 | 33.9924
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12544 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2756 | 0 | 0.29562 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.609 | 0 | 0.29564 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12562 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.9067 | 0 | 0.29579 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12568 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2426 | 0 | 0.29586 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12609 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1304 | 0 | 0.29626 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12612 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1338 | 0 | 0.29629 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12617 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1408 | 0 | 0.29635 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12617 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.3983 | 0 | 0.29635 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12617 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.4746 | 0 | 0.29635 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12624 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.4038 | 0 | 0.29641 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12631 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7351 | 0 | 0.29648 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12631 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7351 | 0 | 0.29648 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12632 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8427 | 0 | 0.2965 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12632 | west | 8 | N | N | Nwest | Nwest | 1 | 9.2722 | 0 | 0.2965 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12632 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8932 | 0 | 0.2965 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9798 | 0 | 0.29671 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.837 | 0 | 0.29671 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.3064 | 0 | 0.29671 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4243 | 0 | 0.29671 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.12666 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.5995 | 0 | 0.29683 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3609 | 66 | 0.29686 | 19.5925
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7409 | 69 | 0.29686 | 20.483
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7409 | 69 | 0.29686 | 20.483
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4876 | 67 | 0.29686 | 19.8893
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4876 | 67 | 0.29686 | 19.8893
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12668 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2342 | 65 | 0.29686 | 19.2956
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9837 | 0 | 0.2969 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8758 | 0 | 0.29695 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2135 | 0 | 0.29695 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.1268 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5531 | 0 | 0.29697 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.1268 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7347 | 0 | 0.29697 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.1268 | west | 7 | N | N | Nwest | Nwest | 1 | 3.17 | 0 | 0.29697 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.1268 | west | 7 | N | N | Nwest | Nwest | 1 | 5.7947 | 0 | 0.29697 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.1268 | west | 7 | N | N | Nwest | Nwest | 1 | 5.7947 | 0 | 0.29697 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12697 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6653 | 0 | 0.29714 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12701 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0523 | 0 | 0.29719 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12701 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8285 | 0 | 0.29719 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12722 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9026 | 0 | 0.2974 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12722 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9026 | 0 | 0.2974 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7846 | 0 | 0.29777 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7159 | 0 | 0.29777 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2247 | 0 | 0.29777 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1832 | 0 | 0.29777 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.397 | 0 | 0.29777 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12759 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.271 | 0 | 0.29777 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.692 | 0 | 0.29789 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1557 | 0 | 0.29789 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.8005 | 0 | 0.29789 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.1595 | 0 | 0.29789 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1569 | 0 | 0.29789 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.12869 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7212 | 0 | 0.29886 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13014 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.0544 | 0 | 0.30031 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13014 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.7133 | 0 | 0.30032 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13097 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.6101 | 0 | 0.30115 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.13149 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.5988 | 73 | 0.30167 | 22.0216
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.13149 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.6473 | 119 | 0.30167 | 35.8982
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.13149 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.9554 | 205 | 0.30167 | 61.8415
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.13149 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.412 | 102 | 0.30167 | 30.7699
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.13149 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.623 | 96 | 0.30167 | 28.9599
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13168 | west | 4 | Y | N | Ywest | Nwest | 1 | 85.5551 | 0 | 0.30186 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.13203 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1815 | 168 | 0.30221 | 50.7711
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.13203 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.883 | 90 | 0.30221 | 27.1988
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.13267 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 32.1066 | 242 | 0.30285 | 73.2892
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.13322 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.9859 | 0 | 0.30339 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.3365 | 70 | 0.30355 | 21.2488
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.2032 | 69 | 0.30355 | 20.9453
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.2032 | 69 | 0.30355 | 20.9453
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.13338 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.0698 | 68 | 0.30355 | 20.6417
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13342 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6011 | 0 | 0.3036 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13342 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6011 | 0 | 0.3036 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.1336 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.8965 | 366 | 0.30377 | 111.1808
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6751 | 20 | 0.30393 | 6.0786
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6751 | 20 | 0.30393 | 6.0786
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6751 | 20 | 0.30393 | 6.0786
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.13375 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2738 | 17 | 0.30393 | 5.1668
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.13457 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4223 | 18 | 0.30475 | 5.4855
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.13457 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4223 | 18 | 0.30475 | 5.4855
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.13457 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.1138 | 38 | 0.30475 | 11.5805
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.13491 | north | 3 | N | N | Nnorth | Nnorth | 1 | 156.0909 | 0 | 0.30509 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.13491 | north | 3 | N | N | Nnorth | Nnorth | 1 | 156.2258 | 0 | 0.30509 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.13528 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.397 | 217.3 | 0.30546 | 66.3762
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.13528 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.733 | 205 | 0.30546 | 62.6191
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.13528 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 36.8511 | 272.4 | 0.30546 | 83.207
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.13562 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3058 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.13577 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.6973 | 204 | 0.30595 | 62.4131
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.13577 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.29 | 201 | 0.30595 | 61.4953
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.13577 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.8566 | 242 | 0.30595 | 74.0391
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.4297 | 224 | 0.30602 | 68.5491
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.7014 | 226 | 0.30602 | 69.1612
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.7996 | 212 | 0.30602 | 64.8768
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.13585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.6637 | 211 | 0.30602 | 64.5708
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.13654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 39.3238 | 288 | 0.30672 | 88.3344
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.13654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.0715 | 147 | 0.30672 | 45.0874
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.13654 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.0715 | 147 | 0.30672 | 45.0874
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.13749 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.7537 | 216.4 | 0.30767 | 66.5797
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.13749 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.7125 | 216.1 | 0.30767 | 66.4874
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.13809 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30827 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.13809 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30827 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.13809 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30827 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.13825 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.6076 | 395 | 0.30842 | 121.827
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.13825 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 60.1374 | 435 | 0.30842 | 134.1639
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.13862 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 60.298 | 435 | 0.30879 | 134.3244
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.1389 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.6258 | 0 | 0.30907 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14058 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4345 | 60 | 0.31075 | 18.645
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14058 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.8562 | 63 | 0.31075 | 19.5773
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.9833 | 196 | 0.31295 | 61.3378
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.8477 | 111 | 0.31295 | 34.7372
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14325 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31343 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14346 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.9283 | 118 | 0.31364 | 37.009
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14346 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.4979 | 115 | 0.31364 | 36.0681
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14346 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 79.7638 | 556 | 0.31364 | 174.3815
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14361 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31379 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14411 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.7644 | 0 | 0.31429 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14411 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.7644 | 0 | 0.31429 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14438 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 24.5453 | 170 | 0.31456 | 53.4752
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14438 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.0797 | 520 | 0.31456 | 163.5711
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14472 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 53.5449 | 370 | 0.31489 | 116.51
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.2602 | 0 | 0.31489 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.405 | 0 | 0.31489 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.7172 | 0 | 0.31489 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.6944 | 0 | 0.31489 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.8391 | 0 | 0.31489 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14472 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.862 | 0 | 0.31489 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1798 | 160 | 0.31505 | 50.408
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.6003 | 156 | 0.31505 | 49.1478
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.3953 | 196 | 0.31505 | 61.7498
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.6003 | 156 | 0.31505 | 49.1478
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7452 | 157 | 0.31505 | 49.4628
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14487 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.6851 | 198 | 0.31505 | 62.3799
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.145 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.8751 | 0 | 0.31518 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.145 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.5421 | 0 | 0.31518 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.145 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.8181 | 0 | 0.31518 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14514 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.9892 | 0 | 0.31532 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14514 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 84.0372 | 0 | 0.31532 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14514 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 117.2747 | 0 | 0.31532 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14525 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31542 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14525 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31542 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.8115 | 40 | 0.31546 | 12.6186
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.4782 | 79 | 0.31547 | 24.9221
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.4012 | 106 | 0.31547 | 33.4398
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14529 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 21.2129 | 146 | 0.31547 | 46.0586
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.0423 | 76 | 0.31547 | 23.9757
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.14555 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.6388 | 25 | 0.31573 | 7.8932
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.14555 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.9676 | 41 | 0.31573 | 12.9448
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.14555 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.9111 | 20 | 0.31573 | 6.3146
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14567 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 56.5215 | 388 | 0.31585 | 122.5497
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14567 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.0221 | 515 | 0.31585 | 162.6626
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6523 | 161 | 0.31708 | 51.0507
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.0931 | 164 | 0.31708 | 52.0019
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.0931 | 164 | 0.31708 | 52.0019
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 60.8203 | 414 | 0.31708 | 131.2731
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.7993 | 162 | 0.31708 | 51.3677
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6523 | 161 | 0.31708 | 51.0507
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.9462 | 163 | 0.31708 | 51.6848
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 60.0858 | 409 | 0.31708 | 129.6877
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.14989 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.5747 | 224 | 0.32006 | 71.6941
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.15289 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 120.0171 | 0 | 0.32306 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.15289 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 121.546 | 0 | 0.32306 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.15289 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 119.2526 | 0 | 0.32306 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.7248 | 0 | 0.32372 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.961 | 0 | 0.32372 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.2642 | 0 | 0.32372 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.15355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 61.2649 | 0 | 0.32372 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.15469 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.32487 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.15473 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.7367 | 0 | 0.32491 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.15601 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 28.3931 | 182 | 0.32618 | 59.3651
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.15601 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.5069 | 484 | 0.32618 | 157.872
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.16059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.3292 | 151.5 | 0.33076 | 50.1109
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.16059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.4577 | 152.3 | 0.33076 | 50.3755
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.16059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.5045 | 177.5 | 0.33076 | 58.7108
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.16086 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2416 | 150.7 | 0.33104 | 49.8871
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.16086 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2899 | 151 | 0.33104 | 49.9864
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.16086 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.5366 | 177.4 | 0.33104 | 58.7258
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.16249 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 99.9338 | 0 | 0.33267 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.16249 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 95.384 | 0 | 0.33267 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.1826 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 151.011 | 0 | 0.35278 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.1826 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 149.5502 | 0 | 0.35278 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.1826 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.7649 | 48 | 0.35278 | 16.9333
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.1826 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.3997 | 46 | 0.35278 | 16.2278
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.1826 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 19.1732 | 105 | 0.35278 | 37.0417
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.35554 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.35554 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.18536 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.1512 | 17 | 0.35554 | 6.0442
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.35554 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.18536 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.35554 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.18548 | north | 7 | N | N | Nnorth | Nnorth | 1 | 5.9354 | 0 | 0.35566 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.19262 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 89.1844 | 0 | 0.3628 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 167.5578 | 0 | 0.36615 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 167.5578 | 0 | 0.36615 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 29.8468 | 0 | 0.36615 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.19597 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 29.984 | 0 | 0.36615 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1450
| 25 | 1450
| 30 | 1450
| 35 | 1450
| 40 | 1450
| 45 | 1441
| 50 | 1415
| 55 | 1388
| 60 | 1362
| 65 | 1334
| 70 | 1306
| 75 | 1276
| 80 | 1246
| 85 | 1215
| 90 | 1183
| 95 | 1149
| 100 | 1116
| 105 | 1080
| 110 | 1043
| 115 | 1005
| Max | 1450
| Min | 1005
| Avg | 1290.45