## test results
CRE test for: |  | 975 JKCREEK1 345 3400 TWIN_OAK 345 1 | [5 empty] | PASS
Line Rating: |  | 1376
Direction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 975 JKCREEK1 345 3400 TWIN_OAK 345 1
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.13011
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.040391
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.11659
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.14463
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 975 JKCREEK1 345 3400 TWIN_OAK 345 1
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.12305
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.041809
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.11687
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.14658
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 975 JKCREEK1 345 3400 TWIN_OAK 345 1
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.17192
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.013237
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.27669
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.15726
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.10424
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.26317
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.27669 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.27669 | 0.17192
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.35396
[6 empty] | Concentration |  | 1.2792 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.28444
[6 empty] | Concentration |  | 1.028 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 210.1296
| Percent of line rating => | [6 empty] | 15.27% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.2431
[7 empty] | B1(N-S) | 0.014639 | 0.22835 | 0.21371 | 0.014639
[7 empty] | B2 (N-W) | 0.0096782 | 0.026133 | 0.016455 | 0.0096782
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.0037937 | -0.19929 | -0.1955 | -0.0037937
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.011043 | 0.11854 | 0.12958 | -0.011043
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0096843 | 0.31747 | 0.32715 | -0.0096843
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 4.256%
Deployment Error Percent | [6 empty] | B2 | 2.814%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -1.103%
[7 empty] | B5 | -3.211%
[7 empty] | B6 | -2.816%
[7 empty] | Max Abs Error | 4.256% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-H
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:975 JKCREEK1 345 3400 TWIN_OAK 345 1 C: JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_98 (3391-44645) 3390 - 44645 CKT 1 & 3391 - 44645 CKT 1 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:975 JKCREEK1 345 3400 TWIN_OAK 345 1 C: JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_98 (3391-44645) 3390 - 44645 CKT 1 & 3391 - 44645 CKT 1
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.094995 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 24.2237
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.094995 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 14.1543
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.10166 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.5249
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.10166 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.5249
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.094995 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 14.5342
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.09713 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 14.5695
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.09713 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 7.7704
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12229 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 8.9272
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12229 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 14.5525
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12229 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 25.0694
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12229 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 12.4736
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12229 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 11.7398
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.12397 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.4876
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.12397 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.4876
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.12294 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 20.6531
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.12294 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 11.0641
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.12503 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.2506
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.12503 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.2506
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.12503 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 4.7512
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.12675 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 36.504
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.12675 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 18.6322
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.12675 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 18.6322
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.12876 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 14.4855
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.13398 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 5.3594
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.134 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 10.5861
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.134 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 14.2041
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.134 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 19.5641
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.134 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 10.1841
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.13025 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 7.815
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.13025 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 8.2058
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.13417 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.6835
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.13417 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.3544
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.13417 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 5.5011
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.2161 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -100.0566
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 7.6167
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 7.5013
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 7.7321
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 7.7321
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 7.7321
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.1154 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 13.1561
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.1154 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 59.4331
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 7.7717
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.125
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.125
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 7.8895
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 7.8895
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 7.6539
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.11743 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 8.2198
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.11743 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 8.6191
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.11743 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 8.2668
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 17.6425
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 25.8757
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11786 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 11.6683
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11786 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 7.1896
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.11784 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 16.616
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11786 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 2.9465
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11786 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.3863
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11786 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.3863
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.11784 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 14.1413
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.11684 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 3.0144
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.11664 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 11.722
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.11721 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 14.0651
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.11662 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 6.7638
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.11678 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 25.0136
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 17.7093
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.11599 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.76551
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.11599 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 3.9783
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 11.9243
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.11724 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 14.0682
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.1241 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 45.4202
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.12326 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 29.8299
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.12092 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 48.3692
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.12093 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 28.5388
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.12169 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 20.0787
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.12609 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 25.7215
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.12609 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 25.3433
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.12609 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 30.5128
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.4846
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.4846
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.4846
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 2.1119
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.12379 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 14.8543
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.11793 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 7.0757
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.13372 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 10.0292
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.13372 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 10.6444
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.13372 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 11.8211
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 21.3851
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 20.8505
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 26.1968
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 20.8505
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 20.9841
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 26.4641
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.13328 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 22.6574
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.13328 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 69.3051
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13355 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 49.4139
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.13385 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 74.6894
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.13385 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 77.5003
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.13385 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 108.1524
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.12821 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 14.359
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.12821 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 12.8205
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.12821 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 48.4615
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.1258 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 27.3359
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.1258 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 25.7886
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.1258 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 34.2674
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.1261 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 97.097
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 8.684
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 8.5599
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 8.5599
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 8.4359
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.12545 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 145.1468
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.12545 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 145.2723
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 28.3391
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 28.5922
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.12805 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 27.71
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.12805 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 27.6716
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 26.821
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 26.6945
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.12845 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 50.7389
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.12877 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 56.0132
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.12845 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 55.8771
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.13246 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 18.2793
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.13294 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 15.687
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.13294 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 15.2882
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.13294 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 73.9152
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 52.1732
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.13447 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 69.2505
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13871 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 108.8866
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13871 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 110.2737
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13871 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 108.193
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13884 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 25.2689
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13884 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 67.1986
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.13284 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 29.7557
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.13959 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 6.9796
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.13951 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 5.8593
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.14834 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 91.2297
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.14834 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 87.0762
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.092754 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 49.8089
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.092754 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 72.9974
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.088231 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 6.6173
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.088231 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 19.5873
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.011155 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 6.3472
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.044036 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -9.2035
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.044036 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -9.5118
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.043841 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -17.8433
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -2.0257
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -2.0697
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -2.0257
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -2.0257
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.043929 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -18.6259
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.043929 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -18.6698
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.043827 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -2.542
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.043827 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -3.9006
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.9284
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.9284
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -1.8846
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.9722
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.043904 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -18.0884
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.043904 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -17.5616
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.045875 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -25.0478
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.045875 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -34.4062
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.044114 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -2.691
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.044114 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -4.1908
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.044114 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -6.6612
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.045027 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -6.9792
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.045027 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -7.6546
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.045027 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -6.9792
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.069541 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.5299
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.069541 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.76495
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.069541 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.76495
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -3.289
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -2.5719
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -3.1717
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -3.3096
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.059609 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.71531
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.059609 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.6557
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.044103 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.0585
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.044103 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.0585
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.044103 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -1.0144
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.051128 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -20.2467
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.10846 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -144.5785
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.10846 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -144.0362
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.06467 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -2.4575
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.06467 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -1.2481
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.06467 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.97005
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.06467 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -3.0395
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10884 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 8.1627
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 17.8052
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.1155 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 19.5766
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.083139 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 12.4709
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.11779 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 7.4211
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.12234 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 79.4817
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.13307 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.3228
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.13307 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.3228
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.003341 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -1.4099
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.02012 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -2.6558
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.02012 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -2.6961
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.02012 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -6.4988
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.021736 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -3.4343
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.021736 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -3.4778
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.021736 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -3.8038
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.036908 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -21.5543
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.036908 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -21.9603
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.037027 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -16.0327
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -7.8983
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -7.9371
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -7.923
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -7.9971
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.01138 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.09104
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.01138 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.09104
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.005091 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.091638
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.005091 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.091638
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.005091 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.076365
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.003682 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.050443
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.004984 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.089712
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.004984 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.089712
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.008709 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.30482
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.008709 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.29611
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.008709 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.30482
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.003054 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.085512
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.003054 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.088566
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.11546 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 4.0412
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.11546 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.4639
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.7104
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.7104
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.7104
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.7104
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.030092 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.18055
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.038538 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.092491
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.038538 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.092491
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.038538 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.10791
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.039721 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.15888
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.040835 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.098004
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.040835 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.098004
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -6.3439
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -5.9555
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -6.0418
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -6.3439
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -7.8544
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -8.5449
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.019508 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -2.975
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.019508 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -2.9164
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.019508 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -4.5376
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -5.5846
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -5.7026
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -5.9385
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -11.4051
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.001402 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.046266
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.001402 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.03505
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.059609 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.71531
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.069005 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -5.0374
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -6.013
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -6.1652
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -2.022
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.50551
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -6.013
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -6.0891
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -5.9673
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.9028
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -3.5012
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.062115 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -39.0703
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.067815 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -9.7654
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.067815 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -12.7492
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.04824 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.57888
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.015294 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.091764
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.0662 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -22.2432
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.065929 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -22.0203
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.065929 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -22.4159
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.065726 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -2.4976
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.065862 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.6465
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.065862 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.6465
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.065764 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -2.499
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.06513 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -1.8888
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.066186 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -9.8154
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.066186 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -9.8352
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.066186 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -10.1265
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -10.6582
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -10.3209
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -6.7457
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -9.7813
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -9.9162
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -8.567
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.063557 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -9.3111
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.063557 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -9.4001
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.063557 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -10.9954
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.064207 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -13.2908
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.064207 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -13.9137
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.064207 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -15.5381
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.064211 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -9.2464
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.064211 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -9.2464
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.064211 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -10.9801
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.011598 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -3.5954
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.011598 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -4.79
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.44222
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.46328
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.46328
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.49486
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.65606
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.61589
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.61589
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.62928
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013389 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -2.0619
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013389 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -1.9816
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.64267
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.64267
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.1612
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.1612
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 10.8194
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.327
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.327
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 13.4076
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 24.2713
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 16.5656
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 15.4348
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 15.8545
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 17.1368
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 24.4812
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 24.8083
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 15.0155
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 29.5563
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 23.3839
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 23.5234
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 14.3375
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.11566 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 17.2336
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.11741 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 21.1338
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.11741 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 21.1338
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.11735 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 26.4035
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.11825 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 14.781
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.11825 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 14.781
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 18.6971
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 18.8307
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 41.2673
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 19.0978
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 19.2313
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 41.4008
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.13052 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 25.5815
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.13052 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 14.4875
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.13278 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 21.7876
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 22.1936
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 22.1936
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 56.0254
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 21.923
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 21.7876
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 22.0583
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 55.3487
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.13427 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.13427 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 20.622
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 18.1139
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 20.204
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 55.5959
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.14694 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 22.144
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.14694 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 22.1881
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.14694 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 26.0673
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.14661 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 22.2119
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.14661 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 22.3292
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.14661 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 26.0238
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.011155 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 6.4811
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 177.3048
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 177.3048
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.23795 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -7.6145
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.2455 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -11.784
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.2455 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -11.293
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -2.9131
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -12.3807
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.24276 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -4.1269
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -5.3407
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -6.069
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.2455 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -25.7775
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.11802 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 9.9135
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.10872 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 8.6974
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.10866 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.2984
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.10866 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.2984
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -10.1342
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -9.5474
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -7.5864
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -21.9289
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -21.9718
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -21.8001
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -13.7413
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -34.9259
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -5.7256
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -14.3545
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -13.2955
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -14.698
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -14.5978
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.14312 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -4.5797
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.14312 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -4.2935
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -14.3522
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -14.3522
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -15.3866
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -14.1582
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 31.5831
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 31.7282
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.15154 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -20.6097
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.13853 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -4.5715
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -6.3665
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -6.3665
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -5.7602
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -5.7602
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.12705 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -9.0206
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.12705 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -1.2705
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.13774 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -22.4519
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.13774 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -22.4519
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.13774 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -33.7468
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -9.646
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -8.904
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -9.646
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -9.646
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.15045 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -22.4165
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.15045 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -9.794
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -13.4484
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -12.946
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -12.8573
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -8.0543
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -1.803
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.15414 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -114.529
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.1531 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -112.5314
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.15446 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -26.5664
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.15446 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -26.5664
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.15446 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -26.5664
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -27.7191
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.15175 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -26.2524
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.15175 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -20.486
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -25.2651
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -25.0478
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -24.6598
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -41.7774
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -9.6329
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -9.5125
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -12.4325
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -11.0778
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -24.4562
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -23.5421
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -23.602
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -23.5271
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -40.3107
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.15409 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.77046
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.15409 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -3.2359
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -30.9597
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -31.3211
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -31.3211
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -76.2949
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.15545 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -61.8703
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -6.8694
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -6.8694
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -6.8694
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -8.2134
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -8.2134
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -8.064
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.17418 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 144.0469
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.17418 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 142.6534
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.13733 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -6.3309
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -8.2899
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -8.2899
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -11.4531
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -8.0717
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -8.0717
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -11.1259
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.15053 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -27.0961
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.15053 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -23.8747
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.15053 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -23.6338
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.15012 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -5.2542
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.14621 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -67.1113
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -10.0165
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -10.1706
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -10.787
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -9.7083
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -9.5542
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -16.0264
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -9.0919
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -24.9953
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -24.6748
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -24.6748
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.16023 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -25.9566
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.15434 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -24.2311
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -10.7153
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -10.8662
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -5.8859
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -4.5276
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.14954 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -11.6644
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.14954 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -11.9635
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -2.4382
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.15043 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -24.8208
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.15041 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -25.4188
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.1505 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -32.0567
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.15052 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -34.3195
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.15039 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -1.8047
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.15039 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -2.7071
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.14489 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -7.2446
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -15.8856
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -15.8856
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.2483
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -8.0955
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.2483
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -8.7065
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.2483
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.2483
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -8.8593
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -8.8593
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.1537 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -1.8444
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -8.7306
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -9.1983
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -8.7306
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -8.7306
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -9.1983
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -8.7306
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.11256 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -7.4292
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13898 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -22.3751
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13898 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -23.07
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13898 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -34.466
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13898 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -75.8809
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13898 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -89.3616
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.13767 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -89.6264
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.13767 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -77.6487
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.13767 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -82.605
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13898 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -1.8067
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.15412 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -1.8494
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -5.2142
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -5.3215
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -5.0148
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -7.0391
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -2.7144
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -3.1285
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -3.0518
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -5.3675
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -2.7604
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -13.0968
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -22.697
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -7.7022
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -8.87
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -5.5903
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -12.5471
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -10.6837
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -10.9322
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -6.2115
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -2.2361
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -11.6775
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -8.696
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -7.8264
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -8.9445
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -8.05
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -12.5471
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -12.0502
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -12.7956
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -9.4414
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -9.9383
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -9.9383
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -21.2432
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35749
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.10585 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 8.0976
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10884 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 8.7069
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10884 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 4.3534
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.10932 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.7454
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.10873 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 8.6985
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.10626 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 8.5004
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.10544 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 8.8573
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.10932 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.7454
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -4.1424
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.11729 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 14.0742
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.11729 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 27.3274
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.11729 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 19.9619
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -8.0668
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -6.686
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -8.1395
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -4.1788
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -3.6337
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.11959 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.1756
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.02392 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.092524 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.1111 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.53327
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.447
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 12.7481
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 16.0092
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 14.1119
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 12.4516
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 9.5463
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.11657 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 17.4851
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 13.0848
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 17.3882
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 21.6335
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 24.9483
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.06467 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.018525 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.050246 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -2.1312
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -3.3186
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -5.6324
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.0954
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -2.6586
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -2.4641
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -1.2321
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.0954
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -2.3344
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -2.7883
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.4266
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.8164
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0832
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.50551
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0832
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.8164
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.8164
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -9.5971
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.2422
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -3.5665
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.2422
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.067457 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.80948
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.071031 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.0655
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.071031 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.6337
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.07521 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -3.6101
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.071747 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.57398
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.066162 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -11.9092
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.0662 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -11.916
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.065929 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -11.8672
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.065929 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -11.8672
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050243 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -5.0243
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050243 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -5.0243
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6738
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6738
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6738
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -1.0712
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6738
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6738
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6738
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -1.0043
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050243 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050243 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -25.1215
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050243 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -25.1215
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050243 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.059191 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.001402 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.055832 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.061785 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:975 JKCREEK1 345 3400 TWIN_OAK 345 1 C: JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_98 (3391-44645) 3390 - 44645 CKT 1 & 3391 - 44645 CKT 1 | [7 empty] | 210.1296
Number of Bus | Name of Bus | ID | Max MW | L:975 JKCREEK1 345 3400 TWIN_OAK 345 1 C: JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_98 (3391-44645) 3390 - 44645 CKT 1 & 3391 - 44645 CKT 1 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.094995 | north | Y | -0.035115 | 0.13539 | -0.021596 | 0.23962 | 0.021596 | west | Y | 0.035115 | 3.4471
239 | BOSQUESW | 1 | 149 | 0.094995 | north | Y | -0.035115 | 0.13539 | -0.021596 | 0.23962 | 0.021596 | west | Y | 0.035115 | 2.0142
244 | WHITNYDM | 1 | 15 | 0.10166 | north | N | -0.028447 | 0.14205 | -0.014928 | 0.24629 | 0.014928 | west | Y | 0.028447 | 0
245 | WHITNYDM | 2 | 15 | 0.10166 | north | N | -0.028447 | 0.14205 | -0.014928 | 0.24629 | 0.014928 | west | Y | 0.028447 | 0
247 | BOSQUESW | 2 | 153 | 0.094995 | north | Y | -0.035115 | 0.13539 | -0.021596 | 0.23962 | 0.021596 | west | Y | 0.035115 | 2.0683
251 | BOSQUESW | 2 | 150 | 0.09713 | north | Y | -0.03298 | 0.13752 | -0.019461 | 0.24176 | 0.019461 | west | Y | 0.03298 | 2.0277
253 | BOSQUESW | 2 | 80 | 0.09713 | north | Y | -0.03298 | 0.13752 | -0.019461 | 0.24176 | 0.019461 | west | Y | 0.03298 | 1.0815
332 | RWMILLER | 1 | 73 | 0.12229 | north | Y | -0.0078195 | 0.16268 | 0.0056987 | 0.26692 | 0.0056987 | west | Y | 0.0078195 | 0.15482
333 | RWMILLER | 2 | 119 | 0.12229 | north | Y | -0.0078195 | 0.16268 | 0.0056987 | 0.26692 | 0.0056987 | west | Y | 0.0078195 | 0.25238
334 | RWMILLER | 3 | 205 | 0.12229 | north | Y | -0.0078195 | 0.16268 | 0.0056987 | 0.26692 | 0.0056987 | west | Y | 0.0078195 | 0.43478
335 | RWMILLER | 4 | 102 | 0.12229 | north | Y | -0.0078195 | 0.16268 | 0.0056987 | 0.26692 | 0.0056987 | west | Y | 0.0078195 | 0.21633
336 | RWMILLER | 5 | 96 | 0.12229 | north | Y | -0.0078195 | 0.16268 | 0.0056987 | 0.26692 | 0.0056987 | west | Y | 0.0078195 | 0.2036
344 | MRSSHPRD | 1 | 12 | 0.12397 | north | N | -0.0061435 | 0.16436 | 0.0073747 | 0.2686 | 0.0061435 | North | N | 0.0061435 | 0
345 | MRSSHPRD | 2 | 12 | 0.12397 | north | N | -0.0061435 | 0.16436 | 0.0073747 | 0.2686 | 0.0061435 | North | N | 0.0061435 | 0
366 | JNSNCNTY | 1 | 168 | 0.12294 | north | Y | -0.0071745 | 0.16333 | 0.0063437 | 0.26756 | 0.0063437 | west | Y | 0.0071745 | 0.13958
367 | JNSNCNTY | 2 | 90 | 0.12294 | north | Y | -0.0071745 | 0.16333 | 0.0063437 | 0.26756 | 0.0063437 | west | Y | 0.0071745 | 0.074777
503 | NTHTEXAS | 1 | 18 | 0.12503 | north | Y | -0.0050785 | 0.16542 | 0.0084397 | 0.26966 | 0.0050785 | North | N | 0.0050785 | 0
504 | NTHTEXAS | 2 | 18 | 0.12503 | north | Y | -0.0050785 | 0.16542 | 0.0084397 | 0.26966 | 0.0050785 | North | N | 0.0050785 | 0
505 | NTHTEXAS | 3 | 38 | 0.12503 | north | Y | -0.0050785 | 0.16542 | 0.0084397 | 0.26966 | 0.0050785 | North | N | 0.0050785 | 0
580 | JCKCNTY8 | 1 | 288 | 0.12675 | north | Y | -0.0033595 | 0.16714 | 0.010159 | 0.27138 | 0.0033595 | North | N | 0.0033595 | 0
581 | JCKCNTY8 | 2 | 147 | 0.12675 | north | Y | -0.0033595 | 0.16714 | 0.010159 | 0.27138 | 0.0033595 | North | N | 0.0033595 | 0
582 | JCKCNTY8 | 3 | 147 | 0.12675 | north | Y | -0.0033595 | 0.16714 | 0.010159 | 0.27138 | 0.0033595 | North | N | 0.0033595 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.12876 | north | Y | -0.0013495 | 0.16915 | 0.012169 | 0.27339 | 0.0013495 | North | N | 0.0013495 | 0
837 | NEWMAN_G | 1 | 40 | 0.13398 | north | Y | 0.0038755 | 0.17438 | 0.017394 | 0.27861 | 0.0038755 | North | N | 0.0038755 | 0
842 | OLINGER_ | 1 | 79 | 0.134 | north | Y | 0.0038915 | 0.17439 | 0.01741 | 0.27863 | 0.0038915 | North | N | 0.0038915 | 0
843 | OLINGER_ | 1 | 106 | 0.134 | north | Y | 0.0038915 | 0.17439 | 0.01741 | 0.27863 | 0.0038915 | North | N | 0.0038915 | 0
844 | OLINGER_ | 1 | 146 | 0.134 | north | Y | 0.0038915 | 0.17439 | 0.01741 | 0.27863 | 0.0038915 | North | N | 0.0038915 | 0
845 | OLINGER_ | 1 | 76 | 0.134 | north | Y | 0.0038915 | 0.17439 | 0.01741 | 0.27863 | 0.0038915 | North | N | 0.0038915 | 0
923 | SPENCER_ | 1 | 60 | 0.13025 | north | Y | 0.00014045 | 0.17064 | 0.013659 | 0.27488 | 0.00014045 | North | N | 0.00014045 | 0
924 | SPENCER_ | 1 | 63 | 0.13025 | north | Y | 0.00014045 | 0.17064 | 0.013659 | 0.27488 | 0.00014045 | North | N | 0.00014045 | 0
948 | STEAM1 | 1 | 20 | 0.13417 | north | Y | 0.0040645 | 0.17456 | 0.017583 | 0.2788 | 0.0040645 | North | N | 0.0040645 | 0
949 | STEAM2 | 1 | 25 | 0.13417 | north | Y | 0.0040645 | 0.17456 | 0.017583 | 0.2788 | 0.0040645 | North | N | 0.0040645 | 0
950 | STEAM3 | 1 | 41 | 0.13417 | north | Y | 0.0040645 | 0.17456 | 0.017583 | 0.2788 | 0.0040645 | North | N | 0.0040645 | 0
990 | GIBN_CRE | 1 | 463 | -0.2161 | north | Y | -0.34621 | -0.17571 | -0.3327 | -0.071476 | 0.071476 | houston | Y | 0.34621 | 127.2041
1002 | PBCTAGE_ | A | 66 | 0.1154 | west | Y | -0.014706 | 0.15579 | -0.0011873 | 0.26003 | 0.0011873 | west | N | 0.0011873 | 0
1003 | PBCTBGE_ | B | 65 | 0.1154 | west | Y | -0.014706 | 0.15579 | -0.0011873 | 0.26003 | 0.0011873 | west | N | 0.0011873 | 0
1004 | PBCTCGE_ | C | 67 | 0.1154 | west | Y | -0.014706 | 0.15579 | -0.0011873 | 0.26003 | 0.0011873 | west | N | 0.0011873 | 0
1005 | PBCTDGE_ | D | 67 | 0.1154 | west | Y | -0.014706 | 0.15579 | -0.0011873 | 0.26003 | 0.0011873 | west | N | 0.0011873 | 0
1006 | PBCTEGE_ | E | 67 | 0.1154 | west | Y | -0.014706 | 0.15579 | -0.0011873 | 0.26003 | 0.0011873 | west | N | 0.0011873 | 0
1007 | PB5GEN_6 | MB | 114 | 0.1154 | west | Y | -0.014706 | 0.15579 | -0.0011873 | 0.26003 | 0.0011873 | west | N | 0.0011873 | 0
1008 | PB6GEN_7 | MB | 515 | 0.1154 | west | Y | -0.014706 | 0.15579 | -0.0011873 | 0.26003 | 0.0011873 | west | N | 0.0011873 | 0
1039 | MRGNAG_1 | A | 66 | 0.11775 | west | Y | -0.012357 | 0.15814 | 0.0011617 | 0.26238 | 0.0011617 | west | N | 0.0011617 | 0
1040 | MRGNBG_2 | B | 69 | 0.11775 | west | Y | -0.012357 | 0.15814 | 0.0011617 | 0.26238 | 0.0011617 | west | N | 0.0011617 | 0
1041 | MRGNCG_3 | C | 69 | 0.11775 | west | Y | -0.012357 | 0.15814 | 0.0011617 | 0.26238 | 0.0011617 | west | N | 0.0011617 | 0
1042 | MRGNDG_4 | D | 67 | 0.11775 | west | Y | -0.012357 | 0.15814 | 0.0011617 | 0.26238 | 0.0011617 | west | N | 0.0011617 | 0
1043 | MRGNEG_5 | E | 67 | 0.11775 | west | Y | -0.012357 | 0.15814 | 0.0011617 | 0.26238 | 0.0011617 | west | N | 0.0011617 | 0
1044 | MRGNFG_6 | F | 65 | 0.11775 | west | Y | -0.012357 | 0.15814 | 0.0011617 | 0.26238 | 0.0011617 | west | N | 0.0011617 | 0
1045 | CALENG1G | 1 | 70 | 0.11743 | west | N | -0.012684 | 0.15782 | 0.00083469 | 0.26206 | 0.00083469 | west | N | 0.00083469 | 0
1046 | CALENG2G | 2 | 73.4 | 0.11743 | west | N | -0.012684 | 0.15782 | 0.00083469 | 0.26206 | 0.00083469 | west | N | 0.00083469 | 0
1047 | CALENG3G | 3 | 70.4 | 0.11743 | west | N | -0.012684 | 0.15782 | 0.00083469 | 0.26206 | 0.00083469 | west | N | 0.00083469 | 0
1058 | LONGSHOR | 1 | 150 | 0.11762 | west | Y | -0.012493 | 0.15801 | 0.0010257 | 0.26225 | 0.0010257 | west | N | 0.0010257 | 0
1058 | LONGSHOR | 2 | 220 | 0.11762 | west | Y | -0.012493 | 0.15801 | 0.0010257 | 0.26225 | 0.0010257 | west | N | 0.0010257 | 0
1061 | CIELOGEN | 1 | 99 | 0.11786 | west | Y | -0.012248 | 0.15825 | 0.0012707 | 0.26249 | 0.0012707 | west | N | 0.0012707 | 0
1062 | CIELOGEN | 1 | 61 | 0.11786 | west | Y | -0.012248 | 0.15825 | 0.0012707 | 0.26249 | 0.0012707 | west | N | 0.0012707 | 0
1068 | SCURRYCW | 1 | 141 | 0.11784 | west | Y | -0.012266 | 0.15823 | 0.0012527 | 0.26247 | 0.0012527 | west | N | 0.0012527 | 0
1069 | KINDERMG | 1 | 25 | 0.11786 | west | N | -0.012248 | 0.15825 | 0.0012707 | 0.26249 | 0.0012707 | west | N | 0.0012707 | 0
1070 | KINDERMG | 1 | 45.7 | 0.11786 | west | N | -0.012248 | 0.15825 | 0.0012707 | 0.26249 | 0.0012707 | west | N | 0.0012707 | 0
1071 | KINDERMG | 1 | 45.7 | 0.11786 | west | N | -0.012248 | 0.15825 | 0.0012707 | 0.26249 | 0.0012707 | west | N | 0.0012707 | 0
1073 | SCURRYCW | 2 | 120 | 0.11784 | west | Y | -0.012266 | 0.15823 | 0.0012527 | 0.26247 | 0.0012527 | west | N | 0.0012527 | 0
1320 | BSP 1 | 1 | 25.8 | 0.11684 | west | N | -0.013273 | 0.15723 | 0.00024569 | 0.26147 | 0.00024569 | west | N | 0.00024569 | 0
1326 | STANTONW | 1 | 100.5 | 0.11664 | west | Y | -0.013473 | 0.15703 | 4.5685e-05 | 0.26127 | 4.5685e-05 | west | N | 4.5685e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.11721 | west | Y | -0.012901 | 0.1576 | 0.00061769 | 0.26184 | 0.00061769 | west | N | 0.00061769 | 0
1328 | OCOTILLO | 1 | 58 | 0.11662 | west | Y | -0.013492 | 0.15701 | 2.6685e-05 | 0.26125 | 2.6685e-05 | west | N | 2.6685e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.11678 | west | Y | -0.013333 | 0.15717 | 0.00018569 | 0.26141 | 0.00018569 | west | N | 0.00018569 | 0
1343 | TRENTIPP | 1 | 150 | 0.11806 | west | Y | -0.012048 | 0.15845 | 0.0014707 | 0.26269 | 0.0014707 | west | N | 0.0014707 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.11599 | west | Y | -0.014124 | 0.15638 | -0.00060531 | 0.26062 | 0.00060531 | west | N | 0.00060531 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.11599 | west | Y | -0.014124 | 0.15638 | -0.00060531 | 0.26062 | 0.00060531 | west | N | 0.00060531 | 0
1354 | AEPWIND_ | 1 | 101 | 0.11806 | west | Y | -0.012048 | 0.15845 | 0.0014707 | 0.26269 | 0.0014707 | west | N | 0.0014707 | 0
1360 | GUNSIGHT | 1 | 120 | 0.11724 | west | Y | -0.012875 | 0.15763 | 0.00064369 | 0.26186 | 0.00064369 | west | N | 0.00064369 | 0
1432 | GRHAMSES | 2 | 366 | 0.1241 | north | Y | -0.0060105 | 0.16449 | 0.0075077 | 0.26873 | 0.0060105 | North | N | 0.0060105 | 0
1433 | GRHAMSES | 1 | 242 | 0.12326 | north | Y | -0.0068455 | 0.16365 | 0.0066727 | 0.26789 | 0.0066727 | west | Y | 0.0068455 | 0.041832
1437 | MESQUITW | 1 | 400 | 0.12092 | west | Y | -0.0091865 | 0.16131 | 0.0043317 | 0.26555 | 0.0043317 | west | N | 0.0043317 | 0
1438 | MESQUITW | 1 | 236 | 0.12093 | west | Y | -0.0091825 | 0.16132 | 0.0043357 | 0.26556 | 0.0043357 | west | N | 0.0043357 | 0
1442 | COKFIELD | 1 | 165 | 0.12169 | west | Y | -0.0084205 | 0.16208 | 0.0050977 | 0.26632 | 0.0050977 | west | N | 0.0050977 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.12609 | north | Y | -0.0040235 | 0.16648 | 0.0094947 | 0.27072 | 0.0040235 | North | N | 0.0040235 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.12609 | north | Y | -0.0040235 | 0.16648 | 0.0094947 | 0.27072 | 0.0040235 | North | N | 0.0040235 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.12609 | north | Y | -0.0040235 | 0.16648 | 0.0094947 | 0.27072 | 0.0040235 | North | N | 0.0040235 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.12423 | west | Y | -0.0058795 | 0.16462 | 0.0076387 | 0.26886 | 0.0058795 | North | Y | 0.0076387 | 0.035183
1479 | WFCOGEN_ | 2 | 20 | 0.12423 | west | Y | -0.0058795 | 0.16462 | 0.0076387 | 0.26886 | 0.0058795 | North | Y | 0.0076387 | 0.035183
1482 | WFCOGEN_ | 1 | 20 | 0.12423 | west | Y | -0.0058795 | 0.16462 | 0.0076387 | 0.26886 | 0.0058795 | North | Y | 0.0076387 | 0.035183
1482 | WFCOGEN_ | 2 | 17 | 0.12423 | west | Y | -0.0058795 | 0.16462 | 0.0076387 | 0.26886 | 0.0058795 | North | Y | 0.0076387 | 0.029905
1600 | BARTNWND | 1 | 120 | 0.12379 | north | Y | -0.0063235 | 0.16418 | 0.0071947 | 0.26842 | 0.0063235 | North | N | 0.0063235 | 0
1643 | SLSTR1PP | 1 | 60 | 0.11793 | north | Y | -0.012181 | 0.15832 | 0.0013377 | 0.26256 | 0.0013377 | west | Y | 0.012181 | 0.65057
1675 | PEC_1G | 1 | 75 | 0.13372 | north | N | 0.0036135 | 0.17411 | 0.017132 | 0.27835 | 0.0036135 | North | N | 0.0036135 | 0
1676 | PEC_2G | 2 | 79.6 | 0.13372 | north | N | 0.0036135 | 0.17411 | 0.017132 | 0.27835 | 0.0036135 | North | N | 0.0036135 | 0
1677 | PEC_3G | 3 | 88.4 | 0.13372 | north | N | 0.0036135 | 0.17411 | 0.017132 | 0.27835 | 0.0036135 | North | N | 0.0036135 | 0
1678 | LAMARPWR | 1 | 160 | 0.13366 | north | Y | 0.0035475 | 0.17405 | 0.017066 | 0.27829 | 0.0035475 | North | N | 0.0035475 | 0
1679 | LAMARPWR | 2 | 156 | 0.13366 | north | Y | 0.0035475 | 0.17405 | 0.017066 | 0.27829 | 0.0035475 | North | N | 0.0035475 | 0
1680 | LAMARPWR | 3 | 196 | 0.13366 | north | Y | 0.0035475 | 0.17405 | 0.017066 | 0.27829 | 0.0035475 | North | N | 0.0035475 | 0
1681 | LAMARPWR | 4 | 156 | 0.13366 | north | Y | 0.0035475 | 0.17405 | 0.017066 | 0.27829 | 0.0035475 | North | N | 0.0035475 | 0
1682 | LAMARPWR | 5 | 157 | 0.13366 | north | Y | 0.0035475 | 0.17405 | 0.017066 | 0.27829 | 0.0035475 | North | N | 0.0035475 | 0
1683 | LAMARPWR | 6 | 198 | 0.13366 | north | Y | 0.0035475 | 0.17405 | 0.017066 | 0.27829 | 0.0035475 | North | N | 0.0035475 | 0
1687 | VALLEY_1 | 1 | 170 | 0.13328 | north | Y | 0.0031695 | 0.17367 | 0.016688 | 0.27791 | 0.0031695 | North | N | 0.0031695 | 0
1688 | VALLEY_2 | 2 | 520 | 0.13328 | north | Y | 0.0031695 | 0.17367 | 0.016688 | 0.27791 | 0.0031695 | North | N | 0.0031695 | 0
1689 | VALLEY_3 | 3 | 370 | 0.13355 | north | Y | 0.0034415 | 0.17394 | 0.01696 | 0.27818 | 0.0034415 | North | N | 0.0034415 | 0
1701 | MOSES_1G | 1 | 558 | 0.13385 | north | Y | 0.0037425 | 0.17424 | 0.017261 | 0.27848 | 0.0037425 | North | N | 0.0037425 | 0
1702 | MOSES_2G | 2 | 579 | 0.13385 | north | Y | 0.0037425 | 0.17424 | 0.017261 | 0.27848 | 0.0037425 | North | N | 0.0037425 | 0
1703 | MOSES_3G | 3 | 808 | 0.13385 | north | Y | 0.0037425 | 0.17424 | 0.017261 | 0.27848 | 0.0037425 | North | N | 0.0037425 | 0
1861 | EAGLEMNT | MB | 112 | 0.12821 | north | Y | -0.0019045 | 0.1686 | 0.011614 | 0.27283 | 0.0019045 | North | N | 0.0019045 | 0
1862 | EAGLEMNT | MB | 100 | 0.12821 | north | Y | -0.0019045 | 0.1686 | 0.011614 | 0.27283 | 0.0019045 | North | N | 0.0019045 | 0
1863 | EAGLEMNT | MB | 378 | 0.12821 | north | Y | -0.0019045 | 0.1686 | 0.011614 | 0.27283 | 0.0019045 | North | N | 0.0019045 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.1258 | north | Y | -0.0043115 | 0.16619 | 0.0092067 | 0.27043 | 0.0043115 | North | N | 0.0043115 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.1258 | north | Y | -0.0043115 | 0.16619 | 0.0092067 | 0.27043 | 0.0043115 | North | N | 0.0043115 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.1258 | north | Y | -0.0043115 | 0.16619 | 0.0092067 | 0.27043 | 0.0043115 | North | N | 0.0043115 | 0
1889 | DECRDOVA | MB | 770 | 0.1261 | north | Y | -0.0040095 | 0.16649 | 0.0095087 | 0.27073 | 0.0040095 | North | N | 0.0040095 | 0
1892 | DECRDOVA | A | 70 | 0.12406 | north | Y | -0.0060525 | 0.16445 | 0.0074657 | 0.26869 | 0.0060525 | North | N | 0.0060525 | 0
1893 | DECRDOVA | B | 69 | 0.12406 | north | Y | -0.0060525 | 0.16445 | 0.0074657 | 0.26869 | 0.0060525 | North | N | 0.0060525 | 0
1894 | DECRDOVA | C | 69 | 0.12406 | north | Y | -0.0060525 | 0.16445 | 0.0074657 | 0.26869 | 0.0060525 | North | N | 0.0060525 | 0
1895 | DECRDOVA | D | 68 | 0.12406 | north | Y | -0.0060525 | 0.16445 | 0.0074657 | 0.26869 | 0.0060525 | North | N | 0.0060525 | 0
1898 | COMCHEPK | 1 | 1157 | 0.12545 | north | N | -0.0046585 | 0.16584 | 0.0088597 | 0.27008 | 0.0046585 | North | N | 0.0046585 | 0
1899 | COMCHEPK | 2 | 1158 | 0.12545 | north | N | -0.0046585 | 0.16584 | 0.0088597 | 0.27008 | 0.0046585 | North | N | 0.0046585 | 0
1937 | MDLTHELP | 5 | 224 | 0.12651 | north | Y | -0.0035955 | 0.1669 | 0.0099227 | 0.27114 | 0.0035955 | North | N | 0.0035955 | 0
1938 | MDLTHELP | 6 | 226 | 0.12651 | north | Y | -0.0035955 | 0.1669 | 0.0099227 | 0.27114 | 0.0035955 | North | N | 0.0035955 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.12805 | north | Y | -0.0020595 | 0.16844 | 0.011459 | 0.27268 | 0.0020595 | North | N | 0.0020595 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.12805 | north | Y | -0.0020595 | 0.16844 | 0.011459 | 0.27268 | 0.0020595 | North | N | 0.0020595 | 0
1943 | MDLTHELP | 3 | 212 | 0.12651 | north | Y | -0.0035955 | 0.1669 | 0.0099227 | 0.27114 | 0.0035955 | North | N | 0.0035955 | 0
1944 | MDLTHELP | 4 | 211 | 0.12651 | north | Y | -0.0035955 | 0.1669 | 0.0099227 | 0.27114 | 0.0035955 | North | N | 0.0035955 | 0
1947 | HANDLEY_ | 3 | 395 | 0.12845 | north | Y | -0.0016565 | 0.16884 | 0.011862 | 0.27308 | 0.0016565 | North | N | 0.0016565 | 0
1948 | HANDLEY_ | 4 | 435 | 0.12877 | north | Y | -0.0013435 | 0.16916 | 0.012175 | 0.2734 | 0.0013435 | North | N | 0.0013435 | 0
1949 | HANDLEY_ | 5 | 435 | 0.12845 | north | Y | -0.0016565 | 0.16884 | 0.011862 | 0.27308 | 0.0016565 | North | N | 0.0016565 | 0
2371 | COLLIN_1 | MB | 138 | 0.13246 | north | Y | 0.0023495 | 0.17285 | 0.015868 | 0.27709 | 0.0023495 | North | N | 0.0023495 | 0
2413 | MTCK6_G | 6 | 118 | 0.13294 | north | Y | 0.0028315 | 0.17333 | 0.01635 | 0.27757 | 0.0028315 | North | N | 0.0028315 | 0
2414 | MTCK7_G | 7 | 115 | 0.13294 | north | Y | 0.0028315 | 0.17333 | 0.01635 | 0.27757 | 0.0028315 | North | N | 0.0028315 | 0
2417 | MTCK8_G | 8 | 556 | 0.13294 | north | Y | 0.0028315 | 0.17333 | 0.01635 | 0.27757 | 0.0028315 | North | N | 0.0028315 | 0
2451 | LKHB1_G | 1 | 388 | 0.13447 | north | Y | 0.0043575 | 0.17486 | 0.017876 | 0.2791 | 0.0043575 | North | N | 0.0043575 | 0
2452 | LKHB2_G | 2 | 515 | 0.13447 | north | Y | 0.0043575 | 0.17486 | 0.017876 | 0.2791 | 0.0043575 | North | N | 0.0043575 | 0
3097 | MARTLAKE | 1 | 785 | 0.13871 | north | Y | 0.0085995 | 0.1791 | 0.022118 | 0.28334 | 0.0085995 | North | N | 0.0085995 | 0
3098 | MARTLAKE | 2 | 795 | 0.13871 | north | Y | 0.0085995 | 0.1791 | 0.022118 | 0.28334 | 0.0085995 | North | N | 0.0085995 | 0
3099 | MARTLAKE | 3 | 780 | 0.13871 | north | Y | 0.0085995 | 0.1791 | 0.022118 | 0.28334 | 0.0085995 | North | N | 0.0085995 | 0
3107 | STRYKER_ | 1 | 182 | 0.13884 | north | Y | 0.0087305 | 0.17923 | 0.022249 | 0.28347 | 0.0087305 | North | N | 0.0087305 | 0
3108 | STRYKER_ | 2 | 484 | 0.13884 | north | Y | 0.0087305 | 0.17923 | 0.022249 | 0.28347 | 0.0087305 | North | N | 0.0087305 | 0
3126 | TRINIDAD | 1 | 224 | 0.13284 | north | Y | 0.0027285 | 0.17323 | 0.016247 | 0.27747 | 0.0027285 | North | N | 0.0027285 | 0
3309 | ASPN_G | 1 | 50 | 0.13959 | north | Y | 0.0094825 | 0.17998 | 0.023001 | 0.28422 | 0.0094825 | North | N | 0.0094825 | 0
3348 | CHAMPION | MB | 42 | 0.13951 | north | N | 0.0093975 | 0.1799 | 0.022916 | 0.28414 | 0.0093975 | North | N | 0.0093975 | 0
3381 | BBRN_1G | 1 | 615 | 0.14834 | north | Y | 0.018231 | 0.18873 | 0.03175 | 0.29297 | 0.018231 | North | N | 0.018231 | 0
3382 | BBRN_2G | 2 | 587 | 0.14834 | north | Y | 0.018231 | 0.18873 | 0.03175 | 0.29297 | 0.018231 | North | N | 0.018231 | 0
3403 | THOUSE_1 | MB | 537 | 0.092754 | north | Y | -0.037356 | 0.13314 | -0.023837 | 0.23738 | 0.023837 | west | Y | 0.037356 | 0
3404 | THOUSE_2 | 2 | 787 | 0.092754 | north | Y | -0.037356 | 0.13314 | -0.023837 | 0.23738 | 0.023837 | west | Y | 0.037356 | 10.6388
3416 | LAKE_CRK | MB | 75 | 0.088231 | north | Y | -0.041879 | 0.12862 | -0.02836 | 0.23286 | 0.02836 | west | Y | 0.041879 | 0
3417 | LAKE_CRK | MB | 222 | 0.088231 | north | Y | -0.041879 | 0.12862 | -0.02836 | 0.23286 | 0.02836 | west | Y | 0.041879 | 0
3432 | SANDOW_4 | 4 | 569 | 0.011155 | south | Y | -0.11895 | 0.051546 | -0.10544 | 0.15578 | 0.051546 | south | N | 0.051546 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.044036 | south | Y | -0.17415 | -0.0036452 | -0.16063 | 0.10059 | 0.0036452 | south | N | 0.0036452 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.044036 | south | Y | -0.17415 | -0.0036452 | -0.16063 | 0.10059 | 0.0036452 | south | N | 0.0036452 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.043841 | south | Y | -0.17395 | -0.0034502 | -0.16043 | 0.10079 | 0.0034502 | south | N | 0.0034502 | 0
5031 | BRA_VHBC | 1 | 46 | -0.044036 | south | Y | -0.17415 | -0.0036452 | -0.16063 | 0.10059 | 0.0036452 | south | N | 0.0036452 | 0
5032 | BRA_VHBC | 2 | 47 | -0.044036 | south | Y | -0.17415 | -0.0036452 | -0.16063 | 0.10059 | 0.0036452 | south | N | 0.0036452 | 0
5033 | BRA_VHBC | 3 | 46 | -0.044036 | south | Y | -0.17415 | -0.0036452 | -0.16063 | 0.10059 | 0.0036452 | south | N | 0.0036452 | 0
5034 | BRA_VHBC | 4 | 46 | -0.044036 | south | Y | -0.17415 | -0.0036452 | -0.16063 | 0.10059 | 0.0036452 | south | N | 0.0036452 | 0
5111 | CALAVER_ | 1 | 424 | -0.043929 | south | Y | -0.17404 | -0.0035382 | -0.16052 | 0.1007 | 0.0035382 | south | N | 0.0035382 | 0
5112 | CALAVER_ | 2 | 425 | -0.043929 | south | Y | -0.17404 | -0.0035382 | -0.16052 | 0.1007 | 0.0035382 | south | N | 0.0035382 | 0
5264 | LEON_LCP | 3 | 58 | -0.043827 | south | Y | -0.17394 | -0.0034362 | -0.16042 | 0.1008 | 0.0034362 | south | N | 0.0034362 | 0
5265 | LEON_LCP | 4 | 89 | -0.043827 | south | Y | -0.17394 | -0.0034362 | -0.16042 | 0.1008 | 0.0034362 | south | N | 0.0034362 | 0
5266 | LEON_LCP | 1 | 44 | -0.043827 | south | Y | -0.17394 | -0.0034362 | -0.16042 | 0.1008 | 0.0034362 | south | N | 0.0034362 | 0
5267 | LEON_LCP | 2 | 44 | -0.043827 | south | Y | -0.17394 | -0.0034362 | -0.16042 | 0.1008 | 0.0034362 | south | N | 0.0034362 | 0
5268 | LEON_LCP | 3 | 43 | -0.043827 | south | Y | -0.17394 | -0.0034362 | -0.16042 | 0.1008 | 0.0034362 | south | N | 0.0034362 | 0
5269 | LEON_LCP | 4 | 45 | -0.043827 | south | Y | -0.17394 | -0.0034362 | -0.16042 | 0.1008 | 0.0034362 | south | N | 0.0034362 | 0
5396 | CALAVER_ | 1 | 412 | -0.043904 | south | Y | -0.17401 | -0.0035132 | -0.1605 | 0.10073 | 0.0035132 | south | N | 0.0035132 | 0
5397 | CALAVER_ | 2 | 400 | -0.043904 | south | Y | -0.17401 | -0.0035132 | -0.1605 | 0.10073 | 0.0035132 | south | N | 0.0035132 | 0
5401 | CALAVER_ | 1 | 546 | -0.045875 | south | Y | -0.17598 | -0.0054842 | -0.16247 | 0.098754 | 0.0054842 | south | N | 0.0054842 | 0
5402 | CALAVER_ | 2 | 750 | -0.045875 | south | Y | -0.17598 | -0.0054842 | -0.16247 | 0.098754 | 0.0054842 | south | N | 0.0054842 | 0
5436 | TUTTL_WB | MB | 61 | -0.044114 | south | Y | -0.17422 | -0.0037232 | -0.16071 | 0.10052 | 0.0037232 | south | N | 0.0037232 | 0
5438 | TUTTL_WB | MB | 95 | -0.044114 | south | Y | -0.17422 | -0.0037232 | -0.16071 | 0.10052 | 0.0037232 | south | N | 0.0037232 | 0
5439 | TUTTL_WB | MB | 151 | -0.044114 | south | Y | -0.17422 | -0.0037232 | -0.16071 | 0.10052 | 0.0037232 | south | N | 0.0037232 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.045027 | south | Y | -0.17514 | -0.0046362 | -0.16162 | 0.099602 | 0.0046362 | south | N | 0.0046362 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.045027 | south | Y | -0.17514 | -0.0046362 | -0.16162 | 0.099602 | 0.0046362 | south | N | 0.0046362 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.045027 | south | Y | -0.17514 | -0.0046362 | -0.16162 | 0.099602 | 0.0046362 | south | N | 0.0046362 | 0
5503 | RAYBURNG | 1 | 22 | -0.069541 | south | Y | -0.19965 | -0.02915 | -0.18613 | 0.075088 | 0.02915 | south | N | 0.02915 | 0
5505 | RAYBURNG | 1 | 11 | -0.069541 | south | Y | -0.19965 | -0.02915 | -0.18613 | 0.075088 | 0.02915 | south | N | 0.02915 | 0
5506 | RAYBURNG | 1 | 11 | -0.069541 | south | Y | -0.19965 | -0.02915 | -0.18613 | 0.075088 | 0.02915 | south | N | 0.02915 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.068951 | south | Y | -0.19906 | -0.02856 | -0.18554 | 0.075678 | 0.02856 | south | N | 0.02856 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.068951 | south | Y | -0.19906 | -0.02856 | -0.18554 | 0.075678 | 0.02856 | south | N | 0.02856 | 0
5511 | RAYBURNC | 1 | 46 | -0.068951 | south | Y | -0.19906 | -0.02856 | -0.18554 | 0.075678 | 0.02856 | south | N | 0.02856 | 0
5512 | RAYBURNC | 1 | 48 | -0.068951 | south | Y | -0.19906 | -0.02856 | -0.18554 | 0.075678 | 0.02856 | south | N | 0.02856 | 0
5728 | FALCONHY | 2 | 12 | -0.059609 | south | N | -0.18972 | -0.019218 | -0.1762 | 0.08502 | 0.019218 | south | N | 0.019218 | 0
5729 | FALCONHY | 3 | 11 | -0.059609 | south | N | -0.18972 | -0.019218 | -0.1762 | 0.08502 | 0.019218 | south | N | 0.019218 | 0
5890 | PEARSALL | 1 | 24 | -0.044103 | south | Y | -0.17421 | -0.0037122 | -0.16069 | 0.10053 | 0.0037122 | south | N | 0.0037122 | 0
5891 | PEARSALL | 1 | 24 | -0.044103 | south | Y | -0.17421 | -0.0037122 | -0.16069 | 0.10053 | 0.0037122 | south | N | 0.0037122 | 0
5892 | PEARSALL | 1 | 23 | -0.044103 | south | Y | -0.17421 | -0.0037122 | -0.16069 | 0.10053 | 0.0037122 | south | N | 0.0037122 | 0
5903 | SANMIGUE | 1 | 396 | -0.051128 | south | Y | -0.18124 | -0.010737 | -0.16772 | 0.093501 | 0.010737 | south | N | 0.010737 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.10846 | houston | N | -0.23857 | -0.06807 | -0.22505 | 0.036168 | 0.036168 | houston | N | 0.036168 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.10846 | houston | N | -0.23857 | -0.06807 | -0.22505 | 0.036168 | 0.036168 | houston | N | 0.036168 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | Y | 0.13011 | 0
5932 | SI_RAY9 | 9 | 38 | -0.06467 | south | Y | -0.19478 | -0.024279 | -0.18126 | 0.079959 | 0.024279 | south | N | 0.024279 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.06467 | south | Y | -0.19478 | -0.024279 | -0.18126 | 0.079959 | 0.024279 | south | N | 0.024279 | 0
5934 | SI_RAY5 | 5 | 15 | -0.06467 | south | Y | -0.19478 | -0.024279 | -0.18126 | 0.079959 | 0.024279 | south | N | 0.024279 | 0
5935 | SI_RAY10 | 10 | 47 | -0.06467 | south | Y | -0.19478 | -0.024279 | -0.18126 | 0.079959 | 0.024279 | south | N | 0.024279 | 0
6016 | SWMESA | 1 | 75 | 0.10884 | west | Y | -0.021274 | 0.14923 | -0.0077553 | 0.25347 | 0.0077553 | west | N | 0.0077553 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | Y | 0.11659 | 0
6144 | MCADOO1A | 1 | 150 | 0.1187 | west | Y | -0.011409 | 0.15909 | 0.0021097 | 0.26333 | 0.0021097 | west | N | 0.0021097 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.1155 | west | Y | -0.014614 | 0.15589 | -0.0010953 | 0.26013 | 0.0010953 | west | N | 0.0010953 | 0
6476 | LANGFORD | 1 | 150 | 0.083139 | west | Y | -0.046971 | 0.12353 | -0.033452 | 0.22777 | 0.033452 | west | N | 0.033452 | 0
6637 | SNYDERW1 | 1 | 63 | 0.11779 | west | Y | -0.012315 | 0.15819 | 0.0012037 | 0.26242 | 0.0012037 | west | N | 0.0012037 | 0
6752 | OKLA0A | 1 | 649.7 | 0.12234 | west | Y | -0.0077735 | 0.16273 | 0.0057447 | 0.26697 | 0.0057447 | west | N | 0.0057447 | 0
6948 | DENISNDM | 1 | 40 | 0.13307 | north | N | 0.0029595 | 0.17346 | 0.016478 | 0.2777 | 0.0029595 | North | N | 0.0029595 | 0
6948 | DENISNDM | 2 | 40 | 0.13307 | north | N | 0.0029595 | 0.17346 | 0.016478 | 0.2777 | 0.0029595 | North | N | 0.0029595 | 0
7000 | L_FERGUS | 1 | 422 | -0.003341 | south | Y | -0.13345 | 0.03705 | -0.11993 | 0.14129 | 0.03705 | south | N | 0.03705 | 0
7004 | L_SIMGID | 1 | 132 | -0.02012 | south | Y | -0.15023 | 0.020271 | -0.13671 | 0.12451 | 0.020271 | south | N | 0.020271 | 0
7005 | L_SIMGID | 2 | 134 | -0.02012 | south | Y | -0.15023 | 0.020271 | -0.13671 | 0.12451 | 0.020271 | south | N | 0.020271 | 0
7006 | L_SIMGID | 3 | 323 | -0.02012 | south | Y | -0.15023 | 0.020271 | -0.13671 | 0.12451 | 0.020271 | south | N | 0.020271 | 0
7007 | L_LOSTPI | 1 | 158 | -0.021736 | south | Y | -0.15185 | 0.018655 | -0.13833 | 0.12289 | 0.018655 | south | N | 0.018655 | 0
7008 | L_LOSTPI | 2 | 160 | -0.021736 | south | Y | -0.15185 | 0.018655 | -0.13833 | 0.12289 | 0.018655 | south | N | 0.018655 | 0
7009 | L_LOSTPI | 3 | 175 | -0.021736 | south | Y | -0.15185 | 0.018655 | -0.13833 | 0.12289 | 0.018655 | south | N | 0.018655 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.036908 | south | Y | -0.16702 | 0.0034828 | -0.1535 | 0.10772 | 0.0034828 | south | N | 0.0034828 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.036908 | south | Y | -0.16702 | 0.0034828 | -0.1535 | 0.10772 | 0.0034828 | south | N | 0.0034828 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.037027 | south | Y | -0.16714 | 0.0033638 | -0.15362 | 0.1076 | 0.0033638 | south | N | 0.0033638 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.035276 | south | Y | -0.16539 | 0.0051148 | -0.15187 | 0.10935 | 0.0051148 | south | N | 0.0051148 | 0
7015 | L_HAYSEN | 2 | 225 | -0.035276 | south | Y | -0.16539 | 0.0051148 | -0.15187 | 0.10935 | 0.0051148 | south | N | 0.0051148 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.035276 | south | Y | -0.16539 | 0.0051148 | -0.15187 | 0.10935 | 0.0051148 | south | N | 0.0051148 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.035276 | south | Y | -0.16539 | 0.0051148 | -0.15187 | 0.10935 | 0.0051148 | south | N | 0.0051148 | 0
7020 | L_AUSTPL | 1 | 8 | -0.01138 | south | N | -0.14149 | 0.029011 | -0.12797 | 0.13325 | 0.029011 | south | N | 0.029011 | 0
7020 | L_AUSTPL | 2 | 8 | -0.01138 | south | N | -0.14149 | 0.029011 | -0.12797 | 0.13325 | 0.029011 | south | N | 0.029011 | 0
7022 | L_BUCHAN | 1 | 18 | 0.005091 | south | N | -0.12502 | 0.045482 | -0.1115 | 0.14972 | 0.045482 | south | N | 0.045482 | 0
7023 | L_BUCHAN | 2 | 18 | 0.005091 | south | N | -0.12502 | 0.045482 | -0.1115 | 0.14972 | 0.045482 | south | N | 0.045482 | 0
7024 | L_BUCHAN | 3 | 15 | 0.005091 | south | N | -0.12502 | 0.045482 | -0.1115 | 0.14972 | 0.045482 | south | N | 0.045482 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.003682 | south | N | -0.12643 | 0.044073 | -0.11291 | 0.14831 | 0.044073 | south | N | 0.044073 | 0
7028 | L_MARBFA | 1 | 18 | -0.004984 | south | N | -0.13509 | 0.035407 | -0.12158 | 0.13965 | 0.035407 | south | N | 0.035407 | 0
7029 | L_MARBFA | 2 | 18 | -0.004984 | south | N | -0.13509 | 0.035407 | -0.12158 | 0.13965 | 0.035407 | south | N | 0.035407 | 0
7031 | L_MARSFO | 1 | 35 | -0.008709 | south | N | -0.13882 | 0.031682 | -0.1253 | 0.13592 | 0.031682 | south | N | 0.031682 | 0
7032 | L_MARSFO | 2 | 34 | -0.008709 | south | N | -0.13882 | 0.031682 | -0.1253 | 0.13592 | 0.031682 | south | N | 0.031682 | 0
7033 | L_MARSFO | 3 | 35 | -0.008709 | south | N | -0.13882 | 0.031682 | -0.1253 | 0.13592 | 0.031682 | south | N | 0.031682 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.003054 | south | N | -0.13316 | 0.037337 | -0.11965 | 0.14158 | 0.037337 | south | N | 0.037337 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.003054 | south | N | -0.13316 | 0.037337 | -0.11965 | 0.14158 | 0.037337 | south | N | 0.037337 | 0
7038 | L_DELAWA | 1 | 35 | 0.11546 | west | Y | -0.014647 | 0.15585 | -0.0011283 | 0.26009 | 0.0011283 | west | N | 0.0011283 | 0
7038 | L_DELAWA | 2 | 30 | 0.11546 | west | Y | -0.014647 | 0.15585 | -0.0011283 | 0.26009 | 0.0011283 | west | N | 0.0011283 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.034207 | south | Y | -0.16432 | 0.0061838 | -0.1508 | 0.11042 | 0.0061838 | south | N | 0.0061838 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.034207 | south | Y | -0.16432 | 0.0061838 | -0.1508 | 0.11042 | 0.0061838 | south | N | 0.0061838 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.034207 | south | Y | -0.16432 | 0.0061838 | -0.1508 | 0.11042 | 0.0061838 | south | N | 0.0061838 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.034207 | south | Y | -0.16432 | 0.0061838 | -0.1508 | 0.11042 | 0.0061838 | south | N | 0.0061838 | 0
7487 | L_CANYHY | 1 | 6 | -0.030092 | south | N | -0.1602 | 0.010299 | -0.14668 | 0.11454 | 0.010299 | south | N | 0.010299 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.038538 | south | N | -0.16865 | 0.0018528 | -0.15513 | 0.10609 | 0.0018528 | south | N | 0.0018528 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.038538 | south | N | -0.16865 | 0.0018528 | -0.15513 | 0.10609 | 0.0018528 | south | N | 0.0018528 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.038538 | south | N | -0.16865 | 0.0018528 | -0.15513 | 0.10609 | 0.0018528 | south | N | 0.0018528 | 0
7609 | L_SCHUMA | 1 | 4 | -0.039721 | south | N | -0.16983 | 0.00066976 | -0.15631 | 0.10491 | 0.00066976 | south | N | 0.00066976 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.040835 | south | N | -0.17094 | -0.00044424 | -0.15743 | 0.10379 | 0.00044424 | south | N | 0.00044424 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.040835 | south | N | -0.17094 | -0.00044424 | -0.15743 | 0.10379 | 0.00044424 | south | N | 0.00044424 | 0
7800 | L_GUADGE | 1 | 147 | -0.043156 | south | Y | -0.17327 | -0.0027652 | -0.15975 | 0.10147 | 0.0027652 | south | N | 0.0027652 | 0
7801 | L_GUADGE | 2 | 138 | -0.043156 | south | Y | -0.17327 | -0.0027652 | -0.15975 | 0.10147 | 0.0027652 | south | N | 0.0027652 | 0
7802 | L_GUADGE | 3 | 140 | -0.043156 | south | Y | -0.17327 | -0.0027652 | -0.15975 | 0.10147 | 0.0027652 | south | N | 0.0027652 | 0
7803 | L_GUADGE | 4 | 147 | -0.043156 | south | Y | -0.17327 | -0.0027652 | -0.15975 | 0.10147 | 0.0027652 | south | N | 0.0027652 | 0
7804 | L_GUADGE | 5 | 182 | -0.043156 | south | Y | -0.17327 | -0.0027652 | -0.15975 | 0.10147 | 0.0027652 | south | N | 0.0027652 | 0
7805 | L_GUADGE | 6 | 198 | -0.043156 | south | Y | -0.17327 | -0.0027652 | -0.15975 | 0.10147 | 0.0027652 | south | N | 0.0027652 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.019508 | south | Y | -0.14962 | 0.020883 | -0.1361 | 0.12512 | 0.020883 | south | N | 0.020883 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.019508 | south | Y | -0.14962 | 0.020883 | -0.1361 | 0.12512 | 0.020883 | south | N | 0.020883 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.019508 | south | Y | -0.14962 | 0.020883 | -0.1361 | 0.12512 | 0.020883 | south | N | 0.020883 | 0
7810 | L_RIONOG | 1 | 142 | -0.039328 | south | Y | -0.16944 | 0.0010628 | -0.15592 | 0.1053 | 0.0010628 | south | N | 0.0010628 | 0
7811 | L_RIONOG | 2 | 145 | -0.039328 | south | Y | -0.16944 | 0.0010628 | -0.15592 | 0.1053 | 0.0010628 | south | N | 0.0010628 | 0
7812 | L_RIONOG | 3 | 151 | -0.039328 | south | Y | -0.16944 | 0.0010628 | -0.15592 | 0.1053 | 0.0010628 | south | N | 0.0010628 | 0
7813 | L_RIONOG | 4 | 290 | -0.039328 | south | Y | -0.16944 | 0.0010628 | -0.15592 | 0.1053 | 0.0010628 | south | N | 0.0010628 | 0
8032 | AMISTADH | 1 | 33 | -0.001402 | south | N | -0.13151 | 0.038989 | -0.11799 | 0.14323 | 0.038989 | south | N | 0.038989 | 0
8033 | AMISTADH | 2 | 25 | -0.001402 | south | N | -0.13151 | 0.038989 | -0.11799 | 0.14323 | 0.038989 | south | N | 0.038989 | 0
8048 | FALCONHY | 1 | 12 | -0.059609 | south | N | -0.18972 | -0.019218 | -0.1762 | 0.08502 | 0.019218 | south | N | 0.019218 | 0
8066 | DUP1V#1 | 1 | 73 | -0.069005 | south | N | -0.19911 | -0.028614 | -0.1856 | 0.075624 | 0.028614 | south | N | 0.028614 | 0
8134 | FOR69CG0 | 1 | 79 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
8138 | FOR69CG0 | 2 | 81 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | N | 0.040391 | 0
8147 | UCAR #2 | 10 | 28 | -0.072216 | south | N | -0.20233 | -0.031825 | -0.18881 | 0.072413 | 0.031825 | south | N | 0.031825 | 0
8148 | UCAR #1 | 2 | 7 | -0.072216 | south | N | -0.20233 | -0.031825 | -0.18881 | 0.072413 | 0.031825 | south | N | 0.031825 | 0
8153 | FOR69CG0 | 3 | 79 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
8154 | FOR69CG0 | 4 | 80 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
8156 | FOR69CG0 | 6 | 25 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
8157 | FOR69CG0 | 7 | 46 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
8161 | COLETOU1 | 1 | 629 | -0.062115 | south | Y | -0.19222 | -0.021724 | -0.17871 | 0.082514 | 0.021724 | south | N | 0.021724 | 0
8173 | VICEC51A | 5 | 144 | -0.067815 | south | Y | -0.19792 | -0.027424 | -0.18441 | 0.076814 | 0.027424 | south | N | 0.027424 | 0
8174 | VICEC61A | 6 | 188 | -0.067815 | south | Y | -0.19792 | -0.027424 | -0.18441 | 0.076814 | 0.027424 | south | N | 0.027424 | 0
8189 | CUERO 2 | 1 | 12 | -0.04824 | south | N | -0.17835 | -0.0078492 | -0.16483 | 0.096389 | 0.0078492 | south | N | 0.0078492 | 0
8262 | ELPS | 1 | 6 | -0.015294 | south | N | -0.1454 | 0.025097 | -0.13189 | 0.12934 | 0.025097 | south | N | 0.025097 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | N | 0.040391 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | N | 0.040391 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | N | 0.040391 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | N | 0.040391 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | N | 0.040391 | 0
8442 | NBEC71A | 1 | 336 | -0.0662 | south | Y | -0.19631 | -0.025809 | -0.18279 | 0.078429 | 0.025809 | south | N | 0.025809 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | N | 0.040391 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.13011 | 0.040391 | -0.11659 | 0.14463 | 0.040391 | south | N | 0.040391 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.065929 | south | Y | -0.19604 | -0.025538 | -0.18252 | 0.0787 | 0.025538 | south | N | 0.025538 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.065929 | south | Y | -0.19604 | -0.025538 | -0.18252 | 0.0787 | 0.025538 | south | N | 0.025538 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.065726 | south | N | -0.19584 | -0.025335 | -0.18232 | 0.078903 | 0.025335 | south | N | 0.025335 | 0
8506 | VAL #1 | 1 | 25 | -0.065862 | south | N | -0.19597 | -0.025471 | -0.18245 | 0.078767 | 0.025471 | south | N | 0.025471 | 0
8507 | VAL #2 | 2 | 25 | -0.065862 | south | N | -0.19597 | -0.025471 | -0.18245 | 0.078767 | 0.025471 | south | N | 0.025471 | 0
8511 | OXY_CC0A | 1 | 38 | -0.065764 | south | N | -0.19587 | -0.025373 | -0.18236 | 0.078865 | 0.025373 | south | N | 0.025373 | 0
8517 | CELANEBI | 1 | 29 | -0.06513 | south | N | -0.19524 | -0.024739 | -0.18172 | 0.079499 | 0.024739 | south | N | 0.024739 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.066186 | south | N | -0.1963 | -0.025795 | -0.18278 | 0.078443 | 0.025795 | south | N | 0.025795 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.066186 | south | N | -0.1963 | -0.025795 | -0.18278 | 0.078443 | 0.025795 | south | N | 0.025795 | 0
8562 | CNOPST1 | 3 | 153 | -0.066186 | south | N | -0.1963 | -0.025795 | -0.18278 | 0.078443 | 0.025795 | south | N | 0.025795 | 0
8926 | LGE_GT10 | 1 | 158 | -0.067457 | south | N | -0.19757 | -0.027066 | -0.18405 | 0.077172 | 0.027066 | south | N | 0.027066 | 0
8927 | LGE_GT20 | 2 | 153 | -0.067457 | south | N | -0.19757 | -0.027066 | -0.18405 | 0.077172 | 0.027066 | south | N | 0.027066 | 0
8928 | LGE_STG0 | 3 | 100 | -0.067457 | south | N | -0.19757 | -0.027066 | -0.18405 | 0.077172 | 0.027066 | south | N | 0.027066 | 0
8930 | ICPGN10A | 1 | 145 | -0.067457 | south | N | -0.19757 | -0.027066 | -0.18405 | 0.077172 | 0.027066 | south | N | 0.027066 | 0
8931 | ICPGN20A | 2 | 147 | -0.067457 | south | N | -0.19757 | -0.027066 | -0.18405 | 0.077172 | 0.027066 | south | N | 0.027066 | 0
8932 | ICPGN30A | 3 | 127 | -0.067457 | south | N | -0.19757 | -0.027066 | -0.18405 | 0.077172 | 0.027066 | south | N | 0.027066 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.063557 | south | Y | -0.19367 | -0.023166 | -0.18015 | 0.081072 | 0.023166 | south | N | 0.023166 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.063557 | south | Y | -0.19367 | -0.023166 | -0.18015 | 0.081072 | 0.023166 | south | N | 0.023166 | 0
8935 | FGNTS201 | 3 | 173 | -0.063557 | south | Y | -0.19367 | -0.023166 | -0.18015 | 0.081072 | 0.023166 | south | N | 0.023166 | 0
8936 | MVGN#1 | 1 | 207 | -0.064207 | south | Y | -0.19432 | -0.023816 | -0.1808 | 0.080422 | 0.023816 | south | N | 0.023816 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.064207 | south | Y | -0.19432 | -0.023816 | -0.1808 | 0.080422 | 0.023816 | south | N | 0.023816 | 0
8938 | MVGN#3 | 3 | 242 | -0.064207 | south | Y | -0.19432 | -0.023816 | -0.1808 | 0.080422 | 0.023816 | south | N | 0.023816 | 0
8981 | HECN1 | 1 | 144 | -0.064211 | south | Y | -0.19432 | -0.02382 | -0.1808 | 0.080418 | 0.02382 | south | N | 0.02382 | 0
8982 | HECN2 | 2 | 144 | -0.064211 | south | Y | -0.19432 | -0.02382 | -0.1808 | 0.080418 | 0.02382 | south | N | 0.02382 | 0
8983 | HECN3 | 3 | 171 | -0.064211 | south | Y | -0.19432 | -0.02382 | -0.1808 | 0.080418 | 0.02382 | south | N | 0.02382 | 0
9000 | DECKR_G1 | 1 | 310 | -0.011598 | south | Y | -0.14171 | 0.028793 | -0.12819 | 0.13303 | 0.028793 | south | N | 0.028793 | 0
9001 | DECKR_G2 | 2 | 413 | -0.011598 | south | Y | -0.14171 | 0.028793 | -0.12819 | 0.13303 | 0.028793 | south | N | 0.028793 | 0
9002 | DECKR_G3 | 3 | 42 | -0.010529 | south | Y | -0.14064 | 0.029862 | -0.12712 | 0.1341 | 0.029862 | south | N | 0.029862 | 0
9003 | DECKR_G4 | 4 | 44 | -0.010529 | south | Y | -0.14064 | 0.029862 | -0.12712 | 0.1341 | 0.029862 | south | N | 0.029862 | 0
9004 | DECKR_G5 | 5 | 44 | -0.010529 | south | Y | -0.14064 | 0.029862 | -0.12712 | 0.1341 | 0.029862 | south | N | 0.029862 | 0
9005 | DECKR_G6 | 6 | 47 | -0.010529 | south | Y | -0.14064 | 0.029862 | -0.12712 | 0.1341 | 0.029862 | south | N | 0.029862 | 0
9016 | SANDH_G1 | 1 | 49 | -0.013389 | south | Y | -0.1435 | 0.027002 | -0.12998 | 0.13124 | 0.027002 | south | N | 0.027002 | 0
9017 | SANDH_G2 | 2 | 46 | -0.013389 | south | Y | -0.1435 | 0.027002 | -0.12998 | 0.13124 | 0.027002 | south | N | 0.027002 | 0
9018 | SANDH_G3 | 3 | 46 | -0.013389 | south | Y | -0.1435 | 0.027002 | -0.12998 | 0.13124 | 0.027002 | south | N | 0.027002 | 0
9019 | SANDH_G4 | 4 | 47 | -0.013389 | south | Y | -0.1435 | 0.027002 | -0.12998 | 0.13124 | 0.027002 | south | N | 0.027002 | 0
9020 | SANDHG5A | 5A | 154 | -0.013389 | south | Y | -0.1435 | 0.027002 | -0.12998 | 0.13124 | 0.027002 | south | N | 0.027002 | 0
9021 | SANDHG5C | 5C | 148 | -0.013389 | south | Y | -0.1435 | 0.027002 | -0.12998 | 0.13124 | 0.027002 | south | N | 0.027002 | 0
9022 | SANDH_G6 | 6 | 48 | -0.013389 | south | Y | -0.1435 | 0.027002 | -0.12998 | 0.13124 | 0.027002 | south | N | 0.027002 | 0
9023 | SANDH_G7 | 7 | 48 | -0.013389 | south | Y | -0.1435 | 0.027002 | -0.12998 | 0.13124 | 0.027002 | south | N | 0.027002 | 0
11001 | NAV1CT | 1 | 70 | 0.11659 | west | Y | -0.013522 | 0.15698 | -3.3146e-06 | 0.26122 | 3.3146e-06 | west | N | 3.3146e-06 | 0
11009 | NAV2CT | 1 | 70 | 0.11659 | west | Y | -0.013522 | 0.15698 | -3.3146e-06 | 0.26122 | 3.3146e-06 | west | N | 3.3146e-06 | 0
11011 | NAV3ST | 1 | 92.8 | 0.11659 | west | Y | -0.013522 | 0.15698 | -3.3146e-06 | 0.26122 | 3.3146e-06 | west | N | 3.3146e-06 | 0
11012 | NAV4CT | 1 | 80 | 0.11659 | west | Y | -0.013522 | 0.15698 | -3.3146e-06 | 0.26122 | 3.3146e-06 | west | N | 3.3146e-06 | 0
11013 | NAV5CT | 1 | 80 | 0.11659 | west | Y | -0.013522 | 0.15698 | -3.3146e-06 | 0.26122 | 3.3146e-06 | west | N | 3.3146e-06 | 0
11014 | NAV6ST | 1 | 115 | 0.11659 | west | Y | -0.013522 | 0.15698 | -3.3146e-06 | 0.26122 | 3.3146e-06 | west | N | 3.3146e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.11658 | west | Y | -0.013533 | 0.15697 | -1.4315e-05 | 0.26121 | 1.4315e-05 | west | N | 1.4315e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.11658 | west | Y | -0.013533 | 0.15697 | -1.4315e-05 | 0.26121 | 1.4315e-05 | west | N | 1.4315e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.11658 | west | Y | -0.013533 | 0.15697 | -1.4315e-05 | 0.26121 | 1.4315e-05 | west | N | 1.4315e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.11658 | west | Y | -0.013533 | 0.15697 | -1.4315e-05 | 0.26121 | 1.4315e-05 | west | N | 1.4315e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.11658 | west | Y | -0.013533 | 0.15697 | -1.4315e-05 | 0.26121 | 1.4315e-05 | west | N | 1.4315e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.11658 | west | Y | -0.013533 | 0.15697 | -1.4315e-05 | 0.26121 | 1.4315e-05 | west | N | 1.4315e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.1187 | west | Y | -0.01141 | 0.15909 | 0.0021087 | 0.26333 | 0.0021087 | west | N | 0.0021087 | 0
11057 | CHAMPION | 1 | 126.5 | 0.1187 | west | Y | -0.01141 | 0.15909 | 0.0021087 | 0.26333 | 0.0021087 | west | N | 0.0021087 | 0
11058 | PYRON_1G | 1 | 249 | 0.1187 | west | Y | -0.01141 | 0.15909 | 0.0021087 | 0.26333 | 0.0021087 | west | N | 0.0021087 | 0
11059 | INADALE_ | 1 | 197 | 0.1187 | west | Y | -0.01141 | 0.15909 | 0.0021087 | 0.26333 | 0.0021087 | west | N | 0.0021087 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.11762 | west | Y | -0.012493 | 0.15801 | 0.0010257 | 0.26225 | 0.0010257 | west | N | 0.0010257 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.11762 | west | Y | -0.012493 | 0.15801 | 0.0010257 | 0.26225 | 0.0010257 | west | N | 0.0010257 | 0
11147 | NOTREES_ | 1 | 149 | 0.11566 | west | Y | -0.014448 | 0.15605 | -0.00092931 | 0.26029 | 0.00092931 | west | N | 0.00092931 | 0
11309 | BULLCREK | 1 | 180 | 0.11741 | west | Y | -0.0127 | 0.1578 | 0.00081869 | 0.26204 | 0.00081869 | west | N | 0.00081869 | 0
11310 | BULLCREK | 1 | 180 | 0.11741 | west | Y | -0.0127 | 0.1578 | 0.00081869 | 0.26204 | 0.00081869 | west | N | 0.00081869 | 0
11320 | COYOTE_1 | 1 | 225 | 0.11735 | west | Y | -0.012761 | 0.15774 | 0.00075769 | 0.26198 | 0.00075769 | west | N | 0.00075769 | 0
11415 | LORAINE_ | 1 | 125 | 0.11825 | west | Y | -0.011862 | 0.15864 | 0.0016567 | 0.26288 | 0.0016567 | west | N | 0.0016567 | 0
11416 | LORAINE_ | 1 | 125 | 0.11825 | west | Y | -0.011862 | 0.15864 | 0.0016567 | 0.26288 | 0.0016567 | west | N | 0.0016567 | 0
11691 | KMICHICT | 1 | 140 | 0.13355 | north | N | 0.0034415 | 0.17394 | 0.01696 | 0.27818 | 0.0034415 | North | N | 0.0034415 | 0
11692 | KMICHICT | 2 | 141 | 0.13355 | north | N | 0.0034415 | 0.17394 | 0.01696 | 0.27818 | 0.0034415 | North | N | 0.0034415 | 0
11693 | KMICHIST | 3 | 309 | 0.13355 | north | N | 0.0034415 | 0.17394 | 0.01696 | 0.27818 | 0.0034415 | North | N | 0.0034415 | 0
11694 | KMICHICT | 4 | 143 | 0.13355 | north | N | 0.0034415 | 0.17394 | 0.01696 | 0.27818 | 0.0034415 | North | N | 0.0034415 | 0
11695 | KMICHICT | 5 | 144 | 0.13355 | north | N | 0.0034415 | 0.17394 | 0.01696 | 0.27818 | 0.0034415 | North | N | 0.0034415 | 0
11696 | KMICHIST | 6 | 310 | 0.13355 | north | N | 0.0034415 | 0.17394 | 0.01696 | 0.27818 | 0.0034415 | North | N | 0.0034415 | 0
12322 | ENNSTRAC | 1 | 196 | 0.13052 | north | Y | 0.00040845 | 0.17091 | 0.013927 | 0.27515 | 0.00040845 | North | N | 0.00040845 | 0
12323 | ENNSTRAC | 2 | 111 | 0.13052 | north | Y | 0.00040845 | 0.17091 | 0.013927 | 0.27515 | 0.00040845 | North | N | 0.00040845 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.13278 | north | N | 0.0026725 | 0.17317 | 0.016191 | 0.27741 | 0.0026725 | North | N | 0.0026725 | 0
12411 | FPLEFR1A | 1 | 161 | 0.13533 | north | Y | 0.0052175 | 0.17572 | 0.018736 | 0.27996 | 0.0052175 | North | N | 0.0052175 | 0
12412 | FPLEFR1B | 2 | 164 | 0.13533 | north | Y | 0.0052175 | 0.17572 | 0.018736 | 0.27996 | 0.0052175 | North | N | 0.0052175 | 0
12413 | FPLEFR1C | 3 | 164 | 0.13533 | north | Y | 0.0052175 | 0.17572 | 0.018736 | 0.27996 | 0.0052175 | North | N | 0.0052175 | 0
12414 | FPLEFR1S | 4 | 414 | 0.13533 | north | Y | 0.0052175 | 0.17572 | 0.018736 | 0.27996 | 0.0052175 | North | N | 0.0052175 | 0
12421 | FPLEFR2A | 1 | 162 | 0.13533 | north | Y | 0.0052175 | 0.17572 | 0.018736 | 0.27996 | 0.0052175 | North | N | 0.0052175 | 0
12422 | FPLEFR2B | 2 | 161 | 0.13533 | north | Y | 0.0052175 | 0.17572 | 0.018736 | 0.27996 | 0.0052175 | North | N | 0.0052175 | 0
12423 | FPLEFR2C | 3 | 163 | 0.13533 | north | Y | 0.0052175 | 0.17572 | 0.018736 | 0.27996 | 0.0052175 | North | N | 0.0052175 | 0
12424 | FPLEFR2S | 4 | 409 | 0.13533 | north | Y | 0.0052175 | 0.17572 | 0.018736 | 0.27996 | 0.0052175 | North | N | 0.0052175 | 0
12440 | PARKD_1S | 1 | 0 | 0.13427 | north | N | 0.0041585 | 0.17466 | 0.017677 | 0.2789 | 0.0041585 | North | N | 0.0041585 | 0
12449 | PARKD_2S | 1 | 0 | 0.13427 | north | N | 0.0041585 | 0.17466 | 0.017677 | 0.2789 | 0.0041585 | North | N | 0.0041585 | 0
13116 | TGATEWAY | 1 | 148 | 0.13934 | north | N | 0.0092285 | 0.17973 | 0.022747 | 0.28397 | 0.0092285 | North | N | 0.0092285 | 0
13117 | TGATEWAY | 2 | 130 | 0.13934 | north | N | 0.0092285 | 0.17973 | 0.022747 | 0.28397 | 0.0092285 | North | N | 0.0092285 | 0
13118 | TGATEWAY | 3 | 145 | 0.13934 | north | N | 0.0092285 | 0.17973 | 0.022747 | 0.28397 | 0.0092285 | North | N | 0.0092285 | 0
13119 | TGATEWAY | 4 | 399 | 0.13934 | north | N | 0.0092285 | 0.17973 | 0.022747 | 0.28397 | 0.0092285 | North | N | 0.0092285 | 0
13131 | CALFREST | 1 | 150.7 | 0.14694 | north | Y | 0.016831 | 0.18733 | 0.03035 | 0.29157 | 0.016831 | North | N | 0.016831 | 0
13132 | CALFREST | 2 | 151 | 0.14694 | north | Y | 0.016831 | 0.18733 | 0.03035 | 0.29157 | 0.016831 | North | N | 0.016831 | 0
13133 | CALFREST | 3 | 177.4 | 0.14694 | north | Y | 0.016831 | 0.18733 | 0.03035 | 0.29157 | 0.016831 | North | N | 0.016831 | 0
13134 | CALFREST | 4 | 151.5 | 0.14661 | north | Y | 0.016503 | 0.187 | 0.030022 | 0.29124 | 0.016503 | North | N | 0.016503 | 0
13135 | CALFREST | 5 | 152.3 | 0.14661 | north | Y | 0.016503 | 0.187 | 0.030022 | 0.29124 | 0.016503 | North | N | 0.016503 | 0
13136 | CALFREST | 6 | 177.5 | 0.14661 | north | Y | 0.016503 | 0.187 | 0.030022 | 0.29124 | 0.016503 | North | N | 0.016503 | 0
13432 | SANDOW_5 | 5 | 581 | 0.011155 | south | Y | -0.11895 | 0.051546 | -0.10544 | 0.15578 | 0.051546 | south | N | 0.051546 | 0
13691 | OAKGROVE | 1 | 855 | 0.20737 | north | Y | 0.077264 | 0.24776 | 0.090783 | 0.352 | 0.077264 | North | N | 0.077264 | 0
13692 | OAKGROVE | 2 | 855 | 0.20737 | north | Y | 0.077264 | 0.24776 | 0.090783 | 0.352 | 0.077264 | North | N | 0.077264 | 0
32798 | BRYN_TAM | 1 | 32 | -0.23795 | north | N | -0.36806 | -0.19756 | -0.35454 | -0.093323 | 0.093323 | houston | Y | 0.36806 | 0
32883 | BRYN_DNS | 1 | 48 | -0.2455 | north | Y | -0.37561 | -0.20511 | -0.36209 | -0.10087 | 0.10087 | houston | Y | 0.37561 | 13.1875
32884 | BRYN_DNS | 1 | 46 | -0.2455 | north | Y | -0.37561 | -0.20511 | -0.36209 | -0.10087 | 0.10087 | houston | Y | 0.37561 | 12.638
32886 | BRYN_ATK | MB | 12 | -0.24276 | north | Y | -0.37287 | -0.20237 | -0.35935 | -0.098129 | 0.098129 | houston | Y | 0.37287 | 0
32887 | BRYN_ATK | MB | 51 | -0.24276 | north | Y | -0.37287 | -0.20237 | -0.35935 | -0.098129 | 0.098129 | houston | Y | 0.37287 | 0
32888 | BRYN_ATK | 1 | 17 | -0.24276 | north | Y | -0.37287 | -0.20237 | -0.35935 | -0.098129 | 0.098129 | houston | Y | 0.37287 | 4.6706
32890 | BRYN_ATK | MB | 22 | -0.24276 | north | Y | -0.37287 | -0.20237 | -0.35935 | -0.098129 | 0.098129 | houston | Y | 0.37287 | 0
32891 | BRYN_ATK | MB | 25 | -0.24276 | north | Y | -0.37287 | -0.20237 | -0.35935 | -0.098129 | 0.098129 | houston | Y | 0.37287 | 0
32892 | BRYN_DNS | 1 | 105 | -0.2455 | north | Y | -0.37561 | -0.20511 | -0.36209 | -0.10087 | 0.10087 | houston | Y | 0.37561 | 28.8476
36998 | RDCNYNG1 | 1 | 84 | 0.11802 | west | Y | -0.012092 | 0.15841 | 0.0014267 | 0.26265 | 0.0014267 | west | N | 0.0014267 | 0
38332 | WDWRDU2 | 1 | 80 | 0.10872 | west | Y | -0.021393 | 0.14911 | -0.0078743 | 0.25335 | 0.0078743 | west | N | 0.0078743 | 0
38437 | TNSRBNMS | 1 | 150 | 0.10866 | west | Y | -0.021454 | 0.14905 | -0.0079353 | 0.25329 | 0.0079353 | west | N | 0.0079353 | 0
38438 | TNSRBNMS | 1 | 150 | 0.10866 | west | Y | -0.021454 | 0.14905 | -0.0079353 | 0.25329 | 0.0079353 | west | N | 0.0079353 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.14314 | houston | N | -0.27325 | -0.10275 | -0.25973 | 0.0014904 | 0.0014904 | houston | N | 0.0014904 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.14314 | houston | N | -0.27325 | -0.10275 | -0.25973 | 0.0014904 | 0.0014904 | houston | N | 0.0014904 | 0
38600 | TNBP_CGN | 5 | 53 | -0.14314 | houston | N | -0.27325 | -0.10275 | -0.25973 | 0.0014904 | 0.0014904 | houston | N | 0.0014904 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.14314 | houston | N | -0.27325 | -0.10275 | -0.25973 | 0.0014904 | 0.0014904 | houston | N | 0.0014904 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.14314 | houston | N | -0.27325 | -0.10275 | -0.25973 | 0.0014904 | 0.0014904 | houston | N | 0.0014904 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.14314 | houston | N | -0.27325 | -0.10275 | -0.25973 | 0.0014904 | 0.0014904 | houston | N | 0.0014904 | 0
38614 | TNBPAMCG | 4 | 96 | -0.14314 | houston | N | -0.27325 | -0.10275 | -0.25973 | 0.0014904 | 0.0014904 | houston | N | 0.0014904 | 0
38615 | TNBPAMCG | 1 | 244 | -0.14314 | houston | N | -0.27325 | -0.10275 | -0.25973 | 0.0014904 | 0.0014904 | houston | N | 0.0014904 | 0
38690 | TNBP_CGN | 3 | 40 | -0.14314 | houston | N | -0.27325 | -0.10275 | -0.25973 | 0.0014904 | 0.0014904 | houston | N | 0.0014904 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.14312 | houston | N | -0.27323 | -0.10273 | -0.25971 | 0.0015134 | 0.0015134 | houston | N | 0.0015134 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.14312 | houston | N | -0.27323 | -0.10273 | -0.25971 | 0.0015134 | 0.0015134 | houston | N | 0.0015134 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.14312 | houston | N | -0.27323 | -0.10273 | -0.25971 | 0.0015134 | 0.0015134 | houston | N | 0.0015134 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.14312 | houston | N | -0.27323 | -0.10273 | -0.25971 | 0.0015134 | 0.0015134 | houston | N | 0.0015134 | 0
39470 | TNDOWCGN | 1 | 32 | -0.14312 | houston | N | -0.27323 | -0.10273 | -0.25971 | 0.0015124 | 0.0015124 | houston | N | 0.0015124 | 0
39480 | TNDOWCGN | 1 | 30 | -0.14312 | houston | N | -0.27323 | -0.10273 | -0.25971 | 0.0015124 | 0.0015124 | houston | N | 0.0015124 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.1293 | houston | N | -0.25941 | -0.088908 | -0.24589 | 0.01533 | 0.01533 | houston | N | 0.01533 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.1293 | houston | N | -0.25941 | -0.088908 | -0.24589 | 0.01533 | 0.01533 | houston | N | 0.01533 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.1293 | houston | N | -0.25941 | -0.088908 | -0.24589 | 0.01533 | 0.01533 | houston | N | 0.01533 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.1293 | houston | N | -0.25941 | -0.088908 | -0.24589 | 0.01533 | 0.01533 | houston | N | 0.01533 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.20737 | north | Y | 0.077264 | 0.24776 | 0.090783 | 0.352 | 0.077264 | North | N | 0.077264 | 0
39970 | TNTNPONE | 1 | 153 | 0.20737 | north | Y | 0.077264 | 0.24776 | 0.090783 | 0.352 | 0.077264 | North | N | 0.077264 | 0
48500 | APD_GT1_ | 1 | 136 | -0.15154 | houston | N | -0.28165 | -0.11115 | -0.26813 | -0.0069126 | 0.0069126 | houston | N | 0.0069126 | 0
48510 | AK_GT1__ | 1 | 33 | -0.13853 | houston | N | -0.26864 | -0.098138 | -0.25512 | 0.0061004 | 0.0061004 | houston | N | 0.0061004 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.15158 | houston | Y | -0.28169 | -0.11119 | -0.26817 | -0.0069536 | 0.0069536 | houston | N | 0.0069536 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.15158 | houston | Y | -0.28169 | -0.11119 | -0.26817 | -0.0069536 | 0.0069536 | houston | N | 0.0069536 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.15158 | houston | Y | -0.28169 | -0.11119 | -0.26817 | -0.0069536 | 0.0069536 | houston | N | 0.0069536 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.15158 | houston | Y | -0.28169 | -0.11119 | -0.26817 | -0.0069536 | 0.0069536 | houston | N | 0.0069536 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.12705 | houston | N | -0.25716 | -0.08666 | -0.24364 | 0.017578 | 0.017578 | houston | N | 0.017578 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.12705 | houston | N | -0.25716 | -0.08666 | -0.24364 | 0.017578 | 0.017578 | houston | N | 0.017578 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.13774 | houston | N | -0.26785 | -0.097351 | -0.25433 | 0.0068874 | 0.0068874 | houston | N | 0.0068874 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.13774 | houston | N | -0.26785 | -0.097351 | -0.25433 | 0.0068874 | 0.0068874 | houston | N | 0.0068874 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.13774 | houston | N | -0.26785 | -0.097351 | -0.25433 | 0.0068874 | 0.0068874 | houston | N | 0.0068874 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.1484 | houston | N | -0.27851 | -0.10801 | -0.26499 | -0.0037706 | 0.0037706 | houston | N | 0.0037706 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.1484 | houston | N | -0.27851 | -0.10801 | -0.26499 | -0.0037706 | 0.0037706 | houston | N | 0.0037706 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.1484 | houston | N | -0.27851 | -0.10801 | -0.26499 | -0.0037706 | 0.0037706 | houston | N | 0.0037706 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.1484 | houston | N | -0.27851 | -0.10801 | -0.26499 | -0.0037706 | 0.0037706 | houston | N | 0.0037706 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.15045 | houston | N | -0.28056 | -0.11006 | -0.26704 | -0.0058166 | 0.0058166 | houston | N | 0.0058166 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.15045 | houston | N | -0.28056 | -0.11006 | -0.26704 | -0.0058166 | 0.0058166 | houston | N | 0.0058166 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.14778 | houston | N | -0.27789 | -0.10739 | -0.26438 | -0.0031556 | 0.0031556 | houston | N | 0.0031556 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.14778 | houston | N | -0.27789 | -0.10739 | -0.26438 | -0.0031556 | 0.0031556 | houston | N | 0.0031556 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.14778 | houston | N | -0.27789 | -0.10739 | -0.26438 | -0.0031556 | 0.0031556 | houston | N | 0.0031556 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.14778 | houston | N | -0.27789 | -0.10739 | -0.26438 | -0.0031556 | 0.0031556 | houston | N | 0.0031556 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.14778 | houston | N | -0.27789 | -0.10739 | -0.26438 | -0.0031556 | 0.0031556 | houston | N | 0.0031556 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.15414 | houston | Y | -0.28425 | -0.11375 | -0.27074 | -0.0095146 | 0.0095146 | houston | N | 0.0095146 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.1531 | houston | Y | -0.28321 | -0.11271 | -0.2697 | -0.0084746 | 0.0084746 | houston | N | 0.0084746 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.15446 | houston | Y | -0.28457 | -0.11407 | -0.27105 | -0.0098266 | 0.0098266 | houston | N | 0.0098266 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.15446 | houston | Y | -0.28457 | -0.11407 | -0.27105 | -0.0098266 | 0.0098266 | houston | N | 0.0098266 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.15446 | houston | Y | -0.28457 | -0.11407 | -0.27105 | -0.0098266 | 0.0098266 | houston | N | 0.0098266 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.16023 | houston | N | -0.29034 | -0.11984 | -0.27682 | -0.015597 | 0.015597 | houston | N | 0.015597 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.15175 | houston | N | -0.28186 | -0.11136 | -0.26834 | -0.0071186 | 0.0071186 | houston | N | 0.0071186 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.15175 | houston | N | -0.28186 | -0.11136 | -0.26834 | -0.0071186 | 0.0071186 | houston | N | 0.0071186 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.15519 | houston | N | -0.2853 | -0.1148 | -0.27178 | -0.010562 | 0.010562 | houston | N | 0.010562 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.15519 | houston | N | -0.2853 | -0.1148 | -0.27178 | -0.010562 | 0.010562 | houston | N | 0.010562 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.15519 | houston | N | -0.2853 | -0.1148 | -0.27178 | -0.010562 | 0.010562 | houston | N | 0.010562 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.15519 | houston | N | -0.2853 | -0.1148 | -0.27178 | -0.010562 | 0.010562 | houston | N | 0.010562 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.15051 | houston | N | -0.28062 | -0.11012 | -0.26711 | -0.0058846 | 0.0058846 | houston | N | 0.0058846 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.15051 | houston | N | -0.28062 | -0.11012 | -0.26711 | -0.0058846 | 0.0058846 | houston | N | 0.0058846 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.15051 | houston | N | -0.28062 | -0.11012 | -0.26711 | -0.0058846 | 0.0058846 | houston | N | 0.0058846 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.15051 | houston | N | -0.28062 | -0.11012 | -0.26711 | -0.0058846 | 0.0058846 | houston | N | 0.0058846 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.14985 | houston | N | -0.27996 | -0.10946 | -0.26645 | -0.0052246 | 0.0052246 | houston | N | 0.0052246 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.14985 | houston | N | -0.27996 | -0.10946 | -0.26645 | -0.0052246 | 0.0052246 | houston | N | 0.0052246 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.14985 | houston | N | -0.27996 | -0.10946 | -0.26645 | -0.0052246 | 0.0052246 | houston | N | 0.0052246 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.14985 | houston | N | -0.27996 | -0.10946 | -0.26645 | -0.0052246 | 0.0052246 | houston | N | 0.0052246 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.14985 | houston | N | -0.27996 | -0.10946 | -0.26645 | -0.0052246 | 0.0052246 | houston | N | 0.0052246 | 0
48651 | EP_1_2 | 1 | 5 | -0.15409 | houston | N | -0.2842 | -0.1137 | -0.27068 | -0.0094616 | 0.0094616 | houston | N | 0.0094616 | 0
48651 | EP_1_2 | 2 | 21 | -0.15409 | houston | N | -0.2842 | -0.1137 | -0.27068 | -0.0094616 | 0.0094616 | houston | N | 0.0094616 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.20078 | north | N | -0.33089 | -0.16039 | -0.31737 | -0.056147 | 0.056147 | houston | Y | 0.33089 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.20078 | north | N | -0.33089 | -0.16039 | -0.31737 | -0.056147 | 0.056147 | houston | Y | 0.33089 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.20078 | north | N | -0.33089 | -0.16039 | -0.31737 | -0.056147 | 0.056147 | houston | Y | 0.33089 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.20078 | north | N | -0.33089 | -0.16039 | -0.31737 | -0.056147 | 0.056147 | houston | Y | 0.33089 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.15545 | houston | Y | -0.28556 | -0.11506 | -0.27204 | -0.010824 | 0.010824 | houston | N | 0.010824 | 0
48691 | GBY_7374 | A | 46 | -0.14933 | houston | Y | -0.27944 | -0.10894 | -0.26593 | -0.0047046 | 0.0047046 | houston | N | 0.0047046 | 0
48691 | GBY_7374 | B | 46 | -0.14933 | houston | Y | -0.27944 | -0.10894 | -0.26593 | -0.0047046 | 0.0047046 | houston | N | 0.0047046 | 0
48692 | GBY_8182 | C | 46 | -0.14933 | houston | Y | -0.27944 | -0.10894 | -0.26593 | -0.0047046 | 0.0047046 | houston | N | 0.0047046 | 0
48692 | GBY_8182 | D | 55 | -0.14933 | houston | Y | -0.27944 | -0.10894 | -0.26593 | -0.0047046 | 0.0047046 | houston | N | 0.0047046 | 0
48693 | GBY_8384 | E | 55 | -0.14933 | houston | Y | -0.27944 | -0.10894 | -0.26593 | -0.0047046 | 0.0047046 | houston | N | 0.0047046 | 0
48693 | GBY_8384 | F | 54 | -0.14933 | houston | Y | -0.27944 | -0.10894 | -0.26593 | -0.0047046 | 0.0047046 | houston | N | 0.0047046 | 0
48721 | LEG_1___ | 1 | 827 | 0.17418 | north | Y | 0.04407 | 0.21457 | 0.057589 | 0.31881 | 0.04407 | North | N | 0.04407 | 0
48722 | LEG_2___ | 2 | 819 | 0.17418 | north | Y | 0.04407 | 0.21457 | 0.057589 | 0.31881 | 0.04407 | North | N | 0.04407 | 0
48730 | MNS_GT | 1 | 46.1 | -0.13733 | houston | N | -0.26744 | -0.096938 | -0.25392 | 0.0073004 | 0.0073004 | houston | N | 0.0073004 | 0
48731 | CBE_GT1 | 1 | 76 | -0.10908 | houston | Y | -0.23919 | -0.068686 | -0.22567 | 0.035552 | 0.035552 | houston | N | 0.035552 | 0
48732 | CBE_GT2 | 1 | 76 | -0.10908 | houston | Y | -0.23919 | -0.068686 | -0.22567 | 0.035552 | 0.035552 | houston | N | 0.035552 | 0
48733 | CBE_ST12 | 1 | 105 | -0.10908 | houston | Y | -0.23919 | -0.068686 | -0.22567 | 0.035552 | 0.035552 | houston | N | 0.035552 | 0
48734 | CBE_GT3 | 1 | 74 | -0.10908 | houston | Y | -0.23919 | -0.068686 | -0.22567 | 0.035552 | 0.035552 | houston | N | 0.035552 | 0
48735 | CBE_GT4 | 1 | 74 | -0.10908 | houston | Y | -0.23919 | -0.068686 | -0.22567 | 0.035552 | 0.035552 | houston | N | 0.035552 | 0
48736 | CBE_ST34 | 1 | 102 | -0.10908 | houston | Y | -0.23919 | -0.068686 | -0.22567 | 0.035552 | 0.035552 | houston | N | 0.035552 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.15053 | houston | N | -0.28064 | -0.11014 | -0.26713 | -0.0059046 | 0.0059046 | houston | N | 0.0059046 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.15053 | houston | N | -0.28064 | -0.11014 | -0.26713 | -0.0059046 | 0.0059046 | houston | N | 0.0059046 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.15053 | houston | N | -0.28064 | -0.11014 | -0.26713 | -0.0059046 | 0.0059046 | houston | N | 0.0059046 | 0
48761 | PR_GT1__ | 1 | 35 | -0.15012 | houston | N | -0.28023 | -0.10973 | -0.26671 | -0.0054896 | 0.0054896 | houston | N | 0.0054896 | 0
48772 | PHR_GN2_ | MB | 459 | -0.14621 | houston | Y | -0.27632 | -0.10582 | -0.2628 | -0.0015826 | 0.0015826 | houston | N | 0.0015826 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.1541 | houston | N | -0.28421 | -0.11371 | -0.27069 | -0.0094706 | 0.0094706 | houston | N | 0.0094706 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.1541 | houston | N | -0.28421 | -0.11371 | -0.27069 | -0.0094706 | 0.0094706 | houston | N | 0.0094706 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.1541 | houston | N | -0.28421 | -0.11371 | -0.27069 | -0.0094706 | 0.0094706 | houston | N | 0.0094706 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.1541 | houston | N | -0.28421 | -0.11371 | -0.27069 | -0.0094706 | 0.0094706 | houston | N | 0.0094706 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.1541 | houston | N | -0.28421 | -0.11371 | -0.27069 | -0.0094706 | 0.0094706 | houston | N | 0.0094706 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.1541 | houston | N | -0.28421 | -0.11371 | -0.27069 | -0.0094706 | 0.0094706 | houston | N | 0.0094706 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.1541 | houston | N | -0.28421 | -0.11371 | -0.27069 | -0.0094706 | 0.0094706 | houston | N | 0.0094706 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.16023 | houston | N | -0.29034 | -0.11984 | -0.27682 | -0.015597 | 0.015597 | houston | N | 0.015597 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.16023 | houston | N | -0.29034 | -0.11984 | -0.27682 | -0.015597 | 0.015597 | houston | N | 0.015597 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.16023 | houston | N | -0.29034 | -0.11984 | -0.27682 | -0.015597 | 0.015597 | houston | N | 0.015597 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.16023 | houston | N | -0.29034 | -0.11984 | -0.27682 | -0.015597 | 0.015597 | houston | N | 0.015597 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.15434 | houston | N | -0.28445 | -0.11395 | -0.27093 | -0.0097086 | 0.0097086 | houston | N | 0.0097086 | 0
48820 | SHELLG1_ | 1 | 71 | -0.15092 | houston | N | -0.28103 | -0.11053 | -0.26751 | -0.0062906 | 0.0062906 | houston | N | 0.0062906 | 0
48821 | SHELLG2 | 2 | 72 | -0.15092 | houston | N | -0.28103 | -0.11053 | -0.26751 | -0.0062906 | 0.0062906 | houston | N | 0.0062906 | 0
48822 | SHELLG3_ | 1 | 39 | -0.15092 | houston | N | -0.28103 | -0.11053 | -0.26751 | -0.0062906 | 0.0062906 | houston | N | 0.0062906 | 0
48822 | SHELLG3_ | 2 | 30 | -0.15092 | houston | N | -0.28103 | -0.11053 | -0.26751 | -0.0062906 | 0.0062906 | houston | N | 0.0062906 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.14954 | houston | N | -0.27965 | -0.10915 | -0.26614 | -0.0049146 | 0.0049146 | houston | N | 0.0049146 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.14954 | houston | N | -0.27965 | -0.10915 | -0.26614 | -0.0049146 | 0.0049146 | houston | N | 0.0049146 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.15051 | houston | N | -0.28062 | -0.11012 | -0.2671 | -0.0058786 | 0.0058786 | houston | N | 0.0058786 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.15043 | houston | Y | -0.28054 | -0.11004 | -0.26702 | -0.0057996 | 0.0057996 | houston | N | 0.0057996 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.15041 | houston | Y | -0.28052 | -0.11002 | -0.267 | -0.0057776 | 0.0057776 | houston | N | 0.0057776 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.1505 | houston | Y | -0.28061 | -0.11011 | -0.26709 | -0.0058716 | 0.0058716 | houston | N | 0.0058716 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.15052 | houston | Y | -0.28063 | -0.11013 | -0.26712 | -0.0058946 | 0.0058946 | houston | N | 0.0058946 | 0
48855 | SRB_GT21 | B2 | 12 | -0.15039 | houston | Y | -0.2805 | -0.11 | -0.26698 | -0.0057626 | 0.0057626 | houston | N | 0.0057626 | 0
48855 | SRB_GT21 | MB | 18 | -0.15039 | houston | Y | -0.2805 | -0.11 | -0.26698 | -0.0057626 | 0.0057626 | houston | N | 0.0057626 | 0
48865 | TECO_GT1 | 1 | 50 | -0.14489 | houston | Y | -0.275 | -0.1045 | -0.26148 | -0.00026261 | 0.00026261 | houston | N | 0.00026261 | 0
48873 | THW_ST3_ | 3 | 104 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48874 | THW_ST4_ | 4 | 104 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48875 | THW_3132 | A | 54 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48875 | THW_3132 | B | 53 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48877 | THW_3334 | C | 54 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48877 | THW_3334 | D | 57 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48879 | THW_4142 | E | 54 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48879 | THW_4142 | F | 54 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48881 | THW_4344 | G | 58 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48881 | THW_4344 | H | 58 | -0.15275 | houston | Y | -0.28286 | -0.11236 | -0.26934 | -0.0081166 | 0.0081166 | houston | N | 0.0081166 | 0
48883 | THW_GT1_ | B2 | 12 | -0.1537 | houston | Y | -0.28381 | -0.11331 | -0.27029 | -0.0090676 | 0.0090676 | houston | N | 0.0090676 | 0
48885 | THW_5152 | A | 56 | -0.1559 | houston | Y | -0.28601 | -0.11551 | -0.2725 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48885 | THW_5152 | B | 59 | -0.1559 | houston | Y | -0.28601 | -0.11551 | -0.2725 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48886 | THW_5354 | C | 56 | -0.1559 | houston | Y | -0.28601 | -0.11551 | -0.2725 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48886 | THW_5354 | D | 56 | -0.1559 | houston | Y | -0.28601 | -0.11551 | -0.2725 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48887 | THW_5556 | E | 59 | -0.1559 | houston | Y | -0.28601 | -0.11551 | -0.2725 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48887 | THW_5556 | F | 56 | -0.1559 | houston | Y | -0.28601 | -0.11551 | -0.2725 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.11256 | houston | Y | -0.24267 | -0.072173 | -0.22916 | 0.032065 | 0.032065 | houston | N | 0.032065 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.13898 | houston | Y | -0.26909 | -0.098585 | -0.25557 | 0.0056534 | 0.0056534 | houston | N | 0.0056534 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.13898 | houston | Y | -0.26909 | -0.098585 | -0.25557 | 0.0056534 | 0.0056534 | houston | N | 0.0056534 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.13898 | houston | Y | -0.26909 | -0.098585 | -0.25557 | 0.0056534 | 0.0056534 | houston | N | 0.0056534 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.13898 | houston | Y | -0.26909 | -0.098585 | -0.25557 | 0.0056534 | 0.0056534 | houston | N | 0.0056534 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.13898 | houston | N | -0.26909 | -0.098585 | -0.25557 | 0.0056534 | 0.0056534 | houston | N | 0.0056534 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.13767 | houston | Y | -0.26778 | -0.097284 | -0.25427 | 0.0069544 | 0.0069544 | houston | N | 0.0069544 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.13767 | houston | Y | -0.26778 | -0.097284 | -0.25427 | 0.0069544 | 0.0069544 | houston | N | 0.0069544 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.13767 | houston | Y | -0.26778 | -0.097284 | -0.25427 | 0.0069544 | 0.0069544 | houston | N | 0.0069544 | 0
48929 | WAPGT21_ | B1 | 13 | -0.13898 | houston | Y | -0.26909 | -0.098585 | -0.25557 | 0.0056534 | 0.0056534 | houston | N | 0.0056534 | 0
48940 | WARVUE_G | G1 | 12 | -0.15412 | houston | Y | -0.28423 | -0.11373 | -0.27071 | -0.0094866 | 0.0094866 | houston | N | 0.0094866 | 0
49803 | EXN_15GT | 1 | 34 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49826 | EXN938GT | 5 | 45.9 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49828 | EXN941GT | 10 | 17.7 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49829 | EXN942GT | 11 | 20.4 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49830 | EXN943GT | 12 | 19.9 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49831 | EXN944GT | 13 | 35 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49832 | EXN945GT | 9 | 18 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49837 | EXN_GT | 4 | 85.4 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49838 | EXN_14GT | 14 | 148 | -0.15336 | houston | N | -0.28347 | -0.11297 | -0.26995 | -0.0087286 | 0.0087286 | houston | N | 0.0087286 | 0
49851 | DOW17000 | 37 | 62 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49858 | DOW38100 | 31 | 71.4 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49859 | DOW38200 | 33 | 45 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49860 | DOW38300 | 32 | 101 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49862 | DOW39100 | 36 | 86 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49863 | DOW39200 | 35 | 88 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49865 | DOW41000 | 41 | 50 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49866 | DOW42000 | 42 | 18 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49869 | DOW49000 | 45 | 94 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49870 | DOW61000 | 61 | 70 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49871 | DOW62000 | 62 | 63 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49872 | DOW63000 | 63 | 72 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49873 | DOW64000 | 64 | 64.8 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49876 | DOW65000 | 65 | 101 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49877 | DOW66000 | 66 | 97 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49878 | DOW67000 | 67 | 103 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49882 | DOW81000 | 81 | 76 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49884 | DOW82000 | 82 | 80 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49885 | DOW83000 | 83 | 80 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
49886 | DOW84000 | 84 | 171 | -0.12423 | houston | N | -0.25434 | -0.083838 | -0.24082 | 0.0204 | 0.0204 | houston | N | 0.0204 | 0
58909 | PEARSALL | 1 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58909 | PEARSALL | 2 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58909 | PEARSALL | 3 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58909 | PEARSALL | 4 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58909 | PEARSALL | 5 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58909 | PEARSALL | 6 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58919 | PEARSALL | 1 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58919 | PEARSALL | 2 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58919 | PEARSALL | 3 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58919 | PEARSALL | 4 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58919 | PEARSALL | 5 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58919 | PEARSALL | 6 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58929 | PEARSALL | 1 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58929 | PEARSALL | 2 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58929 | PEARSALL | 3 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58929 | PEARSALL | 4 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58929 | PEARSALL | 5 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58929 | PEARSALL | 6 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58949 | PEARSALL | 1 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58949 | PEARSALL | 2 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58949 | PEARSALL | 3 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58949 | PEARSALL | 4 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58949 | PEARSALL | 5 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
58949 | PEARSALL | 6 | 8.4 | -0.042558 | south | Y | -0.17267 | -0.0021672 | -0.15915 | 0.10207 | 0.0021672 | south | N | 0.0021672 | 0
60000 | DSKY2 | 1 | 76.5 | 0.10585 | west | Y | -0.024259 | 0.14624 | -0.01074 | 0.25048 | 0.01074 | west | N | 0.01074 | 0
60003 | KING_NE1 | 1 | 80 | 0.10884 | west | Y | -0.021274 | 0.14923 | -0.0077553 | 0.25347 | 0.0077553 | west | N | 0.0077553 | 0
60005 | KING_SE1 | 1 | 40 | 0.10884 | west | Y | -0.021274 | 0.14923 | -0.0077553 | 0.25347 | 0.0077553 | west | N | 0.0077553 | 0
60007 | KING_SW1 | 1 | 80 | 0.10932 | west | Y | -0.020793 | 0.14971 | -0.0072743 | 0.25395 | 0.0072743 | west | N | 0.0072743 | 0
60016 | WOODWRD1 | 1 | 80 | 0.10873 | west | Y | -0.021379 | 0.14912 | -0.0078603 | 0.25336 | 0.0078603 | west | N | 0.0078603 | 0
60017 | ORNNWP1 | 1 | 80 | 0.10626 | west | Y | -0.023855 | 0.14665 | -0.010336 | 0.25088 | 0.010336 | west | N | 0.010336 | 0
60018 | DSKY1 | 1 | 84 | 0.10544 | west | Y | -0.024666 | 0.14583 | -0.011147 | 0.25007 | 0.011147 | west | N | 0.011147 | 0
60019 | KING_NW1 | 1 | 80 | 0.10932 | west | Y | -0.020793 | 0.14971 | -0.0072743 | 0.25395 | 0.0072743 | west | N | 0.0072743 | 0
60057 | CALLAHAN | 1 | 114 | -0.036337 | south | Y | -0.16645 | 0.0040538 | -0.15293 | 0.10829 | 0.0040538 | south | N | 0.0040538 | 0
60058 | BUFF_GAP | 1 | 120 | 0.11729 | west | Y | -0.012825 | 0.15768 | 0.00069369 | 0.26191 | 0.00069369 | west | N | 0.00069369 | 0
60060 | CIRELLO | 1 | 233 | 0.11729 | west | Y | -0.012825 | 0.15768 | 0.00069369 | 0.26191 | 0.00069369 | west | N | 0.00069369 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.11729 | west | Y | -0.012825 | 0.15768 | 0.00069369 | 0.26191 | 0.00069369 | west | N | 0.00069369 | 0
60066 | H_HOLLOW | 1 | 222 | -0.036337 | south | Y | -0.16645 | 0.0040538 | -0.15293 | 0.10829 | 0.0040538 | south | N | 0.0040538 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.036337 | south | Y | -0.16645 | 0.0040538 | -0.15293 | 0.10829 | 0.0040538 | south | N | 0.0040538 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.036337 | south | Y | -0.16645 | 0.0040538 | -0.15293 | 0.10829 | 0.0040538 | south | N | 0.0040538 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.036337 | south | Y | -0.16645 | 0.0040538 | -0.15293 | 0.10829 | 0.0040538 | south | N | 0.0040538 | 0
60074 | HORSH5 | 1 | 100 | -0.036337 | south | Y | -0.16645 | 0.0040538 | -0.15293 | 0.10829 | 0.0040538 | south | N | 0.0040538 | 0
60081 | WHRLWIND | 1 | 60 | 0.11959 | west | Y | -0.010516 | 0.15998 | 0.0030027 | 0.26422 | 0.0030027 | west | N | 0.0030027 | 0
60201 | RIO DRCS | F | 0 | 0.02392 | south | N | -0.10619 | 0.064311 | -0.092671 | 0.16855 | 0.064311 | south | N | 0.064311 | 0
60202 | FRIEND_R | F | 0 | 0.092524 | west | N | -0.037586 | 0.13291 | -0.024067 | 0.23715 | 0.024067 | west | N | 0.024067 | 0
60203 | PRES0A | BT | 4.8 | 0.1111 | west | N | -0.019012 | 0.15149 | -0.0054933 | 0.25573 | 0.0054933 | west | N | 0.0054933 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.11859 | west | Y | -0.011523 | 0.15898 | 0.0019957 | 0.26322 | 0.0019957 | west | N | 0.0019957 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.11859 | west | Y | -0.011523 | 0.15898 | 0.0019957 | 0.26322 | 0.0019957 | west | N | 0.0019957 | 0
71057 | L_SWEETW | W1 | 135 | 0.11859 | west | Y | -0.011523 | 0.15898 | 0.0019957 | 0.26322 | 0.0019957 | west | N | 0.0019957 | 0
71059 | L_SWEETW | W1 | 119 | 0.11859 | west | Y | -0.011523 | 0.15898 | 0.0019957 | 0.26322 | 0.0019957 | west | N | 0.0019957 | 0
71060 | L_SWEETW | W1 | 105 | 0.11859 | west | Y | -0.011523 | 0.15898 | 0.0019957 | 0.26322 | 0.0019957 | west | N | 0.0019957 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.11859 | west | Y | -0.011523 | 0.15898 | 0.0019957 | 0.26322 | 0.0019957 | west | N | 0.0019957 | 0
76031 | L_GASCCR | W1 | 150 | 0.11657 | west | Y | -0.013543 | 0.15696 | -2.4315e-05 | 0.2612 | 2.4315e-05 | west | N | 2.4315e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.11631 | west | Y | -0.013801 | 0.1567 | -0.00028231 | 0.26094 | 0.00028231 | west | N | 0.00028231 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.11631 | west | Y | -0.013801 | 0.1567 | -0.00028231 | 0.26094 | 0.00028231 | west | N | 0.00028231 | 0
76096 | L_CAPRSI | W1 | 186 | 0.11631 | west | Y | -0.013801 | 0.1567 | -0.00028231 | 0.26094 | 0.00028231 | west | N | 0.00028231 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.11631 | west | Y | -0.013801 | 0.1567 | -0.00028231 | 0.26094 | 0.00028231 | west | N | 0.00028231 | 0
80003 | MILHWYS | F | 0 | -0.06467 | south | N | -0.19478 | -0.024279 | -0.18126 | 0.079959 | 0.024279 | south | N | 0.024279 | 0
80010 | EPLVT1 | F | 0 | -0.018525 | south | N | -0.14863 | 0.021866 | -0.13512 | 0.1261 | 0.021866 | south | N | 0.021866 | 0
80012 | LAR | F | 0 | -0.050246 | south | N | -0.18036 | -0.0098552 | -0.16684 | 0.094383 | 0.0098552 | south | N | 0.0098552 | 0
80051 | FORPVCM0 | 8 | 28 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
80053 | FOR69CG0 | 10 | 74 | -0.076114 | south | N | -0.20622 | -0.035723 | -0.19271 | 0.068515 | 0.035723 | south | N | 0.035723 | 0
80080 | GWINDT11 | 1 | 94 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80080 | GWINDT11 | 2 | 41 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80080 | GWINDT11 | 3 | 38 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80080 | GWINDT11 | 4 | 19 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80081 | GWINDT21 | 1 | 94 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80081 | GWINDT21 | 2 | 36 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80081 | GWINDT21 | 3 | 43 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80081 | GWINDT21 | 4 | 22 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80137 | CSDR89 | 8 | 39 | -0.072216 | south | N | -0.20233 | -0.031825 | -0.18881 | 0.072413 | 0.031825 | south | N | 0.031825 | 0
80137 | CSDR89 | 9 | 15 | -0.072216 | south | N | -0.20233 | -0.031825 | -0.18881 | 0.072413 | 0.031825 | south | N | 0.031825 | 0
80138 | CSDR7 | 7 | 7 | -0.072216 | south | N | -0.20233 | -0.031825 | -0.18881 | 0.072413 | 0.031825 | south | N | 0.031825 | 0
80139 | CSDR56 | 5 | 15 | -0.072216 | south | N | -0.20233 | -0.031825 | -0.18881 | 0.072413 | 0.031825 | south | N | 0.031825 | 0
80139 | CSDR56 | 6 | 39 | -0.072216 | south | N | -0.20233 | -0.031825 | -0.18881 | 0.072413 | 0.031825 | south | N | 0.031825 | 0
80140 | CSDR11 | 11 | 39 | -0.072216 | south | N | -0.20233 | -0.031825 | -0.18881 | 0.072413 | 0.031825 | south | N | 0.031825 | 0
80180 | PNSCALT1 | 1 | 148 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80180 | PNSCALT1 | 2 | 50 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80181 | PNSCALT2 | 1 | 55 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80181 | PNSCALT2 | 2 | 50 | -0.064845 | south | Y | -0.19495 | -0.024454 | -0.18144 | 0.079784 | 0.024454 | south | N | 0.024454 | 0
80223 | REYSHR G | 1 | 12 | -0.067457 | south | N | -0.19757 | -0.027066 | -0.18405 | 0.077172 | 0.027066 | south | N | 0.027066 | 0
80224 | VISTRONG | 1 | 15 | -0.071031 | south | N | -0.20114 | -0.03064 | -0.18762 | 0.073598 | 0.03064 | south | N | 0.03064 | 0
80225 | VISTRONG | 2 | 23 | -0.071031 | south | N | -0.20114 | -0.03064 | -0.18762 | 0.073598 | 0.03064 | south | N | 0.03064 | 0
80226 | ALCOA G | 1 | 48 | -0.07521 | south | N | -0.20532 | -0.034819 | -0.1918 | 0.069419 | 0.034819 | south | N | 0.034819 | 0
80227 | AIRCO G | 1 | 8 | -0.071747 | south | N | -0.20186 | -0.031356 | -0.18834 | 0.072882 | 0.031356 | south | N | 0.031356 | 0
80261 | NBEC81A | 1 | 180 | -0.066162 | south | Y | -0.19627 | -0.025771 | -0.18275 | 0.078467 | 0.025771 | south | N | 0.025771 | 0
80262 | NBEC91A | 1 | 180 | -0.0662 | south | Y | -0.19631 | -0.025809 | -0.18279 | 0.078429 | 0.025809 | south | N | 0.025809 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.065929 | south | Y | -0.19604 | -0.025538 | -0.18252 | 0.0787 | 0.025538 | south | N | 0.025538 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.065929 | south | Y | -0.19604 | -0.025538 | -0.18252 | 0.0787 | 0.025538 | south | N | 0.025538 | 0
80265 | LARECU40 | 4 | 100 | -0.050243 | south | Y | -0.18035 | -0.0098522 | -0.16683 | 0.094386 | 0.0098522 | south | N | 0.0098522 | 0
80266 | LARECU50 | 5 | 100 | -0.050243 | south | Y | -0.18035 | -0.0098522 | -0.16683 | 0.094386 | 0.0098522 | south | N | 0.0098522 | 0
80291 | PAPALOTE | 1 | 25 | -0.066953 | south | Y | -0.19706 | -0.026562 | -0.18354 | 0.077676 | 0.026562 | south | N | 0.026562 | 0
80291 | PAPALOTE | 2 | 25 | -0.066953 | south | Y | -0.19706 | -0.026562 | -0.18354 | 0.077676 | 0.026562 | south | N | 0.026562 | 0
80291 | PAPALOTE | 3 | 25 | -0.066953 | south | Y | -0.19706 | -0.026562 | -0.18354 | 0.077676 | 0.026562 | south | N | 0.026562 | 0
80291 | PAPALOTE | 4 | 16 | -0.066953 | south | Y | -0.19706 | -0.026562 | -0.18354 | 0.077676 | 0.026562 | south | N | 0.026562 | 0
80294 | PAPALOTE | 5 | 25 | -0.066953 | south | Y | -0.19706 | -0.026562 | -0.18354 | 0.077676 | 0.026562 | south | N | 0.026562 | 0
80294 | PAPALOTE | 6 | 25 | -0.066953 | south | Y | -0.19706 | -0.026562 | -0.18354 | 0.077676 | 0.026562 | south | N | 0.026562 | 0
80294 | PAPALOTE | 7 | 25 | -0.066953 | south | Y | -0.19706 | -0.026562 | -0.18354 | 0.077676 | 0.026562 | south | N | 0.026562 | 0
80294 | PAPALOTE | 8 | 15 | -0.066953 | south | Y | -0.19706 | -0.026562 | -0.18354 | 0.077676 | 0.026562 | south | N | 0.026562 | 0
86104 | CID-138 | EQ | 0 | -0.050243 | south | N | -0.18035 | -0.0098522 | -0.16683 | 0.094386 | 0.0098522 | south | N | 0.0098522 | 0
86105 | CID-230 | EQ | 500 | -0.050243 | south | N | -0.18035 | -0.0098522 | -0.16683 | 0.094386 | 0.0098522 | south | N | 0.0098522 | 0
86106 | CUF-230 | EQ | 500 | -0.050243 | south | N | -0.18035 | -0.0098522 | -0.16683 | 0.094386 | 0.0098522 | south | N | 0.0098522 | 0
86107 | CUF-138 | EQ | 0 | -0.050243 | south | N | -0.18035 | -0.0098522 | -0.16683 | 0.094386 | 0.0098522 | south | N | 0.0098522 | 0
88198 | BEEVILLE | F | 0 | -0.059191 | south | N | -0.1893 | -0.0188 | -0.17578 | 0.085438 | 0.0188 | south | N | 0.0188 | 0
88253 | HAMILTON | F | 0 | -0.001402 | south | N | -0.13151 | 0.038989 | -0.11799 | 0.14323 | 0.038989 | south | N | 0.038989 | 0
88299 | ZAPATA | F | 0 | -0.055832 | south | N | -0.18594 | -0.015441 | -0.17242 | 0.088797 | 0.015441 | south | N | 0.015441 | 0
88508 | FALFURRI | F | 0 | -0.061785 | south | N | -0.19189 | -0.021394 | -0.17838 | 0.082844 | 0.021394 | south | N | 0.021394 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:975 JKCREEK1 345 3400 TWIN_OAK 345 1 C: JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_98 (3391-44645) 3390 - 44645 CKT 1 & 3391 - 44645 CKT 1 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 177.3048 | 855 | 0.35396 | 302.6334 | 855 | 302.6334
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 177.3048 | 855 | 0.35396 | 302.6334 | 1710 | 605.2668
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 31.5831 | 152.3 | 0.35396 | 53.9077 | 1862.3 | 659.1745
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 31.7282 | 153 | 0.35396 | 54.1555 | 2015.3 | 713.33 | Weighted Shift Factors
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.17418 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 144.0469 | 827 | 0.32076 | 265.2712 |  |  | North | 0.13011
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.17418 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 142.6534 | 819 | 0.32076 | 262.7051 |  |  | Houston | -0.14658
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.14834 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.2297 | 615 | 0.29492 | 181.3784 |  |  |  | 0.27669
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.14834 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 87.0762 | 587 | 0.29492 | 173.1205
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.14694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.144 | 150.7 | 0.29352 | 44.2341 |  |  | Line Rating | 1376
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.14694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1881 | 151 | 0.29352 | 44.3222 |  |  | Conc Gen | 2015.3
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.14694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.0673 | 177.4 | 0.29352 | 52.0712 |  |  | Weighted Imp. | 713.33
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.14661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.2119 | 151.5 | 0.2932 | 44.4192 |  |  | PTDF | 0.35396
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.14661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.3292 | 152.3 | 0.2932 | 44.6538
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.14661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.0238 | 177.5 | 0.2932 | 52.0423 |  |  | Concentration | 1.2792
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.13959 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.9796 | 50 | 0.28618 | 14.3088
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.13951 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.28609 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.622 | 0 | 0.28592 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.1139 | 0 | 0.28592 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.204 | 0 | 0.28592 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | 1 | 55.5959 | 0 | 0.28592 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13884 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.2689 | 182 | 0.28542 | 51.947
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13884 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 67.1986 | 484 | 0.28542 | 138.1448
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.13871 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.8866 | 785 | 0.28529 | 223.9544
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.13871 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 110.2737 | 795 | 0.28529 | 226.8073
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.13871 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.193 | 780 | 0.28529 | 222.5279
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7876 | 161 | 0.28191 | 45.3875
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1936 | 164 | 0.28191 | 46.2333
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1936 | 164 | 0.28191 | 46.2333
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 56.0254 | 414 | 0.28191 | 116.7108
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.923 | 162 | 0.28191 | 45.6695
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7876 | 161 | 0.28191 | 45.3875
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0583 | 163 | 0.28191 | 45.9514
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 55.3487 | 409 | 0.28191 | 115.3013
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 52.1732 | 388 | 0.28105 | 109.0475
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.13447 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.2505 | 515 | 0.28105 | 144.7409
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13427 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.28085 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13427 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.28085 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.13417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6835 | 20 | 0.28076 | 5.6151
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.13417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.3544 | 25 | 0.28076 | 7.0189
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.13417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.5011 | 41 | 0.28076 | 11.511
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.134 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.5861 | 79 | 0.28058 | 22.1662
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.134 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.2041 | 106 | 0.28058 | 29.7419
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.134 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 19.5641 | 146 | 0.28058 | 40.9653
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.134 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1841 | 76 | 0.28058 | 21.3244
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.13398 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.3594 | 40 | 0.28057 | 11.2227
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.13385 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 74.6894 | 558 | 0.28044 | 156.4828
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.13385 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.5003 | 579 | 0.28044 | 162.372
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.13385 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.1524 | 808 | 0.28044 | 226.5916
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.13372 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.0292 | 0 | 0.28031 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.13372 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.6444 | 0 | 0.28031 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.13372 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.8211 | 0 | 0.28031 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3851 | 160 | 0.28024 | 44.8384
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.8505 | 156 | 0.28024 | 43.7175
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.1968 | 196 | 0.28024 | 54.9271
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.8505 | 156 | 0.28024 | 43.7175
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9841 | 157 | 0.28024 | 43.9977
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.4641 | 198 | 0.28024 | 55.4876
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.13355 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 49.4139 | 370 | 0.28013 | 103.6497
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.6971 | 0 | 0.28013 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.8307 | 0 | 0.28013 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 41.2673 | 0 | 0.28013 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.0978 | 0 | 0.28013 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.2313 | 0 | 0.28013 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 41.4008 | 0 | 0.28013 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.13328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 22.6574 | 170 | 0.27986 | 47.5766
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.13328 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.3051 | 520 | 0.27986 | 145.5283
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.13307 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.3228 | 0 | 0.27965 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.13307 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.3228 | 0 | 0.27965 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.13294 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.687 | 118 | 0.27952 | 32.9839
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.13294 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.2882 | 115 | 0.27952 | 32.1453
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.13294 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 73.9152 | 556 | 0.27952 | 155.4155
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.13284 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.7557 | 224 | 0.27942 | 62.5904
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.13278 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27937 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.13246 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27904 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.13052 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.5815 | 196 | 0.2771 | 54.3118
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.13052 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.4875 | 111 | 0.2771 | 30.7582
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.13025 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.815 | 60 | 0.27683 | 16.61
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.13025 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.2058 | 63 | 0.27683 | 17.4405
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.12877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 56.0132 | 435 | 0.27535 | 119.7769
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.12876 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 14.4855 | 112.5 | 0.27534 | 30.9761
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.12845 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 50.7389 | 395 | 0.27504 | 108.6393
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.12845 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 55.8771 | 435 | 0.27504 | 119.6408
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.12821 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27479 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.12821 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27479 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.12821 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27479 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.12805 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.71 | 216.4 | 0.27463 | 59.4306
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.12805 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.6716 | 216.1 | 0.27463 | 59.3482
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.12675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 36.504 | 288 | 0.27333 | 78.72
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.12675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.6322 | 147 | 0.27333 | 40.18
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.12675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.6322 | 147 | 0.27333 | 40.18
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.3391 | 224 | 0.2731 | 61.1738
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.5922 | 226 | 0.2731 | 61.72
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.821 | 212 | 0.2731 | 57.8966
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.6945 | 211 | 0.2731 | 57.6235
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.1261 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27268 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.12609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.7215 | 204 | 0.27267 | 55.6245
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.12609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.3433 | 201 | 0.27267 | 54.8065
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.12609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.5128 | 242 | 0.27267 | 65.9859
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.1258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.3359 | 217.3 | 0.27238 | 59.1884
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.1258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.7886 | 205 | 0.27238 | 55.8381
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.1258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.2674 | 272.4 | 0.27238 | 74.1966
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.12545 | north | 3 | N | N | Nnorth | Nnorth | 1 | 145.1468 | 0 | 0.27203 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.12545 | north | 3 | N | N | Nnorth | Nnorth | 1 | 145.2723 | 0 | 0.27203 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.12503 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.2506 | 18 | 0.27161 | 4.8891
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.12503 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.2506 | 18 | 0.27161 | 4.8891
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.12503 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.7512 | 38 | 0.27161 | 10.3213
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4846 | 20 | 0.27081 | 5.4163
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4846 | 20 | 0.27081 | 5.4163
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4846 | 20 | 0.27081 | 5.4163
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1119 | 17 | 0.27081 | 4.6038
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.1241 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 45.4202 | 366 | 0.27068 | 99.0697
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.684 | 70 | 0.27064 | 18.9448
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.5599 | 69 | 0.27064 | 18.6742
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.5599 | 69 | 0.27064 | 18.6742
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.4359 | 68 | 0.27064 | 18.4035
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.12397 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4876 | 0 | 0.27055 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.12397 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4876 | 0 | 0.27055 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.12379 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 14.8543 | 120 | 0.27037 | 32.4443
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.12326 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.8299 | 242 | 0.26985 | 65.303
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.12294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.6531 | 168 | 0.26952 | 45.2791
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.12294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.0641 | 90 | 0.26952 | 24.2566
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.12234 | west | 4 | Y | N | Ywest | Nwest | 1 | 79.4817 | 649.7 | 0.26892 | 174.7168
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.12229 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.9272 | 73 | 0.26887 | 19.6277
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.12229 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.5525 | 119 | 0.26887 | 31.9959
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.12229 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.0694 | 205 | 0.26887 | 55.119
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.12229 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.4736 | 102 | 0.26887 | 27.4251
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.12229 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.7398 | 96 | 0.26887 | 25.8118
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.12169 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.0787 | 165 | 0.26827 | 44.2649
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.12093 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.5388 | 236 | 0.26751 | 63.1324
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.12092 | west | 6 | Y | N | Ywest | Nwest | 1 | 48.3692 | 400 | 0.26751 | 107.0025
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.11959 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1756 | 60 | 0.26618 | 15.9706
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8052 | 150 | 0.26528 | 39.7926
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.8083 | 209 | 0.26528 | 55.4442
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0155 | 126.5 | 0.26528 | 33.5583
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.5563 | 249 | 0.26528 | 66.0555
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.3839 | 197 | 0.26528 | 52.2608
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.447 | 37.5 | 0.26517 | 9.9439
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7481 | 107.5 | 0.26517 | 28.5058
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0092 | 135 | 0.26517 | 35.798
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1119 | 119 | 0.26517 | 31.5553
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4516 | 105 | 0.26517 | 27.8429
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5463 | 80.5 | 0.26517 | 21.3462
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.11825 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.781 | 125 | 0.26483 | 33.1039
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.11825 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.781 | 125 | 0.26483 | 33.1039
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.7093 | 150 | 0.26465 | 39.6968
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9243 | 101 | 0.26465 | 26.7292
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.11802 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9135 | 84 | 0.2646 | 22.2265
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.11793 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.0757 | 60 | 0.26451 | 15.8707
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.11786 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6683 | 99 | 0.26445 | 26.1801
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.11786 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1896 | 61 | 0.26445 | 16.1312
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.11786 | west | 7 | N | N | Nwest | Nwest | 1 | 2.9465 | 0 | 0.26445 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.11786 | west | 7 | N | N | Nwest | Nwest | 1 | 5.3863 | 0 | 0.26445 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.11786 | west | 7 | N | N | Nwest | Nwest | 1 | 5.3863 | 0 | 0.26445 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.11784 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.616 | 141 | 0.26443 | 37.2842
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.11784 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1413 | 120 | 0.26443 | 31.7313
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.11779 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4211 | 63 | 0.26438 | 16.6558
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7717 | 66 | 0.26434 | 17.4462
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.125 | 69 | 0.26434 | 18.2392
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.125 | 69 | 0.26434 | 18.2392
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8895 | 67 | 0.26434 | 17.7105
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8895 | 67 | 0.26434 | 17.7105
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.6539 | 65 | 0.26434 | 17.1819
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6425 | 150 | 0.2642 | 39.63
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.8757 | 220 | 0.2642 | 58.124
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.5234 | 200 | 0.2642 | 52.84
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3375 | 121.9 | 0.2642 | 32.206
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.11743 | west | 8 | N | N | Nwest | Nwest | 1 | 8.2198 | 0 | 0.26401 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.11743 | west | 8 | N | N | Nwest | Nwest | 1 | 8.6191 | 0 | 0.26401 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.11743 | west | 8 | N | N | Nwest | Nwest | 1 | 8.2668 | 0 | 0.26401 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.11741 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1338 | 180 | 0.26399 | 47.5188
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.11741 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1338 | 180 | 0.26399 | 47.5188
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.11735 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.4035 | 225 | 0.26393 | 59.3847
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.11729 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0742 | 120 | 0.26387 | 31.6642
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.11729 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.3274 | 233 | 0.26387 | 61.4813
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.11729 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.9619 | 170.2 | 0.26387 | 44.9104
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.11724 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0682 | 120 | 0.26382 | 31.6582
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.11721 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0651 | 120 | 0.26379 | 31.6551
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.11684 | west | 8 | N | N | Nwest | Nwest | 1 | 3.0144 | 0 | 0.26342 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.11678 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.0136 | 214.2 | 0.26336 | 56.4118
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.11664 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.722 | 100.5 | 0.26322 | 26.4536
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.11662 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7638 | 58 | 0.2632 | 15.2657
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.1612 | 70 | 0.26317 | 18.422
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.1612 | 70 | 0.26317 | 18.422
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.8194 | 92.8 | 0.26317 | 24.4223
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.327 | 80 | 0.26317 | 21.0537
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.327 | 80 | 0.26317 | 21.0537
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.4076 | 115 | 0.26317 | 30.2647
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 24.2713 | 208.2 | 0.26316 | 54.79
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.5656 | 142.1 | 0.26316 | 37.3951
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.4348 | 132.4 | 0.26316 | 34.8424
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.8545 | 136 | 0.26316 | 35.7898
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.1368 | 147 | 0.26316 | 38.6846
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 24.4812 | 210 | 0.26316 | 55.2636
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.11657 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.4851 | 150 | 0.26315 | 39.4725
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.0848 | 112.5 | 0.26289 | 29.5754
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.3882 | 149.5 | 0.26289 | 39.3024
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.6335 | 186 | 0.26289 | 48.898
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.9483 | 214.5 | 0.26289 | 56.3904
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.11599 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.76551 | 6.6 | 0.26257 | 1.733
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.11599 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9783 | 34.3 | 0.26257 | 9.0061
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.11566 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2336 | 149 | 0.26225 | 39.0745
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.1155 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.5766 | 169.5 | 0.26208 | 44.4224
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.11546 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0412 | 35 | 0.26205 | 9.1716
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.11546 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4639 | 30 | 0.26205 | 7.8614
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.6167 | 66 | 0.26199 | 17.2912
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.5013 | 65 | 0.26199 | 17.0292
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7321 | 67 | 0.26199 | 17.5531
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7321 | 67 | 0.26199 | 17.5531
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7321 | 67 | 0.26199 | 17.5531
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.1154 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26199 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.1154 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26199 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.1111 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.53327 | 0 | 0.25768 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10932 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7454 | 80 | 0.2559 | 20.472
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10932 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7454 | 80 | 0.2559 | 20.472
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.10884 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1627 | 75 | 0.25542 | 19.1564
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10884 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7069 | 80 | 0.25542 | 20.4335
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.10884 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3534 | 40 | 0.25542 | 10.2168
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10873 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6985 | 80 | 0.25531 | 20.4251
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.10872 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6974 | 80 | 0.2553 | 20.424
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.10866 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2984 | 150 | 0.25524 | 38.2859
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.10866 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2984 | 150 | 0.25524 | 38.2859
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10626 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5004 | 80 | 0.25284 | 20.2271
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10585 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0976 | 76.5 | 0.25243 | 19.3112
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10544 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8573 | 84 | 0.25203 | 21.1703
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.10166 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5249 | 0 | 0.24825 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.10166 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5249 | 0 | 0.24825 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.09713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.5695 | 150 | 0.24371 | 36.557
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.09713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.7704 | 80 | 0.24371 | 19.4971
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.094995 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2237 | 255 | 0.24158 | 61.6024
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.094995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.1543 | 149 | 0.24158 | 35.9952
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.094995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.5342 | 153 | 0.24158 | 36.9615
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.092754 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23934 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.092754 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 72.9974 | 787 | 0.23934 | 188.3584
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.092524 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.23911 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.088231 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23481 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.088231 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23481 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.083139 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4709 | 150 | 0.22972 | 34.4583
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.02392 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.1705 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14658 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.14658 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.6337 | 100 | 0.11025 | 11.0246
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | 1 | -30.9597 | 0 | -0.054193 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | 1 | -31.3211 | 0 | -0.054193 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | 1 | -31.3211 | 0 | -0.054193 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | 1 | -76.2949 | 0 | -0.054193 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.2161 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -100.0566 | 463 | -0.069522 | -32.1886
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.23795 | north | 7 | N | N | Nnorth | Nnorth | 1 | -7.6145 | 0 | -0.091369 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096175 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096175 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.24276 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.1269 | 17 | -0.096175 | -1.635
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096175 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096175 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.2455 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -11.784 | 48 | -0.098917 | -4.748
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.2455 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -11.293 | 46 | -0.098917 | -4.5502
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.2455 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -25.7775 | 105 | -0.098917 | -10.3863
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.011155 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3472 | 569 | -0.11895 | -67.6851
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.011155 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.4811 | 581 | -0.11895 | -69.1126
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.005091 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.091638 | 0 | -0.12502 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.005091 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.091638 | 0 | -0.12502 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.005091 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.076365 | 0 | -0.12502 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.003682 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.050443 | 0 | -0.12643 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13011 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13011 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.001402 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.046266 | 0 | -0.13151 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.001402 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03505 | 0 | -0.13151 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.001402 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13151 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.003054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.085512 | 0 | -0.13316 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.003054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.088566 | 0 | -0.13316 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.003341 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4099 | 422 | -0.13345 | -56.3161
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004984 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.089712 | 0 | -0.13509 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004984 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.089712 | 0 | -0.13509 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.008709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.30482 | 0 | -0.13882 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.008709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29611 | 0 | -0.13882 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.008709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.30482 | 0 | -0.13882 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.44222 | 42 | -0.14064 | -5.9068
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.46328 | 44 | -0.14064 | -6.1881
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.46328 | 44 | -0.14064 | -6.1881
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.49486 | 47 | -0.14064 | -6.61
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.01138 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.09104 | 0 | -0.14149 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.01138 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.09104 | 0 | -0.14149 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.011598 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.5954 | 310 | -0.14171 | -43.9293
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.011598 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.79 | 413 | -0.14171 | -58.5252
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.65606 | 49 | -0.1435 | -7.0314
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.61589 | 46 | -0.1435 | -6.6009
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.61589 | 46 | -0.1435 | -6.6009
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.62928 | 47 | -0.1435 | -6.7444
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.013389 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.0619 | 154 | -0.1435 | -22.0988
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.013389 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9816 | 148 | -0.1435 | -21.2378
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.64267 | 48 | -0.1435 | -6.8879
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.64267 | 48 | -0.1435 | -6.8879
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.015294 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091764 | 0 | -0.1454 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.018525 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14863 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.019508 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.975 | 152.5 | -0.14962 | -22.8167
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.019508 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9164 | 149.5 | -0.14962 | -22.3678
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.019508 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5376 | 232.6 | -0.14962 | -34.801
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.02012 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.6558 | 132 | -0.15023 | -19.8303
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.02012 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.6961 | 134 | -0.15023 | -20.1308
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.02012 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.4988 | 323 | -0.15023 | -48.5241
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.021736 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4343 | 158 | -0.15185 | -23.9916
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.021736 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4778 | 160 | -0.15185 | -24.2953
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.021736 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8038 | 175 | -0.15185 | -26.573
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.030092 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18055 | 0 | -0.1602 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7104 | 50 | -0.16432 | -8.2158
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7104 | 50 | -0.16432 | -8.2158
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7104 | 50 | -0.16432 | -8.2158
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7104 | 50 | -0.16432 | -8.2158
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.8983 | 223.9 | -0.16539 | -37.0298
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.9371 | 225 | -0.16539 | -37.2117
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.923 | 224.6 | -0.16539 | -37.1456
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.9971 | 226.7 | -0.16539 | -37.4929
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.1424 | 114 | -0.16645 | -18.9749
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.0668 | 222 | -0.16645 | -36.9511
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.686 | 184 | -0.16645 | -30.6262
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.1395 | 224 | -0.16645 | -37.284
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.1788 | 115 | -0.16645 | -19.1414
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.036908 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.5543 | 584 | -0.16702 | -97.5382
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.036908 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.9603 | 595 | -0.16702 | -99.3754
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.037027 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.0327 | 433 | -0.16714 | -72.3701
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.038538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.092491 | 0 | -0.16865 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.038538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.092491 | 0 | -0.16865 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.038538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10791 | 0 | -0.16865 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.5846 | 142 | -0.16944 | -24.0601
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7026 | 145 | -0.16944 | -24.5684
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.9385 | 151 | -0.16944 | -25.5851
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.4051 | 290 | -0.16944 | -49.1369
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.039721 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15888 | 0 | -0.16983 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.040835 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.098004 | 0 | -0.17094 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.040835 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.098004 | 0 | -0.17094 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3439 | 147 | -0.17327 | -25.47
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.9555 | 138 | -0.17327 | -23.9106
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.0418 | 140 | -0.17327 | -24.2572
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3439 | 147 | -0.17327 | -25.47
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.8544 | 182 | -0.17327 | -31.5343
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.5449 | 198 | -0.17327 | -34.3066
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.043827 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.542 | 58 | -0.17394 | -10.0883
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.043827 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.9006 | 89 | -0.17394 | -15.4804
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9284 | 44 | -0.17394 | -7.6532
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9284 | 44 | -0.17394 | -7.6532
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8846 | 43 | -0.17394 | -7.4793
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9722 | 45 | -0.17394 | -7.8271
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.043841 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.8433 | 407 | -0.17395 | -70.7979
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.043904 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.0884 | 412 | -0.17401 | -71.6936
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.043904 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.5616 | 400 | -0.17401 | -69.6054
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.043929 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.6259 | 424 | -0.17404 | -73.7923
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.043929 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.6698 | 425 | -0.17404 | -73.9664
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.044036 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.2035 | 209 | -0.17415 | -36.3964
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.044036 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.5118 | 216 | -0.17415 | -37.6154
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0257 | 46 | -0.17415 | -8.0107
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0697 | 47 | -0.17415 | -8.1848
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0257 | 46 | -0.17415 | -8.0107
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0257 | 46 | -0.17415 | -8.0107
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.044103 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0585 | 24 | -0.17421 | -4.1811
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.044103 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.0585 | 24 | -0.17421 | -4.1811
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.044103 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.0144 | 23 | -0.17421 | -4.0069
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.044114 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17422 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.044114 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17422 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.044114 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17422 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.045027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9792 | 155 | -0.17514 | -27.1462
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.045027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6546 | 170 | -0.17514 | -29.7732
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.045027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9792 | 155 | -0.17514 | -27.1462
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.045875 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -25.0478 | 546 | -0.17598 | -96.0876
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.045875 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -34.4062 | 750 | -0.17598 | -131.9884
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.04824 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.57888 | 0 | -0.17835 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.050243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0243 | 100 | -0.18035 | -18.0353
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.050243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0243 | 100 | -0.18035 | -18.0353
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.050243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18035 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.050243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18035 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.050243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18035 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.050243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18035 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.050246 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18036 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.051128 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -20.2467 | 396 | -0.18124 | -71.7701
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.055832 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18594 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.059191 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1893 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.059609 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.71531 | 0 | -0.18972 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.059609 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6557 | 0 | -0.18972 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.059609 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.71531 | 0 | -0.18972 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.061785 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19189 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.062115 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -39.0703 | 629 | -0.19222 | -120.9092
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.063557 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.3111 | 146.5 | -0.19367 | -28.3721
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.063557 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4001 | 147.9 | -0.19367 | -28.6433
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.063557 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9954 | 173 | -0.19367 | -33.5043
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.064207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2908 | 207 | -0.19432 | -40.2235
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.064207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.9137 | 216.7 | -0.19432 | -42.1084
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.064207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.5381 | 242 | -0.19432 | -47.0246
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.064211 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2464 | 144 | -0.19432 | -27.9822
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.064211 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2464 | 144 | -0.19432 | -27.9822
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.064211 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9801 | 171 | -0.19432 | -33.2288
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.06467 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19478 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.06467 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.4575 | 38 | -0.19478 | -7.4016
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.06467 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2481 | 19.3 | -0.19478 | -3.7592
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.06467 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.97005 | 15 | -0.19478 | -2.9217
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.06467 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.0395 | 47 | -0.19478 | -9.1546
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.0954 | 94 | -0.19495 | -18.3257
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6586 | 41 | -0.19495 | -7.9931
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4641 | 38 | -0.19495 | -7.4083
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2321 | 19 | -0.19495 | -3.7041
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.0954 | 94 | -0.19495 | -18.3257
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.3344 | 36 | -0.19495 | -7.0184
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7883 | 43 | -0.19495 | -8.383
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4266 | 22 | -0.19495 | -4.289
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.5971 | 148 | -0.19495 | -28.8533
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2422 | 50 | -0.19495 | -9.7477
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5665 | 55 | -0.19495 | -10.7225
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2422 | 50 | -0.19495 | -9.7477
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.06513 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8888 | 0 | -0.19524 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.065726 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4976 | 0 | -0.19584 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.065764 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.499 | 0 | -0.19587 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.065862 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6465 | 0 | -0.19597 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.065862 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6465 | 0 | -0.19597 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.065929 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.0203 | 334 | -0.19604 | -65.4769
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.065929 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.4159 | 340 | -0.19604 | -66.6531
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.065929 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.8672 | 180 | -0.19604 | -35.2869
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.065929 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.8672 | 180 | -0.19604 | -35.2869
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.066162 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.9092 | 180 | -0.19627 | -35.3289
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.066186 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.8154 | 0 | -0.1963 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.066186 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.8352 | 0 | -0.1963 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.066186 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.1265 | 0 | -0.1963 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.0662 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.2432 | 336 | -0.19631 | -65.96
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.0662 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.916 | 180 | -0.19631 | -35.3357
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 25 | -0.19706 | -4.9266
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 25 | -0.19706 | -4.9266
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 25 | -0.19706 | -4.9266
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0712 | 16 | -0.19706 | -3.153
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 25 | -0.19706 | -4.9266
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 25 | -0.19706 | -4.9266
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 25 | -0.19706 | -4.9266
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0043 | 15 | -0.19706 | -2.9559
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.6582 | 0 | -0.19757 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.3209 | 0 | -0.19757 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.7457 | 0 | -0.19757 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7813 | 0 | -0.19757 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.9162 | 0 | -0.19757 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.567 | 0 | -0.19757 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.067457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.80948 | 0 | -0.19757 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.067815 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.7654 | 144 | -0.19792 | -28.5011
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.067815 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7492 | 188 | -0.19792 | -37.2098
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.289 | 47.7 | -0.19906 | -9.4952
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5719 | 37.3 | -0.19906 | -7.425
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1717 | 46 | -0.19906 | -9.1568
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3096 | 48 | -0.19906 | -9.5549
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.069005 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0374 | 0 | -0.19911 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.069541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5299 | 22 | -0.19965 | -4.3923
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.069541 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.76495 | 11 | -0.19965 | -2.1962
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.069541 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.76495 | 11 | -0.19965 | -2.1962
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.071031 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0655 | 0 | -0.20114 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.071031 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6337 | 0 | -0.20114 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.071747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.57398 | 0 | -0.20186 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.022 | 0 | -0.20233 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.50551 | 0 | -0.20233 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8164 | 0 | -0.20233 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0832 | 0 | -0.20233 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.50551 | 0 | -0.20233 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0832 | 0 | -0.20233 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8164 | 0 | -0.20233 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8164 | 0 | -0.20233 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.07521 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6101 | 0 | -0.20532 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.013 | 0 | -0.20622 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1652 | 0 | -0.20622 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.013 | 0 | -0.20622 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0891 | 0 | -0.20622 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9673 | 0 | -0.20622 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9028 | 0 | -0.20622 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5012 | 0 | -0.20622 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1312 | 0 | -0.20622 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3186 | 0 | -0.20622 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6324 | 0 | -0.20622 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.10846 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -144.5785 | 0 | -0.23857 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.10846 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -144.0362 | 0 | -0.23857 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2899 | 76 | -0.23919 | -18.1782
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2899 | 76 | -0.23919 | -18.1782
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.4531 | 105 | -0.23919 | -25.1146
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0717 | 74 | -0.23919 | -17.6998
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0717 | 74 | -0.23919 | -17.6998
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.1259 | 102 | -0.23919 | -24.397
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.11256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.4292 | 66 | -0.24267 | -16.0165
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.7022 | 0 | -0.25434 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.87 | 0 | -0.25434 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5903 | 0 | -0.25434 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5471 | 0 | -0.25434 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6837 | 0 | -0.25434 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9322 | 0 | -0.25434 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2115 | 0 | -0.25434 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2361 | 0 | -0.25434 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.6775 | 0 | -0.25434 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.696 | 0 | -0.25434 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.8264 | 0 | -0.25434 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.9445 | 0 | -0.25434 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.05 | 0 | -0.25434 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5471 | 0 | -0.25434 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.0502 | 0 | -0.25434 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.7956 | 0 | -0.25434 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4414 | 0 | -0.25434 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.9383 | 0 | -0.25434 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.9383 | 0 | -0.25434 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -21.2432 | 0 | -0.25434 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.12705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0206 | 0 | -0.25716 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.12705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2705 | 0 | -0.25716 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.3522 | 0 | -0.25941 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.3522 | 0 | -0.25941 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.3866 | 0 | -0.25941 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.1582 | 0 | -0.25941 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.13733 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3309 | 0 | -0.26744 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.13767 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -89.6264 | 651 | -0.26778 | -174.3277
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.13767 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -77.6487 | 564 | -0.26778 | -151.0305
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.13767 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -82.605 | 600 | -0.26778 | -160.6707
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.13774 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.4519 | 0 | -0.26785 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.13774 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.4519 | 0 | -0.26785 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.13774 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -33.7468 | 0 | -0.26785 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.13853 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5715 | 0 | -0.26864 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.13898 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -22.3751 | 161 | -0.26909 | -43.3228
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.13898 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -23.07 | 166 | -0.26909 | -44.6682
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.13898 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -34.466 | 248 | -0.26909 | -66.7332
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.13898 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -75.8809 | 546 | -0.26909 | -146.9207
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.13898 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -89.3616 | 0 | -0.26909 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.13898 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8067 | 13 | -0.26909 | -3.4981
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.3545 | 0 | -0.27323 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.2955 | 0 | -0.27323 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.698 | 0 | -0.27323 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.5978 | 0 | -0.27323 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.14312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5797 | 0 | -0.27323 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.14312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2935 | 0 | -0.27323 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.1342 | 0 | -0.27325 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5474 | 0 | -0.27325 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5864 | 0 | -0.27325 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.9289 | 0 | -0.27325 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.9718 | 0 | -0.27325 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.8001 | 0 | -0.27325 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.7413 | 0 | -0.27325 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -34.9259 | 0 | -0.27325 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.7256 | 0 | -0.27325 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.14489 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.2446 | 50 | -0.275 | -13.7501
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.14621 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.27632 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4484 | 0 | -0.27789 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.946 | 0 | -0.27789 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.8573 | 0 | -0.27789 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0543 | 0 | -0.27789 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.803 | 0 | -0.27789 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.646 | 0 | -0.27851 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.904 | 0 | -0.27851 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.646 | 0 | -0.27851 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.646 | 0 | -0.27851 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8694 | 46 | -0.27944 | -12.8544
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8694 | 46 | -0.27944 | -12.8544
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8694 | 46 | -0.27944 | -12.8544
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2134 | 55 | -0.27944 | -15.3694
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2134 | 55 | -0.27944 | -15.3694
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.064 | 54 | -0.27944 | -15.09
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.14954 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6644 | 0 | -0.27965 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.14954 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.9635 | 0 | -0.27965 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.4562 | 0 | -0.27996 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.5421 | 0 | -0.27996 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.602 | 0 | -0.27996 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.5271 | 0 | -0.27996 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -40.3107 | 0 | -0.27996 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.15012 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2542 | 0 | -0.28023 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.15039 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8047 | 12 | -0.2805 | -3.366
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.15039 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.2805 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.15041 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.4188 | 169 | -0.28052 | -47.4073
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.15043 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -24.8208 | 165 | -0.28054 | -46.2889
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.15045 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.4165 | 0 | -0.28056 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.15045 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.794 | 0 | -0.28056 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.1505 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -32.0567 | 213 | -0.28061 | -59.77
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4382 | 0 | -0.28062 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.6329 | 0 | -0.28062 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5125 | 0 | -0.28062 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.4325 | 0 | -0.28062 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0778 | 0 | -0.28062 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.15052 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -34.3195 | 228 | -0.28063 | -63.9844
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.15053 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.0961 | 0 | -0.28064 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.15053 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.8747 | 0 | -0.28064 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.15053 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.6338 | 0 | -0.28064 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.7153 | 0 | -0.28103 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.8662 | 0 | -0.28103 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8859 | 0 | -0.28103 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5276 | 0 | -0.28103 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.15154 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.6097 | 0 | -0.28165 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.3665 | 42 | -0.28169 | -11.8311
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.3665 | 42 | -0.28169 | -11.8311
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.7602 | 38 | -0.28169 | -10.7043
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.7602 | 38 | -0.28169 | -10.7043
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.15175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.2524 | 0 | -0.28186 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.15175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.486 | 0 | -0.28186 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -15.8856 | 104 | -0.28286 | -29.417
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -15.8856 | 104 | -0.28286 | -29.417
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2483 | 54 | -0.28286 | -15.2742
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0955 | 53 | -0.28286 | -14.9913
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2483 | 54 | -0.28286 | -15.2742
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.7065 | 57 | -0.28286 | -16.1228
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2483 | 54 | -0.28286 | -15.2742
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2483 | 54 | -0.28286 | -15.2742
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.8593 | 58 | -0.28286 | -16.4056
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.8593 | 58 | -0.28286 | -16.4056
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.1531 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -112.5314 | 735 | -0.28321 | -208.162
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2142 | 0 | -0.28347 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3215 | 0 | -0.28347 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0148 | 0 | -0.28347 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0391 | 0 | -0.28347 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7144 | 0 | -0.28347 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1285 | 0 | -0.28347 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0518 | 0 | -0.28347 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3675 | 0 | -0.28347 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7604 | 0 | -0.28347 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.0968 | 0 | -0.28347 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.697 | 0 | -0.28347 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.1537 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8444 | 12 | -0.28381 | -3.4057
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.15409 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.77046 | 0 | -0.2842 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.15409 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2359 | 0 | -0.2842 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0165 | 0 | -0.28421 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.1706 | 0 | -0.28421 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.787 | 0 | -0.28421 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.7083 | 0 | -0.28421 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5542 | 0 | -0.28421 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -16.0264 | 0 | -0.28421 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0919 | 0 | -0.28421 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.15412 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -1.8494 | 12 | -0.28423 | -3.4107
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.15414 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -114.529 | 743 | -0.28425 | -211.2004
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.15434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.2311 | 0 | -0.28445 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.15446 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -26.5664 | 172 | -0.28457 | -48.9453
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.15446 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -26.5664 | 172 | -0.28457 | -48.9453
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.15446 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -26.5664 | 172 | -0.28457 | -48.9453
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -25.2651 | 0 | -0.2853 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -25.0478 | 0 | -0.2853 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.6598 | 0 | -0.2853 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -41.7774 | 0 | -0.2853 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.15545 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -61.8703 | 398 | -0.28556 | -113.6539
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7306 | 56 | -0.28601 | -16.0168
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1983 | 59 | -0.28601 | -16.8748
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7306 | 56 | -0.28601 | -16.0168
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7306 | 56 | -0.28601 | -16.0168
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1983 | 59 | -0.28601 | -16.8748
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7306 | 56 | -0.28601 | -16.0168
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.7191 | 0 | -0.29034 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.9953 | 0 | -0.29034 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6748 | 0 | -0.29034 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6748 | 0 | -0.29034 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.16023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -25.9566 | 0 | -0.29034 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:975 JKCREEK1 345 3400 TWIN_OAK 345 1 C: JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_98 (3391-44645) 3390 - 44645 CKT 1 & 3391 - 44645 CKT 1 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.7191 | 0 | -0.29034 | 0 | 0 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.9953 | 0 | -0.29034 | 0 | 0 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6748 | 0 | -0.29034 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.16023 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6748 | 0 | -0.29034 | 0 | 0 | 0 | Weighted Shift Factors
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.16023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -25.9566 | 0 | -0.29034 | 0 | 0 | 0 | North | 0.13011
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7306 | 56 | -0.28601 | -16.0168 | 56 | 16.0168 | Houston | -0.14658
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1983 | 59 | -0.28601 | -16.8748 | 115 | 32.8916 |  | 0.27669
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7306 | 56 | -0.28601 | -16.0168 | 171 | 48.9083
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7306 | 56 | -0.28601 | -16.0168 | 227 | 64.9251 | Line Rating | 1376
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1983 | 59 | -0.28601 | -16.8748 | 286 | 81.7999 | Conc Gen | 2746
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.1559 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7306 | 56 | -0.28601 | -16.0168 | 342 | 97.8166 | Weighted Imp. | 781.0744
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.15545 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -61.8703 | 398 | -0.28556 | -113.6539 | 740 | 211.4705 | PTDF | 0.28444
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -25.2651 | 0 | -0.2853 | 0 | 740 | 211.4705
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -25.0478 | 0 | -0.2853 | 0 | 740 | 211.4705 | Concentration | 1.028
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.6598 | 0 | -0.2853 | 0 | 740 | 211.4705
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.15519 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -41.7774 | 0 | -0.2853 | 0 | 740 | 211.4705
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.15446 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -26.5664 | 172 | -0.28457 | -48.9453 | 912 | 260.4158
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.15446 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -26.5664 | 172 | -0.28457 | -48.9453 | 1084 | 309.3611
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.15446 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -26.5664 | 172 | -0.28457 | -48.9453 | 1256 | 358.3063
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.15434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.2311 | 0 | -0.28445 | 0 | 1256 | 358.3063
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.15414 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -114.529 | 743 | -0.28425 | -211.2004 | 1999 | 569.5067
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.15412 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -1.8494 | 0 | -0.28423 | 0 | 1999 | 569.5067
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0165 | 0 | -0.28421 | 0 | 1999 | 569.5067
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.1706 | 0 | -0.28421 | 0 | 1999 | 569.5067
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.787 | 0 | -0.28421 | 0 | 1999 | 569.5067
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.7083 | 0 | -0.28421 | 0 | 1999 | 569.5067
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5542 | 0 | -0.28421 | 0 | 1999 | 569.5067
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -16.0264 | 0 | -0.28421 | 0 | 1999 | 569.5067
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.1541 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0919 | 0 | -0.28421 | 0 | 1999 | 569.5067
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.15409 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.77046 | 0 | -0.2842 | 0 | 1999 | 569.5067
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.15409 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2359 | 0 | -0.2842 | 0 | 1999 | 569.5067
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.1537 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8444 | 12 | -0.28381 | -3.4057 | 2011 | 572.9124
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2142 | 0 | -0.28347 | 0 | 2011 | 572.9124
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3215 | 0 | -0.28347 | 0 | 2011 | 572.9124
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0148 | 0 | -0.28347 | 0 | 2011 | 572.9124
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0391 | 0 | -0.28347 | 0 | 2011 | 572.9124
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7144 | 0 | -0.28347 | 0 | 2011 | 572.9124
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1285 | 0 | -0.28347 | 0 | 2011 | 572.9124
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0518 | 0 | -0.28347 | 0 | 2011 | 572.9124
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3675 | 0 | -0.28347 | 0 | 2011 | 572.9124
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7604 | 0 | -0.28347 | 0 | 2011 | 572.9124
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.0968 | 0 | -0.28347 | 0 | 2011 | 572.9124
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.15336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.697 | 0 | -0.28347 | 0 | 2011 | 572.9124
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.1531 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -112.5314 | 735 | -0.28321 | -208.162 | 2746 | 781.0744
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -15.8856 | 104 | -0.28286 | -29.417
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -15.8856 | 104 | -0.28286 | -29.417
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2483 | 54 | -0.28286 | -15.2742
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0955 | 53 | -0.28286 | -14.9913
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2483 | 54 | -0.28286 | -15.2742
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.7065 | 57 | -0.28286 | -16.1228
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2483 | 54 | -0.28286 | -15.2742
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2483 | 54 | -0.28286 | -15.2742
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.8593 | 58 | -0.28286 | -16.4056
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.15275 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.8593 | 58 | -0.28286 | -16.4056
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.15175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.2524 | 0 | -0.28186 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.15175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.486 | 0 | -0.28186 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.3665 | 42 | -0.28169 | -11.8311
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.3665 | 42 | -0.28169 | -11.8311
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.7602 | 38 | -0.28169 | -10.7043
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.15158 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.7602 | 38 | -0.28169 | -10.7043
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.15154 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -20.6097 | 0 | -0.28165 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.7153 | 0 | -0.28103 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.8662 | 0 | -0.28103 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8859 | 0 | -0.28103 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.15092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5276 | 0 | -0.28103 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.15053 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.0961 | 0 | -0.28064 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.15053 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.8747 | 0 | -0.28064 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.15053 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.6338 | 0 | -0.28064 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.15052 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -34.3195 | 228 | -0.28063 | -63.9844
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.6329 | 0 | -0.28062 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5125 | 0 | -0.28062 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.4325 | 0 | -0.28062 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0778 | 0 | -0.28062 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.15051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4382 | 0 | -0.28062 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.1505 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -32.0567 | 213 | -0.28061 | -59.77
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.15045 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.4165 | 0 | -0.28056 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.15045 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.794 | 0 | -0.28056 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.15043 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -24.8208 | 165 | -0.28054 | -46.2889
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.15041 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.4188 | 169 | -0.28052 | -47.4073
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.15039 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8047 | 12 | -0.2805 | -3.366
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.15039 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.2805 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.15012 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2542 | 0 | -0.28023 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.4562 | 0 | -0.27996 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.5421 | 0 | -0.27996 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.602 | 0 | -0.27996 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.5271 | 0 | -0.27996 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.14985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -40.3107 | 0 | -0.27996 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.14954 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6644 | 0 | -0.27965 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.14954 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.9635 | 0 | -0.27965 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8694 | 46 | -0.27944 | -12.8544
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8694 | 46 | -0.27944 | -12.8544
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8694 | 46 | -0.27944 | -12.8544
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2134 | 55 | -0.27944 | -15.3694
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2134 | 55 | -0.27944 | -15.3694
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.14933 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.064 | 54 | -0.27944 | -15.09
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.646 | 0 | -0.27851 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.904 | 0 | -0.27851 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.646 | 0 | -0.27851 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.1484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.646 | 0 | -0.27851 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4484 | 0 | -0.27789 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.946 | 0 | -0.27789 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.8573 | 0 | -0.27789 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0543 | 0 | -0.27789 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.14778 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.803 | 0 | -0.27789 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.14621 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.27632 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.14489 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.2446 | 50 | -0.275 | -13.7501
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.1342 | 0 | -0.27325 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5474 | 0 | -0.27325 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5864 | 0 | -0.27325 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.9289 | 0 | -0.27325 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.9718 | 0 | -0.27325 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.8001 | 0 | -0.27325 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.7413 | 0 | -0.27325 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.14314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -34.9259 | 0 | -0.27325 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.14314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.7256 | 0 | -0.27325 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.14312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5797 | 0 | -0.27323 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.14312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2935 | 0 | -0.27323 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.3545 | 0 | -0.27323 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.2955 | 0 | -0.27323 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.698 | 0 | -0.27323 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.14312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.5978 | 0 | -0.27323 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.13898 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -22.3751 | 161 | -0.26909 | -43.3228
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.13898 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -23.07 | 166 | -0.26909 | -44.6682
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.13898 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -34.466 | 248 | -0.26909 | -66.7332
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.13898 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -75.8809 | 546 | -0.26909 | -146.9207
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.13898 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -89.3616 | 0 | -0.26909 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.13898 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8067 | 13 | -0.26909 | -3.4981
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.13853 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5715 | 0 | -0.26864 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.13774 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.4519 | 0 | -0.26785 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.13774 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.4519 | 0 | -0.26785 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.13774 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -33.7468 | 0 | -0.26785 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.13767 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -89.6264 | 0 | -0.26778 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.13767 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -77.6487 | 0 | -0.26778 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.13767 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -82.605 | 0 | -0.26778 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.13733 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3309 | 0 | -0.26744 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.3522 | 0 | -0.25941 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.3522 | 0 | -0.25941 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.3866 | 0 | -0.25941 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.1293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.1582 | 0 | -0.25941 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.12705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0206 | 0 | -0.25716 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.12705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2705 | 0 | -0.25716 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.7022 | 0 | -0.25434 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.87 | 0 | -0.25434 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5903 | 0 | -0.25434 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5471 | 0 | -0.25434 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6837 | 0 | -0.25434 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9322 | 0 | -0.25434 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2115 | 0 | -0.25434 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2361 | 0 | -0.25434 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.6775 | 0 | -0.25434 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.696 | 0 | -0.25434 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.8264 | 0 | -0.25434 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.9445 | 0 | -0.25434 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.05 | 0 | -0.25434 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5471 | 0 | -0.25434 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.0502 | 0 | -0.25434 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.7956 | 0 | -0.25434 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4414 | 0 | -0.25434 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.9383 | 0 | -0.25434 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.9383 | 0 | -0.25434 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.12423 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -21.2432 | 0 | -0.25434 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.11256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.4292 | 66 | -0.24267 | -16.0165
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2899 | 76 | -0.23919 | -18.1782
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2899 | 76 | -0.23919 | -18.1782
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.4531 | 105 | -0.23919 | -25.1146
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0717 | 74 | -0.23919 | -17.6998
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0717 | 74 | -0.23919 | -17.6998
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.10908 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.1259 | 102 | -0.23919 | -24.397
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.10846 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -144.5785 | 0 | -0.23857 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.10846 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -144.0362 | 0 | -0.23857 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.013 | 0 | -0.20622 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1652 | 0 | -0.20622 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.013 | 0 | -0.20622 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0891 | 0 | -0.20622 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9673 | 0 | -0.20622 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9028 | 0 | -0.20622 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5012 | 0 | -0.20622 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1312 | 0 | -0.20622 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3186 | 0 | -0.20622 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.076114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6324 | 0 | -0.20622 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.07521 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6101 | 0 | -0.20532 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.022 | 0 | -0.20233 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.50551 | 0 | -0.20233 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8164 | 0 | -0.20233 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0832 | 0 | -0.20233 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.50551 | 0 | -0.20233 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0832 | 0 | -0.20233 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8164 | 0 | -0.20233 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.072216 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8164 | 0 | -0.20233 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.071747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.57398 | 0 | -0.20186 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.071031 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0655 | 0 | -0.20114 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.071031 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6337 | 0 | -0.20114 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.069541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5299 | 22 | -0.19965 | -4.3923
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.069541 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.76495 | 11 | -0.19965 | -2.1962
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.069541 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.76495 | 11 | -0.19965 | -2.1962
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.069005 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0374 | 0 | -0.19911 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.289 | 47.7 | -0.19906 | -9.4952
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5719 | 37.3 | -0.19906 | -7.425
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1717 | 46 | -0.19906 | -9.1568
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.068951 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3096 | 48 | -0.19906 | -9.5549
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.067815 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.7654 | 144 | -0.19792 | -28.5011
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.067815 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7492 | 188 | -0.19792 | -37.2098
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.6582 | 0 | -0.19757 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.3209 | 0 | -0.19757 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.7457 | 0 | -0.19757 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7813 | 0 | -0.19757 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.9162 | 0 | -0.19757 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.067457 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.567 | 0 | -0.19757 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.067457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.80948 | 0 | -0.19757 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 0 | -0.19706 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 0 | -0.19706 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 0 | -0.19706 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0712 | 0 | -0.19706 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 0 | -0.19706 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 0 | -0.19706 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6738 | 0 | -0.19706 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.066953 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0043 | 0 | -0.19706 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.0662 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.2432 | 336 | -0.19631 | -65.96
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.0662 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.916 | 180 | -0.19631 | -35.3357
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.066186 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.8154 | 0 | -0.1963 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.066186 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.8352 | 0 | -0.1963 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.066186 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.1265 | 0 | -0.1963 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.066162 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.9092 | 180 | -0.19627 | -35.3289
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.065929 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.0203 | 334 | -0.19604 | -65.4769
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.065929 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.4159 | 340 | -0.19604 | -66.6531
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.065929 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.8672 | 180 | -0.19604 | -35.2869
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.065929 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.8672 | 180 | -0.19604 | -35.2869
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.065862 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6465 | 0 | -0.19597 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.065862 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6465 | 0 | -0.19597 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.065764 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.499 | 0 | -0.19587 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.065726 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4976 | 0 | -0.19584 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.06513 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8888 | 0 | -0.19524 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.0954 | 0 | -0.19495 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6586 | 0 | -0.19495 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4641 | 0 | -0.19495 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2321 | 0 | -0.19495 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.0954 | 0 | -0.19495 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.3344 | 0 | -0.19495 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7883 | 0 | -0.19495 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4266 | 0 | -0.19495 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.5971 | 0 | -0.19495 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2422 | 0 | -0.19495 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5665 | 0 | -0.19495 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.064845 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2422 | 0 | -0.19495 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.06467 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.4575 | 38 | -0.19478 | -7.4016
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.06467 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2481 | 19.3 | -0.19478 | -3.7592
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.06467 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.97005 | 15 | -0.19478 | -2.9217
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.06467 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.0395 | 47 | -0.19478 | -9.1546
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.06467 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19478 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.064211 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2464 | 144 | -0.19432 | -27.9822
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.064211 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2464 | 144 | -0.19432 | -27.9822
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.064211 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9801 | 171 | -0.19432 | -33.2288
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.064207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2908 | 207 | -0.19432 | -40.2235
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.064207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.9137 | 216.7 | -0.19432 | -42.1084
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.064207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.5381 | 242 | -0.19432 | -47.0246
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.063557 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.3111 | 146.5 | -0.19367 | -28.3721
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.063557 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4001 | 147.9 | -0.19367 | -28.6433
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.063557 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9954 | 173 | -0.19367 | -33.5043
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.062115 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -39.0703 | 0 | -0.19222 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.061785 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19189 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.059609 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.71531 | 0 | -0.18972 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.059609 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6557 | 0 | -0.18972 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.059609 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.71531 | 0 | -0.18972 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.059191 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1893 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.055832 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18594 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.051128 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -20.2467 | 0 | -0.18124 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.050246 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18036 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.050243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0243 | 100 | -0.18035 | -18.0353
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.050243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0243 | 100 | -0.18035 | -18.0353
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.050243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18035 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.050243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18035 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.050243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18035 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.050243 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.18035 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.04824 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.57888 | 0 | -0.17835 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.045875 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -25.0478 | 0 | -0.17598 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.045875 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -34.4062 | 0 | -0.17598 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.045027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9792 | 155 | -0.17514 | -27.1462
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.045027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6546 | 170 | -0.17514 | -29.7732
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.045027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9792 | 155 | -0.17514 | -27.1462
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.044114 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17422 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.044114 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17422 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.044114 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17422 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.044103 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0585 | 24 | -0.17421 | -4.1811
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.044103 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.0585 | 24 | -0.17421 | -4.1811
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.044103 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.0144 | 23 | -0.17421 | -4.0069
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.044036 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.2035 | 209 | -0.17415 | -36.3964
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.044036 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.5118 | 216 | -0.17415 | -37.6154
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0257 | 46 | -0.17415 | -8.0107
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0697 | 47 | -0.17415 | -8.1848
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0257 | 46 | -0.17415 | -8.0107
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.044036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0257 | 46 | -0.17415 | -8.0107
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.043929 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.6259 | 0 | -0.17404 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.043929 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.6698 | 0 | -0.17404 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.043904 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.0884 | 412 | -0.17401 | -71.6936
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.043904 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.5616 | 400 | -0.17401 | -69.6054
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.043841 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.8433 | 407 | -0.17395 | -70.7979
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.043827 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.542 | 58 | -0.17394 | -10.0883
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.043827 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.9006 | 89 | -0.17394 | -15.4804
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9284 | 44 | -0.17394 | -7.6532
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9284 | 44 | -0.17394 | -7.6532
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8846 | 43 | -0.17394 | -7.4793
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.043827 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9722 | 45 | -0.17394 | -7.8271
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3439 | 147 | -0.17327 | -25.47
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.9555 | 138 | -0.17327 | -23.9106
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.0418 | 140 | -0.17327 | -24.2572
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3439 | 147 | -0.17327 | -25.47
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.8544 | 182 | -0.17327 | -31.5343
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.043156 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.5449 | 198 | -0.17327 | -34.3066
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042558 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35749 | 8.4 | -0.17267 | -1.4504
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.040835 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.098004 | 0 | -0.17094 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.040835 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.098004 | 0 | -0.17094 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.039721 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15888 | 0 | -0.16983 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.5846 | 142 | -0.16944 | -24.0601
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7026 | 145 | -0.16944 | -24.5684
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.9385 | 151 | -0.16944 | -25.5851
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.039328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.4051 | 290 | -0.16944 | -49.1369
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.038538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.092491 | 0 | -0.16865 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.038538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.092491 | 0 | -0.16865 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.038538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10791 | 0 | -0.16865 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.037027 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.0327 | 0 | -0.16714 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.036908 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.5543 | 0 | -0.16702 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.036908 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.9603 | 0 | -0.16702 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.1424 | 0 | -0.16645 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.0668 | 0 | -0.16645 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.686 | 0 | -0.16645 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.1395 | 0 | -0.16645 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.1788 | 0 | -0.16645 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.8983 | 223.9 | -0.16539 | -37.0298
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.9371 | 225 | -0.16539 | -37.2117
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.923 | 224.6 | -0.16539 | -37.1456
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.035276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.9971 | 226.7 | -0.16539 | -37.4929
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7104 | 50 | -0.16432 | -8.2158
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7104 | 50 | -0.16432 | -8.2158
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7104 | 50 | -0.16432 | -8.2158
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.034207 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7104 | 50 | -0.16432 | -8.2158
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.030092 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18055 | 0 | -0.1602 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.021736 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4343 | 158 | -0.15185 | -23.9916
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.021736 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4778 | 160 | -0.15185 | -24.2953
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.021736 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8038 | 175 | -0.15185 | -26.573
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.02012 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.6558 | 132 | -0.15023 | -19.8303
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.02012 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.6961 | 134 | -0.15023 | -20.1308
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.02012 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.4988 | 323 | -0.15023 | -48.5241
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.019508 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.975 | 152.5 | -0.14962 | -22.8167
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.019508 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9164 | 149.5 | -0.14962 | -22.3678
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.019508 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5376 | 232.6 | -0.14962 | -34.801
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.018525 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14863 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.015294 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.091764 | 0 | -0.1454 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.65606 | 49 | -0.1435 | -7.0314
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.61589 | 46 | -0.1435 | -6.6009
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.61589 | 46 | -0.1435 | -6.6009
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.62928 | 47 | -0.1435 | -6.7444
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.013389 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.0619 | 154 | -0.1435 | -22.0988
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.013389 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9816 | 148 | -0.1435 | -21.2378
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.64267 | 48 | -0.1435 | -6.8879
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.013389 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.64267 | 48 | -0.1435 | -6.8879
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.011598 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.5954 | 310 | -0.14171 | -43.9293
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.011598 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.79 | 413 | -0.14171 | -58.5252
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.01138 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.09104 | 0 | -0.14149 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.01138 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.09104 | 0 | -0.14149 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.44222 | 42 | -0.14064 | -5.9068
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.46328 | 44 | -0.14064 | -6.1881
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.46328 | 44 | -0.14064 | -6.1881
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.010529 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.49486 | 47 | -0.14064 | -6.61
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.008709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.30482 | 0 | -0.13882 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.008709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29611 | 0 | -0.13882 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.008709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.30482 | 0 | -0.13882 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004984 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.089712 | 0 | -0.13509 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004984 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.089712 | 0 | -0.13509 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.003341 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4099 | 422 | -0.13345 | -56.3161
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.003054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.085512 | 0 | -0.13316 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.003054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.088566 | 0 | -0.13316 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.001402 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.046266 | 0 | -0.13151 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.001402 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03505 | 0 | -0.13151 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.001402 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13151 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13011 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13011 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13011 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.003682 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.050443 | 0 | -0.12643 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.005091 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.091638 | 0 | -0.12502 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.005091 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.091638 | 0 | -0.12502 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.005091 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.076365 | 0 | -0.12502 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.011155 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3472 | 0 | -0.11895 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.011155 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.4811 | 0 | -0.11895 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.2455 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -11.784 | 48 | -0.098917 | -4.748
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.2455 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -11.293 | 46 | -0.098917 | -4.5502
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.2455 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -25.7775 | 105 | -0.098917 | -10.3863
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096175 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096175 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.24276 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.1269 | 17 | -0.096175 | -1.635
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096175 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.24276 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096175 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.23795 | north | 7 | N | N | Nnorth | Nnorth | 1 | -7.6145 | 0 | -0.091369 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.2161 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -100.0566 | 0 | -0.069522 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | 1 | -30.9597 | 0 | -0.054193 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | 1 | -31.3211 | 0 | -0.054193 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | 1 | -31.3211 | 0 | -0.054193 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.20078 | north | 1 | N | N | Nnorth | Nnorth | 1 | -76.2949 | 0 | -0.054193 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.036337 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.6337 | 0 | 0.11025 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14658 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.14658 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.02392 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.1705 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.083139 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4709 | 0 | 0.22972 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.088231 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23481 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.088231 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23481 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.092524 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.23911 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.092754 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23934 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.092754 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 72.9974 | 787 | 0.23934 | 188.3584
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.094995 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2237 | 255 | 0.24158 | 61.6024
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.094995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.1543 | 149 | 0.24158 | 35.9952
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.094995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.5342 | 153 | 0.24158 | 36.9615
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.09713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.5695 | 150 | 0.24371 | 36.557
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.09713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.7704 | 80 | 0.24371 | 19.4971
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.10166 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5249 | 0 | 0.24825 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.10166 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5249 | 0 | 0.24825 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10544 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8573 | 0 | 0.25203 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10585 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0976 | 0 | 0.25243 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10626 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5004 | 0 | 0.25284 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.10866 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2984 | 0 | 0.25524 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.10866 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2984 | 0 | 0.25524 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.10872 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6974 | 0 | 0.2553 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10873 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6985 | 0 | 0.25531 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.10884 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1627 | 0 | 0.25542 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10884 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7069 | 0 | 0.25542 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.10884 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3534 | 0 | 0.25542 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10932 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7454 | 0 | 0.2559 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10932 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7454 | 0 | 0.2559 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.1111 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.53327 | 0 | 0.25768 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.6167 | 66 | 0.26199 | 17.2912
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.5013 | 65 | 0.26199 | 17.0292
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7321 | 67 | 0.26199 | 17.5531
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7321 | 67 | 0.26199 | 17.5531
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.1154 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7321 | 67 | 0.26199 | 17.5531
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.1154 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26199 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.1154 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26199 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.11546 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0412 | 0 | 0.26205 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.11546 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4639 | 0 | 0.26205 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.1155 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.5766 | 0 | 0.26208 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.11566 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2336 | 0 | 0.26225 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.11599 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.76551 | 0 | 0.26257 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.11599 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9783 | 0 | 0.26257 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.0848 | 0 | 0.26289 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.3882 | 0 | 0.26289 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.6335 | 0 | 0.26289 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.11631 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.9483 | 0 | 0.26289 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.11657 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.4851 | 0 | 0.26315 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 24.2713 | 208.2 | 0.26316 | 54.79
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.5656 | 142.1 | 0.26316 | 37.3951
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.4348 | 132.4 | 0.26316 | 34.8424
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.8545 | 136 | 0.26316 | 35.7898
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.1368 | 147 | 0.26316 | 38.6846
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.11658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 24.4812 | 210 | 0.26316 | 55.2636
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.1612 | 70 | 0.26317 | 18.422
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.1612 | 70 | 0.26317 | 18.422
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.8194 | 92.8 | 0.26317 | 24.4223
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.327 | 80 | 0.26317 | 21.0537
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.327 | 80 | 0.26317 | 21.0537
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.11659 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.4076 | 115 | 0.26317 | 30.2647
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.11662 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7638 | 0 | 0.2632 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.11664 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.722 | 0 | 0.26322 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.11678 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.0136 | 0 | 0.26336 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.11684 | west | 8 | N | N | Nwest | Nwest | 1 | 3.0144 | 0 | 0.26342 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.11721 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0651 | 0 | 0.26379 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.11724 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0682 | 0 | 0.26382 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.11729 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0742 | 0 | 0.26387 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.11729 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.3274 | 0 | 0.26387 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.11729 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.9619 | 0 | 0.26387 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.11735 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.4035 | 0 | 0.26393 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.11741 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1338 | 0 | 0.26399 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.11741 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1338 | 0 | 0.26399 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.11743 | west | 8 | N | N | Nwest | Nwest | 1 | 8.2198 | 0 | 0.26401 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.11743 | west | 8 | N | N | Nwest | Nwest | 1 | 8.6191 | 0 | 0.26401 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.11743 | west | 8 | N | N | Nwest | Nwest | 1 | 8.2668 | 0 | 0.26401 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6425 | 0 | 0.2642 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.8757 | 0 | 0.2642 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.5234 | 0 | 0.2642 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3375 | 0 | 0.2642 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7717 | 66 | 0.26434 | 17.4462
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.125 | 69 | 0.26434 | 18.2392
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.125 | 69 | 0.26434 | 18.2392
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8895 | 67 | 0.26434 | 17.7105
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8895 | 67 | 0.26434 | 17.7105
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.11775 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.6539 | 65 | 0.26434 | 17.1819
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.11779 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4211 | 0 | 0.26438 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.11784 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.616 | 0 | 0.26443 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.11784 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1413 | 0 | 0.26443 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.11786 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6683 | 0 | 0.26445 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.11786 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1896 | 0 | 0.26445 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.11786 | west | 7 | N | N | Nwest | Nwest | 1 | 2.9465 | 0 | 0.26445 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.11786 | west | 7 | N | N | Nwest | Nwest | 1 | 5.3863 | 0 | 0.26445 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.11786 | west | 7 | N | N | Nwest | Nwest | 1 | 5.3863 | 0 | 0.26445 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.11793 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.0757 | 0 | 0.26451 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.11802 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9135 | 0 | 0.2646 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.7093 | 0 | 0.26465 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9243 | 0 | 0.26465 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.11825 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.781 | 0 | 0.26483 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.11825 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.781 | 0 | 0.26483 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.447 | 0 | 0.26517 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7481 | 0 | 0.26517 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0092 | 0 | 0.26517 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1119 | 0 | 0.26517 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4516 | 0 | 0.26517 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.11859 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5463 | 0 | 0.26517 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.8083 | 0 | 0.26528 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0155 | 0 | 0.26528 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.5563 | 0 | 0.26528 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.3839 | 0 | 0.26528 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.1187 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8052 | 0 | 0.26528 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.11959 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1756 | 0 | 0.26618 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.12092 | west | 6 | Y | N | Ywest | Nwest | 1 | 48.3692 | 0 | 0.26751 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.12093 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.5388 | 0 | 0.26751 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.12169 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.0787 | 0 | 0.26827 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.12229 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.9272 | 73 | 0.26887 | 19.6277
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.12229 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.5525 | 119 | 0.26887 | 31.9959
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.12229 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.0694 | 205 | 0.26887 | 55.119
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.12229 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.4736 | 102 | 0.26887 | 27.4251
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.12229 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.7398 | 96 | 0.26887 | 25.8118
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.12234 | west | 4 | Y | N | Ywest | Nwest | 1 | 79.4817 | 0 | 0.26892 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.12294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.6531 | 168 | 0.26952 | 45.2791
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.12294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.0641 | 90 | 0.26952 | 24.2566
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.12326 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.8299 | 242 | 0.26985 | 65.303
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.12379 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 14.8543 | 0 | 0.27037 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.12397 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4876 | 0 | 0.27055 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.12397 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4876 | 0 | 0.27055 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.684 | 70 | 0.27064 | 18.9448
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.5599 | 69 | 0.27064 | 18.6742
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.5599 | 69 | 0.27064 | 18.6742
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.12406 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.4359 | 68 | 0.27064 | 18.4035
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.1241 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 45.4202 | 366 | 0.27068 | 99.0697
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4846 | 20 | 0.27081 | 5.4163
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4846 | 20 | 0.27081 | 5.4163
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4846 | 20 | 0.27081 | 5.4163
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.12423 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1119 | 17 | 0.27081 | 4.6038
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.12503 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.2506 | 18 | 0.27161 | 4.8891
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.12503 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.2506 | 18 | 0.27161 | 4.8891
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.12503 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.7512 | 38 | 0.27161 | 10.3213
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.12545 | north | 3 | N | N | Nnorth | Nnorth | 1 | 145.1468 | 0 | 0.27203 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.12545 | north | 3 | N | N | Nnorth | Nnorth | 1 | 145.2723 | 0 | 0.27203 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.1258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.3359 | 217.3 | 0.27238 | 59.1884
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.1258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.7886 | 205 | 0.27238 | 55.8381
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.1258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.2674 | 272.4 | 0.27238 | 74.1966
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.12609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.7215 | 204 | 0.27267 | 55.6245
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.12609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.3433 | 201 | 0.27267 | 54.8065
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.12609 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.5128 | 242 | 0.27267 | 65.9859
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.1261 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27268 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.3391 | 224 | 0.2731 | 61.1738
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.5922 | 226 | 0.2731 | 61.72
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.821 | 212 | 0.2731 | 57.8966
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.12651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.6945 | 211 | 0.2731 | 57.6235
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.12675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 36.504 | 288 | 0.27333 | 78.72
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.12675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.6322 | 147 | 0.27333 | 40.18
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.12675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.6322 | 147 | 0.27333 | 40.18
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.12805 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.71 | 216.4 | 0.27463 | 59.4306
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.12805 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.6716 | 216.1 | 0.27463 | 59.3482
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.12821 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27479 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.12821 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27479 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.12821 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27479 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.12845 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 50.7389 | 395 | 0.27504 | 108.6393
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.12845 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 55.8771 | 435 | 0.27504 | 119.6408
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.12876 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 14.4855 | 0 | 0.27534 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.12877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 56.0132 | 435 | 0.27535 | 119.7769
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.13025 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.815 | 60 | 0.27683 | 16.61
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.13025 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.2058 | 63 | 0.27683 | 17.4405
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.13052 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.5815 | 196 | 0.2771 | 54.3118
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.13052 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.4875 | 111 | 0.2771 | 30.7582
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.13246 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27904 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.13278 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27937 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.13284 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.7557 | 224 | 0.27942 | 62.5904
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.13294 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.687 | 118 | 0.27952 | 32.9839
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.13294 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.2882 | 115 | 0.27952 | 32.1453
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.13294 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 73.9152 | 556 | 0.27952 | 155.4155
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.13307 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.3228 | 0 | 0.27965 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.13307 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.3228 | 0 | 0.27965 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.13328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 22.6574 | 170 | 0.27986 | 47.5766
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.13328 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.3051 | 520 | 0.27986 | 145.5283
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.13355 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 49.4139 | 370 | 0.28013 | 103.6497
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.6971 | 0 | 0.28013 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.8307 | 0 | 0.28013 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 41.2673 | 0 | 0.28013 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.0978 | 0 | 0.28013 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.2313 | 0 | 0.28013 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.13355 | north | 1 | N | N | Nnorth | Nnorth | 1 | 41.4008 | 0 | 0.28013 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3851 | 160 | 0.28024 | 44.8384
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.8505 | 156 | 0.28024 | 43.7175
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.1968 | 196 | 0.28024 | 54.9271
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.8505 | 156 | 0.28024 | 43.7175
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9841 | 157 | 0.28024 | 43.9977
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.13366 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.4641 | 198 | 0.28024 | 55.4876
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.13372 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.0292 | 0 | 0.28031 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.13372 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.6444 | 0 | 0.28031 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.13372 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.8211 | 0 | 0.28031 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.13385 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 74.6894 | 0 | 0.28044 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.13385 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.5003 | 0 | 0.28044 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.13385 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.1524 | 0 | 0.28044 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.13398 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.3594 | 40 | 0.28057 | 11.2227
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.134 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.5861 | 79 | 0.28058 | 22.1662
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.134 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.2041 | 106 | 0.28058 | 29.7419
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.134 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 19.5641 | 146 | 0.28058 | 40.9653
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.134 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1841 | 76 | 0.28058 | 21.3244
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.13417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6835 | 20 | 0.28076 | 5.6151
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.13417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.3544 | 25 | 0.28076 | 7.0189
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.13417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.5011 | 41 | 0.28076 | 11.511
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13427 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.28085 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13427 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.28085 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 52.1732 | 388 | 0.28105 | 109.0475
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.13447 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.2505 | 515 | 0.28105 | 144.7409
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7876 | 161 | 0.28191 | 45.3875
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1936 | 164 | 0.28191 | 46.2333
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1936 | 164 | 0.28191 | 46.2333
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 56.0254 | 414 | 0.28191 | 116.7108
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.923 | 162 | 0.28191 | 45.6695
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7876 | 161 | 0.28191 | 45.3875
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0583 | 163 | 0.28191 | 45.9514
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.13533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 55.3487 | 409 | 0.28191 | 115.3013
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.13871 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.8866 | 0 | 0.28529 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.13871 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 110.2737 | 0 | 0.28529 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.13871 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.193 | 0 | 0.28529 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13884 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.2689 | 182 | 0.28542 | 51.947
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13884 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 67.1986 | 484 | 0.28542 | 138.1448
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.622 | 0 | 0.28592 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.1139 | 0 | 0.28592 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.204 | 0 | 0.28592 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.13934 | north | 1 | N | N | Nnorth | Nnorth | 1 | 55.5959 | 0 | 0.28592 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.13951 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.28609 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.13959 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.9796 | 0 | 0.28618 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.14661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.2119 | 151.5 | 0.2932 | 44.4192
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.14661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.3292 | 152.3 | 0.2932 | 44.6538
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.14661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.0238 | 177.5 | 0.2932 | 52.0423
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.14694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.144 | 150.7 | 0.29352 | 44.2341
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.14694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1881 | 151 | 0.29352 | 44.3222
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.14694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.0673 | 177.4 | 0.29352 | 52.0712
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.14834 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.2297 | 0 | 0.29492 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.14834 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 87.0762 | 0 | 0.29492 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.17418 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 144.0469 | 0 | 0.32076 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.17418 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 142.6534 | 0 | 0.32076 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 177.3048 | 0 | 0.35396 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 177.3048 | 0 | 0.35396 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 31.5831 | 0 | 0.35396 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.20737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 31.7282 | 0 | 0.35396 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1376
| 25 | 1376
| 30 | 1376
| 35 | 1376
| 40 | 1376
| 45 | 1376
| 50 | 1376
| 55 | 1376
| 60 | 1376
| 65 | 1376
| 70 | 1376
| 75 | 1376
| 80 | 1376
| 85 | 1376
| 90 | 1376
| 95 | 1376
| 100 | 1376
| 105 | 1376
| 110 | 1376
| 115 | 1376
| Max | 1376
| Min | 1376
| Avg | 1376