## test results
CRE test for: |  | Garrot - Midtown 138kV 47660-47705 | [5 empty] | FAIL
Line Rating: |  | 247
Direction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Garrot - Midtown 138kV 47660-47705
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.0047502
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.015653
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.0060093
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.015968
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Garrot - Midtown 138kV 47660-47705
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.0052627
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.015832
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.005992
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.027666
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Garrot - Midtown 138kV 47660-47705
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.011081
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.0012418
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.032416
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.0096614
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.031621
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.033676
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.032416 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.032416 | -0.011081
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.078739
[6 empty] | Concentration |  | 2.429 | FAIL
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.18532
[6 empty] | Concentration |  | 5.717 | FAIL
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 115.951
| Percent of line rating => | [6 empty] | 46.94% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 10.6106
[7 empty] | B1(N-S) | 0.34593 | 0.22835 | -0.11758 | 0.34593
[7 empty] | B2 (N-W) | 0.039309 | 0.026133 | -0.013176 | 0.039309
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.3018 | -0.19929 | 0.10251 | -0.3018
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.21698 | 0.11854 | 0.33552 | -0.21698
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.039849 | 0.31747 | 0.35732 | -0.039849
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 100.6%
Deployment Error Percent | [6 empty] | B2 | 11.43%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -87.74%
[7 empty] | B5 | -63.08%
[7 empty] | B6 | -11.59%
[7 empty] | Max Abs Error | 100.6% | FAIL

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-H
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:Garrot - Midtown 138kV 47660-47705 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45972 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:Garrot - Midtown 138kV 47660-47705 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45972
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.006974 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 1.7784
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.006974 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.0391
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.006601 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.099015
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.006601 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.099015
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.006974 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.067
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.006861 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 1.0292
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.006861 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.54888
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005626 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 0.4107
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005626 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 0.66949
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005626 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 1.1533
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005626 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 0.57385
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005626 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 0.5401
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.00555 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.0666
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.00555 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.0666
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.005575 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 0.9366
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.005575 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 0.50175
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.005483 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.098694
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.005483 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.098694
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.005483 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.20835
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.005394 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 1.5535
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.005394 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 0.79292
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.005394 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 0.79292
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.005287 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 0.59479
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.1998
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 0.3946
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 0.52947
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 0.72927
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004995 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 0.37962
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.005206 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 0.31236
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.005206 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 0.32798
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.004985 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.0997
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.004985 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.12462
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.004985 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.20439
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.001117 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 0.51717
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 0.40148
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 0.39539
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.40756
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.40756
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.40756
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.006083 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 0.69346
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.006083 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 3.1327
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 0.39184
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 0.40965
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 0.40965
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 0.39778
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 0.39778
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 0.3859
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.005957 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 0.41699
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.005957 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 0.43724
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.005957 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 0.41937
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 0.8919
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 1.3081
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.00593 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 0.58707
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.00593 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 0.36173
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.005931 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 0.83627
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.00593 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.14825
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.00593 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.271
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.00593 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.271
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.005931 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 0.71172
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.005993 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.15462
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.006006 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 0.6036
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.00597 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 0.7164
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.006007 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 0.34841
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.005997 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 1.2846
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.005915 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 0.88725
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.006044 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.03989
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.006044 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 0.20731
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.005915 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 0.59742
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.005969 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 0.71628
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.005556 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 2.0335
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.0056 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 1.3552
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.005746 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 2.2984
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.005745 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 1.3558
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 0.9405
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.005439 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 1.1096
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.005439 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 1.0932
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.005439 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 1.3162
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.11096
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.11096
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.11096
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.094316
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.00556 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 0.6672
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.005866 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 0.35196
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.005011 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 0.37583
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.005011 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 0.39888
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.005011 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 0.44297
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 0.8024
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.78234
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 0.98294
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.78234
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 0.78736
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 0.99297
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.005037 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 0.85629
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.005037 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 2.6192
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.005022 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 1.8581
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.005004 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 2.7922
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.005004 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 2.8973
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.005004 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 4.0432
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.005315 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 0.59528
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.005315 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 0.5315
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.005315 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 2.0091
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.005442 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 1.1825
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.005442 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 1.1156
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.005442 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 1.4824
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.005424 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 4.1765
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 0.38682
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.38129
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.38129
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.37577
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.005461 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 6.3184
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.005461 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 6.3238
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 1.2067
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 1.2175
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.005308 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 1.1487
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.005308 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 1.1471
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 1.142
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 1.1367
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.005297 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 2.0923
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.005281 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 2.2972
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.005297 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 2.3042
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.005084 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 0.70159
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.005064 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 0.59755
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.005064 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 0.58236
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.005064 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 2.8156
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.004976 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 1.9307
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.004976 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 2.5626
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004695 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 3.6856
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004695 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 3.7325
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004695 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 3.6621
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.004624 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 0.84157
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.004624 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 2.238
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.004913 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 1.1005
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.004628 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.2314
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.004632 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.19454
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.00419 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 2.5768
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.00419 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 2.4595
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.007104 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 3.8148
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.007104 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 5.5908
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.007191 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.53933
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.007191 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 1.5964
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.011096 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 6.3136
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015978 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 3.3394
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015978 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 3.4512
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.015954 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 6.4933
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.73499
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.75097
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.73499
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.73499
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.015954 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 6.7645
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.015954 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 6.7805
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015969 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.9262
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015969 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 1.4212
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.70264
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.70264
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.68667
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.71861
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.015962 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 6.5763
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.015962 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 6.3848
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.016122 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 8.8026
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.016122 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 12.0915
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.015961 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.97362
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.015961 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 1.5163
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.015961 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 2.4101
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.016048 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 2.4874
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.016048 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 2.7282
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.016048 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 2.4874
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.018976 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.41747
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.018976 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.20874
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.018976 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.20874
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.90382
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.70676
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.87161
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.9095
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.017453 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.20944
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.017453 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.19198
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.016201 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.38882
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.016201 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.38882
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.016201 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.37262
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.016625 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 6.5835
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.020755 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 27.6664
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.020755 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 27.5626
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017872 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.67914
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017872 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.34493
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017872 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.26808
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017872 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.83998
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.006492 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 0.4869
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.005878 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 0.8817
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.006069 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 1.0287
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.008063 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 1.2094
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.005934 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 0.37384
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.005661 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 3.678
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.005049 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.20196
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.005049 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.20196
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.012954 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 5.4666
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.013579 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 1.7924
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.013579 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 1.8196
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.013579 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 4.386
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.013843 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 2.1872
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.013843 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 2.2149
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.013843 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 2.4225
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.014699 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 8.5842
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.014699 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 8.7459
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.014715 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 6.3716
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 3.3932
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 3.4099
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 3.4038
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 3.4356
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.013273 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.10618
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.013273 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.10618
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.0124 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.2232
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.0124 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.2232
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.0124 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.186
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.012503 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.17129
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.013017 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.23431
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.013017 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.23431
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.013159 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.46057
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.013159 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.44741
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.013159 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.46057
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.012926 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.36193
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.012926 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.37485
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.006079 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 0.21277
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.006079 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 0.18237
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.7077
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.7077
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.7077
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.7077
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.014764 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.088584
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.015463 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.037111
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.015463 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.037111
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.015463 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.043296
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.015564 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.062256
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.015676 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.037622
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.015676 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.037622
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 2.3275
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 2.185
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 2.2166
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 2.3275
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 2.8816
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 3.1349
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.013804 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 2.1051
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.013804 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 2.0637
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.013804 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 3.2108
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 2.2016
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 2.2481
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 2.3411
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 4.4962
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.013469 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.44448
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.013469 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.33672
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.017453 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.20944
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.01899 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 1.3863
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.5639
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 1.6035
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.54034
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.13509
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.5639
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 1.5837
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 1.552
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.4949
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.91062
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.017973 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 11.305
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.01887 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 2.7173
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.01887 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 3.5476
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.016473 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.19768
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.014362 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.086172
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.018039 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 6.0611
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.01801 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 6.0153
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.01801 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 6.1234
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.018007 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.68427
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.018016 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.4504
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.018016 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.4504
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.018 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.684
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.017923 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.51977
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.018038 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 2.675
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.018038 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 2.6804
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.018038 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 2.7598
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 2.8705
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 2.7797
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 1.8168
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 2.6344
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 2.6707
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 2.3073
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.017779 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 2.6046
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.017779 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 2.6295
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.017779 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 3.0758
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.017832 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 3.6912
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.017832 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 3.8642
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.017832 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 4.3153
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.017833 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 2.568
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.017833 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 2.568
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.017833 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 3.0494
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.01327 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 4.1137
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.01327 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 5.4805
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.55322
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.57957
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.57957
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.61908
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.6567
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.61649
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.61649
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.62989
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013402 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 2.0639
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013402 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 1.9835
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.6433
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.6433
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 0.42063
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 0.42063
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 0.55764
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 0.48072
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 0.48072
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 0.69103
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 1.2513
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 0.85402
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 0.79572
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 0.81736
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 0.88347
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 1.2621
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 1.2289
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 0.74382
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 1.4641
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 1.1584
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 1.1892
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 0.72482
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.006067 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 0.90398
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.005958 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 1.0724
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.005958 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 1.0724
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.005962 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 1.3415
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.005907 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 0.73838
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.005907 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 0.73838
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 0.70308
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 0.7081
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 1.5518
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 0.71815
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 0.72317
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 1.5568
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.005128 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 1.0051
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.005128 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 0.56921
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.005067 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.79292
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.8077
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.8077
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 2.0389
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 0.79785
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.79292
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 0.80278
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 2.0143
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.004991 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.004991 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 0.68983
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 0.60593
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 0.67585
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 1.8597
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.00427 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 0.64349
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.00427 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 0.64477
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.00427 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 0.7575
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.004285 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 0.64918
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.004285 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 0.65261
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.004285 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 0.76059
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.011096 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 6.4468
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 2.2717
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 2.2717
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.001939 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.062048
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.002218 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.10646
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.002218 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.10203
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.023556
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.10011
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001963 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.033371
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.043186
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.049075
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.002218 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.23289
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.00592 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 0.49728
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.006499 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 0.51992
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.006503 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 0.97545
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.006503 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 0.97545
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -1.3875
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -1.3071
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -1.0386
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -3.0023
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -3.0081
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -2.9846
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -1.8813
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -4.7817
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.78388
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -1.9555
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -1.8113
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -2.0023
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -1.9887
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.0195 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.624
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.0195 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.585
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 4.637
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 4.637
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 4.9712
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 4.5744
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 0.40466
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 0.40652
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.19038 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -25.8915
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.017143 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.56572
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -2.2042
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -2.2042
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.9943
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.9943
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.030124 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 2.1388
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.030124 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.30124
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.02606 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 4.2478
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.02606 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 4.2478
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.02606 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 6.3847
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.4118
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -2.2263
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.4118
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.4118
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.05058 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -7.5364
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.05058 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -3.2928
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -2.7559
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -2.653
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -2.6348
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -1.6505
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.36948
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.056324 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -41.8487
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.054433 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -40.0083
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.049682 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -8.5453
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.049682 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -8.5453
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.049682 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -8.5453
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -11.6308
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.18383 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -31.8019
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.18383 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -24.8165
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -8.2628
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -8.1917
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -8.0648
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -13.663
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -3.2154
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -3.1752
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -4.1499
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -3.6977
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -5.8085
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -5.5913
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -5.6056
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -5.5878
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -9.574
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.068018 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.34009
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.068018 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -1.4284
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 0.1158
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.11716
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.11716
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 0.28538
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.10764 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -42.8395
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.3064
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.3064
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.3064
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.9315
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.9315
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -9.7509
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.00326 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 2.696
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.00326 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 2.6699
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.021033 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.96962
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 2.2035
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 2.2035
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 3.0444
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 2.1456
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 2.1456
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 2.9574
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.051205 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -9.2169
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.051205 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -8.1211
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.051205 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -8.0392
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.073823 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -2.5838
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.024557 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -11.2717
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -5.822
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -5.9116
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -6.2698
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -5.6428
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -5.5533
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -9.3152
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -5.2846
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -10.4879
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -10.3534
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -10.3534
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.06723 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -10.8913
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.092748 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -14.5614
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -3.6658
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -3.7174
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -2.0136
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -1.5489
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.045533 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -3.5516
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.045533 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -3.6426
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.050105 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.8117
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.052 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -8.58
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.052466 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -8.8668
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.049922 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -10.6334
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.050502 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -11.5145
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.052878 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.63454
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.052878 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.9518
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.18936 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 9.4682
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.8333
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.8333
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4711
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.4439
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4711
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -1.5529
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4711
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4711
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5801
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5801
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.041987 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.50384
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3116
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.3818
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3116
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3116
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.3818
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3116
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.031942 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 2.1082
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.0673 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 10.8353
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.0673 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 11.1718
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.0673 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 16.6904
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.0673 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 36.7458
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.0673 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 43.2739
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.025604 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 16.6682
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.025604 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 14.4407
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.025604 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 15.3624
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.0673 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.8749
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.062431 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.74917
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -2.1084
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -2.1518
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -2.0278
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -2.8463
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -1.0976
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -1.265
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -1.234
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -2.1704
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -1.1162
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -5.2957
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -9.1776
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 1.1673
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 1.3443
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.84726
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.9016
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 1.6192
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 1.6569
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.9414
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.3389
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 1.7698
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 1.318
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 1.1862
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 1.3556
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 1.2201
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.9016
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 1.8263
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 1.9393
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 1.4309
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 1.5062
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 1.5062
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 3.2196
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13512
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.006678 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 0.51087
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.006492 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 0.51936
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.006492 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 0.25968
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.006462 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 0.51696
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.006498 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 0.51984
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.006653 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 0.53224
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.006703 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 0.56305
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.006462 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 0.51696
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 1.7481
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.005961 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 0.71532
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.005961 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 1.3889
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.005961 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 1.0146
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 3.4041
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 2.8215
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 3.4348
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 1.7634
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 1.5334
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.005823 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 0.34938
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.011508 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.007508 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.006351 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.030485
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 0.22073
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 0.63275
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 0.79461
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 0.70043
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 0.61803
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 0.47382
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.006006 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 0.9009
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 0.67748
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 0.90029
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 1.1201
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 1.2917
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.017871 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.01457 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.016666 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.55429
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.86311
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 1.4649
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 1.6813
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.73333
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.67967
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.33983
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 1.6813
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.6439
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.7691
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.39349
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.75262
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.28947
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.13509
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.28947
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.75262
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.75262
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 2.6471
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.8943
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.98373
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.8943
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.018168 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.21802
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.019162 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.28743
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.019162 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.44073
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.019685 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.94488
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.019205 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.15364
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.018035 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 3.2463
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.018039 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 3.247
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.01801 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 3.2418
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.01801 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 3.2418
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016665 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 1.6665
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016665 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 1.6665
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.45265
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.45265
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.45265
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.2897
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.45265
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.45265
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.45265
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.27159
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016665 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016665 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 8.3325
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016665 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 8.3325
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016665 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.017551 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.013469 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.017141 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.017638 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:Garrot - Midtown 138kV 47660-47705 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45972 | [7 empty] | 115.951
Number of Bus | Name of Bus | ID | Max MW | L:Garrot - Midtown 138kV 47660-47705 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45972 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.006974 | north | Y | 0.0022238 | -0.0086795 | 0.00096467 | 0.022942 | 0.00096467 | west | Y | 0.0022238 | 0.32107
239 | BOSQUESW | 1 | 149 | 0.006974 | north | Y | 0.0022238 | -0.0086795 | 0.00096467 | 0.022942 | 0.00096467 | west | Y | 0.0022238 | 0.1876
244 | WHITNYDM | 1 | 15 | 0.006601 | north | N | 0.0018508 | -0.0090525 | 0.00059167 | 0.022569 | 0.00059167 | west | Y | 0.0018508 | 0
245 | WHITNYDM | 2 | 15 | 0.006601 | north | N | 0.0018508 | -0.0090525 | 0.00059167 | 0.022569 | 0.00059167 | west | Y | 0.0018508 | 0
247 | BOSQUESW | 2 | 153 | 0.006974 | north | Y | 0.0022238 | -0.0086795 | 0.00096467 | 0.022942 | 0.00096467 | west | Y | 0.0022238 | 0.19264
251 | BOSQUESW | 2 | 150 | 0.006861 | north | Y | 0.0021108 | -0.0087925 | 0.00085167 | 0.022829 | 0.00085167 | west | Y | 0.0021108 | 0.18886
253 | BOSQUESW | 2 | 80 | 0.006861 | north | Y | 0.0021108 | -0.0087925 | 0.00085167 | 0.022829 | 0.00085167 | west | Y | 0.0021108 | 0.10073
332 | RWMILLER | 1 | 73 | 0.005626 | north | Y | 0.00087576 | -0.010027 | -0.00038333 | 0.021594 | 0.00038333 | west | Y | 0.00087576 | 0.035947
333 | RWMILLER | 2 | 119 | 0.005626 | north | Y | 0.00087576 | -0.010027 | -0.00038333 | 0.021594 | 0.00038333 | west | Y | 0.00087576 | 0.058598
334 | RWMILLER | 3 | 205 | 0.005626 | north | Y | 0.00087576 | -0.010027 | -0.00038333 | 0.021594 | 0.00038333 | west | Y | 0.00087576 | 0.10095
335 | RWMILLER | 4 | 102 | 0.005626 | north | Y | 0.00087576 | -0.010027 | -0.00038333 | 0.021594 | 0.00038333 | west | Y | 0.00087576 | 0.050227
336 | RWMILLER | 5 | 96 | 0.005626 | north | Y | 0.00087576 | -0.010027 | -0.00038333 | 0.021594 | 0.00038333 | west | Y | 0.00087576 | 0.047272
344 | MRSSHPRD | 1 | 12 | 0.00555 | north | N | 0.00079976 | -0.010103 | -0.00045933 | 0.021518 | 0.00045933 | west | Y | 0.00079976 | 0
345 | MRSSHPRD | 2 | 12 | 0.00555 | north | N | 0.00079976 | -0.010103 | -0.00045933 | 0.021518 | 0.00045933 | west | Y | 0.00079976 | 0
366 | JNSNCNTY | 1 | 168 | 0.005575 | north | Y | 0.00082476 | -0.010078 | -0.00043433 | 0.021543 | 0.00043433 | west | Y | 0.00082476 | 0.065591
367 | JNSNCNTY | 2 | 90 | 0.005575 | north | Y | 0.00082476 | -0.010078 | -0.00043433 | 0.021543 | 0.00043433 | west | Y | 0.00082476 | 0.035138
503 | NTHTEXAS | 1 | 18 | 0.005483 | north | Y | 0.00073276 | -0.01017 | -0.00052633 | 0.021451 | 0.00052633 | west | Y | 0.00073276 | 0.0037156
504 | NTHTEXAS | 2 | 18 | 0.005483 | north | Y | 0.00073276 | -0.01017 | -0.00052633 | 0.021451 | 0.00052633 | west | Y | 0.00073276 | 0.0037156
505 | NTHTEXAS | 3 | 38 | 0.005483 | north | Y | 0.00073276 | -0.01017 | -0.00052633 | 0.021451 | 0.00052633 | west | Y | 0.00073276 | 0.007844
580 | JCKCNTY8 | 1 | 288 | 0.005394 | north | Y | 0.00064376 | -0.010259 | -0.00061533 | 0.021362 | 0.00061533 | west | Y | 0.00064376 | 0.0081854
581 | JCKCNTY8 | 2 | 147 | 0.005394 | north | Y | 0.00064376 | -0.010259 | -0.00061533 | 0.021362 | 0.00061533 | west | Y | 0.00064376 | 0.0041779
582 | JCKCNTY8 | 3 | 147 | 0.005394 | north | Y | 0.00064376 | -0.010259 | -0.00061533 | 0.021362 | 0.00061533 | west | Y | 0.00064376 | 0.0041779
728 | WOLFRIDG | 1 | 112.5 | 0.005287 | north | Y | 0.00053676 | -0.010366 | -0.00072233 | 0.021255 | 0.00053676 | North | N | 0.00053676 | 0
837 | NEWMAN_G | 1 | 40 | 0.004995 | north | Y | 0.00024476 | -0.010658 | -0.0010143 | 0.020963 | 0.00024476 | North | N | 0.00024476 | 0
842 | OLINGER_ | 1 | 79 | 0.004995 | north | Y | 0.00024476 | -0.010658 | -0.0010143 | 0.020963 | 0.00024476 | North | N | 0.00024476 | 0
843 | OLINGER_ | 1 | 106 | 0.004995 | north | Y | 0.00024476 | -0.010658 | -0.0010143 | 0.020963 | 0.00024476 | North | N | 0.00024476 | 0
844 | OLINGER_ | 1 | 146 | 0.004995 | north | Y | 0.00024476 | -0.010658 | -0.0010143 | 0.020963 | 0.00024476 | North | N | 0.00024476 | 0
845 | OLINGER_ | 1 | 76 | 0.004995 | north | Y | 0.00024476 | -0.010658 | -0.0010143 | 0.020963 | 0.00024476 | North | N | 0.00024476 | 0
923 | SPENCER_ | 1 | 60 | 0.005206 | north | Y | 0.00045576 | -0.010447 | -0.00080333 | 0.021174 | 0.00045576 | North | N | 0.00045576 | 0
924 | SPENCER_ | 1 | 63 | 0.005206 | north | Y | 0.00045576 | -0.010447 | -0.00080333 | 0.021174 | 0.00045576 | North | N | 0.00045576 | 0
948 | STEAM1 | 1 | 20 | 0.004985 | north | Y | 0.00023476 | -0.010668 | -0.0010243 | 0.020953 | 0.00023476 | North | N | 0.00023476 | 0
949 | STEAM2 | 1 | 25 | 0.004985 | north | Y | 0.00023476 | -0.010668 | -0.0010243 | 0.020953 | 0.00023476 | North | N | 0.00023476 | 0
950 | STEAM3 | 1 | 41 | 0.004985 | north | Y | 0.00023476 | -0.010668 | -0.0010243 | 0.020953 | 0.00023476 | North | N | 0.00023476 | 0
990 | GIBN_CRE | 1 | 463 | 0.001117 | north | Y | -0.0036332 | -0.014536 | -0.0048923 | 0.017085 | 0.0036332 | North | N | 0.0036332 | 0
1002 | PBCTAGE_ | A | 66 | 0.006083 | west | Y | 0.0013328 | -0.0095705 | 7.3665e-05 | 0.022051 | 7.3665e-05 | west | N | 7.3665e-05 | 0
1003 | PBCTBGE_ | B | 65 | 0.006083 | west | Y | 0.0013328 | -0.0095705 | 7.3665e-05 | 0.022051 | 7.3665e-05 | west | N | 7.3665e-05 | 0
1004 | PBCTCGE_ | C | 67 | 0.006083 | west | Y | 0.0013328 | -0.0095705 | 7.3665e-05 | 0.022051 | 7.3665e-05 | west | N | 7.3665e-05 | 0
1005 | PBCTDGE_ | D | 67 | 0.006083 | west | Y | 0.0013328 | -0.0095705 | 7.3665e-05 | 0.022051 | 7.3665e-05 | west | N | 7.3665e-05 | 0
1006 | PBCTEGE_ | E | 67 | 0.006083 | west | Y | 0.0013328 | -0.0095705 | 7.3665e-05 | 0.022051 | 7.3665e-05 | west | N | 7.3665e-05 | 0
1007 | PB5GEN_6 | MB | 114 | 0.006083 | west | Y | 0.0013328 | -0.0095705 | 7.3665e-05 | 0.022051 | 7.3665e-05 | west | N | 7.3665e-05 | 0
1008 | PB6GEN_7 | MB | 515 | 0.006083 | west | Y | 0.0013328 | -0.0095705 | 7.3665e-05 | 0.022051 | 7.3665e-05 | west | N | 7.3665e-05 | 0
1039 | MRGNAG_1 | A | 66 | 0.005937 | west | Y | 0.0011868 | -0.0097165 | -7.2335e-05 | 0.021905 | 7.2335e-05 | west | N | 7.2335e-05 | 0
1040 | MRGNBG_2 | B | 69 | 0.005937 | west | Y | 0.0011868 | -0.0097165 | -7.2335e-05 | 0.021905 | 7.2335e-05 | west | N | 7.2335e-05 | 0
1041 | MRGNCG_3 | C | 69 | 0.005937 | west | Y | 0.0011868 | -0.0097165 | -7.2335e-05 | 0.021905 | 7.2335e-05 | west | N | 7.2335e-05 | 0
1042 | MRGNDG_4 | D | 67 | 0.005937 | west | Y | 0.0011868 | -0.0097165 | -7.2335e-05 | 0.021905 | 7.2335e-05 | west | N | 7.2335e-05 | 0
1043 | MRGNEG_5 | E | 67 | 0.005937 | west | Y | 0.0011868 | -0.0097165 | -7.2335e-05 | 0.021905 | 7.2335e-05 | west | N | 7.2335e-05 | 0
1044 | MRGNFG_6 | F | 65 | 0.005937 | west | Y | 0.0011868 | -0.0097165 | -7.2335e-05 | 0.021905 | 7.2335e-05 | west | N | 7.2335e-05 | 0
1045 | CALENG1G | 1 | 70 | 0.005957 | west | N | 0.0012068 | -0.0096965 | -5.2335e-05 | 0.021925 | 5.2335e-05 | west | N | 5.2335e-05 | 0
1046 | CALENG2G | 2 | 73.4 | 0.005957 | west | N | 0.0012068 | -0.0096965 | -5.2335e-05 | 0.021925 | 5.2335e-05 | west | N | 5.2335e-05 | 0
1047 | CALENG3G | 3 | 70.4 | 0.005957 | west | N | 0.0012068 | -0.0096965 | -5.2335e-05 | 0.021925 | 5.2335e-05 | west | N | 5.2335e-05 | 0
1058 | LONGSHOR | 1 | 150 | 0.005946 | west | Y | 0.0011958 | -0.0097075 | -6.3335e-05 | 0.021914 | 6.3335e-05 | west | N | 6.3335e-05 | 0
1058 | LONGSHOR | 2 | 220 | 0.005946 | west | Y | 0.0011958 | -0.0097075 | -6.3335e-05 | 0.021914 | 6.3335e-05 | west | N | 6.3335e-05 | 0
1061 | CIELOGEN | 1 | 99 | 0.00593 | west | Y | 0.0011798 | -0.0097235 | -7.9335e-05 | 0.021898 | 7.9335e-05 | west | N | 7.9335e-05 | 0
1062 | CIELOGEN | 1 | 61 | 0.00593 | west | Y | 0.0011798 | -0.0097235 | -7.9335e-05 | 0.021898 | 7.9335e-05 | west | N | 7.9335e-05 | 0
1068 | SCURRYCW | 1 | 141 | 0.005931 | west | Y | 0.0011808 | -0.0097225 | -7.8335e-05 | 0.021899 | 7.8335e-05 | west | N | 7.8335e-05 | 0
1069 | KINDERMG | 1 | 25 | 0.00593 | west | N | 0.0011798 | -0.0097235 | -7.9335e-05 | 0.021898 | 7.9335e-05 | west | N | 7.9335e-05 | 0
1070 | KINDERMG | 1 | 45.7 | 0.00593 | west | N | 0.0011798 | -0.0097235 | -7.9335e-05 | 0.021898 | 7.9335e-05 | west | N | 7.9335e-05 | 0
1071 | KINDERMG | 1 | 45.7 | 0.00593 | west | N | 0.0011798 | -0.0097235 | -7.9335e-05 | 0.021898 | 7.9335e-05 | west | N | 7.9335e-05 | 0
1073 | SCURRYCW | 2 | 120 | 0.005931 | west | Y | 0.0011808 | -0.0097225 | -7.8335e-05 | 0.021899 | 7.8335e-05 | west | N | 7.8335e-05 | 0
1320 | BSP 1 | 1 | 25.8 | 0.005993 | west | N | 0.0012428 | -0.0096605 | -1.6335e-05 | 0.021961 | 1.6335e-05 | west | N | 1.6335e-05 | 0
1326 | STANTONW | 1 | 100.5 | 0.006006 | west | Y | 0.0012558 | -0.0096475 | -3.3348e-06 | 0.021974 | 3.3348e-06 | west | N | 3.3348e-06 | 0
1327 | WILDHRSE | 1 | 120 | 0.00597 | west | Y | 0.0012198 | -0.0096835 | -3.9335e-05 | 0.021938 | 3.9335e-05 | west | N | 3.9335e-05 | 0
1328 | OCOTILLO | 1 | 58 | 0.006007 | west | Y | 0.0012568 | -0.0096465 | -2.3348e-06 | 0.021975 | 2.3348e-06 | west | N | 2.3348e-06 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.005997 | west | Y | 0.0012468 | -0.0096565 | -1.2335e-05 | 0.021965 | 1.2335e-05 | west | N | 1.2335e-05 | 0
1343 | TRENTIPP | 1 | 150 | 0.005915 | west | Y | 0.0011648 | -0.0097385 | -9.4335e-05 | 0.021883 | 9.4335e-05 | west | N | 9.4335e-05 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.006044 | west | Y | 0.0012938 | -0.0096095 | 3.4665e-05 | 0.022012 | 3.4665e-05 | west | N | 3.4665e-05 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.006044 | west | Y | 0.0012938 | -0.0096095 | 3.4665e-05 | 0.022012 | 3.4665e-05 | west | N | 3.4665e-05 | 0
1354 | AEPWIND_ | 1 | 101 | 0.005915 | west | Y | 0.0011648 | -0.0097385 | -9.4335e-05 | 0.021883 | 9.4335e-05 | west | N | 9.4335e-05 | 0
1360 | GUNSIGHT | 1 | 120 | 0.005969 | west | Y | 0.0012188 | -0.0096845 | -4.0335e-05 | 0.021937 | 4.0335e-05 | west | N | 4.0335e-05 | 0
1432 | GRHAMSES | 2 | 366 | 0.005556 | north | Y | 0.00080576 | -0.010097 | -0.00045333 | 0.021524 | 0.00045333 | west | Y | 0.00080576 | 0.12899
1433 | GRHAMSES | 1 | 242 | 0.0056 | north | Y | 0.00084976 | -0.010053 | -0.00040933 | 0.021568 | 0.00040933 | west | Y | 0.00084976 | 0.10658
1437 | MESQUITW | 1 | 400 | 0.005746 | west | Y | 0.00099576 | -0.0099075 | -0.00026333 | 0.021714 | 0.00026333 | west | N | 0.00026333 | 0
1438 | MESQUITW | 1 | 236 | 0.005745 | west | Y | 0.00099476 | -0.0099085 | -0.00026433 | 0.021713 | 0.00026433 | west | N | 0.00026433 | 0
1442 | COKFIELD | 1 | 165 | 0.0057 | west | Y | 0.00094976 | -0.0099535 | -0.00030933 | 0.021668 | 0.00030933 | west | N | 0.00030933 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.005439 | north | Y | 0.00068876 | -0.010214 | -0.00057033 | 0.021407 | 0.00057033 | west | Y | 0.00068876 | 0.024158
1454 | WCPWRCO_ | 2 | 201 | 0.005439 | north | Y | 0.00068876 | -0.010214 | -0.00057033 | 0.021407 | 0.00057033 | west | Y | 0.00068876 | 0.023803
1455 | WCPWRCO_ | 3 | 242 | 0.005439 | north | Y | 0.00068876 | -0.010214 | -0.00057033 | 0.021407 | 0.00057033 | west | Y | 0.00068876 | 0.028658
1479 | WFCOGEN_ | 1 | 20 | 0.005548 | west | Y | 0.00079776 | -0.010105 | -0.00046133 | 0.021516 | 0.00046133 | west | N | 0.00046133 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.005548 | west | Y | 0.00079776 | -0.010105 | -0.00046133 | 0.021516 | 0.00046133 | west | N | 0.00046133 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.005548 | west | Y | 0.00079776 | -0.010105 | -0.00046133 | 0.021516 | 0.00046133 | west | N | 0.00046133 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.005548 | west | Y | 0.00079776 | -0.010105 | -0.00046133 | 0.021516 | 0.00046133 | west | N | 0.00046133 | 0
1600 | BARTNWND | 1 | 120 | 0.00556 | north | Y | 0.00080976 | -0.010093 | -0.00044933 | 0.021528 | 0.00044933 | west | Y | 0.00080976 | 0.043251
1643 | SLSTR1PP | 1 | 60 | 0.005866 | north | Y | 0.0011158 | -0.0097875 | -0.00014333 | 0.021834 | 0.00014333 | west | Y | 0.0011158 | 0.058345
1675 | PEC_1G | 1 | 75 | 0.005011 | north | N | 0.00026076 | -0.010642 | -0.00099833 | 0.020979 | 0.00026076 | North | N | 0.00026076 | 0
1676 | PEC_2G | 2 | 79.6 | 0.005011 | north | N | 0.00026076 | -0.010642 | -0.00099833 | 0.020979 | 0.00026076 | North | N | 0.00026076 | 0
1677 | PEC_3G | 3 | 88.4 | 0.005011 | north | N | 0.00026076 | -0.010642 | -0.00099833 | 0.020979 | 0.00026076 | North | N | 0.00026076 | 0
1678 | LAMARPWR | 1 | 160 | 0.005015 | north | Y | 0.00026476 | -0.010638 | -0.00099433 | 0.020983 | 0.00026476 | North | N | 0.00026476 | 0
1679 | LAMARPWR | 2 | 156 | 0.005015 | north | Y | 0.00026476 | -0.010638 | -0.00099433 | 0.020983 | 0.00026476 | North | N | 0.00026476 | 0
1680 | LAMARPWR | 3 | 196 | 0.005015 | north | Y | 0.00026476 | -0.010638 | -0.00099433 | 0.020983 | 0.00026476 | North | N | 0.00026476 | 0
1681 | LAMARPWR | 4 | 156 | 0.005015 | north | Y | 0.00026476 | -0.010638 | -0.00099433 | 0.020983 | 0.00026476 | North | N | 0.00026476 | 0
1682 | LAMARPWR | 5 | 157 | 0.005015 | north | Y | 0.00026476 | -0.010638 | -0.00099433 | 0.020983 | 0.00026476 | North | N | 0.00026476 | 0
1683 | LAMARPWR | 6 | 198 | 0.005015 | north | Y | 0.00026476 | -0.010638 | -0.00099433 | 0.020983 | 0.00026476 | North | N | 0.00026476 | 0
1687 | VALLEY_1 | 1 | 170 | 0.005037 | north | Y | 0.00028676 | -0.010616 | -0.00097233 | 0.021005 | 0.00028676 | North | N | 0.00028676 | 0
1688 | VALLEY_2 | 2 | 520 | 0.005037 | north | Y | 0.00028676 | -0.010616 | -0.00097233 | 0.021005 | 0.00028676 | North | N | 0.00028676 | 0
1689 | VALLEY_3 | 3 | 370 | 0.005022 | north | Y | 0.00027176 | -0.010631 | -0.00098733 | 0.02099 | 0.00027176 | North | N | 0.00027176 | 0
1701 | MOSES_1G | 1 | 558 | 0.005004 | north | Y | 0.00025376 | -0.010649 | -0.0010053 | 0.020972 | 0.00025376 | North | N | 0.00025376 | 0
1702 | MOSES_2G | 2 | 579 | 0.005004 | north | Y | 0.00025376 | -0.010649 | -0.0010053 | 0.020972 | 0.00025376 | North | N | 0.00025376 | 0
1703 | MOSES_3G | 3 | 808 | 0.005004 | north | Y | 0.00025376 | -0.010649 | -0.0010053 | 0.020972 | 0.00025376 | North | N | 0.00025376 | 0
1861 | EAGLEMNT | MB | 112 | 0.005315 | north | Y | 0.00056476 | -0.010338 | -0.00069433 | 0.021283 | 0.00056476 | North | N | 0.00056476 | 0
1862 | EAGLEMNT | MB | 100 | 0.005315 | north | Y | 0.00056476 | -0.010338 | -0.00069433 | 0.021283 | 0.00056476 | North | N | 0.00056476 | 0
1863 | EAGLEMNT | MB | 378 | 0.005315 | north | Y | 0.00056476 | -0.010338 | -0.00069433 | 0.021283 | 0.00056476 | North | N | 0.00056476 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.005442 | north | Y | 0.00069176 | -0.010211 | -0.00056733 | 0.02141 | 0.00056733 | west | Y | 0.00069176 | 0.027037
1878 | WLFHOLW_ | 2 | 205 | 0.005442 | north | Y | 0.00069176 | -0.010211 | -0.00056733 | 0.02141 | 0.00056733 | west | Y | 0.00069176 | 0.025506
1879 | WLFHOLW_ | 3 | 272.4 | 0.005442 | north | Y | 0.00069176 | -0.010211 | -0.00056733 | 0.02141 | 0.00056733 | west | Y | 0.00069176 | 0.033892
1889 | DECRDOVA | MB | 770 | 0.005424 | north | Y | 0.00067376 | -0.010229 | -0.00058533 | 0.021392 | 0.00058533 | west | Y | 0.00067376 | 0
1892 | DECRDOVA | A | 70 | 0.005526 | north | Y | 0.00077576 | -0.010127 | -0.00048333 | 0.021494 | 0.00048333 | west | Y | 0.00077576 | 0.020469
1893 | DECRDOVA | B | 69 | 0.005526 | north | Y | 0.00077576 | -0.010127 | -0.00048333 | 0.021494 | 0.00048333 | west | Y | 0.00077576 | 0.020177
1894 | DECRDOVA | C | 69 | 0.005526 | north | Y | 0.00077576 | -0.010127 | -0.00048333 | 0.021494 | 0.00048333 | west | Y | 0.00077576 | 0.020177
1895 | DECRDOVA | D | 68 | 0.005526 | north | Y | 0.00077576 | -0.010127 | -0.00048333 | 0.021494 | 0.00048333 | west | Y | 0.00077576 | 0.019885
1898 | COMCHEPK | 1 | 1157 | 0.005461 | north | N | 0.00071076 | -0.010192 | -0.00054833 | 0.021429 | 0.00054833 | west | Y | 0.00071076 | 0
1899 | COMCHEPK | 2 | 1158 | 0.005461 | north | N | 0.00071076 | -0.010192 | -0.00054833 | 0.021429 | 0.00054833 | west | Y | 0.00071076 | 0
1937 | MDLTHELP | 5 | 224 | 0.005387 | north | Y | 0.00063676 | -0.010266 | -0.00062233 | 0.021355 | 0.00062233 | west | Y | 0.00063676 | 0.0032304
1938 | MDLTHELP | 6 | 226 | 0.005387 | north | Y | 0.00063676 | -0.010266 | -0.00062233 | 0.021355 | 0.00062233 | west | Y | 0.00063676 | 0.0032592
1941 | MDLTHELP | 1 | 216.4 | 0.005308 | north | Y | 0.00055776 | -0.010345 | -0.00070133 | 0.021276 | 0.00055776 | North | N | 0.00055776 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.005308 | north | Y | 0.00055776 | -0.010345 | -0.00070133 | 0.021276 | 0.00055776 | North | N | 0.00055776 | 0
1943 | MDLTHELP | 3 | 212 | 0.005387 | north | Y | 0.00063676 | -0.010266 | -0.00062233 | 0.021355 | 0.00062233 | west | Y | 0.00063676 | 0.0030573
1944 | MDLTHELP | 4 | 211 | 0.005387 | north | Y | 0.00063676 | -0.010266 | -0.00062233 | 0.021355 | 0.00062233 | west | Y | 0.00063676 | 0.0030429
1947 | HANDLEY_ | 3 | 395 | 0.005297 | north | Y | 0.00054676 | -0.010356 | -0.00071233 | 0.021265 | 0.00054676 | North | N | 0.00054676 | 0
1948 | HANDLEY_ | 4 | 435 | 0.005281 | north | Y | 0.00053076 | -0.010372 | -0.00072833 | 0.021249 | 0.00053076 | North | N | 0.00053076 | 0
1949 | HANDLEY_ | 5 | 435 | 0.005297 | north | Y | 0.00054676 | -0.010356 | -0.00071233 | 0.021265 | 0.00054676 | North | N | 0.00054676 | 0
2371 | COLLIN_1 | MB | 138 | 0.005084 | north | Y | 0.00033376 | -0.010569 | -0.00092533 | 0.021052 | 0.00033376 | North | N | 0.00033376 | 0
2413 | MTCK6_G | 6 | 118 | 0.005064 | north | Y | 0.00031376 | -0.010589 | -0.00094533 | 0.021032 | 0.00031376 | North | N | 0.00031376 | 0
2414 | MTCK7_G | 7 | 115 | 0.005064 | north | Y | 0.00031376 | -0.010589 | -0.00094533 | 0.021032 | 0.00031376 | North | N | 0.00031376 | 0
2417 | MTCK8_G | 8 | 556 | 0.005064 | north | Y | 0.00031376 | -0.010589 | -0.00094533 | 0.021032 | 0.00031376 | North | N | 0.00031376 | 0
2451 | LKHB1_G | 1 | 388 | 0.004976 | north | Y | 0.00022576 | -0.010677 | -0.0010333 | 0.020944 | 0.00022576 | North | N | 0.00022576 | 0
2452 | LKHB2_G | 2 | 515 | 0.004976 | north | Y | 0.00022576 | -0.010677 | -0.0010333 | 0.020944 | 0.00022576 | North | N | 0.00022576 | 0
3097 | MARTLAKE | 1 | 785 | 0.004695 | north | Y | -5.5244e-05 | -0.010958 | -0.0013143 | 0.020663 | 5.5244e-05 | North | N | 5.5244e-05 | 0
3098 | MARTLAKE | 2 | 795 | 0.004695 | north | Y | -5.5244e-05 | -0.010958 | -0.0013143 | 0.020663 | 5.5244e-05 | North | N | 5.5244e-05 | 0
3099 | MARTLAKE | 3 | 780 | 0.004695 | north | Y | -5.5244e-05 | -0.010958 | -0.0013143 | 0.020663 | 5.5244e-05 | North | N | 5.5244e-05 | 0
3107 | STRYKER_ | 1 | 182 | 0.004624 | north | Y | -0.00012624 | -0.011029 | -0.0013853 | 0.020592 | 0.00012624 | North | N | 0.00012624 | 0
3108 | STRYKER_ | 2 | 484 | 0.004624 | north | Y | -0.00012624 | -0.011029 | -0.0013853 | 0.020592 | 0.00012624 | North | N | 0.00012624 | 0
3126 | TRINIDAD | 1 | 224 | 0.004913 | north | Y | 0.00016276 | -0.01074 | -0.0010963 | 0.020881 | 0.00016276 | North | N | 0.00016276 | 0
3309 | ASPN_G | 1 | 50 | 0.004628 | north | Y | -0.00012224 | -0.011025 | -0.0013813 | 0.020596 | 0.00012224 | North | N | 0.00012224 | 0
3348 | CHAMPION | MB | 42 | 0.004632 | north | N | -0.00011824 | -0.011021 | -0.0013773 | 0.0206 | 0.00011824 | North | N | 0.00011824 | 0
3381 | BBRN_1G | 1 | 615 | 0.00419 | north | Y | -0.00056024 | -0.011463 | -0.0018193 | 0.020158 | 0.00056024 | North | N | 0.00056024 | 0
3382 | BBRN_2G | 2 | 587 | 0.00419 | north | Y | -0.00056024 | -0.011463 | -0.0018193 | 0.020158 | 0.00056024 | North | N | 0.00056024 | 0
3403 | THOUSE_1 | MB | 537 | 0.007104 | north | Y | 0.0023538 | -0.0085495 | 0.0010947 | 0.023072 | 0.0010947 | west | Y | 0.0023538 | 0
3404 | THOUSE_2 | 2 | 787 | 0.007104 | north | Y | 0.0023538 | -0.0085495 | 0.0010947 | 0.023072 | 0.0010947 | west | Y | 0.0023538 | 0.9909
3416 | LAKE_CRK | MB | 75 | 0.007191 | north | Y | 0.0024408 | -0.0084625 | 0.0011817 | 0.023159 | 0.0011817 | west | Y | 0.0024408 | 0
3417 | LAKE_CRK | MB | 222 | 0.007191 | north | Y | 0.0024408 | -0.0084625 | 0.0011817 | 0.023159 | 0.0011817 | west | Y | 0.0024408 | 0
3432 | SANDOW_4 | 4 | 569 | 0.011096 | south | Y | 0.0063458 | -0.0045575 | 0.0050867 | 0.027064 | 0.0045575 | south | N | 0.0045575 | 0
5026 | BRAUNIG_ | 1 | 209 | 0.015978 | south | Y | 0.011228 | 0.00032453 | 0.0099687 | 0.031946 | 0.00032453 | south | N | 0.00032453 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.015978 | south | Y | 0.011228 | 0.00032453 | 0.0099687 | 0.031946 | 0.00032453 | south | N | 0.00032453 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.015954 | south | Y | 0.011204 | 0.00030053 | 0.0099447 | 0.031922 | 0.00030053 | south | N | 0.00030053 | 0
5031 | BRA_VHBC | 1 | 46 | 0.015978 | south | Y | 0.011228 | 0.00032453 | 0.0099687 | 0.031946 | 0.00032453 | south | N | 0.00032453 | 0
5032 | BRA_VHBC | 2 | 47 | 0.015978 | south | Y | 0.011228 | 0.00032453 | 0.0099687 | 0.031946 | 0.00032453 | south | N | 0.00032453 | 0
5033 | BRA_VHBC | 3 | 46 | 0.015978 | south | Y | 0.011228 | 0.00032453 | 0.0099687 | 0.031946 | 0.00032453 | south | N | 0.00032453 | 0
5034 | BRA_VHBC | 4 | 46 | 0.015978 | south | Y | 0.011228 | 0.00032453 | 0.0099687 | 0.031946 | 0.00032453 | south | N | 0.00032453 | 0
5111 | CALAVER_ | 1 | 424 | 0.015954 | south | Y | 0.011204 | 0.00030053 | 0.0099447 | 0.031922 | 0.00030053 | south | N | 0.00030053 | 0
5112 | CALAVER_ | 2 | 425 | 0.015954 | south | Y | 0.011204 | 0.00030053 | 0.0099447 | 0.031922 | 0.00030053 | south | N | 0.00030053 | 0
5264 | LEON_LCP | 3 | 58 | 0.015969 | south | Y | 0.011219 | 0.00031553 | 0.0099597 | 0.031937 | 0.00031553 | south | N | 0.00031553 | 0
5265 | LEON_LCP | 4 | 89 | 0.015969 | south | Y | 0.011219 | 0.00031553 | 0.0099597 | 0.031937 | 0.00031553 | south | N | 0.00031553 | 0
5266 | LEON_LCP | 1 | 44 | 0.015969 | south | Y | 0.011219 | 0.00031553 | 0.0099597 | 0.031937 | 0.00031553 | south | N | 0.00031553 | 0
5267 | LEON_LCP | 2 | 44 | 0.015969 | south | Y | 0.011219 | 0.00031553 | 0.0099597 | 0.031937 | 0.00031553 | south | N | 0.00031553 | 0
5268 | LEON_LCP | 3 | 43 | 0.015969 | south | Y | 0.011219 | 0.00031553 | 0.0099597 | 0.031937 | 0.00031553 | south | N | 0.00031553 | 0
5269 | LEON_LCP | 4 | 45 | 0.015969 | south | Y | 0.011219 | 0.00031553 | 0.0099597 | 0.031937 | 0.00031553 | south | N | 0.00031553 | 0
5396 | CALAVER_ | 1 | 412 | 0.015962 | south | Y | 0.011212 | 0.00030853 | 0.0099527 | 0.03193 | 0.00030853 | south | N | 0.00030853 | 0
5397 | CALAVER_ | 2 | 400 | 0.015962 | south | Y | 0.011212 | 0.00030853 | 0.0099527 | 0.03193 | 0.00030853 | south | N | 0.00030853 | 0
5401 | CALAVER_ | 1 | 546 | 0.016122 | south | Y | 0.011372 | 0.00046853 | 0.010113 | 0.03209 | 0.00046853 | south | N | 0.00046853 | 0
5402 | CALAVER_ | 2 | 750 | 0.016122 | south | Y | 0.011372 | 0.00046853 | 0.010113 | 0.03209 | 0.00046853 | south | N | 0.00046853 | 0
5436 | TUTTL_WB | MB | 61 | 0.015961 | south | Y | 0.011211 | 0.00030753 | 0.0099517 | 0.031929 | 0.00030753 | south | N | 0.00030753 | 0
5438 | TUTTL_WB | MB | 95 | 0.015961 | south | Y | 0.011211 | 0.00030753 | 0.0099517 | 0.031929 | 0.00030753 | south | N | 0.00030753 | 0
5439 | TUTTL_WB | MB | 151 | 0.015961 | south | Y | 0.011211 | 0.00030753 | 0.0099517 | 0.031929 | 0.00030753 | south | N | 0.00030753 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.016048 | south | Y | 0.011298 | 0.00039453 | 0.010039 | 0.032016 | 0.00039453 | south | N | 0.00039453 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.016048 | south | Y | 0.011298 | 0.00039453 | 0.010039 | 0.032016 | 0.00039453 | south | N | 0.00039453 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.016048 | south | Y | 0.011298 | 0.00039453 | 0.010039 | 0.032016 | 0.00039453 | south | N | 0.00039453 | 0
5503 | RAYBURNG | 1 | 22 | 0.018976 | south | Y | 0.014226 | 0.0033225 | 0.012967 | 0.034944 | 0.0033225 | south | N | 0.0033225 | 0
5505 | RAYBURNG | 1 | 11 | 0.018976 | south | Y | 0.014226 | 0.0033225 | 0.012967 | 0.034944 | 0.0033225 | south | N | 0.0033225 | 0
5506 | RAYBURNG | 1 | 11 | 0.018976 | south | Y | 0.014226 | 0.0033225 | 0.012967 | 0.034944 | 0.0033225 | south | N | 0.0033225 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.018948 | south | Y | 0.014198 | 0.0032945 | 0.012939 | 0.034916 | 0.0032945 | south | N | 0.0032945 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.018948 | south | Y | 0.014198 | 0.0032945 | 0.012939 | 0.034916 | 0.0032945 | south | N | 0.0032945 | 0
5511 | RAYBURNC | 1 | 46 | 0.018948 | south | Y | 0.014198 | 0.0032945 | 0.012939 | 0.034916 | 0.0032945 | south | N | 0.0032945 | 0
5512 | RAYBURNC | 1 | 48 | 0.018948 | south | Y | 0.014198 | 0.0032945 | 0.012939 | 0.034916 | 0.0032945 | south | N | 0.0032945 | 0
5728 | FALCONHY | 2 | 12 | 0.017453 | south | N | 0.012703 | 0.0017995 | 0.011444 | 0.033421 | 0.0017995 | south | N | 0.0017995 | 0
5729 | FALCONHY | 3 | 11 | 0.017453 | south | N | 0.012703 | 0.0017995 | 0.011444 | 0.033421 | 0.0017995 | south | N | 0.0017995 | 0
5890 | PEARSALL | 1 | 24 | 0.016201 | south | Y | 0.011451 | 0.00054753 | 0.010192 | 0.032169 | 0.00054753 | south | N | 0.00054753 | 0
5891 | PEARSALL | 1 | 24 | 0.016201 | south | Y | 0.011451 | 0.00054753 | 0.010192 | 0.032169 | 0.00054753 | south | N | 0.00054753 | 0
5892 | PEARSALL | 1 | 23 | 0.016201 | south | Y | 0.011451 | 0.00054753 | 0.010192 | 0.032169 | 0.00054753 | south | N | 0.00054753 | 0
5903 | SANMIGUE | 1 | 396 | 0.016625 | south | Y | 0.011875 | 0.00097153 | 0.010616 | 0.032593 | 0.00097153 | south | N | 0.00097153 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.020755 | houston | N | 0.016005 | 0.0051015 | 0.014746 | 0.036723 | 0.0051015 | south | Y | 0.036723 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.020755 | houston | N | 0.016005 | 0.0051015 | 0.014746 | 0.036723 | 0.0051015 | south | Y | 0.036723 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | N | 0.0047502 | 0
5932 | SI_RAY9 | 9 | 38 | 0.017872 | south | Y | 0.013122 | 0.0022185 | 0.011863 | 0.03384 | 0.0022185 | south | N | 0.0022185 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.017872 | south | Y | 0.013122 | 0.0022185 | 0.011863 | 0.03384 | 0.0022185 | south | N | 0.0022185 | 0
5934 | SI_RAY5 | 5 | 15 | 0.017872 | south | Y | 0.013122 | 0.0022185 | 0.011863 | 0.03384 | 0.0022185 | south | N | 0.0022185 | 0
5935 | SI_RAY10 | 10 | 47 | 0.017872 | south | Y | 0.013122 | 0.0022185 | 0.011863 | 0.03384 | 0.0022185 | south | N | 0.0022185 | 0
6016 | SWMESA | 1 | 75 | 0.006492 | west | Y | 0.0017418 | -0.0091615 | 0.00048267 | 0.02246 | 0.00048267 | west | N | 0.00048267 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | Y | 0.0060093 | 0
6144 | MCADOO1A | 1 | 150 | 0.005878 | west | Y | 0.0011278 | -0.0097755 | -0.00013133 | 0.021846 | 0.00013133 | west | N | 0.00013133 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.006069 | west | Y | 0.0013188 | -0.0095845 | 5.9665e-05 | 0.022037 | 5.9665e-05 | west | N | 5.9665e-05 | 0
6476 | LANGFORD | 1 | 150 | 0.008063 | west | Y | 0.0033128 | -0.0075905 | 0.0020537 | 0.024031 | 0.0020537 | west | N | 0.0020537 | 0
6637 | SNYDERW1 | 1 | 63 | 0.005934 | west | Y | 0.0011838 | -0.0097195 | -7.5335e-05 | 0.021902 | 7.5335e-05 | west | N | 7.5335e-05 | 0
6752 | OKLA0A | 1 | 649.7 | 0.005661 | west | Y | 0.00091076 | -0.0099925 | -0.00034833 | 0.021629 | 0.00034833 | west | N | 0.00034833 | 0
6948 | DENISNDM | 1 | 40 | 0.005049 | north | N | 0.00029876 | -0.010604 | -0.00096033 | 0.021017 | 0.00029876 | North | N | 0.00029876 | 0
6948 | DENISNDM | 2 | 40 | 0.005049 | north | N | 0.00029876 | -0.010604 | -0.00096033 | 0.021017 | 0.00029876 | North | N | 0.00029876 | 0
7000 | L_FERGUS | 1 | 422 | 0.012954 | south | Y | 0.0082038 | -0.0026995 | 0.0069447 | 0.028922 | 0.0026995 | south | N | 0.0026995 | 0
7004 | L_SIMGID | 1 | 132 | 0.013579 | south | Y | 0.0088288 | -0.0020745 | 0.0075697 | 0.029547 | 0.0020745 | south | N | 0.0020745 | 0
7005 | L_SIMGID | 2 | 134 | 0.013579 | south | Y | 0.0088288 | -0.0020745 | 0.0075697 | 0.029547 | 0.0020745 | south | N | 0.0020745 | 0
7006 | L_SIMGID | 3 | 323 | 0.013579 | south | Y | 0.0088288 | -0.0020745 | 0.0075697 | 0.029547 | 0.0020745 | south | N | 0.0020745 | 0
7007 | L_LOSTPI | 1 | 158 | 0.013843 | south | Y | 0.0090928 | -0.0018105 | 0.0078337 | 0.029811 | 0.0018105 | south | N | 0.0018105 | 0
7008 | L_LOSTPI | 2 | 160 | 0.013843 | south | Y | 0.0090928 | -0.0018105 | 0.0078337 | 0.029811 | 0.0018105 | south | N | 0.0018105 | 0
7009 | L_LOSTPI | 3 | 175 | 0.013843 | south | Y | 0.0090928 | -0.0018105 | 0.0078337 | 0.029811 | 0.0018105 | south | N | 0.0018105 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.014699 | south | Y | 0.0099488 | -0.00095447 | 0.0086897 | 0.030667 | 0.00095447 | south | N | 0.00095447 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.014699 | south | Y | 0.0099488 | -0.00095447 | 0.0086897 | 0.030667 | 0.00095447 | south | N | 0.00095447 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.014715 | south | Y | 0.0099648 | -0.00093847 | 0.0087057 | 0.030683 | 0.00093847 | south | N | 0.00093847 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.015155 | south | Y | 0.010405 | -0.00049847 | 0.0091457 | 0.031123 | 0.00049847 | south | N | 0.00049847 | 0
7015 | L_HAYSEN | 2 | 225 | 0.015155 | south | Y | 0.010405 | -0.00049847 | 0.0091457 | 0.031123 | 0.00049847 | south | N | 0.00049847 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.015155 | south | Y | 0.010405 | -0.00049847 | 0.0091457 | 0.031123 | 0.00049847 | south | N | 0.00049847 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.015155 | south | Y | 0.010405 | -0.00049847 | 0.0091457 | 0.031123 | 0.00049847 | south | N | 0.00049847 | 0
7020 | L_AUSTPL | 1 | 8 | 0.013273 | south | N | 0.0085228 | -0.0023805 | 0.0072637 | 0.029241 | 0.0023805 | south | N | 0.0023805 | 0
7020 | L_AUSTPL | 2 | 8 | 0.013273 | south | N | 0.0085228 | -0.0023805 | 0.0072637 | 0.029241 | 0.0023805 | south | N | 0.0023805 | 0
7022 | L_BUCHAN | 1 | 18 | 0.0124 | south | N | 0.0076498 | -0.0032535 | 0.0063907 | 0.028368 | 0.0032535 | south | N | 0.0032535 | 0
7023 | L_BUCHAN | 2 | 18 | 0.0124 | south | N | 0.0076498 | -0.0032535 | 0.0063907 | 0.028368 | 0.0032535 | south | N | 0.0032535 | 0
7024 | L_BUCHAN | 3 | 15 | 0.0124 | south | N | 0.0076498 | -0.0032535 | 0.0063907 | 0.028368 | 0.0032535 | south | N | 0.0032535 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.012503 | south | N | 0.0077528 | -0.0031505 | 0.0064937 | 0.028471 | 0.0031505 | south | N | 0.0031505 | 0
7028 | L_MARBFA | 1 | 18 | 0.013017 | south | N | 0.0082668 | -0.0026365 | 0.0070077 | 0.028985 | 0.0026365 | south | N | 0.0026365 | 0
7029 | L_MARBFA | 2 | 18 | 0.013017 | south | N | 0.0082668 | -0.0026365 | 0.0070077 | 0.028985 | 0.0026365 | south | N | 0.0026365 | 0
7031 | L_MARSFO | 1 | 35 | 0.013159 | south | N | 0.0084088 | -0.0024945 | 0.0071497 | 0.029127 | 0.0024945 | south | N | 0.0024945 | 0
7032 | L_MARSFO | 2 | 34 | 0.013159 | south | N | 0.0084088 | -0.0024945 | 0.0071497 | 0.029127 | 0.0024945 | south | N | 0.0024945 | 0
7033 | L_MARSFO | 3 | 35 | 0.013159 | south | N | 0.0084088 | -0.0024945 | 0.0071497 | 0.029127 | 0.0024945 | south | N | 0.0024945 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.012926 | south | N | 0.0081758 | -0.0027275 | 0.0069167 | 0.028894 | 0.0027275 | south | N | 0.0027275 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.012926 | south | N | 0.0081758 | -0.0027275 | 0.0069167 | 0.028894 | 0.0027275 | south | N | 0.0027275 | 0
7038 | L_DELAWA | 1 | 35 | 0.006079 | west | Y | 0.0013288 | -0.0095745 | 6.9665e-05 | 0.022047 | 6.9665e-05 | west | N | 6.9665e-05 | 0
7038 | L_DELAWA | 2 | 30 | 0.006079 | west | Y | 0.0013288 | -0.0095745 | 6.9665e-05 | 0.022047 | 6.9665e-05 | west | N | 6.9665e-05 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.014154 | south | Y | 0.0094038 | -0.0014995 | 0.0081447 | 0.030122 | 0.0014995 | south | N | 0.0014995 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.014154 | south | Y | 0.0094038 | -0.0014995 | 0.0081447 | 0.030122 | 0.0014995 | south | N | 0.0014995 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.014154 | south | Y | 0.0094038 | -0.0014995 | 0.0081447 | 0.030122 | 0.0014995 | south | N | 0.0014995 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.014154 | south | Y | 0.0094038 | -0.0014995 | 0.0081447 | 0.030122 | 0.0014995 | south | N | 0.0014995 | 0
7487 | L_CANYHY | 1 | 6 | 0.014764 | south | N | 0.010014 | -0.00088947 | 0.0087547 | 0.030732 | 0.00088947 | south | N | 0.00088947 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.015463 | south | N | 0.010713 | -0.00019047 | 0.0094537 | 0.031431 | 0.00019047 | south | N | 0.00019047 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.015463 | south | N | 0.010713 | -0.00019047 | 0.0094537 | 0.031431 | 0.00019047 | south | N | 0.00019047 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.015463 | south | N | 0.010713 | -0.00019047 | 0.0094537 | 0.031431 | 0.00019047 | south | N | 0.00019047 | 0
7609 | L_SCHUMA | 1 | 4 | 0.015564 | south | N | 0.010814 | -8.9467e-05 | 0.0095547 | 0.031532 | 8.9467e-05 | south | N | 8.9467e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.015676 | south | N | 0.010926 | 2.2533e-05 | 0.0096667 | 0.031644 | 2.2533e-05 | south | N | 2.2533e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.015676 | south | N | 0.010926 | 2.2533e-05 | 0.0096667 | 0.031644 | 2.2533e-05 | south | N | 2.2533e-05 | 0
7800 | L_GUADGE | 1 | 147 | 0.015833 | south | Y | 0.011083 | 0.00017953 | 0.0098237 | 0.031801 | 0.00017953 | south | N | 0.00017953 | 0
7801 | L_GUADGE | 2 | 138 | 0.015833 | south | Y | 0.011083 | 0.00017953 | 0.0098237 | 0.031801 | 0.00017953 | south | N | 0.00017953 | 0
7802 | L_GUADGE | 3 | 140 | 0.015833 | south | Y | 0.011083 | 0.00017953 | 0.0098237 | 0.031801 | 0.00017953 | south | N | 0.00017953 | 0
7803 | L_GUADGE | 4 | 147 | 0.015833 | south | Y | 0.011083 | 0.00017953 | 0.0098237 | 0.031801 | 0.00017953 | south | N | 0.00017953 | 0
7804 | L_GUADGE | 5 | 182 | 0.015833 | south | Y | 0.011083 | 0.00017953 | 0.0098237 | 0.031801 | 0.00017953 | south | N | 0.00017953 | 0
7805 | L_GUADGE | 6 | 198 | 0.015833 | south | Y | 0.011083 | 0.00017953 | 0.0098237 | 0.031801 | 0.00017953 | south | N | 0.00017953 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.013804 | south | Y | 0.0090538 | -0.0018495 | 0.0077947 | 0.029772 | 0.0018495 | south | N | 0.0018495 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.013804 | south | Y | 0.0090538 | -0.0018495 | 0.0077947 | 0.029772 | 0.0018495 | south | N | 0.0018495 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.013804 | south | Y | 0.0090538 | -0.0018495 | 0.0077947 | 0.029772 | 0.0018495 | south | N | 0.0018495 | 0
7810 | L_RIONOG | 1 | 142 | 0.015504 | south | Y | 0.010754 | -0.00014947 | 0.0094947 | 0.031472 | 0.00014947 | south | N | 0.00014947 | 0
7811 | L_RIONOG | 2 | 145 | 0.015504 | south | Y | 0.010754 | -0.00014947 | 0.0094947 | 0.031472 | 0.00014947 | south | N | 0.00014947 | 0
7812 | L_RIONOG | 3 | 151 | 0.015504 | south | Y | 0.010754 | -0.00014947 | 0.0094947 | 0.031472 | 0.00014947 | south | N | 0.00014947 | 0
7813 | L_RIONOG | 4 | 290 | 0.015504 | south | Y | 0.010754 | -0.00014947 | 0.0094947 | 0.031472 | 0.00014947 | south | N | 0.00014947 | 0
8032 | AMISTADH | 1 | 33 | 0.013469 | south | N | 0.0087188 | -0.0021845 | 0.0074597 | 0.029437 | 0.0021845 | south | N | 0.0021845 | 0
8033 | AMISTADH | 2 | 25 | 0.013469 | south | N | 0.0087188 | -0.0021845 | 0.0074597 | 0.029437 | 0.0021845 | south | N | 0.0021845 | 0
8048 | FALCONHY | 1 | 12 | 0.017453 | south | N | 0.012703 | 0.0017995 | 0.011444 | 0.033421 | 0.0017995 | south | N | 0.0017995 | 0
8066 | DUP1V#1 | 1 | 73 | 0.01899 | south | N | 0.01424 | 0.0033365 | 0.012981 | 0.034958 | 0.0033365 | south | N | 0.0033365 | 0
8134 | FOR69CG0 | 1 | 79 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
8138 | FOR69CG0 | 2 | 81 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | Y | 0.015653 | 0
8147 | UCAR #2 | 10 | 28 | 0.019298 | south | N | 0.014548 | 0.0036445 | 0.013289 | 0.035266 | 0.0036445 | south | N | 0.0036445 | 0
8148 | UCAR #1 | 2 | 7 | 0.019298 | south | N | 0.014548 | 0.0036445 | 0.013289 | 0.035266 | 0.0036445 | south | N | 0.0036445 | 0
8153 | FOR69CG0 | 3 | 79 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
8154 | FOR69CG0 | 4 | 80 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
8156 | FOR69CG0 | 6 | 25 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
8157 | FOR69CG0 | 7 | 46 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
8161 | COLETOU1 | 1 | 629 | 0.017973 | south | Y | 0.013223 | 0.0023195 | 0.011964 | 0.033941 | 0.0023195 | south | N | 0.0023195 | 0
8173 | VICEC51A | 5 | 144 | 0.01887 | south | Y | 0.01412 | 0.0032165 | 0.012861 | 0.034838 | 0.0032165 | south | N | 0.0032165 | 0
8174 | VICEC61A | 6 | 188 | 0.01887 | south | Y | 0.01412 | 0.0032165 | 0.012861 | 0.034838 | 0.0032165 | south | N | 0.0032165 | 0
8189 | CUERO 2 | 1 | 12 | 0.016473 | south | N | 0.011723 | 0.00081953 | 0.010464 | 0.032441 | 0.00081953 | south | N | 0.00081953 | 0
8262 | ELPS | 1 | 6 | 0.014362 | south | N | 0.0096118 | -0.0012915 | 0.0083527 | 0.03033 | 0.0012915 | south | N | 0.0012915 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | Y | 0.015653 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | Y | 0.015653 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | Y | 0.015653 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | Y | 0.015653 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | Y | 0.015653 | 0
8442 | NBEC71A | 1 | 336 | 0.018039 | south | Y | 0.013289 | 0.0023855 | 0.01203 | 0.034007 | 0.0023855 | south | N | 0.0023855 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | Y | 0.015653 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.0047502 | -0.015653 | -0.0060093 | 0.015968 | 0.0047502 | North | Y | 0.015653 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.01801 | south | Y | 0.01326 | 0.0023565 | 0.012001 | 0.033978 | 0.0023565 | south | N | 0.0023565 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.01801 | south | Y | 0.01326 | 0.0023565 | 0.012001 | 0.033978 | 0.0023565 | south | N | 0.0023565 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.018007 | south | N | 0.013257 | 0.0023535 | 0.011998 | 0.033975 | 0.0023535 | south | N | 0.0023535 | 0
8506 | VAL #1 | 1 | 25 | 0.018016 | south | N | 0.013266 | 0.0023625 | 0.012007 | 0.033984 | 0.0023625 | south | N | 0.0023625 | 0
8507 | VAL #2 | 2 | 25 | 0.018016 | south | N | 0.013266 | 0.0023625 | 0.012007 | 0.033984 | 0.0023625 | south | N | 0.0023625 | 0
8511 | OXY_CC0A | 1 | 38 | 0.018 | south | N | 0.01325 | 0.0023465 | 0.011991 | 0.033968 | 0.0023465 | south | N | 0.0023465 | 0
8517 | CELANEBI | 1 | 29 | 0.017923 | south | N | 0.013173 | 0.0022695 | 0.011914 | 0.033891 | 0.0022695 | south | N | 0.0022695 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.018038 | south | N | 0.013288 | 0.0023845 | 0.012029 | 0.034006 | 0.0023845 | south | N | 0.0023845 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.018038 | south | N | 0.013288 | 0.0023845 | 0.012029 | 0.034006 | 0.0023845 | south | N | 0.0023845 | 0
8562 | CNOPST1 | 3 | 153 | 0.018038 | south | N | 0.013288 | 0.0023845 | 0.012029 | 0.034006 | 0.0023845 | south | N | 0.0023845 | 0
8926 | LGE_GT10 | 1 | 158 | 0.018168 | south | N | 0.013418 | 0.0025145 | 0.012159 | 0.034136 | 0.0025145 | south | N | 0.0025145 | 0
8927 | LGE_GT20 | 2 | 153 | 0.018168 | south | N | 0.013418 | 0.0025145 | 0.012159 | 0.034136 | 0.0025145 | south | N | 0.0025145 | 0
8928 | LGE_STG0 | 3 | 100 | 0.018168 | south | N | 0.013418 | 0.0025145 | 0.012159 | 0.034136 | 0.0025145 | south | N | 0.0025145 | 0
8930 | ICPGN10A | 1 | 145 | 0.018168 | south | N | 0.013418 | 0.0025145 | 0.012159 | 0.034136 | 0.0025145 | south | N | 0.0025145 | 0
8931 | ICPGN20A | 2 | 147 | 0.018168 | south | N | 0.013418 | 0.0025145 | 0.012159 | 0.034136 | 0.0025145 | south | N | 0.0025145 | 0
8932 | ICPGN30A | 3 | 127 | 0.018168 | south | N | 0.013418 | 0.0025145 | 0.012159 | 0.034136 | 0.0025145 | south | N | 0.0025145 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.017779 | south | Y | 0.013029 | 0.0021255 | 0.01177 | 0.033747 | 0.0021255 | south | N | 0.0021255 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.017779 | south | Y | 0.013029 | 0.0021255 | 0.01177 | 0.033747 | 0.0021255 | south | N | 0.0021255 | 0
8935 | FGNTS201 | 3 | 173 | 0.017779 | south | Y | 0.013029 | 0.0021255 | 0.01177 | 0.033747 | 0.0021255 | south | N | 0.0021255 | 0
8936 | MVGN#1 | 1 | 207 | 0.017832 | south | Y | 0.013082 | 0.0021785 | 0.011823 | 0.0338 | 0.0021785 | south | N | 0.0021785 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.017832 | south | Y | 0.013082 | 0.0021785 | 0.011823 | 0.0338 | 0.0021785 | south | N | 0.0021785 | 0
8938 | MVGN#3 | 3 | 242 | 0.017832 | south | Y | 0.013082 | 0.0021785 | 0.011823 | 0.0338 | 0.0021785 | south | N | 0.0021785 | 0
8981 | HECN1 | 1 | 144 | 0.017833 | south | Y | 0.013083 | 0.0021795 | 0.011824 | 0.033801 | 0.0021795 | south | N | 0.0021795 | 0
8982 | HECN2 | 2 | 144 | 0.017833 | south | Y | 0.013083 | 0.0021795 | 0.011824 | 0.033801 | 0.0021795 | south | N | 0.0021795 | 0
8983 | HECN3 | 3 | 171 | 0.017833 | south | Y | 0.013083 | 0.0021795 | 0.011824 | 0.033801 | 0.0021795 | south | N | 0.0021795 | 0
9000 | DECKR_G1 | 1 | 310 | 0.01327 | south | Y | 0.0085198 | -0.0023835 | 0.0072607 | 0.029238 | 0.0023835 | south | N | 0.0023835 | 0
9001 | DECKR_G2 | 2 | 413 | 0.01327 | south | Y | 0.0085198 | -0.0023835 | 0.0072607 | 0.029238 | 0.0023835 | south | N | 0.0023835 | 0
9002 | DECKR_G3 | 3 | 42 | 0.013172 | south | Y | 0.0084218 | -0.0024815 | 0.0071627 | 0.02914 | 0.0024815 | south | N | 0.0024815 | 0
9003 | DECKR_G4 | 4 | 44 | 0.013172 | south | Y | 0.0084218 | -0.0024815 | 0.0071627 | 0.02914 | 0.0024815 | south | N | 0.0024815 | 0
9004 | DECKR_G5 | 5 | 44 | 0.013172 | south | Y | 0.0084218 | -0.0024815 | 0.0071627 | 0.02914 | 0.0024815 | south | N | 0.0024815 | 0
9005 | DECKR_G6 | 6 | 47 | 0.013172 | south | Y | 0.0084218 | -0.0024815 | 0.0071627 | 0.02914 | 0.0024815 | south | N | 0.0024815 | 0
9016 | SANDH_G1 | 1 | 49 | 0.013402 | south | Y | 0.0086518 | -0.0022515 | 0.0073927 | 0.02937 | 0.0022515 | south | N | 0.0022515 | 0
9017 | SANDH_G2 | 2 | 46 | 0.013402 | south | Y | 0.0086518 | -0.0022515 | 0.0073927 | 0.02937 | 0.0022515 | south | N | 0.0022515 | 0
9018 | SANDH_G3 | 3 | 46 | 0.013402 | south | Y | 0.0086518 | -0.0022515 | 0.0073927 | 0.02937 | 0.0022515 | south | N | 0.0022515 | 0
9019 | SANDH_G4 | 4 | 47 | 0.013402 | south | Y | 0.0086518 | -0.0022515 | 0.0073927 | 0.02937 | 0.0022515 | south | N | 0.0022515 | 0
9020 | SANDHG5A | 5A | 154 | 0.013402 | south | Y | 0.0086518 | -0.0022515 | 0.0073927 | 0.02937 | 0.0022515 | south | N | 0.0022515 | 0
9021 | SANDHG5C | 5C | 148 | 0.013402 | south | Y | 0.0086518 | -0.0022515 | 0.0073927 | 0.02937 | 0.0022515 | south | N | 0.0022515 | 0
9022 | SANDH_G6 | 6 | 48 | 0.013402 | south | Y | 0.0086518 | -0.0022515 | 0.0073927 | 0.02937 | 0.0022515 | south | N | 0.0022515 | 0
9023 | SANDH_G7 | 7 | 48 | 0.013402 | south | Y | 0.0086518 | -0.0022515 | 0.0073927 | 0.02937 | 0.0022515 | south | N | 0.0022515 | 0
11001 | NAV1CT | 1 | 70 | 0.006009 | west | Y | 0.0012588 | -0.0096445 | -3.3481e-07 | 0.021977 | 3.3481e-07 | west | N | 3.3481e-07 | 0
11009 | NAV2CT | 1 | 70 | 0.006009 | west | Y | 0.0012588 | -0.0096445 | -3.3481e-07 | 0.021977 | 3.3481e-07 | west | N | 3.3481e-07 | 0
11011 | NAV3ST | 1 | 92.8 | 0.006009 | west | Y | 0.0012588 | -0.0096445 | -3.3481e-07 | 0.021977 | 3.3481e-07 | west | N | 3.3481e-07 | 0
11012 | NAV4CT | 1 | 80 | 0.006009 | west | Y | 0.0012588 | -0.0096445 | -3.3481e-07 | 0.021977 | 3.3481e-07 | west | N | 3.3481e-07 | 0
11013 | NAV5CT | 1 | 80 | 0.006009 | west | Y | 0.0012588 | -0.0096445 | -3.3481e-07 | 0.021977 | 3.3481e-07 | west | N | 3.3481e-07 | 0
11014 | NAV6ST | 1 | 115 | 0.006009 | west | Y | 0.0012588 | -0.0096445 | -3.3481e-07 | 0.021977 | 3.3481e-07 | west | N | 3.3481e-07 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.00601 | west | Y | 0.0012598 | -0.0096435 | 6.6519e-07 | 0.021978 | 6.6519e-07 | west | N | 6.6519e-07 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.00601 | west | Y | 0.0012598 | -0.0096435 | 6.6519e-07 | 0.021978 | 6.6519e-07 | west | N | 6.6519e-07 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.00601 | west | Y | 0.0012598 | -0.0096435 | 6.6519e-07 | 0.021978 | 6.6519e-07 | west | N | 6.6519e-07 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.00601 | west | Y | 0.0012598 | -0.0096435 | 6.6519e-07 | 0.021978 | 6.6519e-07 | west | N | 6.6519e-07 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.00601 | west | Y | 0.0012598 | -0.0096435 | 6.6519e-07 | 0.021978 | 6.6519e-07 | west | N | 6.6519e-07 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.00601 | west | Y | 0.0012598 | -0.0096435 | 6.6519e-07 | 0.021978 | 6.6519e-07 | west | N | 6.6519e-07 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.00588 | west | Y | 0.0011298 | -0.0097735 | -0.00012933 | 0.021848 | 0.00012933 | west | N | 0.00012933 | 0
11057 | CHAMPION | 1 | 126.5 | 0.00588 | west | Y | 0.0011298 | -0.0097735 | -0.00012933 | 0.021848 | 0.00012933 | west | N | 0.00012933 | 0
11058 | PYRON_1G | 1 | 249 | 0.00588 | west | Y | 0.0011298 | -0.0097735 | -0.00012933 | 0.021848 | 0.00012933 | west | N | 0.00012933 | 0
11059 | INADALE_ | 1 | 197 | 0.00588 | west | Y | 0.0011298 | -0.0097735 | -0.00012933 | 0.021848 | 0.00012933 | west | N | 0.00012933 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.005946 | west | Y | 0.0011958 | -0.0097075 | -6.3335e-05 | 0.021914 | 6.3335e-05 | west | N | 6.3335e-05 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.005946 | west | Y | 0.0011958 | -0.0097075 | -6.3335e-05 | 0.021914 | 6.3335e-05 | west | N | 6.3335e-05 | 0
11147 | NOTREES_ | 1 | 149 | 0.006067 | west | Y | 0.0013168 | -0.0095865 | 5.7665e-05 | 0.022035 | 5.7665e-05 | west | N | 5.7665e-05 | 0
11309 | BULLCREK | 1 | 180 | 0.005958 | west | Y | 0.0012078 | -0.0096955 | -5.1335e-05 | 0.021926 | 5.1335e-05 | west | N | 5.1335e-05 | 0
11310 | BULLCREK | 1 | 180 | 0.005958 | west | Y | 0.0012078 | -0.0096955 | -5.1335e-05 | 0.021926 | 5.1335e-05 | west | N | 5.1335e-05 | 0
11320 | COYOTE_1 | 1 | 225 | 0.005962 | west | Y | 0.0012118 | -0.0096915 | -4.7335e-05 | 0.02193 | 4.7335e-05 | west | N | 4.7335e-05 | 0
11415 | LORAINE_ | 1 | 125 | 0.005907 | west | Y | 0.0011568 | -0.0097465 | -0.00010233 | 0.021875 | 0.00010233 | west | N | 0.00010233 | 0
11416 | LORAINE_ | 1 | 125 | 0.005907 | west | Y | 0.0011568 | -0.0097465 | -0.00010233 | 0.021875 | 0.00010233 | west | N | 0.00010233 | 0
11691 | KMICHICT | 1 | 140 | 0.005022 | north | N | 0.00027176 | -0.010631 | -0.00098733 | 0.02099 | 0.00027176 | North | N | 0.00027176 | 0
11692 | KMICHICT | 2 | 141 | 0.005022 | north | N | 0.00027176 | -0.010631 | -0.00098733 | 0.02099 | 0.00027176 | North | N | 0.00027176 | 0
11693 | KMICHIST | 3 | 309 | 0.005022 | north | N | 0.00027176 | -0.010631 | -0.00098733 | 0.02099 | 0.00027176 | North | N | 0.00027176 | 0
11694 | KMICHICT | 4 | 143 | 0.005022 | north | N | 0.00027176 | -0.010631 | -0.00098733 | 0.02099 | 0.00027176 | North | N | 0.00027176 | 0
11695 | KMICHICT | 5 | 144 | 0.005022 | north | N | 0.00027176 | -0.010631 | -0.00098733 | 0.02099 | 0.00027176 | North | N | 0.00027176 | 0
11696 | KMICHIST | 6 | 310 | 0.005022 | north | N | 0.00027176 | -0.010631 | -0.00098733 | 0.02099 | 0.00027176 | North | N | 0.00027176 | 0
12322 | ENNSTRAC | 1 | 196 | 0.005128 | north | Y | 0.00037776 | -0.010525 | -0.00088133 | 0.021096 | 0.00037776 | North | N | 0.00037776 | 0
12323 | ENNSTRAC | 2 | 111 | 0.005128 | north | Y | 0.00037776 | -0.010525 | -0.00088133 | 0.021096 | 0.00037776 | North | N | 0.00037776 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.005067 | north | N | 0.00031676 | -0.010586 | -0.00094233 | 0.021035 | 0.00031676 | North | N | 0.00031676 | 0
12411 | FPLEFR1A | 1 | 161 | 0.004925 | north | Y | 0.00017476 | -0.010728 | -0.0010843 | 0.020893 | 0.00017476 | North | N | 0.00017476 | 0
12412 | FPLEFR1B | 2 | 164 | 0.004925 | north | Y | 0.00017476 | -0.010728 | -0.0010843 | 0.020893 | 0.00017476 | North | N | 0.00017476 | 0
12413 | FPLEFR1C | 3 | 164 | 0.004925 | north | Y | 0.00017476 | -0.010728 | -0.0010843 | 0.020893 | 0.00017476 | North | N | 0.00017476 | 0
12414 | FPLEFR1S | 4 | 414 | 0.004925 | north | Y | 0.00017476 | -0.010728 | -0.0010843 | 0.020893 | 0.00017476 | North | N | 0.00017476 | 0
12421 | FPLEFR2A | 1 | 162 | 0.004925 | north | Y | 0.00017476 | -0.010728 | -0.0010843 | 0.020893 | 0.00017476 | North | N | 0.00017476 | 0
12422 | FPLEFR2B | 2 | 161 | 0.004925 | north | Y | 0.00017476 | -0.010728 | -0.0010843 | 0.020893 | 0.00017476 | North | N | 0.00017476 | 0
12423 | FPLEFR2C | 3 | 163 | 0.004925 | north | Y | 0.00017476 | -0.010728 | -0.0010843 | 0.020893 | 0.00017476 | North | N | 0.00017476 | 0
12424 | FPLEFR2S | 4 | 409 | 0.004925 | north | Y | 0.00017476 | -0.010728 | -0.0010843 | 0.020893 | 0.00017476 | North | N | 0.00017476 | 0
12440 | PARKD_1S | 1 | 0 | 0.004991 | north | N | 0.00024076 | -0.010662 | -0.0010183 | 0.020959 | 0.00024076 | North | N | 0.00024076 | 0
12449 | PARKD_2S | 1 | 0 | 0.004991 | north | N | 0.00024076 | -0.010662 | -0.0010183 | 0.020959 | 0.00024076 | North | N | 0.00024076 | 0
13116 | TGATEWAY | 1 | 148 | 0.004661 | north | N | -8.9244e-05 | -0.010992 | -0.0013483 | 0.020629 | 8.9244e-05 | North | N | 8.9244e-05 | 0
13117 | TGATEWAY | 2 | 130 | 0.004661 | north | N | -8.9244e-05 | -0.010992 | -0.0013483 | 0.020629 | 8.9244e-05 | North | N | 8.9244e-05 | 0
13118 | TGATEWAY | 3 | 145 | 0.004661 | north | N | -8.9244e-05 | -0.010992 | -0.0013483 | 0.020629 | 8.9244e-05 | North | N | 8.9244e-05 | 0
13119 | TGATEWAY | 4 | 399 | 0.004661 | north | N | -8.9244e-05 | -0.010992 | -0.0013483 | 0.020629 | 8.9244e-05 | North | N | 8.9244e-05 | 0
13131 | CALFREST | 1 | 150.7 | 0.00427 | north | Y | -0.00048024 | -0.011383 | -0.0017393 | 0.020238 | 0.00048024 | North | N | 0.00048024 | 0
13132 | CALFREST | 2 | 151 | 0.00427 | north | Y | -0.00048024 | -0.011383 | -0.0017393 | 0.020238 | 0.00048024 | North | N | 0.00048024 | 0
13133 | CALFREST | 3 | 177.4 | 0.00427 | north | Y | -0.00048024 | -0.011383 | -0.0017393 | 0.020238 | 0.00048024 | North | N | 0.00048024 | 0
13134 | CALFREST | 4 | 151.5 | 0.004285 | north | Y | -0.00046524 | -0.011368 | -0.0017243 | 0.020253 | 0.00046524 | North | N | 0.00046524 | 0
13135 | CALFREST | 5 | 152.3 | 0.004285 | north | Y | -0.00046524 | -0.011368 | -0.0017243 | 0.020253 | 0.00046524 | North | N | 0.00046524 | 0
13136 | CALFREST | 6 | 177.5 | 0.004285 | north | Y | -0.00046524 | -0.011368 | -0.0017243 | 0.020253 | 0.00046524 | North | N | 0.00046524 | 0
13432 | SANDOW_5 | 5 | 581 | 0.011096 | south | Y | 0.0063458 | -0.0045575 | 0.0050867 | 0.027064 | 0.0045575 | south | N | 0.0045575 | 0
13691 | OAKGROVE | 1 | 855 | 0.002657 | north | Y | -0.0020932 | -0.012996 | -0.0033523 | 0.018625 | 0.0020932 | North | N | 0.0020932 | 0
13692 | OAKGROVE | 2 | 855 | 0.002657 | north | Y | -0.0020932 | -0.012996 | -0.0033523 | 0.018625 | 0.0020932 | North | N | 0.0020932 | 0
32798 | BRYN_TAM | 1 | 32 | 0.001939 | north | N | -0.0028112 | -0.013714 | -0.0040703 | 0.017907 | 0.0028112 | North | N | 0.0028112 | 0
32883 | BRYN_DNS | 1 | 48 | 0.002218 | north | Y | -0.0025322 | -0.013435 | -0.0037913 | 0.018186 | 0.0025322 | North | N | 0.0025322 | 0
32884 | BRYN_DNS | 1 | 46 | 0.002218 | north | Y | -0.0025322 | -0.013435 | -0.0037913 | 0.018186 | 0.0025322 | North | N | 0.0025322 | 0
32886 | BRYN_ATK | MB | 12 | 0.001963 | north | Y | -0.0027872 | -0.01369 | -0.0040463 | 0.017931 | 0.0027872 | North | N | 0.0027872 | 0
32887 | BRYN_ATK | MB | 51 | 0.001963 | north | Y | -0.0027872 | -0.01369 | -0.0040463 | 0.017931 | 0.0027872 | North | N | 0.0027872 | 0
32888 | BRYN_ATK | 1 | 17 | 0.001963 | north | Y | -0.0027872 | -0.01369 | -0.0040463 | 0.017931 | 0.0027872 | North | N | 0.0027872 | 0
32890 | BRYN_ATK | MB | 22 | 0.001963 | north | Y | -0.0027872 | -0.01369 | -0.0040463 | 0.017931 | 0.0027872 | North | N | 0.0027872 | 0
32891 | BRYN_ATK | MB | 25 | 0.001963 | north | Y | -0.0027872 | -0.01369 | -0.0040463 | 0.017931 | 0.0027872 | North | N | 0.0027872 | 0
32892 | BRYN_DNS | 1 | 105 | 0.002218 | north | Y | -0.0025322 | -0.013435 | -0.0037913 | 0.018186 | 0.0025322 | North | N | 0.0025322 | 0
36998 | RDCNYNG1 | 1 | 84 | 0.00592 | west | Y | 0.0011698 | -0.0097335 | -8.9335e-05 | 0.021888 | 8.9335e-05 | west | N | 8.9335e-05 | 0
38332 | WDWRDU2 | 1 | 80 | 0.006499 | west | Y | 0.0017488 | -0.0091545 | 0.00048967 | 0.022467 | 0.00048967 | west | N | 0.00048967 | 0
38437 | TNSRBNMS | 1 | 150 | 0.006503 | west | Y | 0.0017528 | -0.0091505 | 0.00049367 | 0.022471 | 0.00049367 | west | N | 0.00049367 | 0
38438 | TNSRBNMS | 1 | 150 | 0.006503 | west | Y | 0.0017528 | -0.0091505 | 0.00049367 | 0.022471 | 0.00049367 | west | N | 0.00049367 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.019597 | houston | N | -0.024347 | -0.03525 | -0.025606 | -0.0036295 | 0.0036295 | houston | N | 0.0036295 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.019597 | houston | N | -0.024347 | -0.03525 | -0.025606 | -0.0036295 | 0.0036295 | houston | N | 0.0036295 | 0
38600 | TNBP_CGN | 5 | 53 | -0.019597 | houston | N | -0.024347 | -0.03525 | -0.025606 | -0.0036295 | 0.0036295 | houston | N | 0.0036295 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.019597 | houston | N | -0.024347 | -0.03525 | -0.025606 | -0.0036295 | 0.0036295 | houston | N | 0.0036295 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.019597 | houston | N | -0.024347 | -0.03525 | -0.025606 | -0.0036295 | 0.0036295 | houston | N | 0.0036295 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.019597 | houston | N | -0.024347 | -0.03525 | -0.025606 | -0.0036295 | 0.0036295 | houston | N | 0.0036295 | 0
38614 | TNBPAMCG | 4 | 96 | -0.019597 | houston | N | -0.024347 | -0.03525 | -0.025606 | -0.0036295 | 0.0036295 | houston | N | 0.0036295 | 0
38615 | TNBPAMCG | 1 | 244 | -0.019597 | houston | N | -0.024347 | -0.03525 | -0.025606 | -0.0036295 | 0.0036295 | houston | N | 0.0036295 | 0
38690 | TNBP_CGN | 3 | 40 | -0.019597 | houston | N | -0.024347 | -0.03525 | -0.025606 | -0.0036295 | 0.0036295 | houston | N | 0.0036295 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.019497 | houston | N | -0.024247 | -0.03515 | -0.025506 | -0.0035295 | 0.0035295 | houston | N | 0.0035295 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.019497 | houston | N | -0.024247 | -0.03515 | -0.025506 | -0.0035295 | 0.0035295 | houston | N | 0.0035295 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.019497 | houston | N | -0.024247 | -0.03515 | -0.025506 | -0.0035295 | 0.0035295 | houston | N | 0.0035295 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.019497 | houston | N | -0.024247 | -0.03515 | -0.025506 | -0.0035295 | 0.0035295 | houston | N | 0.0035295 | 0
39470 | TNDOWCGN | 1 | 32 | -0.0195 | houston | N | -0.02425 | -0.035153 | -0.025509 | -0.0035325 | 0.0035325 | houston | N | 0.0035325 | 0
39480 | TNDOWCGN | 1 | 30 | -0.0195 | houston | N | -0.02425 | -0.035153 | -0.025509 | -0.0035325 | 0.0035325 | houston | N | 0.0035325 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.041775 | houston | N | 0.037025 | 0.026122 | 0.035766 | 0.057743 | 0.026122 | south | Y | 0.057743 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.041775 | houston | N | 0.037025 | 0.026122 | 0.035766 | 0.057743 | 0.026122 | south | Y | 0.057743 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.041775 | houston | N | 0.037025 | 0.026122 | 0.035766 | 0.057743 | 0.026122 | south | Y | 0.057743 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.041775 | houston | N | 0.037025 | 0.026122 | 0.035766 | 0.057743 | 0.026122 | south | Y | 0.057743 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.002657 | north | Y | -0.0020932 | -0.012996 | -0.0033523 | 0.018625 | 0.0020932 | North | N | 0.0020932 | 0
39970 | TNTNPONE | 1 | 153 | 0.002657 | north | Y | -0.0020932 | -0.012996 | -0.0033523 | 0.018625 | 0.0020932 | North | N | 0.0020932 | 0
48500 | APD_GT1_ | 1 | 136 | -0.19038 | houston | N | -0.19513 | -0.20603 | -0.19639 | -0.17441 | 0.17441 | houston | N | 0.17441 | 0
48510 | AK_GT1__ | 1 | 33 | 0.017143 | houston | N | 0.012393 | 0.0014895 | 0.011134 | 0.033111 | 0.0014895 | south | Y | 0.033111 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.052481 | houston | Y | -0.057231 | -0.068134 | -0.05849 | -0.036513 | 0.036513 | houston | N | 0.036513 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.052481 | houston | Y | -0.057231 | -0.068134 | -0.05849 | -0.036513 | 0.036513 | houston | N | 0.036513 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.052481 | houston | Y | -0.057231 | -0.068134 | -0.05849 | -0.036513 | 0.036513 | houston | N | 0.036513 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.052481 | houston | Y | -0.057231 | -0.068134 | -0.05849 | -0.036513 | 0.036513 | houston | N | 0.036513 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.030124 | houston | N | 0.025374 | 0.014471 | 0.024115 | 0.046092 | 0.014471 | south | Y | 0.046092 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.030124 | houston | N | 0.025374 | 0.014471 | 0.024115 | 0.046092 | 0.014471 | south | Y | 0.046092 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.02606 | houston | N | 0.02131 | 0.010407 | 0.020051 | 0.042028 | 0.010407 | south | Y | 0.042028 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.02606 | houston | N | 0.02131 | 0.010407 | 0.020051 | 0.042028 | 0.010407 | south | Y | 0.042028 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.02606 | houston | N | 0.02131 | 0.010407 | 0.020051 | 0.042028 | 0.010407 | south | Y | 0.042028 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.037105 | houston | N | -0.041855 | -0.052758 | -0.043114 | -0.021137 | 0.021137 | houston | N | 0.021137 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.037105 | houston | N | -0.041855 | -0.052758 | -0.043114 | -0.021137 | 0.021137 | houston | N | 0.021137 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.037105 | houston | N | -0.041855 | -0.052758 | -0.043114 | -0.021137 | 0.021137 | houston | N | 0.021137 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.037105 | houston | N | -0.041855 | -0.052758 | -0.043114 | -0.021137 | 0.021137 | houston | N | 0.021137 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.05058 | houston | N | -0.05533 | -0.066233 | -0.056589 | -0.034612 | 0.034612 | houston | N | 0.034612 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.05058 | houston | N | -0.05533 | -0.066233 | -0.056589 | -0.034612 | 0.034612 | houston | N | 0.034612 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.030285 | houston | N | -0.035035 | -0.045938 | -0.036294 | -0.014317 | 0.014317 | houston | N | 0.014317 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.030285 | houston | N | -0.035035 | -0.045938 | -0.036294 | -0.014317 | 0.014317 | houston | N | 0.014317 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.030285 | houston | N | -0.035035 | -0.045938 | -0.036294 | -0.014317 | 0.014317 | houston | N | 0.014317 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.030285 | houston | N | -0.035035 | -0.045938 | -0.036294 | -0.014317 | 0.014317 | houston | N | 0.014317 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.030285 | houston | N | -0.035035 | -0.045938 | -0.036294 | -0.014317 | 0.014317 | houston | N | 0.014317 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.056324 | houston | Y | -0.061074 | -0.071977 | -0.062333 | -0.040356 | 0.040356 | houston | N | 0.040356 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.054433 | houston | Y | -0.059183 | -0.070086 | -0.060442 | -0.038465 | 0.038465 | houston | N | 0.038465 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.049682 | houston | Y | -0.054432 | -0.065335 | -0.055691 | -0.033714 | 0.033714 | houston | N | 0.033714 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.049682 | houston | Y | -0.054432 | -0.065335 | -0.055691 | -0.033714 | 0.033714 | houston | N | 0.033714 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.049682 | houston | Y | -0.054432 | -0.065335 | -0.055691 | -0.033714 | 0.033714 | houston | N | 0.033714 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.06723 | houston | N | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.18383 | houston | N | -0.18858 | -0.19948 | -0.18984 | -0.16786 | 0.16786 | houston | N | 0.16786 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.18383 | houston | N | -0.18858 | -0.19948 | -0.18984 | -0.16786 | 0.16786 | houston | N | 0.16786 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.050754 | houston | N | -0.055504 | -0.066407 | -0.056763 | -0.034786 | 0.034786 | houston | N | 0.034786 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.050754 | houston | N | -0.055504 | -0.066407 | -0.056763 | -0.034786 | 0.034786 | houston | N | 0.034786 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.050754 | houston | N | -0.055504 | -0.066407 | -0.056763 | -0.034786 | 0.034786 | houston | N | 0.034786 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.050754 | houston | N | -0.055504 | -0.066407 | -0.056763 | -0.034786 | 0.034786 | houston | N | 0.034786 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.050241 | houston | N | -0.054991 | -0.065894 | -0.05625 | -0.034273 | 0.034273 | houston | N | 0.034273 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.050241 | houston | N | -0.054991 | -0.065894 | -0.05625 | -0.034273 | 0.034273 | houston | N | 0.034273 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.050241 | houston | N | -0.054991 | -0.065894 | -0.05625 | -0.034273 | 0.034273 | houston | N | 0.034273 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.050241 | houston | N | -0.054991 | -0.065894 | -0.05625 | -0.034273 | 0.034273 | houston | N | 0.034273 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.035591 | houston | N | -0.040341 | -0.051244 | -0.0416 | -0.019623 | 0.019623 | houston | N | 0.019623 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.035591 | houston | N | -0.040341 | -0.051244 | -0.0416 | -0.019623 | 0.019623 | houston | N | 0.019623 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.035591 | houston | N | -0.040341 | -0.051244 | -0.0416 | -0.019623 | 0.019623 | houston | N | 0.019623 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.035591 | houston | N | -0.040341 | -0.051244 | -0.0416 | -0.019623 | 0.019623 | houston | N | 0.019623 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.035591 | houston | N | -0.040341 | -0.051244 | -0.0416 | -0.019623 | 0.019623 | houston | N | 0.019623 | 0
48651 | EP_1_2 | 1 | 5 | -0.068018 | houston | N | -0.072768 | -0.083671 | -0.074027 | -0.05205 | 0.05205 | houston | N | 0.05205 | 0
48651 | EP_1_2 | 2 | 21 | -0.068018 | houston | N | -0.072768 | -0.083671 | -0.074027 | -0.05205 | 0.05205 | houston | N | 0.05205 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.000751 | north | N | -0.0039992 | -0.014902 | -0.0052583 | 0.016719 | 0.0039992 | North | N | 0.0039992 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.000751 | north | N | -0.0039992 | -0.014902 | -0.0052583 | 0.016719 | 0.0039992 | North | N | 0.0039992 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.000751 | north | N | -0.0039992 | -0.014902 | -0.0052583 | 0.016719 | 0.0039992 | North | N | 0.0039992 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.000751 | north | N | -0.0039992 | -0.014902 | -0.0052583 | 0.016719 | 0.0039992 | North | N | 0.0039992 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.10764 | houston | Y | -0.11239 | -0.12329 | -0.11365 | -0.091669 | 0.091669 | houston | N | 0.091669 | 0
48691 | GBY_7374 | A | 46 | -0.18057 | houston | Y | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48691 | GBY_7374 | B | 46 | -0.18057 | houston | Y | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48692 | GBY_8182 | C | 46 | -0.18057 | houston | Y | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48692 | GBY_8182 | D | 55 | -0.18057 | houston | Y | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48693 | GBY_8384 | E | 55 | -0.18057 | houston | Y | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48693 | GBY_8384 | F | 54 | -0.18057 | houston | Y | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48721 | LEG_1___ | 1 | 827 | 0.00326 | north | Y | -0.0014902 | -0.012393 | -0.0027493 | 0.019228 | 0.0014902 | North | N | 0.0014902 | 0
48722 | LEG_2___ | 2 | 819 | 0.00326 | north | Y | -0.0014902 | -0.012393 | -0.0027493 | 0.019228 | 0.0014902 | North | N | 0.0014902 | 0
48730 | MNS_GT | 1 | 46.1 | 0.021033 | houston | N | 0.016283 | 0.0053795 | 0.015024 | 0.037001 | 0.0053795 | south | Y | 0.037001 | 0
48731 | CBE_GT1 | 1 | 76 | 0.028994 | houston | Y | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 2.4032
48732 | CBE_GT2 | 1 | 76 | 0.028994 | houston | Y | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 2.4032
48733 | CBE_ST12 | 1 | 105 | 0.028994 | houston | Y | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 3.3202
48734 | CBE_GT3 | 1 | 74 | 0.028994 | houston | Y | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 2.34
48735 | CBE_GT4 | 1 | 74 | 0.028994 | houston | Y | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 2.34
48736 | CBE_ST34 | 1 | 102 | 0.028994 | houston | Y | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 3.2253
48740 | PSG_GN2_ | 1 | 180 | -0.051205 | houston | N | -0.055955 | -0.066858 | -0.057214 | -0.035237 | 0.035237 | houston | N | 0.035237 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.051205 | houston | N | -0.055955 | -0.066858 | -0.057214 | -0.035237 | 0.035237 | houston | N | 0.035237 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.051205 | houston | N | -0.055955 | -0.066858 | -0.057214 | -0.035237 | 0.035237 | houston | N | 0.035237 | 0
48761 | PR_GT1__ | 1 | 35 | -0.073823 | houston | N | -0.078573 | -0.089476 | -0.079832 | -0.057855 | 0.057855 | houston | N | 0.057855 | 0
48772 | PHR_GN2_ | MB | 459 | -0.024557 | houston | Y | -0.029307 | -0.04021 | -0.030566 | -0.0085895 | 0.0085895 | houston | N | 0.0085895 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.089569 | houston | N | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.089569 | houston | N | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.089569 | houston | N | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.089569 | houston | N | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.089569 | houston | N | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.089569 | houston | N | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.089569 | houston | N | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.06723 | houston | N | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.06723 | houston | N | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.06723 | houston | N | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.06723 | houston | N | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.092748 | houston | N | -0.097498 | -0.1084 | -0.098757 | -0.07678 | 0.07678 | houston | N | 0.07678 | 0
48820 | SHELLG1_ | 1 | 71 | -0.051631 | houston | N | -0.056381 | -0.067284 | -0.05764 | -0.035663 | 0.035663 | houston | N | 0.035663 | 0
48821 | SHELLG2 | 2 | 72 | -0.051631 | houston | N | -0.056381 | -0.067284 | -0.05764 | -0.035663 | 0.035663 | houston | N | 0.035663 | 0
48822 | SHELLG3_ | 1 | 39 | -0.051631 | houston | N | -0.056381 | -0.067284 | -0.05764 | -0.035663 | 0.035663 | houston | N | 0.035663 | 0
48822 | SHELLG3_ | 2 | 30 | -0.051631 | houston | N | -0.056381 | -0.067284 | -0.05764 | -0.035663 | 0.035663 | houston | N | 0.035663 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.045533 | houston | N | -0.050283 | -0.061186 | -0.051542 | -0.029565 | 0.029565 | houston | N | 0.029565 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.045533 | houston | N | -0.050283 | -0.061186 | -0.051542 | -0.029565 | 0.029565 | houston | N | 0.029565 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.050105 | houston | N | -0.054855 | -0.065758 | -0.056114 | -0.034137 | 0.034137 | houston | N | 0.034137 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.052 | houston | Y | -0.05675 | -0.067653 | -0.058009 | -0.036032 | 0.036032 | houston | N | 0.036032 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.052466 | houston | Y | -0.057216 | -0.068119 | -0.058475 | -0.036498 | 0.036498 | houston | N | 0.036498 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.049922 | houston | Y | -0.054672 | -0.065575 | -0.055931 | -0.033954 | 0.033954 | houston | N | 0.033954 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.050502 | houston | Y | -0.055252 | -0.066155 | -0.056511 | -0.034534 | 0.034534 | houston | N | 0.034534 | 0
48855 | SRB_GT21 | B2 | 12 | -0.052878 | houston | Y | -0.057628 | -0.068531 | -0.058887 | -0.03691 | 0.03691 | houston | N | 0.03691 | 0
48855 | SRB_GT21 | MB | 18 | -0.052878 | houston | Y | -0.057628 | -0.068531 | -0.058887 | -0.03691 | 0.03691 | houston | N | 0.03691 | 0
48865 | TECO_GT1 | 1 | 50 | 0.18936 | houston | Y | 0.18461 | 0.17371 | 0.18335 | 0.20533 | 0.17371 | south | Y | 0.20533 | 1.581
48873 | THW_ST3_ | 3 | 104 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48874 | THW_ST4_ | 4 | 104 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48875 | THW_3132 | A | 54 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48875 | THW_3132 | B | 53 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48877 | THW_3334 | C | 54 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48877 | THW_3334 | D | 57 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48879 | THW_4142 | E | 54 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48879 | THW_4142 | F | 54 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48881 | THW_4344 | G | 58 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48881 | THW_4344 | H | 58 | -0.027243 | houston | Y | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48883 | THW_GT1_ | B2 | 12 | -0.041987 | houston | Y | -0.046737 | -0.05764 | -0.047996 | -0.026019 | 0.026019 | houston | N | 0.026019 | 0
48885 | THW_5152 | A | 56 | -0.023421 | houston | Y | -0.028171 | -0.039074 | -0.02943 | -0.0074535 | 0.0074535 | houston | N | 0.0074535 | 0
48885 | THW_5152 | B | 59 | -0.023421 | houston | Y | -0.028171 | -0.039074 | -0.02943 | -0.0074535 | 0.0074535 | houston | N | 0.0074535 | 0
48886 | THW_5354 | C | 56 | -0.023421 | houston | Y | -0.028171 | -0.039074 | -0.02943 | -0.0074535 | 0.0074535 | houston | N | 0.0074535 | 0
48886 | THW_5354 | D | 56 | -0.023421 | houston | Y | -0.028171 | -0.039074 | -0.02943 | -0.0074535 | 0.0074535 | houston | N | 0.0074535 | 0
48887 | THW_5556 | E | 59 | -0.023421 | houston | Y | -0.028171 | -0.039074 | -0.02943 | -0.0074535 | 0.0074535 | houston | N | 0.0074535 | 0
48887 | THW_5556 | F | 56 | -0.023421 | houston | Y | -0.028171 | -0.039074 | -0.02943 | -0.0074535 | 0.0074535 | houston | N | 0.0074535 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.031942 | houston | Y | 0.027192 | 0.016289 | 0.025933 | 0.04791 | 0.016289 | south | Y | 0.04791 | 2.087
48921 | WAP_GN1_ | 1 | 161 | 0.0673 | houston | Y | 0.06255 | 0.051647 | 0.061291 | 0.083268 | 0.051647 | south | Y | 0.083268 | 5.091
48922 | WAP_GN2_ | 2 | 166 | 0.0673 | houston | Y | 0.06255 | 0.051647 | 0.061291 | 0.083268 | 0.051647 | south | Y | 0.083268 | 5.2491
48923 | WAP_GN3_ | 3 | 248 | 0.0673 | houston | Y | 0.06255 | 0.051647 | 0.061291 | 0.083268 | 0.051647 | south | Y | 0.083268 | 7.842
48924 | WAP_GN4_ | 4 | 546 | 0.0673 | houston | Y | 0.06255 | 0.051647 | 0.061291 | 0.083268 | 0.051647 | south | Y | 0.083268 | 17.2651
48925 | WAP_GN5_ | 5 | 643 | 0.0673 | houston | N | 0.06255 | 0.051647 | 0.061291 | 0.083268 | 0.051647 | south | Y | 0.083268 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.025604 | houston | Y | 0.020854 | 0.0099505 | 0.019595 | 0.041572 | 0.0099505 | south | Y | 0.041572 | 20.5853
48927 | WAP_GN7_ | 7 | 564 | 0.025604 | houston | Y | 0.020854 | 0.0099505 | 0.019595 | 0.041572 | 0.0099505 | south | Y | 0.041572 | 17.8342
48928 | WAP_GN8_ | 8 | 600 | 0.025604 | houston | Y | 0.020854 | 0.0099505 | 0.019595 | 0.041572 | 0.0099505 | south | Y | 0.041572 | 18.9726
48929 | WAPGT21_ | B1 | 13 | 0.0673 | houston | Y | 0.06255 | 0.051647 | 0.061291 | 0.083268 | 0.051647 | south | Y | 0.083268 | 0.41107
48940 | WARVUE_G | G1 | 12 | -0.062431 | houston | Y | -0.067181 | -0.078084 | -0.06844 | -0.046463 | 0.046463 | houston | N | 0.046463 | 0
49803 | EXN_15GT | 1 | 34 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49826 | EXN938GT | 5 | 45.9 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49828 | EXN941GT | 10 | 17.7 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49829 | EXN942GT | 11 | 20.4 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49830 | EXN943GT | 12 | 19.9 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49831 | EXN944GT | 13 | 35 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49832 | EXN945GT | 9 | 18 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49837 | EXN_GT | 4 | 85.4 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49838 | EXN_14GT | 14 | 148 | -0.062011 | houston | N | -0.066761 | -0.077664 | -0.06802 | -0.046043 | 0.046043 | houston | N | 0.046043 | 0
49851 | DOW17000 | 37 | 62 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49858 | DOW38100 | 31 | 71.4 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49859 | DOW38200 | 33 | 45 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49860 | DOW38300 | 32 | 101 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49862 | DOW39100 | 36 | 86 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49863 | DOW39200 | 35 | 88 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49865 | DOW41000 | 41 | 50 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49866 | DOW42000 | 42 | 18 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49869 | DOW49000 | 45 | 94 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49870 | DOW61000 | 61 | 70 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49871 | DOW62000 | 62 | 63 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49872 | DOW63000 | 63 | 72 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49873 | DOW64000 | 64 | 64.8 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49876 | DOW65000 | 65 | 101 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49877 | DOW66000 | 66 | 97 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49878 | DOW67000 | 67 | 103 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49882 | DOW81000 | 81 | 76 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49884 | DOW82000 | 82 | 80 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49885 | DOW83000 | 83 | 80 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
49886 | DOW84000 | 84 | 171 | 0.018828 | houston | N | 0.014078 | 0.0031745 | 0.012819 | 0.034796 | 0.0031745 | south | Y | 0.034796 | 0
58909 | PEARSALL | 1 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58909 | PEARSALL | 2 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58909 | PEARSALL | 3 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58909 | PEARSALL | 4 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58909 | PEARSALL | 5 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58909 | PEARSALL | 6 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58919 | PEARSALL | 1 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58919 | PEARSALL | 2 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58919 | PEARSALL | 3 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58919 | PEARSALL | 4 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58919 | PEARSALL | 5 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58919 | PEARSALL | 6 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58929 | PEARSALL | 1 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58929 | PEARSALL | 2 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58929 | PEARSALL | 3 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58929 | PEARSALL | 4 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58929 | PEARSALL | 5 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58929 | PEARSALL | 6 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58949 | PEARSALL | 1 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58949 | PEARSALL | 2 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58949 | PEARSALL | 3 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58949 | PEARSALL | 4 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58949 | PEARSALL | 5 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
58949 | PEARSALL | 6 | 8.4 | 0.016086 | south | Y | 0.011336 | 0.00043253 | 0.010077 | 0.032054 | 0.00043253 | south | N | 0.00043253 | 0
60000 | DSKY2 | 1 | 76.5 | 0.006678 | west | Y | 0.0019278 | -0.0089755 | 0.00066867 | 0.022646 | 0.00066867 | west | N | 0.00066867 | 0
60003 | KING_NE1 | 1 | 80 | 0.006492 | west | Y | 0.0017418 | -0.0091615 | 0.00048267 | 0.02246 | 0.00048267 | west | N | 0.00048267 | 0
60005 | KING_SE1 | 1 | 40 | 0.006492 | west | Y | 0.0017418 | -0.0091615 | 0.00048267 | 0.02246 | 0.00048267 | west | N | 0.00048267 | 0
60007 | KING_SW1 | 1 | 80 | 0.006462 | west | Y | 0.0017118 | -0.0091915 | 0.00045267 | 0.02243 | 0.00045267 | west | N | 0.00045267 | 0
60016 | WOODWRD1 | 1 | 80 | 0.006498 | west | Y | 0.0017478 | -0.0091555 | 0.00048867 | 0.022466 | 0.00048867 | west | N | 0.00048867 | 0
60017 | ORNNWP1 | 1 | 80 | 0.006653 | west | Y | 0.0019028 | -0.0090005 | 0.00064367 | 0.022621 | 0.00064367 | west | N | 0.00064367 | 0
60018 | DSKY1 | 1 | 84 | 0.006703 | west | Y | 0.0019528 | -0.0089505 | 0.00069367 | 0.022671 | 0.00069367 | west | N | 0.00069367 | 0
60019 | KING_NW1 | 1 | 80 | 0.006462 | west | Y | 0.0017118 | -0.0091915 | 0.00045267 | 0.02243 | 0.00045267 | west | N | 0.00045267 | 0
60057 | CALLAHAN | 1 | 114 | 0.015334 | south | Y | 0.010584 | -0.00031947 | 0.0093247 | 0.031302 | 0.00031947 | south | N | 0.00031947 | 0
60058 | BUFF_GAP | 1 | 120 | 0.005961 | west | Y | 0.0012108 | -0.0096925 | -4.8335e-05 | 0.021929 | 4.8335e-05 | west | N | 4.8335e-05 | 0
60060 | CIRELLO | 1 | 233 | 0.005961 | west | Y | 0.0012108 | -0.0096925 | -4.8335e-05 | 0.021929 | 4.8335e-05 | west | N | 4.8335e-05 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.005961 | west | Y | 0.0012108 | -0.0096925 | -4.8335e-05 | 0.021929 | 4.8335e-05 | west | N | 4.8335e-05 | 0
60066 | H_HOLLOW | 1 | 222 | 0.015334 | south | Y | 0.010584 | -0.00031947 | 0.0093247 | 0.031302 | 0.00031947 | south | N | 0.00031947 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.015334 | south | Y | 0.010584 | -0.00031947 | 0.0093247 | 0.031302 | 0.00031947 | south | N | 0.00031947 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.015334 | south | Y | 0.010584 | -0.00031947 | 0.0093247 | 0.031302 | 0.00031947 | south | N | 0.00031947 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.015334 | south | Y | 0.010584 | -0.00031947 | 0.0093247 | 0.031302 | 0.00031947 | south | N | 0.00031947 | 0
60074 | HORSH5 | 1 | 100 | 0.015334 | south | Y | 0.010584 | -0.00031947 | 0.0093247 | 0.031302 | 0.00031947 | south | N | 0.00031947 | 0
60081 | WHRLWIND | 1 | 60 | 0.005823 | west | Y | 0.0010728 | -0.0098305 | -0.00018633 | 0.021791 | 0.00018633 | west | N | 0.00018633 | 0
60201 | RIO DRCS | F | 0 | 0.011508 | south | N | 0.0067578 | -0.0041455 | 0.0054987 | 0.027476 | 0.0041455 | south | N | 0.0041455 | 0
60202 | FRIEND_R | F | 0 | 0.007508 | west | N | 0.0027578 | -0.0081455 | 0.0014987 | 0.023476 | 0.0014987 | west | N | 0.0014987 | 0
60203 | PRES0A | BT | 4.8 | 0.006351 | west | N | 0.0016008 | -0.0093025 | 0.00034167 | 0.022319 | 0.00034167 | west | N | 0.00034167 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.005886 | west | Y | 0.0011358 | -0.0097675 | -0.00012333 | 0.021854 | 0.00012333 | west | N | 0.00012333 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.005886 | west | Y | 0.0011358 | -0.0097675 | -0.00012333 | 0.021854 | 0.00012333 | west | N | 0.00012333 | 0
71057 | L_SWEETW | W1 | 135 | 0.005886 | west | Y | 0.0011358 | -0.0097675 | -0.00012333 | 0.021854 | 0.00012333 | west | N | 0.00012333 | 0
71059 | L_SWEETW | W1 | 119 | 0.005886 | west | Y | 0.0011358 | -0.0097675 | -0.00012333 | 0.021854 | 0.00012333 | west | N | 0.00012333 | 0
71060 | L_SWEETW | W1 | 105 | 0.005886 | west | Y | 0.0011358 | -0.0097675 | -0.00012333 | 0.021854 | 0.00012333 | west | N | 0.00012333 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.005886 | west | Y | 0.0011358 | -0.0097675 | -0.00012333 | 0.021854 | 0.00012333 | west | N | 0.00012333 | 0
76031 | L_GASCCR | W1 | 150 | 0.006006 | west | Y | 0.0012558 | -0.0096475 | -3.3348e-06 | 0.021974 | 3.3348e-06 | west | N | 3.3348e-06 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.006022 | west | Y | 0.0012718 | -0.0096315 | 1.2665e-05 | 0.02199 | 1.2665e-05 | west | N | 1.2665e-05 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.006022 | west | Y | 0.0012718 | -0.0096315 | 1.2665e-05 | 0.02199 | 1.2665e-05 | west | N | 1.2665e-05 | 0
76096 | L_CAPRSI | W1 | 186 | 0.006022 | west | Y | 0.0012718 | -0.0096315 | 1.2665e-05 | 0.02199 | 1.2665e-05 | west | N | 1.2665e-05 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.006022 | west | Y | 0.0012718 | -0.0096315 | 1.2665e-05 | 0.02199 | 1.2665e-05 | west | N | 1.2665e-05 | 0
80003 | MILHWYS | F | 0 | 0.017871 | south | N | 0.013121 | 0.0022175 | 0.011862 | 0.033839 | 0.0022175 | south | N | 0.0022175 | 0
80010 | EPLVT1 | F | 0 | 0.01457 | south | N | 0.0098198 | -0.0010835 | 0.0085607 | 0.030538 | 0.0010835 | south | N | 0.0010835 | 0
80012 | LAR | F | 0 | 0.016666 | south | N | 0.011916 | 0.0010125 | 0.010657 | 0.032634 | 0.0010125 | south | N | 0.0010125 | 0
80051 | FORPVCM0 | 8 | 28 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
80053 | FOR69CG0 | 10 | 74 | 0.019796 | south | N | 0.015046 | 0.0041425 | 0.013787 | 0.035764 | 0.0041425 | south | N | 0.0041425 | 0
80080 | GWINDT11 | 1 | 94 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80080 | GWINDT11 | 2 | 41 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80080 | GWINDT11 | 3 | 38 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80080 | GWINDT11 | 4 | 19 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80081 | GWINDT21 | 1 | 94 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80081 | GWINDT21 | 2 | 36 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80081 | GWINDT21 | 3 | 43 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80081 | GWINDT21 | 4 | 22 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80137 | CSDR89 | 8 | 39 | 0.019298 | south | N | 0.014548 | 0.0036445 | 0.013289 | 0.035266 | 0.0036445 | south | N | 0.0036445 | 0
80137 | CSDR89 | 9 | 15 | 0.019298 | south | N | 0.014548 | 0.0036445 | 0.013289 | 0.035266 | 0.0036445 | south | N | 0.0036445 | 0
80138 | CSDR7 | 7 | 7 | 0.019298 | south | N | 0.014548 | 0.0036445 | 0.013289 | 0.035266 | 0.0036445 | south | N | 0.0036445 | 0
80139 | CSDR56 | 5 | 15 | 0.019298 | south | N | 0.014548 | 0.0036445 | 0.013289 | 0.035266 | 0.0036445 | south | N | 0.0036445 | 0
80139 | CSDR56 | 6 | 39 | 0.019298 | south | N | 0.014548 | 0.0036445 | 0.013289 | 0.035266 | 0.0036445 | south | N | 0.0036445 | 0
80140 | CSDR11 | 11 | 39 | 0.019298 | south | N | 0.014548 | 0.0036445 | 0.013289 | 0.035266 | 0.0036445 | south | N | 0.0036445 | 0
80180 | PNSCALT1 | 1 | 148 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80180 | PNSCALT1 | 2 | 50 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80181 | PNSCALT2 | 1 | 55 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80181 | PNSCALT2 | 2 | 50 | 0.017886 | south | Y | 0.013136 | 0.0022325 | 0.011877 | 0.033854 | 0.0022325 | south | N | 0.0022325 | 0
80223 | REYSHR G | 1 | 12 | 0.018168 | south | N | 0.013418 | 0.0025145 | 0.012159 | 0.034136 | 0.0025145 | south | N | 0.0025145 | 0
80224 | VISTRONG | 1 | 15 | 0.019162 | south | N | 0.014412 | 0.0035085 | 0.013153 | 0.03513 | 0.0035085 | south | N | 0.0035085 | 0
80225 | VISTRONG | 2 | 23 | 0.019162 | south | N | 0.014412 | 0.0035085 | 0.013153 | 0.03513 | 0.0035085 | south | N | 0.0035085 | 0
80226 | ALCOA G | 1 | 48 | 0.019685 | south | N | 0.014935 | 0.0040315 | 0.013676 | 0.035653 | 0.0040315 | south | N | 0.0040315 | 0
80227 | AIRCO G | 1 | 8 | 0.019205 | south | N | 0.014455 | 0.0035515 | 0.013196 | 0.035173 | 0.0035515 | south | N | 0.0035515 | 0
80261 | NBEC81A | 1 | 180 | 0.018035 | south | Y | 0.013285 | 0.0023815 | 0.012026 | 0.034003 | 0.0023815 | south | N | 0.0023815 | 0
80262 | NBEC91A | 1 | 180 | 0.018039 | south | Y | 0.013289 | 0.0023855 | 0.01203 | 0.034007 | 0.0023855 | south | N | 0.0023855 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.01801 | south | Y | 0.01326 | 0.0023565 | 0.012001 | 0.033978 | 0.0023565 | south | N | 0.0023565 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.01801 | south | Y | 0.01326 | 0.0023565 | 0.012001 | 0.033978 | 0.0023565 | south | N | 0.0023565 | 0
80265 | LARECU40 | 4 | 100 | 0.016665 | south | Y | 0.011915 | 0.0010115 | 0.010656 | 0.032633 | 0.0010115 | south | N | 0.0010115 | 0
80266 | LARECU50 | 5 | 100 | 0.016665 | south | Y | 0.011915 | 0.0010115 | 0.010656 | 0.032633 | 0.0010115 | south | N | 0.0010115 | 0
80291 | PAPALOTE | 1 | 25 | 0.018106 | south | Y | 0.013356 | 0.0024525 | 0.012097 | 0.034074 | 0.0024525 | south | N | 0.0024525 | 0
80291 | PAPALOTE | 2 | 25 | 0.018106 | south | Y | 0.013356 | 0.0024525 | 0.012097 | 0.034074 | 0.0024525 | south | N | 0.0024525 | 0
80291 | PAPALOTE | 3 | 25 | 0.018106 | south | Y | 0.013356 | 0.0024525 | 0.012097 | 0.034074 | 0.0024525 | south | N | 0.0024525 | 0
80291 | PAPALOTE | 4 | 16 | 0.018106 | south | Y | 0.013356 | 0.0024525 | 0.012097 | 0.034074 | 0.0024525 | south | N | 0.0024525 | 0
80294 | PAPALOTE | 5 | 25 | 0.018106 | south | Y | 0.013356 | 0.0024525 | 0.012097 | 0.034074 | 0.0024525 | south | N | 0.0024525 | 0
80294 | PAPALOTE | 6 | 25 | 0.018106 | south | Y | 0.013356 | 0.0024525 | 0.012097 | 0.034074 | 0.0024525 | south | N | 0.0024525 | 0
80294 | PAPALOTE | 7 | 25 | 0.018106 | south | Y | 0.013356 | 0.0024525 | 0.012097 | 0.034074 | 0.0024525 | south | N | 0.0024525 | 0
80294 | PAPALOTE | 8 | 15 | 0.018106 | south | Y | 0.013356 | 0.0024525 | 0.012097 | 0.034074 | 0.0024525 | south | N | 0.0024525 | 0
86104 | CID-138 | EQ | 0 | 0.016665 | south | N | 0.011915 | 0.0010115 | 0.010656 | 0.032633 | 0.0010115 | south | N | 0.0010115 | 0
86105 | CID-230 | EQ | 500 | 0.016665 | south | N | 0.011915 | 0.0010115 | 0.010656 | 0.032633 | 0.0010115 | south | N | 0.0010115 | 0
86106 | CUF-230 | EQ | 500 | 0.016665 | south | N | 0.011915 | 0.0010115 | 0.010656 | 0.032633 | 0.0010115 | south | N | 0.0010115 | 0
86107 | CUF-138 | EQ | 0 | 0.016665 | south | N | 0.011915 | 0.0010115 | 0.010656 | 0.032633 | 0.0010115 | south | N | 0.0010115 | 0
88198 | BEEVILLE | F | 0 | 0.017551 | south | N | 0.012801 | 0.0018975 | 0.011542 | 0.033519 | 0.0018975 | south | N | 0.0018975 | 0
88253 | HAMILTON | F | 0 | 0.013469 | south | N | 0.0087188 | -0.0021845 | 0.0074597 | 0.029437 | 0.0021845 | south | N | 0.0021845 | 0
88299 | ZAPATA | F | 0 | 0.017141 | south | N | 0.012391 | 0.0014875 | 0.011132 | 0.033109 | 0.0014875 | south | N | 0.0014875 | 0
88508 | FALFURRI | F | 0 | 0.017638 | south | N | 0.012888 | 0.0019845 | 0.011629 | 0.033606 | 0.0019845 | south | N | 0.0019845 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:Garrot - Midtown 138kV 47660-47705 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45972 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.18936 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.4682 | 50 | 0.18461 | 9.2307 | 50 | 9.2307
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.0673 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 10.8353 | 161 | 0.06255 | 10.0705 | 211 | 19.3012
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.0673 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 11.1718 | 166 | 0.06255 | 10.3833 | 377 | 29.6845
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.0673 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 16.6904 | 248 | 0.06255 | 15.5123 |  |  | Weighted Shift Factors
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.0673 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 36.7458 | 546 | 0.06255 | 34.1522 |  |  | North | 0.0047502
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.0673 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 43.2739 | 0 | 0.06255 | 0 |  |  | Houston | -0.027666
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.0673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.8749 | 13 | 0.06255 | 0.81315 |  |  |  | 0.032416
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 1.5334 | 100 | 0.043 | 4.3
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.011508 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.039174 | 0 |  |  | Line Rating | 247
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.637 | 0 | 0.037025 | 0 |  |  | Conc Gen | 377
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.637 | 0 | 0.037025 | 0 |  |  | Weighted Imp. | 29.6845
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.9712 | 0 | 0.037025 | 0 |  |  | PTDF | 0.078739
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.5744 | 0 | 0.037025 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.008063 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2094 | 150 | 0.035729 | 5.3594 |  |  | Concentration | 2.429
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.007508 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.035174 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.007191 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034857 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.007191 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034857 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.007104 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.03477 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.007104 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.5908 | 787 | 0.03477 | 27.3641
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.006974 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7784 | 255 | 0.03464 | 8.8332
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.006974 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0391 | 149 | 0.03464 | 5.1614
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.006974 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.067 | 153 | 0.03464 | 5.2999
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.006861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0292 | 150 | 0.034527 | 5.1791
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.006861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.54888 | 80 | 0.034527 | 2.7622
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.006703 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.56305 | 84 | 0.034369 | 2.887
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.006678 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51087 | 76.5 | 0.034344 | 2.6273
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006653 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.53224 | 80 | 0.034319 | 2.7455
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.006601 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.099015 | 0 | 0.034267 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.006601 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.099015 | 0 | 0.034267 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.006503 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.97545 | 150 | 0.034169 | 5.1254
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.006503 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.97545 | 150 | 0.034169 | 5.1254
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.006499 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51992 | 80 | 0.034165 | 2.7332
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006498 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51984 | 80 | 0.034164 | 2.7331
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.006492 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.4869 | 75 | 0.034158 | 2.5619
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006492 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51936 | 80 | 0.034158 | 2.7327
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.006492 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.25968 | 40 | 0.034158 | 1.3663
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006462 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51696 | 80 | 0.034128 | 2.7303
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006462 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51696 | 80 | 0.034128 | 2.7303
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.006351 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.030485 | 0 | 0.034017 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40148 | 66 | 0.033749 | 2.2274
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39539 | 65 | 0.033749 | 2.1937
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40756 | 67 | 0.033749 | 2.2612
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40756 | 67 | 0.033749 | 2.2612
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40756 | 67 | 0.033749 | 2.2612
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.006083 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033749 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.006083 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033749 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.006079 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.21277 | 35 | 0.033745 | 1.1811
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.006079 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.18237 | 30 | 0.033745 | 1.0124
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.006069 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0287 | 169.5 | 0.033735 | 5.7181
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.006067 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.90398 | 149 | 0.033733 | 5.0262
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.006044 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.03989 | 6.6 | 0.03371 | 0.22249
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.006044 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20731 | 34.3 | 0.03371 | 1.1563
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67748 | 112.5 | 0.033688 | 3.7899
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.90029 | 149.5 | 0.033688 | 5.0364
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1201 | 186 | 0.033688 | 6.266
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2917 | 214.5 | 0.033688 | 7.2261
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2513 | 208.2 | 0.033676 | 7.0114
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.85402 | 142.1 | 0.033676 | 4.7854
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79572 | 132.4 | 0.033676 | 4.4587
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.81736 | 136 | 0.033676 | 4.58
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.88347 | 147 | 0.033676 | 4.9504
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2621 | 210 | 0.033676 | 7.072
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.42063 | 70 | 0.033675 | 2.3573
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.42063 | 70 | 0.033675 | 2.3573
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.55764 | 92.8 | 0.033675 | 3.1251
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.48072 | 80 | 0.033675 | 2.694
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.48072 | 80 | 0.033675 | 2.694
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.69103 | 115 | 0.033675 | 3.8726
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.006007 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34841 | 58 | 0.033673 | 1.953
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.006006 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6036 | 100.5 | 0.033672 | 3.3841
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.006006 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9009 | 150 | 0.033672 | 5.0508
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.005997 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2846 | 214.2 | 0.033663 | 7.2107
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.005993 | west | 8 | N | N | Nwest | Nwest | 1 | 0.15462 | 0 | 0.033659 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.00597 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.7164 | 120 | 0.033636 | 4.0363
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.005969 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.71628 | 120 | 0.033635 | 4.0362
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.005962 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3415 | 225 | 0.033628 | 7.5663
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.005961 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.71532 | 120 | 0.033627 | 4.0353
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.005961 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3889 | 233 | 0.033627 | 7.8351
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.005961 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0146 | 170.2 | 0.033627 | 5.7233
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005958 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0724 | 180 | 0.033624 | 6.0524
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005958 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0724 | 180 | 0.033624 | 6.0524
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.005957 | west | 8 | N | N | Nwest | Nwest | 1 | 0.41699 | 0 | 0.033623 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.005957 | west | 8 | N | N | Nwest | Nwest | 1 | 0.43724 | 0 | 0.033623 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.005957 | west | 8 | N | N | Nwest | Nwest | 1 | 0.41937 | 0 | 0.033623 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8919 | 150 | 0.033612 | 5.0418
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3081 | 220 | 0.033612 | 7.3947
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1892 | 200 | 0.033612 | 6.7224
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.72482 | 121.9 | 0.033612 | 4.0973
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39184 | 66 | 0.033603 | 2.2178
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40965 | 69 | 0.033603 | 2.3186
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40965 | 69 | 0.033603 | 2.3186
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39778 | 67 | 0.033603 | 2.2514
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39778 | 67 | 0.033603 | 2.2514
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.3859 | 65 | 0.033603 | 2.1842
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.005934 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.37384 | 63 | 0.0336 | 2.1168
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.005931 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.83627 | 141 | 0.033597 | 4.7372
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.005931 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.71172 | 120 | 0.033597 | 4.0317
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.00593 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.58707 | 99 | 0.033596 | 3.326
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.00593 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.36173 | 61 | 0.033596 | 2.0494
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.00593 | west | 7 | N | N | Nwest | Nwest | 1 | 0.14825 | 0 | 0.033596 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.00593 | west | 7 | N | N | Nwest | Nwest | 1 | 0.271 | 0 | 0.033596 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.00593 | west | 7 | N | N | Nwest | Nwest | 1 | 0.271 | 0 | 0.033596 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.00592 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49728 | 84 | 0.033586 | 2.8212
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.005915 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.88725 | 150 | 0.033581 | 5.0372
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.005915 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.59742 | 101 | 0.033581 | 3.3917
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005907 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.73838 | 125 | 0.033573 | 4.1966
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005907 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.73838 | 125 | 0.033573 | 4.1966
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.22073 | 37.5 | 0.033552 | 1.2582
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.63275 | 107.5 | 0.033552 | 3.6069
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.79461 | 135 | 0.033552 | 4.5295
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.70043 | 119 | 0.033552 | 3.9927
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.61803 | 105 | 0.033552 | 3.523
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.47382 | 80.5 | 0.033552 | 2.7009
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2289 | 209 | 0.033546 | 7.0111
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.74382 | 126.5 | 0.033546 | 4.2436
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.4641 | 249 | 0.033546 | 8.353
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1584 | 197 | 0.033546 | 6.6086
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.005878 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8817 | 150 | 0.033544 | 5.0316
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.005866 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.35196 | 60 | 0.033532 | 2.0119
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.005823 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34938 | 60 | 0.033489 | 2.0094
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.005746 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2984 | 400 | 0.033412 | 13.3649
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.005745 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3558 | 236 | 0.033411 | 7.885
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9405 | 165 | 0.033366 | 5.5054
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.005661 | west | 4 | Y | N | Ywest | Nwest | 1 | 3.678 | 649.7 | 0.033327 | 21.6527
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.005626 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.4107 | 73 | 0.033292 | 2.4303
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.005626 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.66949 | 119 | 0.033292 | 3.9618
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.005626 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.1533 | 205 | 0.033292 | 6.8249
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.005626 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.57385 | 102 | 0.033292 | 3.3958
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.005626 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5401 | 96 | 0.033292 | 3.196
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.0056 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.3552 | 242 | 0.033266 | 8.0504
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.005575 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9366 | 168 | 0.033241 | 5.5845
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.005575 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.50175 | 90 | 0.033241 | 2.9917
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.00556 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.6672 | 120 | 0.033226 | 3.9871
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.005556 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0335 | 366 | 0.033222 | 12.1593
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.00555 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.0666 | 0 | 0.033216 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.00555 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.0666 | 0 | 0.033216 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.11096 | 20 | 0.033214 | 0.66428
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.11096 | 20 | 0.033214 | 0.66428
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.11096 | 20 | 0.033214 | 0.66428
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.094316 | 17 | 0.033214 | 0.56464
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38682 | 70 | 0.033192 | 2.3235
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38129 | 69 | 0.033192 | 2.2903
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38129 | 69 | 0.033192 | 2.2903
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.37577 | 68 | 0.033192 | 2.2571
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.005483 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.098694 | 18 | 0.033149 | 0.59669
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.005483 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.098694 | 18 | 0.033149 | 0.59669
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.005483 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.20835 | 38 | 0.033149 | 1.2597
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.005461 | north | 3 | N | N | Nnorth | Nnorth | 1 | 6.3184 | 0 | 0.033127 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.005461 | north | 3 | N | N | Nnorth | Nnorth | 1 | 6.3238 | 0 | 0.033127 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.005442 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1825 | 217.3 | 0.033108 | 7.1944
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.005442 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1156 | 205 | 0.033108 | 6.7872
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.005442 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4824 | 272.4 | 0.033108 | 9.0187
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.005439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1096 | 204 | 0.033105 | 6.7535
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.005439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0932 | 201 | 0.033105 | 6.6541
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.005439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3162 | 242 | 0.033105 | 8.0115
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.005424 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.03309 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.005394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.5535 | 288 | 0.03306 | 9.5213
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.005394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79292 | 147 | 0.03306 | 4.8598
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.005394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79292 | 147 | 0.03306 | 4.8598
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2067 | 224 | 0.033053 | 7.4039
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2175 | 226 | 0.033053 | 7.47
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.142 | 212 | 0.033053 | 7.0073
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1367 | 211 | 0.033053 | 6.9742
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.005315 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.005315 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.005315 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.005308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1487 | 216.4 | 0.032974 | 7.1356
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.005308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1471 | 216.1 | 0.032974 | 7.1257
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.005297 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0923 | 395 | 0.032963 | 13.0205
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.005297 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3042 | 435 | 0.032963 | 14.339
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.005287 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.59479 | 112.5 | 0.032953 | 3.7072
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.005281 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.2972 | 435 | 0.032947 | 14.332
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.005206 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.31236 | 60 | 0.032872 | 1.9723
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.005206 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.32798 | 63 | 0.032872 | 2.0709
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.005128 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0051 | 196 | 0.032794 | 6.4277
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.005128 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.56921 | 111 | 0.032794 | 3.6402
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.005084 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.03275 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.005067 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032733 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.005064 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.59755 | 118 | 0.03273 | 3.8622
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.005064 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.58236 | 115 | 0.03273 | 3.764
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.005064 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.8156 | 556 | 0.03273 | 18.198
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.005049 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20196 | 0 | 0.032715 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.005049 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20196 | 0 | 0.032715 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.005037 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.85629 | 170 | 0.032703 | 5.5595
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.005037 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.6192 | 520 | 0.032703 | 17.0056
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.005022 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.8581 | 370 | 0.032688 | 12.0946
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.70308 | 0 | 0.032688 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.7081 | 0 | 0.032688 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5518 | 0 | 0.032688 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.71815 | 0 | 0.032688 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.72317 | 0 | 0.032688 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5568 | 0 | 0.032688 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.8024 | 160 | 0.032681 | 5.229
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.78234 | 156 | 0.032681 | 5.0983
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.98294 | 196 | 0.032681 | 6.4055
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.78234 | 156 | 0.032681 | 5.0983
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.78736 | 157 | 0.032681 | 5.1309
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.99297 | 198 | 0.032681 | 6.4709
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.005011 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.37583 | 0 | 0.032677 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.005011 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.39888 | 0 | 0.032677 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.005011 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.44297 | 0 | 0.032677 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.005004 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.7922 | 558 | 0.03267 | 18.23
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.005004 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.8973 | 579 | 0.03267 | 18.916
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.005004 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.0432 | 808 | 0.03267 | 26.3975
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1998 | 40 | 0.032661 | 1.3064
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.3946 | 79 | 0.032661 | 2.5802
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.52947 | 106 | 0.032661 | 3.4621
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.72927 | 146 | 0.032661 | 4.7685
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.004995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.37962 | 76 | 0.032661 | 2.4822
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004991 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032657 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004991 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032657 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.004985 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.0997 | 20 | 0.032651 | 0.65302
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.004985 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.12462 | 25 | 0.032651 | 0.81628
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.004985 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.20439 | 41 | 0.032651 | 1.3387
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.004976 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.9307 | 388 | 0.032642 | 12.6652
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.004976 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.5626 | 515 | 0.032642 | 16.8107
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79292 | 161 | 0.032591 | 5.2472
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.8077 | 164 | 0.032591 | 5.345
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.8077 | 164 | 0.032591 | 5.345
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0389 | 414 | 0.032591 | 13.4927
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79785 | 162 | 0.032591 | 5.2798
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79292 | 161 | 0.032591 | 5.2472
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.80278 | 163 | 0.032591 | 5.3124
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0143 | 409 | 0.032591 | 13.3298
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.004913 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.1005 | 224 | 0.032579 | 7.2977
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.004695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.6856 | 785 | 0.032361 | 25.4035
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.004695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.7325 | 795 | 0.032361 | 25.7271
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.004695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.6621 | 780 | 0.032361 | 25.2417
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.68983 | 0 | 0.032327 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.60593 | 0 | 0.032327 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.67585 | 0 | 0.032327 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.8597 | 0 | 0.032327 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.004632 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.032298 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.004628 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.2314 | 50 | 0.032294 | 1.6147
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.004624 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.84157 | 182 | 0.03229 | 5.8768
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.004624 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.238 | 484 | 0.03229 | 15.6284
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.004285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64918 | 151.5 | 0.031951 | 4.8406
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.004285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.65261 | 152.3 | 0.031951 | 4.8662
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.004285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76059 | 177.5 | 0.031951 | 5.6713
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.00427 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64349 | 150.7 | 0.031936 | 4.8128
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.00427 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64477 | 151 | 0.031936 | 4.8224
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.00427 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7575 | 177.4 | 0.031936 | 5.6655
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.00419 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.5768 | 615 | 0.031856 | 19.5915
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.00419 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4595 | 587 | 0.031856 | 18.6996
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.00326 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.696 | 827 | 0.030926 | 25.5759
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.00326 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6699 | 819 | 0.030926 | 25.3285
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2717 | 855 | 0.030323 | 25.9263
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2717 | 855 | 0.030323 | 25.9263
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.40466 | 152.3 | 0.030323 | 4.6182
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.40652 | 153 | 0.030323 | 4.6394
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.002218 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.10646 | 48 | 0.029884 | 1.4344
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.002218 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.10203 | 46 | 0.029884 | 1.3747
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.002218 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.23289 | 105 | 0.029884 | 3.1378
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.001963 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.033371 | 17 | 0.029629 | 0.5037
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.001939 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.062048 | 0 | 0.029605 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.001117 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.51717 | 463 | 0.028783 | 13.3266
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.1158 | 0 | 0.028417 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.11716 | 0 | 0.028417 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.11716 | 0 | 0.028417 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.28538 | 0 | 0.028417 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.027666 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.027666 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.031942 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.1082 | 66 | 0.027192 | 1.7947
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.030124 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.1388 | 0 | 0.025374 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.030124 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30124 | 0 | 0.025374 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2035 | 76 | 0.024244 | 1.8425
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2035 | 76 | 0.024244 | 1.8425
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.0444 | 105 | 0.024244 | 2.5456
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1456 | 74 | 0.024244 | 1.794
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1456 | 74 | 0.024244 | 1.794
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.9574 | 102 | 0.024244 | 2.4729
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.02606 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2478 | 0 | 0.02131 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.02606 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2478 | 0 | 0.02131 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.02606 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.3847 | 0 | 0.02131 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.025604 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 16.6682 | 651 | 0.020854 | 13.5758
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.025604 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 14.4407 | 564 | 0.020854 | 11.7615
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.025604 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 15.3624 | 600 | 0.020854 | 12.5123
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.021033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96962 | 0 | 0.016283 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.020755 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 27.6664 | 0 | 0.016005 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.020755 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 27.5626 | 0 | 0.016005 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5639 | 0 | 0.015046 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6035 | 0 | 0.015046 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5639 | 0 | 0.015046 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5837 | 0 | 0.015046 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.552 | 0 | 0.015046 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.4949 | 0 | 0.015046 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.91062 | 0 | 0.015046 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.55429 | 0 | 0.015046 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.86311 | 0 | 0.015046 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4649 | 0 | 0.015046 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.019685 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.94488 | 0 | 0.014935 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.54034 | 0 | 0.014548 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13509 | 0 | 0.014548 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.75262 | 0 | 0.014548 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28947 | 0 | 0.014548 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13509 | 0 | 0.014548 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28947 | 0 | 0.014548 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.75262 | 0 | 0.014548 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.75262 | 0 | 0.014548 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.019205 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15364 | 0 | 0.014455 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.019162 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28743 | 0 | 0.014412 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.019162 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44073 | 0 | 0.014412 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.01899 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.3863 | 0 | 0.01424 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.018976 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.41747 | 22 | 0.014226 | 0.31297
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.018976 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20874 | 11 | 0.014226 | 0.15648
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.018976 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20874 | 11 | 0.014226 | 0.15648
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.90382 | 47.7 | 0.014198 | 0.67723
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70676 | 37.3 | 0.014198 | 0.52958
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.87161 | 46 | 0.014198 | 0.6531
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.9095 | 48 | 0.014198 | 0.68149
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.01887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.7173 | 144 | 0.01412 | 2.0332
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.01887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.5476 | 188 | 0.01412 | 2.6545
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1673 | 0 | 0.014078 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3443 | 0 | 0.014078 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.84726 | 0 | 0.014078 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9016 | 0 | 0.014078 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6192 | 0 | 0.014078 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6569 | 0 | 0.014078 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.9414 | 0 | 0.014078 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3389 | 0 | 0.014078 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7698 | 0 | 0.014078 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.318 | 0 | 0.014078 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1862 | 0 | 0.014078 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3556 | 0 | 0.014078 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2201 | 0 | 0.014078 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9016 | 0 | 0.014078 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8263 | 0 | 0.014078 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9393 | 0 | 0.014078 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4309 | 0 | 0.014078 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5062 | 0 | 0.014078 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5062 | 0 | 0.014078 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.2196 | 0 | 0.014078 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.8705 | 0 | 0.013418 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7797 | 0 | 0.013418 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 1.8168 | 0 | 0.013418 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6344 | 0 | 0.013418 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6707 | 0 | 0.013418 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.3073 | 0 | 0.013418 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.018168 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.21802 | 0 | 0.013418 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 25 | 0.013356 | 0.33389
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 25 | 0.013356 | 0.33389
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 25 | 0.013356 | 0.33389
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.2897 | 16 | 0.013356 | 0.21369
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 25 | 0.013356 | 0.33389
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 25 | 0.013356 | 0.33389
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 25 | 0.013356 | 0.33389
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.27159 | 15 | 0.013356 | 0.20034
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.018039 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0611 | 336 | 0.013289 | 4.465
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.018039 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.247 | 180 | 0.013289 | 2.392
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.018038 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.675 | 0 | 0.013288 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.018038 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6804 | 0 | 0.013288 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.018038 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7598 | 0 | 0.013288 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.018035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2463 | 180 | 0.013285 | 2.3913
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.018016 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.4504 | 0 | 0.013266 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.018016 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.4504 | 0 | 0.013266 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.01801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.0153 | 334 | 0.01326 | 4.4288
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.01801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.1234 | 340 | 0.01326 | 4.5083
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.01801 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2418 | 180 | 0.01326 | 2.3868
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.01801 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2418 | 180 | 0.01326 | 2.3868
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.018007 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.68427 | 0 | 0.013257 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.684 | 0 | 0.01325 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.017973 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.305 | 629 | 0.013223 | 8.3171
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.017923 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.51977 | 0 | 0.013173 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6813 | 94 | 0.013136 | 1.2348
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.73333 | 41 | 0.013136 | 0.53857
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.67967 | 38 | 0.013136 | 0.49916
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.33983 | 19 | 0.013136 | 0.24958
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6813 | 94 | 0.013136 | 1.2348
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6439 | 36 | 0.013136 | 0.47289
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.7691 | 43 | 0.013136 | 0.56484
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.39349 | 22 | 0.013136 | 0.28899
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.6471 | 148 | 0.013136 | 1.9441
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.8943 | 50 | 0.013136 | 0.65679
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.98373 | 55 | 0.013136 | 0.72247
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.8943 | 50 | 0.013136 | 0.65679
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.017872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.67914 | 38 | 0.013122 | 0.49863
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.017872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34493 | 19.3 | 0.013122 | 0.25325
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.017872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.26808 | 15 | 0.013122 | 0.19683
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.017872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.83998 | 47 | 0.013122 | 0.61672
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.017871 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013121 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.017833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.568 | 144 | 0.013083 | 1.8839
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.017833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.568 | 144 | 0.013083 | 1.8839
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.017833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0494 | 171 | 0.013083 | 2.2372
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.017832 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6912 | 207 | 0.013082 | 2.7079
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.017832 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8642 | 216.7 | 0.013082 | 2.8348
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.017832 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3153 | 242 | 0.013082 | 3.1658
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.017779 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6046 | 146.5 | 0.013029 | 1.9087
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.017779 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6295 | 147.9 | 0.013029 | 1.927
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.017779 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0758 | 173 | 0.013029 | 2.254
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.017638 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012888 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.017551 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012801 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.017453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20944 | 0 | 0.012703 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.017453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19198 | 0 | 0.012703 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.017453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20944 | 0 | 0.012703 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.017143 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56572 | 0 | 0.012393 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.017141 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012391 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.016666 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011916 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.016665 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6665 | 100 | 0.011915 | 1.1915
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.016665 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6665 | 100 | 0.011915 | 1.1915
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016665 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016665 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016665 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016665 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.016625 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.5835 | 396 | 0.011875 | 4.7024
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.016473 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19768 | 0 | 0.011723 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.016201 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.38882 | 24 | 0.011451 | 0.27482
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.016201 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.38882 | 24 | 0.011451 | 0.27482
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.016201 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.37262 | 23 | 0.011451 | 0.26337
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.016122 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.8026 | 546 | 0.011372 | 6.209
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.016122 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 12.0915 | 750 | 0.011372 | 8.5288
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.016048 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4874 | 155 | 0.011298 | 1.7512
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.016048 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.7282 | 170 | 0.011298 | 1.9206
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.016048 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4874 | 155 | 0.011298 | 1.7512
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.015978 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.3394 | 209 | 0.011228 | 2.3466
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.015978 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.4512 | 216 | 0.011228 | 2.4252
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.73499 | 46 | 0.011228 | 0.51648
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.75097 | 47 | 0.011228 | 0.5277
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.73499 | 46 | 0.011228 | 0.51648
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.73499 | 46 | 0.011228 | 0.51648
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.015969 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.9262 | 58 | 0.011219 | 0.65069
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.015969 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.4212 | 89 | 0.011219 | 0.99847
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.70264 | 44 | 0.011219 | 0.49363
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.70264 | 44 | 0.011219 | 0.49363
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.68667 | 43 | 0.011219 | 0.48241
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.71861 | 45 | 0.011219 | 0.50484
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.015962 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.5763 | 412 | 0.011212 | 4.6192
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.015962 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.3848 | 400 | 0.011212 | 4.4847
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.015961 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011211 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.015961 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011211 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.015961 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011211 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.015954 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.4933 | 407 | 0.011204 | 4.5599
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.015954 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.7645 | 424 | 0.011204 | 4.7504
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.015954 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.7805 | 425 | 0.011204 | 4.7616
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3275 | 147 | 0.011083 | 1.6292
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.185 | 138 | 0.011083 | 1.5294
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2166 | 140 | 0.011083 | 1.5516
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3275 | 147 | 0.011083 | 1.6292
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.8816 | 182 | 0.011083 | 2.0171
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1349 | 198 | 0.011083 | 2.1944
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015676 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037622 | 0 | 0.010926 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015676 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037622 | 0 | 0.010926 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.015564 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.062256 | 0 | 0.010814 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2016 | 142 | 0.010754 | 1.527
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2481 | 145 | 0.010754 | 1.5593
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3411 | 151 | 0.010754 | 1.6238
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.4962 | 290 | 0.010754 | 3.1186
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015463 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037111 | 0 | 0.010713 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015463 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037111 | 0 | 0.010713 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.015463 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.043296 | 0 | 0.010713 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7481 | 114 | 0.010584 | 1.2065
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.4041 | 222 | 0.010584 | 2.3496
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.8215 | 184 | 0.010584 | 1.9474
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.4348 | 224 | 0.010584 | 2.3708
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7634 | 115 | 0.010584 | 1.2171
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3932 | 223.9 | 0.010405 | 2.3296
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4099 | 225 | 0.010405 | 2.3411
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4038 | 224.6 | 0.010405 | 2.3369
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4356 | 226.7 | 0.010405 | 2.3588
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.014764 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.088584 | 0 | 0.010014 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.014715 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3716 | 433 | 0.0099648 | 4.3147
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.014699 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.5842 | 584 | 0.0099488 | 5.8101
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.014699 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.7459 | 595 | 0.0099488 | 5.9195
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.01457 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0098198 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.014362 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.086172 | 0 | 0.0096118 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7077 | 50 | 0.0094038 | 0.47019
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7077 | 50 | 0.0094038 | 0.47019
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7077 | 50 | 0.0094038 | 0.47019
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7077 | 50 | 0.0094038 | 0.47019
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.013843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1872 | 158 | 0.0090928 | 1.4367
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.013843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2149 | 160 | 0.0090928 | 1.4548
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.013843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4225 | 175 | 0.0090928 | 1.5912
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.013804 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1051 | 152.5 | 0.0090538 | 1.3807
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.013804 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0637 | 149.5 | 0.0090538 | 1.3535
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.013804 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2108 | 232.6 | 0.0090538 | 2.1059
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.013579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7924 | 132 | 0.0088288 | 1.1654
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.013579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8196 | 134 | 0.0088288 | 1.1831
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.013579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.386 | 323 | 0.0088288 | 2.8517
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.013469 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.44448 | 0 | 0.0087188 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.013469 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.33672 | 0 | 0.0087188 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.013469 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0087188 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6567 | 49 | 0.0086518 | 0.42394
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.61649 | 46 | 0.0086518 | 0.39798
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.61649 | 46 | 0.0086518 | 0.39798
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.62989 | 47 | 0.0086518 | 0.40663
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.013402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0639 | 154 | 0.0086518 | 1.3324
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.013402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.9835 | 148 | 0.0086518 | 1.2805
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6433 | 48 | 0.0086518 | 0.41528
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6433 | 48 | 0.0086518 | 0.41528
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.013273 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10618 | 0 | 0.0085228 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.013273 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10618 | 0 | 0.0085228 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.01327 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.1137 | 310 | 0.0085198 | 2.6411
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.01327 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.4805 | 413 | 0.0085198 | 3.5187
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.55322 | 42 | 0.0084218 | 0.35371
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.57957 | 44 | 0.0084218 | 0.37056
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.57957 | 44 | 0.0084218 | 0.37056
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.61908 | 47 | 0.0084218 | 0.39582
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.013159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46057 | 0 | 0.0084088 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.013159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.44741 | 0 | 0.0084088 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.013159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46057 | 0 | 0.0084088 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.013017 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23431 | 0 | 0.0082668 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.013017 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23431 | 0 | 0.0082668 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.012954 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.4666 | 422 | 0.0082038 | 3.462
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.012926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.36193 | 0 | 0.0081758 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.012926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37485 | 0 | 0.0081758 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.012503 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.17129 | 0 | 0.0077528 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.0124 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2232 | 0 | 0.0076498 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.0124 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2232 | 0 | 0.0076498 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.0124 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.186 | 0 | 0.0076498 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.011096 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3136 | 569 | 0.0063458 | 3.6107
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.011096 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.4468 | 581 | 0.0063458 | 3.6869
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0047502 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0047502 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9555 | 0 | -0.024247 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8113 | 0 | -0.024247 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0023 | 0 | -0.024247 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9887 | 0 | -0.024247 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.0195 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.624 | 0 | -0.02425 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.0195 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.585 | 0 | -0.02425 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3875 | 0 | -0.024347 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3071 | 0 | -0.024347 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0386 | 0 | -0.024347 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0023 | 0 | -0.024347 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0081 | 0 | -0.024347 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.9846 | 0 | -0.024347 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8813 | 0 | -0.024347 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7817 | 0 | -0.024347 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78388 | 0 | -0.024347 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3116 | 56 | -0.028171 | -1.5776
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3818 | 59 | -0.028171 | -1.6621
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3116 | 56 | -0.028171 | -1.5776
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3116 | 56 | -0.028171 | -1.5776
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3818 | 59 | -0.028171 | -1.6621
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3116 | 56 | -0.028171 | -1.5776
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.024557 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.029307 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8333 | 104 | -0.031993 | -3.3273
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8333 | 104 | -0.031993 | -3.3273
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4711 | 54 | -0.031993 | -1.7276
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4439 | 53 | -0.031993 | -1.6956
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4711 | 54 | -0.031993 | -1.7276
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5529 | 57 | -0.031993 | -1.8236
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4711 | 54 | -0.031993 | -1.7276
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4711 | 54 | -0.031993 | -1.7276
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5801 | 58 | -0.031993 | -1.8556
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5801 | 58 | -0.031993 | -1.8556
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7559 | 0 | -0.035035 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.653 | 0 | -0.035035 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6348 | 0 | -0.035035 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6505 | 0 | -0.035035 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36948 | 0 | -0.035035 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.8085 | 0 | -0.040341 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.5913 | 0 | -0.040341 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.6056 | 0 | -0.040341 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.5878 | 0 | -0.040341 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.574 | 0 | -0.040341 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4118 | 0 | -0.041855 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2263 | 0 | -0.041855 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4118 | 0 | -0.041855 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4118 | 0 | -0.041855 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.041987 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.50384 | 12 | -0.046737 | -0.56085
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.045533 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5516 | 0 | -0.050283 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.045533 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6426 | 0 | -0.050283 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.049682 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5453 | 172 | -0.054432 | -9.3623
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.049682 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5453 | 172 | -0.054432 | -9.3623
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.049682 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5453 | 172 | -0.054432 | -9.3623
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.049922 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -10.6334 | 213 | -0.054672 | -11.6452
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.050105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8117 | 0 | -0.054855 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2154 | 0 | -0.054991 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1752 | 0 | -0.054991 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1499 | 0 | -0.054991 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6977 | 0 | -0.054991 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.050502 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.5145 | 228 | -0.055252 | -12.5975
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.05058 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5364 | 0 | -0.05533 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.05058 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2928 | 0 | -0.05533 | 0
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2628 | 0 | -0.055504 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1917 | 0 | -0.055504 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0648 | 0 | -0.055504 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.663 | 0 | -0.055504 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.051205 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.2169 | 0 | -0.055955 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.051205 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.1211 | 0 | -0.055955 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.051205 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0392 | 0 | -0.055955 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6658 | 0 | -0.056381 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7174 | 0 | -0.056381 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0136 | 0 | -0.056381 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5489 | 0 | -0.056381 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.052 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.58 | 165 | -0.05675 | -9.3638
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.052466 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.8668 | 169 | -0.057216 | -9.6695
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2042 | 42 | -0.057231 | -2.4037
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2042 | 42 | -0.057231 | -2.4037
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9943 | 38 | -0.057231 | -2.1748
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9943 | 38 | -0.057231 | -2.1748
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.052878 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.63454 | 12 | -0.057628 | -0.69154
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.052878 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.057628 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.054433 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -40.0083 | 735 | -0.059183 | -43.4997
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.056324 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -41.8487 | 743 | -0.061074 | -45.3782
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1084 | 0 | -0.066761 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1518 | 0 | -0.066761 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0278 | 0 | -0.066761 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8463 | 0 | -0.066761 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0976 | 0 | -0.066761 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.265 | 0 | -0.066761 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.234 | 0 | -0.066761 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1704 | 0 | -0.066761 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1162 | 0 | -0.066761 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2957 | 0 | -0.066761 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.1776 | 0 | -0.066761 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.062431 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.74917 | 12 | -0.067181 | -0.80617
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6308 | 0 | -0.07198 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.4879 | 0 | -0.07198 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3534 | 0 | -0.07198 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3534 | 0 | -0.07198 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.06723 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.8913 | 0 | -0.07198 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.068018 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34009 | 0 | -0.072768 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.068018 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4284 | 0 | -0.072768 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.073823 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5838 | 0 | -0.078573 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.822 | 0 | -0.094319 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9116 | 0 | -0.094319 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2698 | 0 | -0.094319 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6428 | 0 | -0.094319 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5533 | 0 | -0.094319 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3152 | 0 | -0.094319 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2846 | 0 | -0.094319 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.092748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.5614 | 0 | -0.097498 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.10764 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -42.8395 | 398 | -0.11239 | -44.7301
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3064 | 46 | -0.18532 | -8.5249
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3064 | 46 | -0.18532 | -8.5249
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3064 | 46 | -0.18532 | -8.5249
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.9315 | 55 | -0.18532 | -10.1928
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.9315 | 55 | -0.18532 | -10.1928
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.7509 | 54 | -0.18532 | -10.0075
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.18383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -31.8019 | 0 | -0.18858 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.18383 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.8165 | 0 | -0.18858 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.19038 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.8915 | 0 | -0.19513 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:Garrot - Midtown 138kV 47660-47705 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45972 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.19038 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.8915 | 0 | -0.19513 | 0 | 0 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.18383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -31.8019 | 0 | -0.18858 | 0 | 0 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.18383 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.8165 | 0 | -0.18858 | 0 | 0 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3064 | 46 | -0.18532 | -8.5249 | 46 | 8.5249 | Weighted Shift Factors
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3064 | 46 | -0.18532 | -8.5249 | 92 | 17.0497 | North | 0.0047502
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3064 | 46 | -0.18532 | -8.5249 | 138 | 25.5746 | Houston | -0.027666
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.9315 | 55 | -0.18532 | -10.1928 | 193 | 35.7674 |  | 0.032416
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.9315 | 55 | -0.18532 | -10.1928 | 248 | 45.9602
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.18057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.7509 | 54 | -0.18532 | -10.0075 | 302 | 55.9676 | Line Rating | 247
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.10764 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -42.8395 | 398 | -0.11239 | -44.7301 |  |  | Conc Gen | 302
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.092748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.5614 | 0 | -0.097498 | 0 |  |  | Weighted Imp. | 55.9676
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.822 | 0 | -0.094319 | 0 |  |  | PTDF | 0.18532
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9116 | 0 | -0.094319 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2698 | 0 | -0.094319 | 0 |  |  | Concentration | 5.717
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6428 | 0 | -0.094319 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5533 | 0 | -0.094319 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3152 | 0 | -0.094319 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.089569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2846 | 0 | -0.094319 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.073823 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5838 | 0 | -0.078573 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.068018 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34009 | 0 | -0.072768 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.068018 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4284 | 0 | -0.072768 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6308 | 0 | -0.07198 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.4879 | 0 | -0.07198 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3534 | 0 | -0.07198 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.06723 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3534 | 0 | -0.07198 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.06723 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.8913 | 0 | -0.07198 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.062431 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.74917 | 0 | -0.067181 | 0
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1084 | 0 | -0.066761 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1518 | 0 | -0.066761 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0278 | 0 | -0.066761 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8463 | 0 | -0.066761 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0976 | 0 | -0.066761 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.265 | 0 | -0.066761 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.234 | 0 | -0.066761 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1704 | 0 | -0.066761 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1162 | 0 | -0.066761 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2957 | 0 | -0.066761 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.062011 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.1776 | 0 | -0.066761 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.056324 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -41.8487 | 743 | -0.061074 | -45.3782
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.054433 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -40.0083 | 735 | -0.059183 | -43.4997
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.052878 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.63454 | 12 | -0.057628 | -0.69154
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.052878 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.057628 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2042 | 42 | -0.057231 | -2.4037
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2042 | 42 | -0.057231 | -2.4037
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9943 | 38 | -0.057231 | -2.1748
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.052481 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9943 | 38 | -0.057231 | -2.1748
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.052466 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.8668 | 169 | -0.057216 | -9.6695
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.052 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.58 | 165 | -0.05675 | -9.3638
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6658 | 0 | -0.056381 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7174 | 0 | -0.056381 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0136 | 0 | -0.056381 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.051631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5489 | 0 | -0.056381 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.051205 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.2169 | 0 | -0.055955 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.051205 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.1211 | 0 | -0.055955 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.051205 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0392 | 0 | -0.055955 | 0
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2628 | 0 | -0.055504 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1917 | 0 | -0.055504 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0648 | 0 | -0.055504 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.050754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.663 | 0 | -0.055504 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.05058 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5364 | 0 | -0.05533 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.05058 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2928 | 0 | -0.05533 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.050502 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.5145 | 228 | -0.055252 | -12.5975
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2154 | 0 | -0.054991 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1752 | 0 | -0.054991 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1499 | 0 | -0.054991 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.050241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6977 | 0 | -0.054991 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.050105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8117 | 0 | -0.054855 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.049922 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -10.6334 | 213 | -0.054672 | -11.6452
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.049682 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5453 | 172 | -0.054432 | -9.3623
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.049682 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5453 | 172 | -0.054432 | -9.3623
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.049682 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5453 | 172 | -0.054432 | -9.3623
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.045533 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5516 | 0 | -0.050283 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.045533 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6426 | 0 | -0.050283 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.041987 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.50384 | 12 | -0.046737 | -0.56085
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4118 | 0 | -0.041855 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2263 | 0 | -0.041855 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4118 | 0 | -0.041855 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.037105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4118 | 0 | -0.041855 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.8085 | 0 | -0.040341 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.5913 | 0 | -0.040341 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.6056 | 0 | -0.040341 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.5878 | 0 | -0.040341 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.035591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.574 | 0 | -0.040341 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7559 | 0 | -0.035035 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.653 | 0 | -0.035035 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6348 | 0 | -0.035035 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6505 | 0 | -0.035035 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.030285 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36948 | 0 | -0.035035 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8333 | 104 | -0.031993 | -3.3273
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8333 | 104 | -0.031993 | -3.3273
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4711 | 54 | -0.031993 | -1.7276
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4439 | 53 | -0.031993 | -1.6956
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4711 | 54 | -0.031993 | -1.7276
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5529 | 57 | -0.031993 | -1.8236
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4711 | 54 | -0.031993 | -1.7276
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4711 | 54 | -0.031993 | -1.7276
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5801 | 58 | -0.031993 | -1.8556
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.027243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5801 | 58 | -0.031993 | -1.8556
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.024557 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.029307 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3116 | 56 | -0.028171 | -1.5776
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3818 | 59 | -0.028171 | -1.6621
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3116 | 56 | -0.028171 | -1.5776
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3116 | 56 | -0.028171 | -1.5776
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3818 | 59 | -0.028171 | -1.6621
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.023421 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3116 | 56 | -0.028171 | -1.5776
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3875 | 0 | -0.024347 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3071 | 0 | -0.024347 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0386 | 0 | -0.024347 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0023 | 0 | -0.024347 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0081 | 0 | -0.024347 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.9846 | 0 | -0.024347 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8813 | 0 | -0.024347 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.019597 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7817 | 0 | -0.024347 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.019597 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78388 | 0 | -0.024347 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.0195 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.624 | 0 | -0.02425 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.0195 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.585 | 0 | -0.02425 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9555 | 0 | -0.024247 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8113 | 0 | -0.024247 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0023 | 0 | -0.024247 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.019497 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9887 | 0 | -0.024247 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0047502 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0047502 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0047502 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.011096 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3136 | 0 | 0.0063458 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.011096 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.4468 | 0 | 0.0063458 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.0124 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2232 | 0 | 0.0076498 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.0124 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2232 | 0 | 0.0076498 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.0124 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.186 | 0 | 0.0076498 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.012503 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.17129 | 0 | 0.0077528 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.012926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.36193 | 0 | 0.0081758 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.012926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37485 | 0 | 0.0081758 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.012954 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.4666 | 422 | 0.0082038 | 3.462
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.013017 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23431 | 0 | 0.0082668 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.013017 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23431 | 0 | 0.0082668 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.013159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46057 | 0 | 0.0084088 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.013159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.44741 | 0 | 0.0084088 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.013159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46057 | 0 | 0.0084088 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.55322 | 42 | 0.0084218 | 0.35371
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.57957 | 44 | 0.0084218 | 0.37056
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.57957 | 44 | 0.0084218 | 0.37056
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.013172 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.61908 | 47 | 0.0084218 | 0.39582
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.01327 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.1137 | 310 | 0.0085198 | 2.6411
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.01327 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.4805 | 413 | 0.0085198 | 3.5187
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.013273 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10618 | 0 | 0.0085228 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.013273 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10618 | 0 | 0.0085228 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6567 | 49 | 0.0086518 | 0.42394
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.61649 | 46 | 0.0086518 | 0.39798
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.61649 | 46 | 0.0086518 | 0.39798
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.62989 | 47 | 0.0086518 | 0.40663
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.013402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0639 | 154 | 0.0086518 | 1.3324
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.013402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.9835 | 148 | 0.0086518 | 1.2805
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6433 | 48 | 0.0086518 | 0.41528
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.013402 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6433 | 48 | 0.0086518 | 0.41528
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.013469 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.44448 | 0 | 0.0087188 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.013469 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.33672 | 0 | 0.0087188 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.013469 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0087188 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.013579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7924 | 132 | 0.0088288 | 1.1654
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.013579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8196 | 134 | 0.0088288 | 1.1831
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.013579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.386 | 323 | 0.0088288 | 2.8517
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.013804 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1051 | 152.5 | 0.0090538 | 1.3807
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.013804 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0637 | 149.5 | 0.0090538 | 1.3535
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.013804 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2108 | 232.6 | 0.0090538 | 2.1059
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.013843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1872 | 158 | 0.0090928 | 1.4367
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.013843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2149 | 160 | 0.0090928 | 1.4548
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.013843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4225 | 175 | 0.0090928 | 1.5912
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7077 | 50 | 0.0094038 | 0.47019
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7077 | 50 | 0.0094038 | 0.47019
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7077 | 50 | 0.0094038 | 0.47019
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.014154 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7077 | 50 | 0.0094038 | 0.47019
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.014362 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.086172 | 0 | 0.0096118 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.01457 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0098198 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.014699 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.5842 | 0 | 0.0099488 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.014699 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.7459 | 0 | 0.0099488 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.014715 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3716 | 0 | 0.0099648 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.014764 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.088584 | 0 | 0.010014 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3932 | 223.9 | 0.010405 | 2.3296
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4099 | 225 | 0.010405 | 2.3411
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4038 | 224.6 | 0.010405 | 2.3369
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.015155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4356 | 226.7 | 0.010405 | 2.3588
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7481 | 0 | 0.010584 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.4041 | 0 | 0.010584 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.8215 | 0 | 0.010584 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.4348 | 0 | 0.010584 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7634 | 0 | 0.010584 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015463 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037111 | 0 | 0.010713 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015463 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037111 | 0 | 0.010713 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.015463 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.043296 | 0 | 0.010713 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2016 | 142 | 0.010754 | 1.527
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2481 | 145 | 0.010754 | 1.5593
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3411 | 151 | 0.010754 | 1.6238
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.015504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.4962 | 290 | 0.010754 | 3.1186
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.015564 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.062256 | 0 | 0.010814 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015676 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037622 | 0 | 0.010926 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015676 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037622 | 0 | 0.010926 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3275 | 147 | 0.011083 | 1.6292
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.185 | 138 | 0.011083 | 1.5294
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2166 | 140 | 0.011083 | 1.5516
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3275 | 147 | 0.011083 | 1.6292
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.8816 | 182 | 0.011083 | 2.0171
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.015833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1349 | 198 | 0.011083 | 2.1944
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.015954 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.7645 | 0 | 0.011204 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.015954 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.7805 | 0 | 0.011204 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.015954 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.4933 | 407 | 0.011204 | 4.5599
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.015961 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011211 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.015961 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011211 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.015961 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011211 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.015962 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.5763 | 412 | 0.011212 | 4.6192
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.015962 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.3848 | 400 | 0.011212 | 4.4847
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.015969 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.9262 | 58 | 0.011219 | 0.65069
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.015969 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.4212 | 89 | 0.011219 | 0.99847
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.70264 | 44 | 0.011219 | 0.49363
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.70264 | 44 | 0.011219 | 0.49363
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.68667 | 43 | 0.011219 | 0.48241
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.015969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.71861 | 45 | 0.011219 | 0.50484
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.015978 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.3394 | 209 | 0.011228 | 2.3466
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.015978 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.4512 | 216 | 0.011228 | 2.4252
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.73499 | 46 | 0.011228 | 0.51648
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.75097 | 47 | 0.011228 | 0.5277
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.73499 | 46 | 0.011228 | 0.51648
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.015978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.73499 | 46 | 0.011228 | 0.51648
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.016048 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4874 | 155 | 0.011298 | 1.7512
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.016048 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.7282 | 170 | 0.011298 | 1.9206
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.016048 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4874 | 155 | 0.011298 | 1.7512
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.016086 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13512 | 8.4 | 0.011336 | 0.09522
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.016122 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.8026 | 0 | 0.011372 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.016122 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 12.0915 | 0 | 0.011372 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.016201 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.38882 | 24 | 0.011451 | 0.27482
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.016201 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.38882 | 24 | 0.011451 | 0.27482
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.016201 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.37262 | 23 | 0.011451 | 0.26337
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.016473 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19768 | 0 | 0.011723 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.016625 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.5835 | 0 | 0.011875 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.016665 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6665 | 100 | 0.011915 | 1.1915
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.016665 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6665 | 100 | 0.011915 | 1.1915
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016665 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016665 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016665 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016665 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.016666 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011916 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.017141 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012391 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.017143 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56572 | 0 | 0.012393 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.017453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20944 | 0 | 0.012703 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.017453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19198 | 0 | 0.012703 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.017453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20944 | 0 | 0.012703 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.017551 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012801 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.017638 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012888 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.017779 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6046 | 146.5 | 0.013029 | 1.9087
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.017779 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6295 | 147.9 | 0.013029 | 1.927
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.017779 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0758 | 173 | 0.013029 | 2.254
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.017832 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6912 | 207 | 0.013082 | 2.7079
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.017832 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8642 | 216.7 | 0.013082 | 2.8348
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.017832 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3153 | 242 | 0.013082 | 3.1658
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.017833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.568 | 144 | 0.013083 | 1.8839
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.017833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.568 | 144 | 0.013083 | 1.8839
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.017833 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0494 | 171 | 0.013083 | 2.2372
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.017871 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013121 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.017872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.67914 | 38 | 0.013122 | 0.49863
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.017872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34493 | 19.3 | 0.013122 | 0.25325
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.017872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.26808 | 15 | 0.013122 | 0.19683
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.017872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.83998 | 47 | 0.013122 | 0.61672
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6813 | 0 | 0.013136 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.73333 | 0 | 0.013136 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.67967 | 0 | 0.013136 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.33983 | 0 | 0.013136 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6813 | 0 | 0.013136 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6439 | 0 | 0.013136 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.7691 | 0 | 0.013136 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.39349 | 0 | 0.013136 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.6471 | 0 | 0.013136 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.8943 | 0 | 0.013136 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.98373 | 0 | 0.013136 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.017886 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.8943 | 0 | 0.013136 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.017923 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.51977 | 0 | 0.013173 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.017973 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.305 | 0 | 0.013223 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.684 | 0 | 0.01325 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.018007 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.68427 | 0 | 0.013257 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.01801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.0153 | 334 | 0.01326 | 4.4288
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.01801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.1234 | 340 | 0.01326 | 4.5083
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.01801 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2418 | 180 | 0.01326 | 2.3868
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.01801 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2418 | 180 | 0.01326 | 2.3868
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.018016 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.4504 | 0 | 0.013266 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.018016 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.4504 | 0 | 0.013266 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.018035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2463 | 180 | 0.013285 | 2.3913
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.018038 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.675 | 0 | 0.013288 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.018038 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6804 | 0 | 0.013288 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.018038 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7598 | 0 | 0.013288 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.018039 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0611 | 336 | 0.013289 | 4.465
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.018039 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.247 | 180 | 0.013289 | 2.392
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 0 | 0.013356 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 0 | 0.013356 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 0 | 0.013356 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.2897 | 0 | 0.013356 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 0 | 0.013356 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 0 | 0.013356 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.45265 | 0 | 0.013356 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.018106 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.27159 | 0 | 0.013356 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.8705 | 0 | 0.013418 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7797 | 0 | 0.013418 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 1.8168 | 0 | 0.013418 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6344 | 0 | 0.013418 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6707 | 0 | 0.013418 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.018168 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.3073 | 0 | 0.013418 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.018168 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.21802 | 0 | 0.013418 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1673 | 0 | 0.014078 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3443 | 0 | 0.014078 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.84726 | 0 | 0.014078 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9016 | 0 | 0.014078 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6192 | 0 | 0.014078 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6569 | 0 | 0.014078 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.9414 | 0 | 0.014078 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3389 | 0 | 0.014078 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7698 | 0 | 0.014078 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.318 | 0 | 0.014078 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1862 | 0 | 0.014078 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3556 | 0 | 0.014078 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2201 | 0 | 0.014078 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9016 | 0 | 0.014078 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8263 | 0 | 0.014078 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9393 | 0 | 0.014078 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4309 | 0 | 0.014078 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5062 | 0 | 0.014078 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5062 | 0 | 0.014078 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.018828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.2196 | 0 | 0.014078 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.01887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.7173 | 144 | 0.01412 | 2.0332
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.01887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.5476 | 188 | 0.01412 | 2.6545
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.90382 | 47.7 | 0.014198 | 0.67723
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70676 | 37.3 | 0.014198 | 0.52958
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.87161 | 46 | 0.014198 | 0.6531
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.018948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.9095 | 48 | 0.014198 | 0.68149
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.018976 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.41747 | 22 | 0.014226 | 0.31297
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.018976 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20874 | 11 | 0.014226 | 0.15648
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.018976 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20874 | 11 | 0.014226 | 0.15648
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.01899 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.3863 | 0 | 0.01424 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.019162 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28743 | 0 | 0.014412 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.019162 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44073 | 0 | 0.014412 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.019205 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15364 | 0 | 0.014455 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.54034 | 0 | 0.014548 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13509 | 0 | 0.014548 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.75262 | 0 | 0.014548 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28947 | 0 | 0.014548 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13509 | 0 | 0.014548 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28947 | 0 | 0.014548 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.75262 | 0 | 0.014548 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.019298 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.75262 | 0 | 0.014548 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.019685 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.94488 | 0 | 0.014935 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5639 | 0 | 0.015046 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6035 | 0 | 0.015046 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5639 | 0 | 0.015046 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5837 | 0 | 0.015046 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.552 | 0 | 0.015046 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.4949 | 0 | 0.015046 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.91062 | 0 | 0.015046 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.55429 | 0 | 0.015046 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.86311 | 0 | 0.015046 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.019796 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4649 | 0 | 0.015046 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.020755 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 27.6664 | 0 | 0.016005 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.020755 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 27.5626 | 0 | 0.016005 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.021033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96962 | 0 | 0.016283 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.025604 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 16.6682 | 0 | 0.020854 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.025604 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 14.4407 | 0 | 0.020854 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.025604 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 15.3624 | 0 | 0.020854 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.02606 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2478 | 0 | 0.02131 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.02606 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2478 | 0 | 0.02131 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.02606 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.3847 | 0 | 0.02131 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2035 | 76 | 0.024244 | 1.8425
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2035 | 76 | 0.024244 | 1.8425
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.0444 | 105 | 0.024244 | 2.5456
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1456 | 74 | 0.024244 | 1.794
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1456 | 74 | 0.024244 | 1.794
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.028994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.9574 | 102 | 0.024244 | 2.4729
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.030124 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.1388 | 0 | 0.025374 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.030124 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30124 | 0 | 0.025374 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.031942 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.1082 | 66 | 0.027192 | 1.7947
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.027666 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.027666 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.1158 | 0 | 0.028417 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.11716 | 0 | 0.028417 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.11716 | 0 | 0.028417 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.000751 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.28538 | 0 | 0.028417 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.001117 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.51717 | 0 | 0.028783 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.001939 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.062048 | 0 | 0.029605 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.001963 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.033371 | 17 | 0.029629 | 0.5037
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.001963 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.002218 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.10646 | 48 | 0.029884 | 1.4344
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.002218 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.10203 | 46 | 0.029884 | 1.3747
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.002218 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.23289 | 105 | 0.029884 | 3.1378
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2717 | 0 | 0.030323 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2717 | 0 | 0.030323 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.40466 | 0 | 0.030323 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.002657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.40652 | 0 | 0.030323 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.00326 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.696 | 0 | 0.030926 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.00326 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6699 | 0 | 0.030926 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.00419 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.5768 | 0 | 0.031856 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.00419 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4595 | 0 | 0.031856 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.00427 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64349 | 150.7 | 0.031936 | 4.8128
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.00427 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64477 | 151 | 0.031936 | 4.8224
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.00427 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7575 | 177.4 | 0.031936 | 5.6655
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.004285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64918 | 151.5 | 0.031951 | 4.8406
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.004285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.65261 | 152.3 | 0.031951 | 4.8662
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.004285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76059 | 177.5 | 0.031951 | 5.6713
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.004624 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.84157 | 182 | 0.03229 | 5.8768
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.004624 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.238 | 484 | 0.03229 | 15.6284
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.004628 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.2314 | 0 | 0.032294 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.004632 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.032298 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.68983 | 0 | 0.032327 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.60593 | 0 | 0.032327 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.67585 | 0 | 0.032327 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.004661 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.8597 | 0 | 0.032327 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.004695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.6856 | 0 | 0.032361 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.004695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.7325 | 0 | 0.032361 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.004695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.6621 | 0 | 0.032361 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.004913 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.1005 | 224 | 0.032579 | 7.2977
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79292 | 161 | 0.032591 | 5.2472
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.8077 | 164 | 0.032591 | 5.345
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.8077 | 164 | 0.032591 | 5.345
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0389 | 414 | 0.032591 | 13.4927
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79785 | 162 | 0.032591 | 5.2798
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79292 | 161 | 0.032591 | 5.2472
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.80278 | 163 | 0.032591 | 5.3124
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.004925 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0143 | 409 | 0.032591 | 13.3298
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.004976 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.9307 | 388 | 0.032642 | 12.6652
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.004976 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.5626 | 515 | 0.032642 | 16.8107
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.004985 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.0997 | 20 | 0.032651 | 0.65302
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.004985 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.12462 | 25 | 0.032651 | 0.81628
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.004985 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.20439 | 41 | 0.032651 | 1.3387
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004991 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032657 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004991 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032657 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.3946 | 79 | 0.032661 | 2.5802
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.52947 | 106 | 0.032661 | 3.4621
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.72927 | 146 | 0.032661 | 4.7685
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.004995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.37962 | 76 | 0.032661 | 2.4822
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.004995 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1998 | 40 | 0.032661 | 1.3064
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.005004 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.7922 | 0 | 0.03267 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.005004 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.8973 | 0 | 0.03267 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.005004 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.0432 | 0 | 0.03267 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.005011 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.37583 | 0 | 0.032677 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.005011 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.39888 | 0 | 0.032677 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.005011 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.44297 | 0 | 0.032677 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.8024 | 160 | 0.032681 | 5.229
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.78234 | 156 | 0.032681 | 5.0983
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.98294 | 196 | 0.032681 | 6.4055
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.78234 | 156 | 0.032681 | 5.0983
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.78736 | 157 | 0.032681 | 5.1309
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.005015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.99297 | 198 | 0.032681 | 6.4709
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.005022 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.8581 | 370 | 0.032688 | 12.0946
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.70308 | 0 | 0.032688 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.7081 | 0 | 0.032688 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5518 | 0 | 0.032688 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.71815 | 0 | 0.032688 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.72317 | 0 | 0.032688 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.005022 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5568 | 0 | 0.032688 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.005037 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.85629 | 170 | 0.032703 | 5.5595
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.005037 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.6192 | 520 | 0.032703 | 17.0056
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.005049 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20196 | 0 | 0.032715 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.005049 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20196 | 0 | 0.032715 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.005064 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.59755 | 118 | 0.03273 | 3.8622
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.005064 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.58236 | 115 | 0.03273 | 3.764
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.005064 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.8156 | 556 | 0.03273 | 18.198
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.005067 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032733 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.005084 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.03275 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.005128 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0051 | 196 | 0.032794 | 6.4277
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.005128 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.56921 | 111 | 0.032794 | 3.6402
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.005206 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.31236 | 60 | 0.032872 | 1.9723
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.005206 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.32798 | 63 | 0.032872 | 2.0709
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.005281 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.2972 | 435 | 0.032947 | 14.332
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.005287 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.59479 | 0 | 0.032953 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.005297 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0923 | 395 | 0.032963 | 13.0205
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.005297 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3042 | 435 | 0.032963 | 14.339
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.005308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1487 | 216.4 | 0.032974 | 7.1356
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.005308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1471 | 216.1 | 0.032974 | 7.1257
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.005315 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.005315 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.005315 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2067 | 224 | 0.033053 | 7.4039
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2175 | 226 | 0.033053 | 7.47
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.142 | 212 | 0.033053 | 7.0073
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.005387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1367 | 211 | 0.033053 | 6.9742
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.005394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.5535 | 288 | 0.03306 | 9.5213
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.005394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79292 | 147 | 0.03306 | 4.8598
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.005394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.79292 | 147 | 0.03306 | 4.8598
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.005424 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.03309 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.005439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1096 | 204 | 0.033105 | 6.7535
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.005439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0932 | 201 | 0.033105 | 6.6541
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.005439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3162 | 242 | 0.033105 | 8.0115
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.005442 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1825 | 217.3 | 0.033108 | 7.1944
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.005442 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1156 | 205 | 0.033108 | 6.7872
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.005442 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4824 | 272.4 | 0.033108 | 9.0187
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.005461 | north | 3 | N | N | Nnorth | Nnorth | 1 | 6.3184 | 0 | 0.033127 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.005461 | north | 3 | N | N | Nnorth | Nnorth | 1 | 6.3238 | 0 | 0.033127 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.005483 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.098694 | 18 | 0.033149 | 0.59669
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.005483 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.098694 | 18 | 0.033149 | 0.59669
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.005483 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.20835 | 38 | 0.033149 | 1.2597
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38682 | 70 | 0.033192 | 2.3235
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38129 | 69 | 0.033192 | 2.2903
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38129 | 69 | 0.033192 | 2.2903
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.005526 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.37577 | 68 | 0.033192 | 2.2571
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.11096 | 20 | 0.033214 | 0.66428
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.11096 | 20 | 0.033214 | 0.66428
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.11096 | 20 | 0.033214 | 0.66428
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.005548 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.094316 | 17 | 0.033214 | 0.56464
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.00555 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.0666 | 0 | 0.033216 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.00555 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.0666 | 0 | 0.033216 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.005556 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0335 | 366 | 0.033222 | 12.1593
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.00556 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.6672 | 0 | 0.033226 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.005575 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9366 | 168 | 0.033241 | 5.5845
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.005575 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.50175 | 90 | 0.033241 | 2.9917
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.0056 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.3552 | 242 | 0.033266 | 8.0504
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.005626 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.4107 | 73 | 0.033292 | 2.4303
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.005626 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.66949 | 119 | 0.033292 | 3.9618
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.005626 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.1533 | 205 | 0.033292 | 6.8249
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.005626 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.57385 | 102 | 0.033292 | 3.3958
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.005626 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5401 | 96 | 0.033292 | 3.196
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.005661 | west | 4 | Y | N | Ywest | Nwest | 1 | 3.678 | 0 | 0.033327 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9405 | 0 | 0.033366 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.005745 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3558 | 0 | 0.033411 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.005746 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2984 | 0 | 0.033412 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.005823 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34938 | 0 | 0.033489 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.005866 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.35196 | 0 | 0.033532 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.005878 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8817 | 0 | 0.033544 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2289 | 0 | 0.033546 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.74382 | 0 | 0.033546 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.4641 | 0 | 0.033546 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.00588 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1584 | 0 | 0.033546 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.22073 | 0 | 0.033552 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.63275 | 0 | 0.033552 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.79461 | 0 | 0.033552 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.70043 | 0 | 0.033552 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.61803 | 0 | 0.033552 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.005886 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.47382 | 0 | 0.033552 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005907 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.73838 | 0 | 0.033573 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005907 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.73838 | 0 | 0.033573 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.005915 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.88725 | 0 | 0.033581 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.005915 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.59742 | 0 | 0.033581 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.00592 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49728 | 0 | 0.033586 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.00593 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.58707 | 0 | 0.033596 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.00593 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.36173 | 0 | 0.033596 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.00593 | west | 7 | N | N | Nwest | Nwest | 1 | 0.14825 | 0 | 0.033596 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.00593 | west | 7 | N | N | Nwest | Nwest | 1 | 0.271 | 0 | 0.033596 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.00593 | west | 7 | N | N | Nwest | Nwest | 1 | 0.271 | 0 | 0.033596 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.005931 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.83627 | 0 | 0.033597 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.005931 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.71172 | 0 | 0.033597 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.005934 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.37384 | 0 | 0.0336 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39184 | 66 | 0.033603 | 2.2178
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40965 | 69 | 0.033603 | 2.3186
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40965 | 69 | 0.033603 | 2.3186
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39778 | 67 | 0.033603 | 2.2514
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39778 | 67 | 0.033603 | 2.2514
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.005937 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.3859 | 65 | 0.033603 | 2.1842
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8919 | 0 | 0.033612 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3081 | 0 | 0.033612 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1892 | 0 | 0.033612 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.72482 | 0 | 0.033612 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.005957 | west | 8 | N | N | Nwest | Nwest | 1 | 0.41699 | 0 | 0.033623 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.005957 | west | 8 | N | N | Nwest | Nwest | 1 | 0.43724 | 0 | 0.033623 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.005957 | west | 8 | N | N | Nwest | Nwest | 1 | 0.41937 | 0 | 0.033623 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005958 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0724 | 0 | 0.033624 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005958 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0724 | 0 | 0.033624 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.005961 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.71532 | 0 | 0.033627 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.005961 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3889 | 0 | 0.033627 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.005961 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0146 | 0 | 0.033627 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.005962 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3415 | 0 | 0.033628 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.005969 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.71628 | 0 | 0.033635 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.00597 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.7164 | 0 | 0.033636 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.005993 | west | 8 | N | N | Nwest | Nwest | 1 | 0.15462 | 0 | 0.033659 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.005997 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2846 | 0 | 0.033663 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.006006 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9009 | 0 | 0.033672 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.006006 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6036 | 0 | 0.033672 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.006007 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34841 | 0 | 0.033673 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.42063 | 70 | 0.033675 | 2.3573
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.42063 | 70 | 0.033675 | 2.3573
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.55764 | 92.8 | 0.033675 | 3.1251
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.48072 | 80 | 0.033675 | 2.694
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.48072 | 80 | 0.033675 | 2.694
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.006009 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.69103 | 115 | 0.033675 | 3.8726
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2513 | 208.2 | 0.033676 | 7.0114
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.85402 | 142.1 | 0.033676 | 4.7854
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79572 | 132.4 | 0.033676 | 4.4587
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.81736 | 136 | 0.033676 | 4.58
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.88347 | 147 | 0.033676 | 4.9504
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.00601 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2621 | 210 | 0.033676 | 7.072
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67748 | 0 | 0.033688 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.90029 | 0 | 0.033688 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1201 | 0 | 0.033688 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.006022 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2917 | 0 | 0.033688 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.006044 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.03989 | 0 | 0.03371 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.006044 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20731 | 0 | 0.03371 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.006067 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.90398 | 0 | 0.033733 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.006069 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0287 | 0 | 0.033735 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.006079 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.21277 | 0 | 0.033745 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.006079 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.18237 | 0 | 0.033745 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40148 | 66 | 0.033749 | 2.2274
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39539 | 65 | 0.033749 | 2.1937
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40756 | 67 | 0.033749 | 2.2612
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40756 | 67 | 0.033749 | 2.2612
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.006083 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.40756 | 67 | 0.033749 | 2.2612
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.006083 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033749 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.006083 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033749 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.006351 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.030485 | 0 | 0.034017 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006462 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51696 | 0 | 0.034128 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006462 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51696 | 0 | 0.034128 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.006492 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.4869 | 0 | 0.034158 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006492 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51936 | 0 | 0.034158 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.006492 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.25968 | 0 | 0.034158 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006498 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51984 | 0 | 0.034164 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.006499 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51992 | 0 | 0.034165 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.006503 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.97545 | 0 | 0.034169 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.006503 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.97545 | 0 | 0.034169 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.006601 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.099015 | 0 | 0.034267 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.006601 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.099015 | 0 | 0.034267 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006653 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.53224 | 0 | 0.034319 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.006678 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51087 | 0 | 0.034344 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.006703 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.56305 | 0 | 0.034369 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.006861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0292 | 150 | 0.034527 | 5.1791
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.006861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.54888 | 80 | 0.034527 | 2.7622
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.006974 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7784 | 255 | 0.03464 | 8.8332
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.006974 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0391 | 149 | 0.03464 | 5.1614
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.006974 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.067 | 153 | 0.03464 | 5.2999
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.007104 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.03477 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.007104 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.5908 | 787 | 0.03477 | 27.3641
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.007191 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034857 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.007191 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034857 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.007508 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.035174 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.008063 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2094 | 0 | 0.035729 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.637 | 0 | 0.037025 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.637 | 0 | 0.037025 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.9712 | 0 | 0.037025 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.041775 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.5744 | 0 | 0.037025 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.011508 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.039174 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.015334 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 1.5334 | 0 | 0.043 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.0673 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 10.8353 | 161 | 0.06255 | 10.0705
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.0673 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 11.1718 | 166 | 0.06255 | 10.3833
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.0673 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 16.6904 | 248 | 0.06255 | 15.5123
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.0673 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 36.7458 | 546 | 0.06255 | 34.1522
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.0673 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 43.2739 | 0 | 0.06255 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.0673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.8749 | 13 | 0.06255 | 0.81315
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.18936 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.4682 | 50 | 0.18461 | 9.2307

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 247
| 25 | 247
| 30 | 247
| 35 | 247
| 40 | 247
| 45 | 247
| 50 | 247
| 55 | 247
| 60 | 247
| 65 | 247
| 70 | 247
| 75 | 247
| 80 | 247
| 85 | 247
| 90 | 247
| 95 | 247
| 100 | 247
| 105 | 247
| 110 | 247
| 115 | 247
| Max | 247
| Min | 247
| Avg | 247