## test results
CRE test for: |  | H_O_C - Knight 138kV 47150-47331 | [5 empty] | FAIL
Line Rating: |  | 378
Direction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | H_O_C - Knight 138kV 47150-47331
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.0043659
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.015646
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.005686
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.00080781
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | H_O_C - Knight 138kV 47150-47331
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.0049149
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.015794
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.0056683
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0073444
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | H_O_C - Knight 138kV 47150-47331
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.011428
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.0013024
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.01171
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.0099773
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.016453
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.01303
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.01171 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.01171 | -0.011428
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.085663
[6 empty] | Concentration |  | 7.3152 | FAIL
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.089005
[6 empty] | Concentration |  | 7.6006 | FAIL
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 65.2325
| Percent of line rating => | [6 empty] | 17.26% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 29.3723
[7 empty] | B1(N-S) | 0.56402 | 0.22835 | -0.33567 | 0.56402
[7 empty] | B2 (N-W) | 0.064386 | 0.026133 | -0.038254 | 0.064386
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.49234 | -0.19929 | 0.29305 | -0.49234
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.36474 | 0.11854 | 0.48327 | -0.36474
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.065262 | 0.31747 | 0.38273 | -0.065262
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 164%
Deployment Error Percent | [6 empty] | B2 | 18.72%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -143.1%
[7 empty] | B5 | -106%
[7 empty] | B6 | -18.97%
[7 empty] | Max Abs Error | 164% | FAIL

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-H
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:H_O_C - Knight 138kV 47150-47331 C:Bellaire - Garrot 138kV 47015-47320 & H_O_C - Garrot 138kV 47155-47660 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:H_O_C - Knight 138kV 47150-47331 C:Bellaire - Garrot 138kV 47015-47320 & H_O_C - Garrot 138kV 47155-47660
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.006761 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 1.7241
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.006761 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.0074
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.006358 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.09537
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.006358 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.09537
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.006761 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.0344
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.006638 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 0.9957
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.006638 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.53104
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005301 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 0.38697
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005301 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 0.63082
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005301 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 1.0867
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005301 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 0.5407
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005301 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 0.5089
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.005216 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.062592
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.005216 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.062592
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.005249 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 0.88183
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.005249 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 0.47241
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.005147 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.092646
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.005147 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.092646
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.005147 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.19559
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.005051 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 1.4547
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.005051 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 0.7425
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.005051 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 0.7425
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.004938 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 0.55553
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.18512
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 0.36561
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 0.49057
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 0.67569
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.004628 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 0.35173
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.004852 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 0.29112
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.004852 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 0.30568
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.004617 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.09234
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.004617 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.11542
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.004617 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.1893
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.000472 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 0.21854
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 0.38023
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 0.37446
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.38599
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.38599
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.38599
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005761 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 0.65675
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005761 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 2.9669
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 0.37039
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 0.38723
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 0.38723
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 0.376
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 0.376
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 0.36478
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.005633 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 0.39431
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.005633 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 0.41346
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.005633 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 0.39656
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 0.84315
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 1.2366
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005605 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 0.5549
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005605 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 0.34191
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.005606 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 0.79045
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005605 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.14012
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005605 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.25615
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005605 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.25615
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.005606 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 0.67272
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.00567 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.14629
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.005683 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 0.57114
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.005646 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 0.67752
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.005684 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 0.32967
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.005674 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 1.2154
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.005591 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 0.83865
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.005722 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.037765
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.005722 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 0.19626
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.005591 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 0.56469
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.005645 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 0.6774
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.005219 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 1.9102
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.005265 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 1.2741
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.005415 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 2.166
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.005415 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 1.2779
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.005368 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 0.88572
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.005097 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 1.0398
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.005097 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 1.0245
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.005097 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 1.2335
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.1042
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.1042
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.1042
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.08857
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.005227 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 0.62724
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.005554 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 0.33324
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.004644 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 0.3483
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.004644 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 0.36966
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.004644 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 0.41053
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 0.74384
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.72524
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 0.9112
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.72524
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 0.72989
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 0.9205
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.004672 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 0.79424
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.004672 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 2.4294
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004656 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 1.7227
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.004637 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 2.5874
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.004637 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 2.6848
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.004637 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 3.7467
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.004968 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 0.55642
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.004968 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 0.4968
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.004968 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 1.8779
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.005104 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 1.1091
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.005104 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 1.0463
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.005104 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 1.3903
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.005086 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 3.9162
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 0.36365
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.35846
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.35846
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.35326
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.005124 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 5.9285
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.005124 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 5.9336
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 1.131
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 1.1411
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.004965 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 1.0744
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.004965 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 1.0729
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 1.0704
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 1.0653
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.00495 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 1.9552
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.004933 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 2.1459
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.00495 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 2.1532
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.004723 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 0.65177
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.004702 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 0.55484
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.004702 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 0.54073
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.004702 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 2.6143
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.004607 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 1.7875
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.004607 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 2.3726
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004306 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 3.3802
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004306 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 3.4233
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004306 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 3.3587
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.004231 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 0.77004
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.004231 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 2.0478
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.004542 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 1.0174
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.004235 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.21175
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.004239 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.17804
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.003767 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 2.3167
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.003767 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 2.2112
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.006902 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 3.7064
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.006902 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 5.4319
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006997 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.52477
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006997 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 1.5533
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.011213 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 6.3802
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015807 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 3.3037
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015807 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 3.4143
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.015768 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 6.4176
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.72712
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.74293
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.72712
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.72712
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.015767 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 6.6852
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.015767 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 6.701
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.01579 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.91582
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.01579 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 1.4053
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.69476
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.69476
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.67897
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.71055
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.015786 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 6.5038
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.015786 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 6.3144
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.015917 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 8.6907
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.015917 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 11.9377
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.015773 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.96215
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.015773 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 1.4984
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.015773 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 2.3817
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.01585 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 2.4567
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.01585 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 2.6945
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.01585 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 2.4567
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.019255 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.42361
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.019255 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.2118
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.019255 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.2118
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.91846
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.71821
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.88573
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.92424
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.017101 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.20521
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.017101 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.18811
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.015992 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.38381
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.015992 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.38381
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.015992 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.36782
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.016365 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 6.4805
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.018783 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 25.0377
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.018783 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 24.9438
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017482 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.66432
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017482 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.3374
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017482 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.26223
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017482 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.82165
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.006177 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 0.46327
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.005552 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 0.8328
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.00575 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 0.97462
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.007791 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 1.1686
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.005609 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 0.35337
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.005328 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 3.4616
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.004685 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.1874
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.004685 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.1874
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.013048 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 5.5063
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.014258 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 1.8821
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.014258 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 1.9106
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.014258 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 4.6053
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.014258 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 2.2528
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.014258 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 2.2813
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.014258 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 2.4952
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.015415 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 9.0024
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.015415 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 9.1719
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.01542 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 6.6769
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 3.3894
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 3.4061
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 3.4
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 3.4318
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.013525 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.1082
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.013525 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.1082
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.012494 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.22489
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.012494 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.22489
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.012494 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.18741
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.012591 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.1725
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.013143 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.23657
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.013143 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.23657
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.013358 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.46753
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.013358 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.45417
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.013358 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.46753
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.013026 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.36473
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.013026 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.37775
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.005757 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 0.2015
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.005757 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 0.17271
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.7761
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.7761
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.7761
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.7761
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.014824 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.088944
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.015533 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.037279
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.015533 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.037279
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.015533 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.043492
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.015471 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.061884
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.015998 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.038395
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.015998 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.038395
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 2.3005
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 2.1597
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 2.191
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 2.3005
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 2.8483
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 3.0987
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.014068 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 2.1454
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.014068 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 2.1032
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.014068 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 3.2722
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 2.1871
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 2.2333
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 2.3257
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 4.4666
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.013227 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.43649
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.013227 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.33067
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.017101 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.20521
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.019346 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 1.4123
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.5942
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 1.6346
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.54905
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.13726
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.5942
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 1.6144
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 1.5821
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.5045
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.92828
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.017987 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 11.3138
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.019237 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 2.7701
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.019237 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 3.6166
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.016895 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.20274
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.014123 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.084738
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.01767 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 5.9371
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.017638 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 5.8911
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.017638 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 5.9969
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.017654 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.67085
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.017658 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.44145
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.017658 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.44145
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.017636 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.67017
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.017543 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.50875
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.017669 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 2.6203
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.017669 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 2.6256
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.017669 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 2.7034
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 2.8129
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 2.7239
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 1.7803
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 2.5814
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 2.617
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 2.261
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.017398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 2.5488
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.017398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 2.5732
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.017398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 3.0099
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.017446 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 3.6113
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.017446 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 3.7805
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.017446 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 4.2219
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.017447 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 2.5124
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.017447 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 2.5124
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.017447 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 2.9834
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.01354 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 4.1974
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.01354 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 5.592
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.56566
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.59259
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.59259
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.633
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.66954
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.62854
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.62854
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.64221
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013664 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 2.1043
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013664 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 2.0223
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.65587
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.65587
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 0.39802
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 0.39802
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 0.52766
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 0.45488
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 0.45488
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 0.65389
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 1.184
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 0.80812
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 0.75296
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 0.77343
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 0.83599
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 1.1943
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 1.1606
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 0.70245
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 1.3827
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 1.0939
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 1.1242
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 0.6852
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.005745 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 0.85601
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 1.0141
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 1.0141
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.005638 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 1.2686
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.005581 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 0.69763
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.005581 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 0.69763
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 0.65184
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 0.6565
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 1.4387
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 0.66581
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 0.67046
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 1.4434
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.004772 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 0.93531
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.004772 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 0.52969
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.004704 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.73303
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.74669
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.74669
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 1.8849
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 0.73759
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.73303
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 0.74214
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 1.8622
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.004624 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.004624 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 0.63211
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 0.55523
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 0.6193
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 1.7041
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.003852 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 0.5805
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.003852 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 0.58165
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.003852 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 0.68334
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.003868 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 0.586
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.003868 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 0.5891
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.003868 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 0.68657
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.011213 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 6.5148
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 1.816
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 1.816
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.001354 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.043328
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001654 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.079392
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001654 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.076084
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.016572
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.070431
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001381 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.023477
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.030382
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.034525
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001654 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.17367
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.005595 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 0.46998
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.006185 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 0.4948
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.006189 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 0.92835
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.006189 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 0.92835
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -3.1619
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -2.9788
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -2.3669
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -6.8418
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -6.8552
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -6.8016
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -4.2873
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -10.8968
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.7864
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -4.4625
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -4.1333
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -4.5693
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -4.5382
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.044497 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -1.4239
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.044497 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -1.3349
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 5.6339
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 5.6339
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 6.04
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 5.5578
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 0.32349
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 0.32497
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.074624 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -10.1489
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.002243 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.074019
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -2.2974
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -2.2974
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -2.0786
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -2.0786
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.032814 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 2.3298
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.032814 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.32814
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.022768 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 3.7112
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.022768 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 3.7112
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.022768 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 5.5782
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -3.4816
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -3.2138
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -3.4816
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -3.4816
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.064213 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -9.5677
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.064213 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -4.1803
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -5.0956
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -4.9052
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -4.8717
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -3.0518
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.68315
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.031172 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -23.1608
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.039014 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -28.6753
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.026854 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.6189
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.026854 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.6189
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.026854 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.6189
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -4.1515
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.072883 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -12.6088
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.072883 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -9.8392
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -4.245
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -4.2085
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -4.1433
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -7.0194
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -3.7117
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -3.6653
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -4.7905
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -4.2685
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -4.3907
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -4.2266
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -4.2374
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -4.2239
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -7.2372
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.03515 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.17575
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.03515 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.73815
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -0.21788
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.22043
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.22043
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -0.53694
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.042987 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -17.1088
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -2.7026
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -2.7026
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -2.7026
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -3.2314
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -3.2314
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -3.1727
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.002771 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 2.2916
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.002771 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 2.2694
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.009882 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.45556
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 2.6909
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 2.6909
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 3.7177
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 2.6201
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 2.6201
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 3.6115
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.068536 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -12.3365
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.068536 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -10.8698
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.068536 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -10.7602
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.061627 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -2.1569
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.048372 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -22.2027
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -2.9058
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -2.9505
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -3.1294
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -2.8164
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -2.7717
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -4.6493
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -2.6376
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -3.7435
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -3.6955
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -3.6955
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.023997 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -3.8875
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.044403 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -6.9713
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -4.3687
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -4.4302
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -2.3997
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -1.8459
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.05407 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -4.2175
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.05407 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -4.3256
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.056902 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.92181
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.05694 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -9.3951
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.056731 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -9.5875
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.055425 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -11.8055
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.060103 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -13.7035
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.056942 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.6833
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.056942 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -1.025
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.35953 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -17.9763
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.40425
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.40425
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.2099
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.20601
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.2099
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.22156
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.2099
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.2099
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.22545
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.22545
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -7.8e-05 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.000936
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.056448
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.059472
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.056448
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.056448
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.059472
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.056448
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.038104 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 2.5149
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.090029 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 14.4947
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.090029 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 14.9448
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.090029 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 22.3272
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.090029 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 49.1558
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.090029 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 57.8886
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.022463 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 14.6234
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.022463 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 12.6691
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.022463 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 13.4778
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.090029 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 1.1704
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.03325 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.399
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -1.3099
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -1.3369
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -1.2598
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -1.7683
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.68191
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.78593
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.76667
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -1.3484
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.69347
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -3.2901
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -5.7018
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.98865
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 1.1385
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.71757
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.6105
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 1.3714
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 1.4032
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.7973
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.28703
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 1.4989
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 1.1162
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 1.0046
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 1.1481
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 1.0333
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.6105
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 1.5468
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 1.6424
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 1.2119
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 1.2757
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 1.2757
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 2.7268
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13332
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.006366 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 0.487
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.006177 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 0.49416
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.006177 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 0.24708
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.006147 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 0.49176
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.006184 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 0.49472
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.006341 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 0.50728
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.006392 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 0.53693
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.006147 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 0.49176
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 1.7374
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.005639 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 0.67668
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.005639 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 1.3139
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.005639 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 0.95976
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 3.3833
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 2.8042
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 3.4138
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 1.7526
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 1.524
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.005496 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 0.32976
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.011423 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.007212 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.006034 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.028963
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 0.2085
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 0.5977
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 0.7506
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 0.66164
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 0.5838
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 0.44758
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.005685 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 0.85275
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 0.64136
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 0.8523
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 1.0604
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 1.2229
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.017482 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.014331 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.56504
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.87985
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 1.4933
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 1.6445
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.7173
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.66481
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.33241
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 1.6445
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.62982
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.75228
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.38489
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.76475
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.29413
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.13726
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.29413
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.76475
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.76475
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 2.5893
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.87475
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.96222
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.87475
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017803 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.21364
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.019464 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.29196
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.019464 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.44767
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.020056 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.96269
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.019468 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.15574
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.017667 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 3.1801
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.01767 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 3.1806
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.017638 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 3.1748
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.017638 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 3.1748
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016388 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 1.6388
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016388 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 1.6388
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4432
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4432
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4432
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.28365
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4432
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4432
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4432
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.26592
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016388 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016388 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 8.194
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016388 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 8.194
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016388 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.017425 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.013227 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.016818 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.01729 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:H_O_C - Knight 138kV 47150-47331 C:Bellaire - Garrot 138kV 47015-47320 & H_O_C - Garrot 138kV 47155-47660 | [7 empty] | 65.2325
Number of Bus | Name of Bus | ID | Max MW | L:H_O_C - Knight 138kV 47150-47331 C:Bellaire - Garrot 138kV 47015-47320 & H_O_C - Garrot 138kV 47155-47660 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.006761 | north | Y | 0.0023951 | -0.0088846 | 0.001075 | 0.0075688 | 0.001075 | west | Y | 0.0023951 | 0.33661
239 | BOSQUESW | 1 | 149 | 0.006761 | north | Y | 0.0023951 | -0.0088846 | 0.001075 | 0.0075688 | 0.001075 | west | Y | 0.0023951 | 0.19669
244 | WHITNYDM | 1 | 15 | 0.006358 | north | N | 0.0019921 | -0.0092876 | 0.00067202 | 0.0071658 | 0.00067202 | west | Y | 0.0019921 | 0
245 | WHITNYDM | 2 | 15 | 0.006358 | north | N | 0.0019921 | -0.0092876 | 0.00067202 | 0.0071658 | 0.00067202 | west | Y | 0.0019921 | 0
247 | BOSQUESW | 2 | 153 | 0.006761 | north | Y | 0.0023951 | -0.0088846 | 0.001075 | 0.0075688 | 0.001075 | west | Y | 0.0023951 | 0.20197
251 | BOSQUESW | 2 | 150 | 0.006638 | north | Y | 0.0022721 | -0.0090076 | 0.00095202 | 0.0074458 | 0.00095202 | west | Y | 0.0022721 | 0.19801
253 | BOSQUESW | 2 | 80 | 0.006638 | north | Y | 0.0022721 | -0.0090076 | 0.00095202 | 0.0074458 | 0.00095202 | west | Y | 0.0022721 | 0.1056
332 | RWMILLER | 1 | 73 | 0.005301 | north | Y | 0.00093506 | -0.010345 | -0.00038498 | 0.0061088 | 0.00038498 | west | Y | 0.00093506 | 0.040156
333 | RWMILLER | 2 | 119 | 0.005301 | north | Y | 0.00093506 | -0.010345 | -0.00038498 | 0.0061088 | 0.00038498 | west | Y | 0.00093506 | 0.065459
334 | RWMILLER | 3 | 205 | 0.005301 | north | Y | 0.00093506 | -0.010345 | -0.00038498 | 0.0061088 | 0.00038498 | west | Y | 0.00093506 | 0.11277
335 | RWMILLER | 4 | 102 | 0.005301 | north | Y | 0.00093506 | -0.010345 | -0.00038498 | 0.0061088 | 0.00038498 | west | Y | 0.00093506 | 0.056108
336 | RWMILLER | 5 | 96 | 0.005301 | north | Y | 0.00093506 | -0.010345 | -0.00038498 | 0.0061088 | 0.00038498 | west | Y | 0.00093506 | 0.052807
344 | MRSSHPRD | 1 | 12 | 0.005216 | north | N | 0.00085006 | -0.01043 | -0.00046998 | 0.0060238 | 0.00046998 | west | Y | 0.00085006 | 0
345 | MRSSHPRD | 2 | 12 | 0.005216 | north | N | 0.00085006 | -0.01043 | -0.00046998 | 0.0060238 | 0.00046998 | west | Y | 0.00085006 | 0
366 | JNSNCNTY | 1 | 168 | 0.005249 | north | Y | 0.00088306 | -0.010397 | -0.00043698 | 0.0060568 | 0.00043698 | west | Y | 0.00088306 | 0.074941
367 | JNSNCNTY | 2 | 90 | 0.005249 | north | Y | 0.00088306 | -0.010397 | -0.00043698 | 0.0060568 | 0.00043698 | west | Y | 0.00088306 | 0.040147
503 | NTHTEXAS | 1 | 18 | 0.005147 | north | Y | 0.00078106 | -0.010499 | -0.00053898 | 0.0059548 | 0.00053898 | west | Y | 0.00078106 | 0.0043574
504 | NTHTEXAS | 2 | 18 | 0.005147 | north | Y | 0.00078106 | -0.010499 | -0.00053898 | 0.0059548 | 0.00053898 | west | Y | 0.00078106 | 0.0043574
505 | NTHTEXAS | 3 | 38 | 0.005147 | north | Y | 0.00078106 | -0.010499 | -0.00053898 | 0.0059548 | 0.00053898 | west | Y | 0.00078106 | 0.0091989
580 | JCKCNTY8 | 1 | 288 | 0.005051 | north | Y | 0.00068506 | -0.010595 | -0.00063498 | 0.0058588 | 0.00063498 | west | Y | 0.00068506 | 0.014422
581 | JCKCNTY8 | 2 | 147 | 0.005051 | north | Y | 0.00068506 | -0.010595 | -0.00063498 | 0.0058588 | 0.00063498 | west | Y | 0.00068506 | 0.0073613
582 | JCKCNTY8 | 3 | 147 | 0.005051 | north | Y | 0.00068506 | -0.010595 | -0.00063498 | 0.0058588 | 0.00063498 | west | Y | 0.00068506 | 0.0073613
728 | WOLFRIDG | 1 | 112.5 | 0.004938 | north | Y | 0.00057206 | -0.010708 | -0.00074798 | 0.0057458 | 0.00057206 | North | N | 0.00057206 | 0
837 | NEWMAN_G | 1 | 40 | 0.004628 | north | Y | 0.00026206 | -0.011018 | -0.001058 | 0.0054358 | 0.00026206 | North | N | 0.00026206 | 0
842 | OLINGER_ | 1 | 79 | 0.004628 | north | Y | 0.00026206 | -0.011018 | -0.001058 | 0.0054358 | 0.00026206 | North | N | 0.00026206 | 0
843 | OLINGER_ | 1 | 106 | 0.004628 | north | Y | 0.00026206 | -0.011018 | -0.001058 | 0.0054358 | 0.00026206 | North | N | 0.00026206 | 0
844 | OLINGER_ | 1 | 146 | 0.004628 | north | Y | 0.00026206 | -0.011018 | -0.001058 | 0.0054358 | 0.00026206 | North | N | 0.00026206 | 0
845 | OLINGER_ | 1 | 76 | 0.004628 | north | Y | 0.00026206 | -0.011018 | -0.001058 | 0.0054358 | 0.00026206 | North | N | 0.00026206 | 0
923 | SPENCER_ | 1 | 60 | 0.004852 | north | Y | 0.00048606 | -0.010794 | -0.00083398 | 0.0056598 | 0.00048606 | North | N | 0.00048606 | 0
924 | SPENCER_ | 1 | 63 | 0.004852 | north | Y | 0.00048606 | -0.010794 | -0.00083398 | 0.0056598 | 0.00048606 | North | N | 0.00048606 | 0
948 | STEAM1 | 1 | 20 | 0.004617 | north | Y | 0.00025106 | -0.011029 | -0.001069 | 0.0054248 | 0.00025106 | North | N | 0.00025106 | 0
949 | STEAM2 | 1 | 25 | 0.004617 | north | Y | 0.00025106 | -0.011029 | -0.001069 | 0.0054248 | 0.00025106 | North | N | 0.00025106 | 0
950 | STEAM3 | 1 | 41 | 0.004617 | north | Y | 0.00025106 | -0.011029 | -0.001069 | 0.0054248 | 0.00025106 | North | N | 0.00025106 | 0
990 | GIBN_CRE | 1 | 463 | 0.000472 | north | Y | -0.0038939 | -0.015174 | -0.005214 | 0.0012798 | 0.0012798 | houston | Y | 0.0038939 | 1.2103
1002 | PBCTAGE_ | A | 66 | 0.005761 | west | Y | 0.0013951 | -0.0098846 | 7.5015e-05 | 0.0065688 | 7.5015e-05 | west | N | 7.5015e-05 | 0
1003 | PBCTBGE_ | B | 65 | 0.005761 | west | Y | 0.0013951 | -0.0098846 | 7.5015e-05 | 0.0065688 | 7.5015e-05 | west | N | 7.5015e-05 | 0
1004 | PBCTCGE_ | C | 67 | 0.005761 | west | Y | 0.0013951 | -0.0098846 | 7.5015e-05 | 0.0065688 | 7.5015e-05 | west | N | 7.5015e-05 | 0
1005 | PBCTDGE_ | D | 67 | 0.005761 | west | Y | 0.0013951 | -0.0098846 | 7.5015e-05 | 0.0065688 | 7.5015e-05 | west | N | 7.5015e-05 | 0
1006 | PBCTEGE_ | E | 67 | 0.005761 | west | Y | 0.0013951 | -0.0098846 | 7.5015e-05 | 0.0065688 | 7.5015e-05 | west | N | 7.5015e-05 | 0
1007 | PB5GEN_6 | MB | 114 | 0.005761 | west | Y | 0.0013951 | -0.0098846 | 7.5015e-05 | 0.0065688 | 7.5015e-05 | west | N | 7.5015e-05 | 0
1008 | PB6GEN_7 | MB | 515 | 0.005761 | west | Y | 0.0013951 | -0.0098846 | 7.5015e-05 | 0.0065688 | 7.5015e-05 | west | N | 7.5015e-05 | 0
1039 | MRGNAG_1 | A | 66 | 0.005612 | west | Y | 0.0012461 | -0.010034 | -7.3985e-05 | 0.0064198 | 7.3985e-05 | west | N | 7.3985e-05 | 0
1040 | MRGNBG_2 | B | 69 | 0.005612 | west | Y | 0.0012461 | -0.010034 | -7.3985e-05 | 0.0064198 | 7.3985e-05 | west | N | 7.3985e-05 | 0
1041 | MRGNCG_3 | C | 69 | 0.005612 | west | Y | 0.0012461 | -0.010034 | -7.3985e-05 | 0.0064198 | 7.3985e-05 | west | N | 7.3985e-05 | 0
1042 | MRGNDG_4 | D | 67 | 0.005612 | west | Y | 0.0012461 | -0.010034 | -7.3985e-05 | 0.0064198 | 7.3985e-05 | west | N | 7.3985e-05 | 0
1043 | MRGNEG_5 | E | 67 | 0.005612 | west | Y | 0.0012461 | -0.010034 | -7.3985e-05 | 0.0064198 | 7.3985e-05 | west | N | 7.3985e-05 | 0
1044 | MRGNFG_6 | F | 65 | 0.005612 | west | Y | 0.0012461 | -0.010034 | -7.3985e-05 | 0.0064198 | 7.3985e-05 | west | N | 7.3985e-05 | 0
1045 | CALENG1G | 1 | 70 | 0.005633 | west | N | 0.0012671 | -0.010013 | -5.2985e-05 | 0.0064408 | 5.2985e-05 | west | N | 5.2985e-05 | 0
1046 | CALENG2G | 2 | 73.4 | 0.005633 | west | N | 0.0012671 | -0.010013 | -5.2985e-05 | 0.0064408 | 5.2985e-05 | west | N | 5.2985e-05 | 0
1047 | CALENG3G | 3 | 70.4 | 0.005633 | west | N | 0.0012671 | -0.010013 | -5.2985e-05 | 0.0064408 | 5.2985e-05 | west | N | 5.2985e-05 | 0
1058 | LONGSHOR | 1 | 150 | 0.005621 | west | Y | 0.0012551 | -0.010025 | -6.4985e-05 | 0.0064288 | 6.4985e-05 | west | N | 6.4985e-05 | 0
1058 | LONGSHOR | 2 | 220 | 0.005621 | west | Y | 0.0012551 | -0.010025 | -6.4985e-05 | 0.0064288 | 6.4985e-05 | west | N | 6.4985e-05 | 0
1061 | CIELOGEN | 1 | 99 | 0.005605 | west | Y | 0.0012391 | -0.010041 | -8.0985e-05 | 0.0064128 | 8.0985e-05 | west | N | 8.0985e-05 | 0
1062 | CIELOGEN | 1 | 61 | 0.005605 | west | Y | 0.0012391 | -0.010041 | -8.0985e-05 | 0.0064128 | 8.0985e-05 | west | N | 8.0985e-05 | 0
1068 | SCURRYCW | 1 | 141 | 0.005606 | west | Y | 0.0012401 | -0.01004 | -7.9985e-05 | 0.0064138 | 7.9985e-05 | west | N | 7.9985e-05 | 0
1069 | KINDERMG | 1 | 25 | 0.005605 | west | N | 0.0012391 | -0.010041 | -8.0985e-05 | 0.0064128 | 8.0985e-05 | west | N | 8.0985e-05 | 0
1070 | KINDERMG | 1 | 45.7 | 0.005605 | west | N | 0.0012391 | -0.010041 | -8.0985e-05 | 0.0064128 | 8.0985e-05 | west | N | 8.0985e-05 | 0
1071 | KINDERMG | 1 | 45.7 | 0.005605 | west | N | 0.0012391 | -0.010041 | -8.0985e-05 | 0.0064128 | 8.0985e-05 | west | N | 8.0985e-05 | 0
1073 | SCURRYCW | 2 | 120 | 0.005606 | west | Y | 0.0012401 | -0.01004 | -7.9985e-05 | 0.0064138 | 7.9985e-05 | west | N | 7.9985e-05 | 0
1320 | BSP 1 | 1 | 25.8 | 0.00567 | west | N | 0.0013041 | -0.0099756 | -1.5985e-05 | 0.0064778 | 1.5985e-05 | west | N | 1.5985e-05 | 0
1326 | STANTONW | 1 | 100.5 | 0.005683 | west | Y | 0.0013171 | -0.0099626 | -2.9847e-06 | 0.0064908 | 2.9847e-06 | west | N | 2.9847e-06 | 0
1327 | WILDHRSE | 1 | 120 | 0.005646 | west | Y | 0.0012801 | -0.0099996 | -3.9985e-05 | 0.0064538 | 3.9985e-05 | west | N | 3.9985e-05 | 0
1328 | OCOTILLO | 1 | 58 | 0.005684 | west | Y | 0.0013181 | -0.0099616 | -1.9847e-06 | 0.0064918 | 1.9847e-06 | west | N | 1.9847e-06 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.005674 | west | Y | 0.0013081 | -0.0099716 | -1.1985e-05 | 0.0064818 | 1.1985e-05 | west | N | 1.1985e-05 | 0
1343 | TRENTIPP | 1 | 150 | 0.005591 | west | Y | 0.0012251 | -0.010055 | -9.4985e-05 | 0.0063988 | 9.4985e-05 | west | N | 9.4985e-05 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.005722 | west | Y | 0.0013561 | -0.0099236 | 3.6015e-05 | 0.0065298 | 3.6015e-05 | west | N | 3.6015e-05 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.005722 | west | Y | 0.0013561 | -0.0099236 | 3.6015e-05 | 0.0065298 | 3.6015e-05 | west | N | 3.6015e-05 | 0
1354 | AEPWIND_ | 1 | 101 | 0.005591 | west | Y | 0.0012251 | -0.010055 | -9.4985e-05 | 0.0063988 | 9.4985e-05 | west | N | 9.4985e-05 | 0
1360 | GUNSIGHT | 1 | 120 | 0.005645 | west | Y | 0.0012791 | -0.010001 | -4.0985e-05 | 0.0064528 | 4.0985e-05 | west | N | 4.0985e-05 | 0
1432 | GRHAMSES | 2 | 366 | 0.005219 | north | Y | 0.00085306 | -0.010427 | -0.00046698 | 0.0060268 | 0.00046698 | west | Y | 0.00085306 | 0.1413
1433 | GRHAMSES | 1 | 242 | 0.005265 | north | Y | 0.00089906 | -0.010381 | -0.00042098 | 0.0060728 | 0.00042098 | west | Y | 0.00089906 | 0.11569
1437 | MESQUITW | 1 | 400 | 0.005415 | west | Y | 0.0010491 | -0.010231 | -0.00027098 | 0.0062228 | 0.00027098 | west | N | 0.00027098 | 0
1438 | MESQUITW | 1 | 236 | 0.005415 | west | Y | 0.0010491 | -0.010231 | -0.00027098 | 0.0062228 | 0.00027098 | west | N | 0.00027098 | 0
1442 | COKFIELD | 1 | 165 | 0.005368 | west | Y | 0.0010021 | -0.010278 | -0.00031798 | 0.0061758 | 0.00031798 | west | N | 0.00031798 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.005097 | north | Y | 0.00073106 | -0.010549 | -0.00058898 | 0.0059048 | 0.00058898 | west | Y | 0.00073106 | 0.028984
1454 | WCPWRCO_ | 2 | 201 | 0.005097 | north | Y | 0.00073106 | -0.010549 | -0.00058898 | 0.0059048 | 0.00058898 | west | Y | 0.00073106 | 0.028557
1455 | WCPWRCO_ | 3 | 242 | 0.005097 | north | Y | 0.00073106 | -0.010549 | -0.00058898 | 0.0059048 | 0.00058898 | west | Y | 0.00073106 | 0.034383
1479 | WFCOGEN_ | 1 | 20 | 0.00521 | west | Y | 0.00084406 | -0.010436 | -0.00047598 | 0.0060178 | 0.00047598 | west | N | 0.00047598 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.00521 | west | Y | 0.00084406 | -0.010436 | -0.00047598 | 0.0060178 | 0.00047598 | west | N | 0.00047598 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.00521 | west | Y | 0.00084406 | -0.010436 | -0.00047598 | 0.0060178 | 0.00047598 | west | N | 0.00047598 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.00521 | west | Y | 0.00084406 | -0.010436 | -0.00047598 | 0.0060178 | 0.00047598 | west | N | 0.00047598 | 0
1600 | BARTNWND | 1 | 120 | 0.005227 | north | Y | 0.00086106 | -0.010419 | -0.00045898 | 0.0060348 | 0.00045898 | west | Y | 0.00086106 | 0.048249
1643 | SLSTR1PP | 1 | 60 | 0.005554 | north | Y | 0.0011881 | -0.010092 | -0.00013198 | 0.0063618 | 0.00013198 | west | Y | 0.0011881 | 0.063365
1675 | PEC_1G | 1 | 75 | 0.004644 | north | N | 0.00027806 | -0.011002 | -0.001042 | 0.0054518 | 0.00027806 | North | N | 0.00027806 | 0
1676 | PEC_2G | 2 | 79.6 | 0.004644 | north | N | 0.00027806 | -0.011002 | -0.001042 | 0.0054518 | 0.00027806 | North | N | 0.00027806 | 0
1677 | PEC_3G | 3 | 88.4 | 0.004644 | north | N | 0.00027806 | -0.011002 | -0.001042 | 0.0054518 | 0.00027806 | North | N | 0.00027806 | 0
1678 | LAMARPWR | 1 | 160 | 0.004649 | north | Y | 0.00028306 | -0.010997 | -0.001037 | 0.0054568 | 0.00028306 | North | N | 0.00028306 | 0
1679 | LAMARPWR | 2 | 156 | 0.004649 | north | Y | 0.00028306 | -0.010997 | -0.001037 | 0.0054568 | 0.00028306 | North | N | 0.00028306 | 0
1680 | LAMARPWR | 3 | 196 | 0.004649 | north | Y | 0.00028306 | -0.010997 | -0.001037 | 0.0054568 | 0.00028306 | North | N | 0.00028306 | 0
1681 | LAMARPWR | 4 | 156 | 0.004649 | north | Y | 0.00028306 | -0.010997 | -0.001037 | 0.0054568 | 0.00028306 | North | N | 0.00028306 | 0
1682 | LAMARPWR | 5 | 157 | 0.004649 | north | Y | 0.00028306 | -0.010997 | -0.001037 | 0.0054568 | 0.00028306 | North | N | 0.00028306 | 0
1683 | LAMARPWR | 6 | 198 | 0.004649 | north | Y | 0.00028306 | -0.010997 | -0.001037 | 0.0054568 | 0.00028306 | North | N | 0.00028306 | 0
1687 | VALLEY_1 | 1 | 170 | 0.004672 | north | Y | 0.00030606 | -0.010974 | -0.001014 | 0.0054798 | 0.00030606 | North | N | 0.00030606 | 0
1688 | VALLEY_2 | 2 | 520 | 0.004672 | north | Y | 0.00030606 | -0.010974 | -0.001014 | 0.0054798 | 0.00030606 | North | N | 0.00030606 | 0
1689 | VALLEY_3 | 3 | 370 | 0.004656 | north | Y | 0.00029006 | -0.01099 | -0.00103 | 0.0054638 | 0.00029006 | North | N | 0.00029006 | 0
1701 | MOSES_1G | 1 | 558 | 0.004637 | north | Y | 0.00027106 | -0.011009 | -0.001049 | 0.0054448 | 0.00027106 | North | N | 0.00027106 | 0
1702 | MOSES_2G | 2 | 579 | 0.004637 | north | Y | 0.00027106 | -0.011009 | -0.001049 | 0.0054448 | 0.00027106 | North | N | 0.00027106 | 0
1703 | MOSES_3G | 3 | 808 | 0.004637 | north | Y | 0.00027106 | -0.011009 | -0.001049 | 0.0054448 | 0.00027106 | North | N | 0.00027106 | 0
1861 | EAGLEMNT | MB | 112 | 0.004968 | north | Y | 0.00060206 | -0.010678 | -0.00071798 | 0.0057758 | 0.00060206 | North | N | 0.00060206 | 0
1862 | EAGLEMNT | MB | 100 | 0.004968 | north | Y | 0.00060206 | -0.010678 | -0.00071798 | 0.0057758 | 0.00060206 | North | N | 0.00060206 | 0
1863 | EAGLEMNT | MB | 378 | 0.004968 | north | Y | 0.00060206 | -0.010678 | -0.00071798 | 0.0057758 | 0.00060206 | North | N | 0.00060206 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.005104 | north | Y | 0.00073806 | -0.010542 | -0.00058198 | 0.0059118 | 0.00058198 | west | Y | 0.00073806 | 0.033916
1878 | WLFHOLW_ | 2 | 205 | 0.005104 | north | Y | 0.00073806 | -0.010542 | -0.00058198 | 0.0059118 | 0.00058198 | west | Y | 0.00073806 | 0.031996
1879 | WLFHOLW_ | 3 | 272.4 | 0.005104 | north | Y | 0.00073806 | -0.010542 | -0.00058198 | 0.0059118 | 0.00058198 | west | Y | 0.00073806 | 0.042515
1889 | DECRDOVA | MB | 770 | 0.005086 | north | Y | 0.00072006 | -0.01056 | -0.00059998 | 0.0058938 | 0.00059998 | west | Y | 0.00072006 | 0
1892 | DECRDOVA | A | 70 | 0.005195 | north | Y | 0.00082906 | -0.010451 | -0.00049098 | 0.0060028 | 0.00049098 | west | Y | 0.00082906 | 0.023665
1893 | DECRDOVA | B | 69 | 0.005195 | north | Y | 0.00082906 | -0.010451 | -0.00049098 | 0.0060028 | 0.00049098 | west | Y | 0.00082906 | 0.023327
1894 | DECRDOVA | C | 69 | 0.005195 | north | Y | 0.00082906 | -0.010451 | -0.00049098 | 0.0060028 | 0.00049098 | west | Y | 0.00082906 | 0.023327
1895 | DECRDOVA | D | 68 | 0.005195 | north | Y | 0.00082906 | -0.010451 | -0.00049098 | 0.0060028 | 0.00049098 | west | Y | 0.00082906 | 0.022989
1898 | COMCHEPK | 1 | 1157 | 0.005124 | north | N | 0.00075806 | -0.010522 | -0.00056198 | 0.0059318 | 0.00056198 | west | Y | 0.00075806 | 0
1899 | COMCHEPK | 2 | 1158 | 0.005124 | north | N | 0.00075806 | -0.010522 | -0.00056198 | 0.0059318 | 0.00056198 | west | Y | 0.00075806 | 0
1937 | MDLTHELP | 5 | 224 | 0.005049 | north | Y | 0.00068306 | -0.010597 | -0.00063698 | 0.0058568 | 0.00063698 | west | Y | 0.00068306 | 0.010321
1938 | MDLTHELP | 6 | 226 | 0.005049 | north | Y | 0.00068306 | -0.010597 | -0.00063698 | 0.0058568 | 0.00063698 | west | Y | 0.00068306 | 0.010413
1941 | MDLTHELP | 1 | 216.4 | 0.004965 | north | Y | 0.00059906 | -0.010681 | -0.00072098 | 0.0057728 | 0.00059906 | North | N | 0.00059906 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.004965 | north | Y | 0.00059906 | -0.010681 | -0.00072098 | 0.0057728 | 0.00059906 | North | N | 0.00059906 | 0
1943 | MDLTHELP | 3 | 212 | 0.005049 | north | Y | 0.00068306 | -0.010597 | -0.00063698 | 0.0058568 | 0.00063698 | west | Y | 0.00068306 | 0.0097683
1944 | MDLTHELP | 4 | 211 | 0.005049 | north | Y | 0.00068306 | -0.010597 | -0.00063698 | 0.0058568 | 0.00063698 | west | Y | 0.00068306 | 0.0097223
1947 | HANDLEY_ | 3 | 395 | 0.00495 | north | Y | 0.00058406 | -0.010696 | -0.00073598 | 0.0057578 | 0.00058406 | North | N | 0.00058406 | 0
1948 | HANDLEY_ | 4 | 435 | 0.004933 | north | Y | 0.00056706 | -0.010713 | -0.00075298 | 0.0057408 | 0.00056706 | North | N | 0.00056706 | 0
1949 | HANDLEY_ | 5 | 435 | 0.00495 | north | Y | 0.00058406 | -0.010696 | -0.00073598 | 0.0057578 | 0.00058406 | North | N | 0.00058406 | 0
2371 | COLLIN_1 | MB | 138 | 0.004723 | north | Y | 0.00035706 | -0.010923 | -0.00096298 | 0.0055308 | 0.00035706 | North | N | 0.00035706 | 0
2413 | MTCK6_G | 6 | 118 | 0.004702 | north | Y | 0.00033606 | -0.010944 | -0.00098398 | 0.0055098 | 0.00033606 | North | N | 0.00033606 | 0
2414 | MTCK7_G | 7 | 115 | 0.004702 | north | Y | 0.00033606 | -0.010944 | -0.00098398 | 0.0055098 | 0.00033606 | North | N | 0.00033606 | 0
2417 | MTCK8_G | 8 | 556 | 0.004702 | north | Y | 0.00033606 | -0.010944 | -0.00098398 | 0.0055098 | 0.00033606 | North | N | 0.00033606 | 0
2451 | LKHB1_G | 1 | 388 | 0.004607 | north | Y | 0.00024106 | -0.011039 | -0.001079 | 0.0054148 | 0.00024106 | North | N | 0.00024106 | 0
2452 | LKHB2_G | 2 | 515 | 0.004607 | north | Y | 0.00024106 | -0.011039 | -0.001079 | 0.0054148 | 0.00024106 | North | N | 0.00024106 | 0
3097 | MARTLAKE | 1 | 785 | 0.004306 | north | Y | -5.9938e-05 | -0.01134 | -0.00138 | 0.0051138 | 5.9938e-05 | North | N | 5.9938e-05 | 0
3098 | MARTLAKE | 2 | 795 | 0.004306 | north | Y | -5.9938e-05 | -0.01134 | -0.00138 | 0.0051138 | 5.9938e-05 | North | N | 5.9938e-05 | 0
3099 | MARTLAKE | 3 | 780 | 0.004306 | north | Y | -5.9938e-05 | -0.01134 | -0.00138 | 0.0051138 | 5.9938e-05 | North | N | 5.9938e-05 | 0
3107 | STRYKER_ | 1 | 182 | 0.004231 | north | Y | -0.00013494 | -0.011415 | -0.001455 | 0.0050388 | 0.00013494 | North | N | 0.00013494 | 0
3108 | STRYKER_ | 2 | 484 | 0.004231 | north | Y | -0.00013494 | -0.011415 | -0.001455 | 0.0050388 | 0.00013494 | North | N | 0.00013494 | 0
3126 | TRINIDAD | 1 | 224 | 0.004542 | north | Y | 0.00017606 | -0.011104 | -0.001144 | 0.0053498 | 0.00017606 | North | N | 0.00017606 | 0
3309 | ASPN_G | 1 | 50 | 0.004235 | north | Y | -0.00013094 | -0.011411 | -0.001451 | 0.0050428 | 0.00013094 | North | N | 0.00013094 | 0
3348 | CHAMPION | MB | 42 | 0.004239 | north | N | -0.00012694 | -0.011407 | -0.001447 | 0.0050468 | 0.00012694 | North | N | 0.00012694 | 0
3381 | BBRN_1G | 1 | 615 | 0.003767 | north | Y | -0.00059894 | -0.011879 | -0.001919 | 0.0045748 | 0.00059894 | North | N | 0.00059894 | 0
3382 | BBRN_2G | 2 | 587 | 0.003767 | north | Y | -0.00059894 | -0.011879 | -0.001919 | 0.0045748 | 0.00059894 | North | N | 0.00059894 | 0
3403 | THOUSE_1 | MB | 537 | 0.006902 | north | Y | 0.0025361 | -0.0087436 | 0.001216 | 0.0077098 | 0.001216 | west | Y | 0.0025361 | 0
3404 | THOUSE_2 | 2 | 787 | 0.006902 | north | Y | 0.0025361 | -0.0087436 | 0.001216 | 0.0077098 | 0.001216 | west | Y | 0.0025361 | 1.0389
3416 | LAKE_CRK | MB | 75 | 0.006997 | north | Y | 0.0026311 | -0.0086486 | 0.001311 | 0.0078048 | 0.001311 | west | Y | 0.0026311 | 0
3417 | LAKE_CRK | MB | 222 | 0.006997 | north | Y | 0.0026311 | -0.0086486 | 0.001311 | 0.0078048 | 0.001311 | west | Y | 0.0026311 | 0
3432 | SANDOW_4 | 4 | 569 | 0.011213 | south | Y | 0.0068471 | -0.0044326 | 0.005527 | 0.012021 | 0.0044326 | south | N | 0.0044326 | 0
5026 | BRAUNIG_ | 1 | 209 | 0.015807 | south | Y | 0.011441 | 0.00016142 | 0.010121 | 0.016615 | 0.00016142 | south | N | 0.00016142 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.015807 | south | Y | 0.011441 | 0.00016142 | 0.010121 | 0.016615 | 0.00016142 | south | N | 0.00016142 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.015768 | south | Y | 0.011402 | 0.00012242 | 0.010082 | 0.016576 | 0.00012242 | south | N | 0.00012242 | 0
5031 | BRA_VHBC | 1 | 46 | 0.015807 | south | Y | 0.011441 | 0.00016142 | 0.010121 | 0.016615 | 0.00016142 | south | N | 0.00016142 | 0
5032 | BRA_VHBC | 2 | 47 | 0.015807 | south | Y | 0.011441 | 0.00016142 | 0.010121 | 0.016615 | 0.00016142 | south | N | 0.00016142 | 0
5033 | BRA_VHBC | 3 | 46 | 0.015807 | south | Y | 0.011441 | 0.00016142 | 0.010121 | 0.016615 | 0.00016142 | south | N | 0.00016142 | 0
5034 | BRA_VHBC | 4 | 46 | 0.015807 | south | Y | 0.011441 | 0.00016142 | 0.010121 | 0.016615 | 0.00016142 | south | N | 0.00016142 | 0
5111 | CALAVER_ | 1 | 424 | 0.015767 | south | Y | 0.011401 | 0.00012142 | 0.010081 | 0.016575 | 0.00012142 | south | N | 0.00012142 | 0
5112 | CALAVER_ | 2 | 425 | 0.015767 | south | Y | 0.011401 | 0.00012142 | 0.010081 | 0.016575 | 0.00012142 | south | N | 0.00012142 | 0
5264 | LEON_LCP | 3 | 58 | 0.01579 | south | Y | 0.011424 | 0.00014442 | 0.010104 | 0.016598 | 0.00014442 | south | N | 0.00014442 | 0
5265 | LEON_LCP | 4 | 89 | 0.01579 | south | Y | 0.011424 | 0.00014442 | 0.010104 | 0.016598 | 0.00014442 | south | N | 0.00014442 | 0
5266 | LEON_LCP | 1 | 44 | 0.01579 | south | Y | 0.011424 | 0.00014442 | 0.010104 | 0.016598 | 0.00014442 | south | N | 0.00014442 | 0
5267 | LEON_LCP | 2 | 44 | 0.01579 | south | Y | 0.011424 | 0.00014442 | 0.010104 | 0.016598 | 0.00014442 | south | N | 0.00014442 | 0
5268 | LEON_LCP | 3 | 43 | 0.01579 | south | Y | 0.011424 | 0.00014442 | 0.010104 | 0.016598 | 0.00014442 | south | N | 0.00014442 | 0
5269 | LEON_LCP | 4 | 45 | 0.01579 | south | Y | 0.011424 | 0.00014442 | 0.010104 | 0.016598 | 0.00014442 | south | N | 0.00014442 | 0
5396 | CALAVER_ | 1 | 412 | 0.015786 | south | Y | 0.01142 | 0.00014042 | 0.0101 | 0.016594 | 0.00014042 | south | N | 0.00014042 | 0
5397 | CALAVER_ | 2 | 400 | 0.015786 | south | Y | 0.01142 | 0.00014042 | 0.0101 | 0.016594 | 0.00014042 | south | N | 0.00014042 | 0
5401 | CALAVER_ | 1 | 546 | 0.015917 | south | Y | 0.011551 | 0.00027142 | 0.010231 | 0.016725 | 0.00027142 | south | N | 0.00027142 | 0
5402 | CALAVER_ | 2 | 750 | 0.015917 | south | Y | 0.011551 | 0.00027142 | 0.010231 | 0.016725 | 0.00027142 | south | N | 0.00027142 | 0
5436 | TUTTL_WB | MB | 61 | 0.015773 | south | Y | 0.011407 | 0.00012742 | 0.010087 | 0.016581 | 0.00012742 | south | N | 0.00012742 | 0
5438 | TUTTL_WB | MB | 95 | 0.015773 | south | Y | 0.011407 | 0.00012742 | 0.010087 | 0.016581 | 0.00012742 | south | N | 0.00012742 | 0
5439 | TUTTL_WB | MB | 151 | 0.015773 | south | Y | 0.011407 | 0.00012742 | 0.010087 | 0.016581 | 0.00012742 | south | N | 0.00012742 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.01585 | south | Y | 0.011484 | 0.00020442 | 0.010164 | 0.016658 | 0.00020442 | south | N | 0.00020442 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.01585 | south | Y | 0.011484 | 0.00020442 | 0.010164 | 0.016658 | 0.00020442 | south | N | 0.00020442 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.01585 | south | Y | 0.011484 | 0.00020442 | 0.010164 | 0.016658 | 0.00020442 | south | N | 0.00020442 | 0
5503 | RAYBURNG | 1 | 22 | 0.019255 | south | Y | 0.014889 | 0.0036094 | 0.013569 | 0.020063 | 0.0036094 | south | N | 0.0036094 | 0
5505 | RAYBURNG | 1 | 11 | 0.019255 | south | Y | 0.014889 | 0.0036094 | 0.013569 | 0.020063 | 0.0036094 | south | N | 0.0036094 | 0
5506 | RAYBURNG | 1 | 11 | 0.019255 | south | Y | 0.014889 | 0.0036094 | 0.013569 | 0.020063 | 0.0036094 | south | N | 0.0036094 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.019255 | south | Y | 0.014889 | 0.0036094 | 0.013569 | 0.020063 | 0.0036094 | south | N | 0.0036094 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.019255 | south | Y | 0.014889 | 0.0036094 | 0.013569 | 0.020063 | 0.0036094 | south | N | 0.0036094 | 0
5511 | RAYBURNC | 1 | 46 | 0.019255 | south | Y | 0.014889 | 0.0036094 | 0.013569 | 0.020063 | 0.0036094 | south | N | 0.0036094 | 0
5512 | RAYBURNC | 1 | 48 | 0.019255 | south | Y | 0.014889 | 0.0036094 | 0.013569 | 0.020063 | 0.0036094 | south | N | 0.0036094 | 0
5728 | FALCONHY | 2 | 12 | 0.017101 | south | N | 0.012735 | 0.0014554 | 0.011415 | 0.017909 | 0.0014554 | south | N | 0.0014554 | 0
5729 | FALCONHY | 3 | 11 | 0.017101 | south | N | 0.012735 | 0.0014554 | 0.011415 | 0.017909 | 0.0014554 | south | N | 0.0014554 | 0
5890 | PEARSALL | 1 | 24 | 0.015992 | south | Y | 0.011626 | 0.00034642 | 0.010306 | 0.0168 | 0.00034642 | south | N | 0.00034642 | 0
5891 | PEARSALL | 1 | 24 | 0.015992 | south | Y | 0.011626 | 0.00034642 | 0.010306 | 0.0168 | 0.00034642 | south | N | 0.00034642 | 0
5892 | PEARSALL | 1 | 23 | 0.015992 | south | Y | 0.011626 | 0.00034642 | 0.010306 | 0.0168 | 0.00034642 | south | N | 0.00034642 | 0
5903 | SANMIGUE | 1 | 396 | 0.016365 | south | Y | 0.011999 | 0.00071942 | 0.010679 | 0.017173 | 0.00071942 | south | N | 0.00071942 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.018783 | houston | N | 0.014417 | 0.0031374 | 0.013097 | 0.019591 | 0.0031374 | south | Y | 0.019591 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.018783 | houston | N | 0.014417 | 0.0031374 | 0.013097 | 0.019591 | 0.0031374 | south | Y | 0.019591 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.0043659 | 0
5932 | SI_RAY9 | 9 | 38 | 0.017482 | south | Y | 0.013116 | 0.0018364 | 0.011796 | 0.01829 | 0.0018364 | south | N | 0.0018364 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.017482 | south | Y | 0.013116 | 0.0018364 | 0.011796 | 0.01829 | 0.0018364 | south | N | 0.0018364 | 0
5934 | SI_RAY5 | 5 | 15 | 0.017482 | south | Y | 0.013116 | 0.0018364 | 0.011796 | 0.01829 | 0.0018364 | south | N | 0.0018364 | 0
5935 | SI_RAY10 | 10 | 47 | 0.017482 | south | Y | 0.013116 | 0.0018364 | 0.011796 | 0.01829 | 0.0018364 | south | N | 0.0018364 | 0
6016 | SWMESA | 1 | 75 | 0.006177 | west | Y | 0.0018111 | -0.0094686 | 0.00049102 | 0.0069848 | 0.00049102 | west | N | 0.00049102 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.005686 | 0
6144 | MCADOO1A | 1 | 150 | 0.005552 | west | Y | 0.0011861 | -0.010094 | -0.00013398 | 0.0063598 | 0.00013398 | west | N | 0.00013398 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.00575 | west | Y | 0.0013841 | -0.0098956 | 6.4015e-05 | 0.0065578 | 6.4015e-05 | west | N | 6.4015e-05 | 0
6476 | LANGFORD | 1 | 150 | 0.007791 | west | Y | 0.0034251 | -0.0078546 | 0.002105 | 0.0085988 | 0.002105 | west | N | 0.002105 | 0
6637 | SNYDERW1 | 1 | 63 | 0.005609 | west | Y | 0.0012431 | -0.010037 | -7.6985e-05 | 0.0064168 | 7.6985e-05 | west | N | 7.6985e-05 | 0
6752 | OKLA0A | 1 | 649.7 | 0.005328 | west | Y | 0.00096206 | -0.010318 | -0.00035798 | 0.0061358 | 0.00035798 | west | N | 0.00035798 | 0
6948 | DENISNDM | 1 | 40 | 0.004685 | north | N | 0.00031906 | -0.010961 | -0.001001 | 0.0054928 | 0.00031906 | North | N | 0.00031906 | 0
6948 | DENISNDM | 2 | 40 | 0.004685 | north | N | 0.00031906 | -0.010961 | -0.001001 | 0.0054928 | 0.00031906 | North | N | 0.00031906 | 0
7000 | L_FERGUS | 1 | 422 | 0.013048 | south | Y | 0.0086821 | -0.0025976 | 0.007362 | 0.013856 | 0.0025976 | south | N | 0.0025976 | 0
7004 | L_SIMGID | 1 | 132 | 0.014258 | south | Y | 0.0098921 | -0.0013876 | 0.008572 | 0.015066 | 0.0013876 | south | N | 0.0013876 | 0
7005 | L_SIMGID | 2 | 134 | 0.014258 | south | Y | 0.0098921 | -0.0013876 | 0.008572 | 0.015066 | 0.0013876 | south | N | 0.0013876 | 0
7006 | L_SIMGID | 3 | 323 | 0.014258 | south | Y | 0.0098921 | -0.0013876 | 0.008572 | 0.015066 | 0.0013876 | south | N | 0.0013876 | 0
7007 | L_LOSTPI | 1 | 158 | 0.014258 | south | Y | 0.0098921 | -0.0013876 | 0.008572 | 0.015066 | 0.0013876 | south | N | 0.0013876 | 0
7008 | L_LOSTPI | 2 | 160 | 0.014258 | south | Y | 0.0098921 | -0.0013876 | 0.008572 | 0.015066 | 0.0013876 | south | N | 0.0013876 | 0
7009 | L_LOSTPI | 3 | 175 | 0.014258 | south | Y | 0.0098921 | -0.0013876 | 0.008572 | 0.015066 | 0.0013876 | south | N | 0.0013876 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.015415 | south | Y | 0.011049 | -0.00023058 | 0.009729 | 0.016223 | 0.00023058 | south | N | 0.00023058 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.015415 | south | Y | 0.011049 | -0.00023058 | 0.009729 | 0.016223 | 0.00023058 | south | N | 0.00023058 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.01542 | south | Y | 0.011054 | -0.00022558 | 0.009734 | 0.016228 | 0.00022558 | south | N | 0.00022558 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.015138 | south | Y | 0.010772 | -0.00050758 | 0.009452 | 0.015946 | 0.00050758 | south | N | 0.00050758 | 0
7015 | L_HAYSEN | 2 | 225 | 0.015138 | south | Y | 0.010772 | -0.00050758 | 0.009452 | 0.015946 | 0.00050758 | south | N | 0.00050758 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.015138 | south | Y | 0.010772 | -0.00050758 | 0.009452 | 0.015946 | 0.00050758 | south | N | 0.00050758 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.015138 | south | Y | 0.010772 | -0.00050758 | 0.009452 | 0.015946 | 0.00050758 | south | N | 0.00050758 | 0
7020 | L_AUSTPL | 1 | 8 | 0.013525 | south | N | 0.0091591 | -0.0021206 | 0.007839 | 0.014333 | 0.0021206 | south | N | 0.0021206 | 0
7020 | L_AUSTPL | 2 | 8 | 0.013525 | south | N | 0.0091591 | -0.0021206 | 0.007839 | 0.014333 | 0.0021206 | south | N | 0.0021206 | 0
7022 | L_BUCHAN | 1 | 18 | 0.012494 | south | N | 0.0081281 | -0.0031516 | 0.006808 | 0.013302 | 0.0031516 | south | N | 0.0031516 | 0
7023 | L_BUCHAN | 2 | 18 | 0.012494 | south | N | 0.0081281 | -0.0031516 | 0.006808 | 0.013302 | 0.0031516 | south | N | 0.0031516 | 0
7024 | L_BUCHAN | 3 | 15 | 0.012494 | south | N | 0.0081281 | -0.0031516 | 0.006808 | 0.013302 | 0.0031516 | south | N | 0.0031516 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.012591 | south | N | 0.0082251 | -0.0030546 | 0.006905 | 0.013399 | 0.0030546 | south | N | 0.0030546 | 0
7028 | L_MARBFA | 1 | 18 | 0.013143 | south | N | 0.0087771 | -0.0025026 | 0.007457 | 0.013951 | 0.0025026 | south | N | 0.0025026 | 0
7029 | L_MARBFA | 2 | 18 | 0.013143 | south | N | 0.0087771 | -0.0025026 | 0.007457 | 0.013951 | 0.0025026 | south | N | 0.0025026 | 0
7031 | L_MARSFO | 1 | 35 | 0.013358 | south | N | 0.0089921 | -0.0022876 | 0.007672 | 0.014166 | 0.0022876 | south | N | 0.0022876 | 0
7032 | L_MARSFO | 2 | 34 | 0.013358 | south | N | 0.0089921 | -0.0022876 | 0.007672 | 0.014166 | 0.0022876 | south | N | 0.0022876 | 0
7033 | L_MARSFO | 3 | 35 | 0.013358 | south | N | 0.0089921 | -0.0022876 | 0.007672 | 0.014166 | 0.0022876 | south | N | 0.0022876 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.013026 | south | N | 0.0086601 | -0.0026196 | 0.00734 | 0.013834 | 0.0026196 | south | N | 0.0026196 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.013026 | south | N | 0.0086601 | -0.0026196 | 0.00734 | 0.013834 | 0.0026196 | south | N | 0.0026196 | 0
7038 | L_DELAWA | 1 | 35 | 0.005757 | west | Y | 0.0013911 | -0.0098886 | 7.1015e-05 | 0.0065648 | 7.1015e-05 | west | N | 7.1015e-05 | 0
7038 | L_DELAWA | 2 | 30 | 0.005757 | west | Y | 0.0013911 | -0.0098886 | 7.1015e-05 | 0.0065648 | 7.1015e-05 | west | N | 7.1015e-05 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.015522 | south | Y | 0.011156 | -0.00012358 | 0.009836 | 0.01633 | 0.00012358 | south | N | 0.00012358 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.015522 | south | Y | 0.011156 | -0.00012358 | 0.009836 | 0.01633 | 0.00012358 | south | N | 0.00012358 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.015522 | south | Y | 0.011156 | -0.00012358 | 0.009836 | 0.01633 | 0.00012358 | south | N | 0.00012358 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.015522 | south | Y | 0.011156 | -0.00012358 | 0.009836 | 0.01633 | 0.00012358 | south | N | 0.00012358 | 0
7487 | L_CANYHY | 1 | 6 | 0.014824 | south | N | 0.010458 | -0.00082158 | 0.009138 | 0.015632 | 0.00082158 | south | N | 0.00082158 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.015533 | south | N | 0.011167 | -0.00011258 | 0.009847 | 0.016341 | 0.00011258 | south | N | 0.00011258 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.015533 | south | N | 0.011167 | -0.00011258 | 0.009847 | 0.016341 | 0.00011258 | south | N | 0.00011258 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.015533 | south | N | 0.011167 | -0.00011258 | 0.009847 | 0.016341 | 0.00011258 | south | N | 0.00011258 | 0
7609 | L_SCHUMA | 1 | 4 | 0.015471 | south | N | 0.011105 | -0.00017458 | 0.009785 | 0.016279 | 0.00017458 | south | N | 0.00017458 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.015998 | south | N | 0.011632 | 0.00035242 | 0.010312 | 0.016806 | 0.00035242 | south | N | 0.00035242 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.015998 | south | N | 0.011632 | 0.00035242 | 0.010312 | 0.016806 | 0.00035242 | south | N | 0.00035242 | 0
7800 | L_GUADGE | 1 | 147 | 0.01565 | south | Y | 0.011284 | 4.4224e-06 | 0.009964 | 0.016458 | 4.4224e-06 | south | N | 4.4224e-06 | 0
7801 | L_GUADGE | 2 | 138 | 0.01565 | south | Y | 0.011284 | 4.4224e-06 | 0.009964 | 0.016458 | 4.4224e-06 | south | N | 4.4224e-06 | 0
7802 | L_GUADGE | 3 | 140 | 0.01565 | south | Y | 0.011284 | 4.4224e-06 | 0.009964 | 0.016458 | 4.4224e-06 | south | N | 4.4224e-06 | 0
7803 | L_GUADGE | 4 | 147 | 0.01565 | south | Y | 0.011284 | 4.4224e-06 | 0.009964 | 0.016458 | 4.4224e-06 | south | N | 4.4224e-06 | 0
7804 | L_GUADGE | 5 | 182 | 0.01565 | south | Y | 0.011284 | 4.4224e-06 | 0.009964 | 0.016458 | 4.4224e-06 | south | N | 4.4224e-06 | 0
7805 | L_GUADGE | 6 | 198 | 0.01565 | south | Y | 0.011284 | 4.4224e-06 | 0.009964 | 0.016458 | 4.4224e-06 | south | N | 4.4224e-06 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.014068 | south | Y | 0.0097021 | -0.0015776 | 0.008382 | 0.014876 | 0.0015776 | south | N | 0.0015776 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.014068 | south | Y | 0.0097021 | -0.0015776 | 0.008382 | 0.014876 | 0.0015776 | south | N | 0.0015776 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.014068 | south | Y | 0.0097021 | -0.0015776 | 0.008382 | 0.014876 | 0.0015776 | south | N | 0.0015776 | 0
7810 | L_RIONOG | 1 | 142 | 0.015402 | south | Y | 0.011036 | -0.00024358 | 0.009716 | 0.01621 | 0.00024358 | south | N | 0.00024358 | 0
7811 | L_RIONOG | 2 | 145 | 0.015402 | south | Y | 0.011036 | -0.00024358 | 0.009716 | 0.01621 | 0.00024358 | south | N | 0.00024358 | 0
7812 | L_RIONOG | 3 | 151 | 0.015402 | south | Y | 0.011036 | -0.00024358 | 0.009716 | 0.01621 | 0.00024358 | south | N | 0.00024358 | 0
7813 | L_RIONOG | 4 | 290 | 0.015402 | south | Y | 0.011036 | -0.00024358 | 0.009716 | 0.01621 | 0.00024358 | south | N | 0.00024358 | 0
8032 | AMISTADH | 1 | 33 | 0.013227 | south | N | 0.0088611 | -0.0024186 | 0.007541 | 0.014035 | 0.0024186 | south | N | 0.0024186 | 0
8033 | AMISTADH | 2 | 25 | 0.013227 | south | N | 0.0088611 | -0.0024186 | 0.007541 | 0.014035 | 0.0024186 | south | N | 0.0024186 | 0
8048 | FALCONHY | 1 | 12 | 0.017101 | south | N | 0.012735 | 0.0014554 | 0.011415 | 0.017909 | 0.0014554 | south | N | 0.0014554 | 0
8066 | DUP1V#1 | 1 | 73 | 0.019346 | south | N | 0.01498 | 0.0037004 | 0.01366 | 0.020154 | 0.0037004 | south | N | 0.0037004 | 0
8134 | FOR69CG0 | 1 | 79 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
8138 | FOR69CG0 | 2 | 81 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.015646 | 0
8147 | UCAR #2 | 10 | 28 | 0.019609 | south | N | 0.015243 | 0.0039634 | 0.013923 | 0.020417 | 0.0039634 | south | N | 0.0039634 | 0
8148 | UCAR #1 | 2 | 7 | 0.019609 | south | N | 0.015243 | 0.0039634 | 0.013923 | 0.020417 | 0.0039634 | south | N | 0.0039634 | 0
8153 | FOR69CG0 | 3 | 79 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
8154 | FOR69CG0 | 4 | 80 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
8156 | FOR69CG0 | 6 | 25 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
8157 | FOR69CG0 | 7 | 46 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
8161 | COLETOU1 | 1 | 629 | 0.017987 | south | Y | 0.013621 | 0.0023414 | 0.012301 | 0.018795 | 0.0023414 | south | N | 0.0023414 | 0
8173 | VICEC51A | 5 | 144 | 0.019237 | south | Y | 0.014871 | 0.0035914 | 0.013551 | 0.020045 | 0.0035914 | south | N | 0.0035914 | 0
8174 | VICEC61A | 6 | 188 | 0.019237 | south | Y | 0.014871 | 0.0035914 | 0.013551 | 0.020045 | 0.0035914 | south | N | 0.0035914 | 0
8189 | CUERO 2 | 1 | 12 | 0.016895 | south | N | 0.012529 | 0.0012494 | 0.011209 | 0.017703 | 0.0012494 | south | N | 0.0012494 | 0
8262 | ELPS | 1 | 6 | 0.014123 | south | N | 0.0097571 | -0.0015226 | 0.008437 | 0.014931 | 0.0015226 | south | N | 0.0015226 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.015646 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.015646 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.015646 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.015646 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.015646 | 0
8442 | NBEC71A | 1 | 336 | 0.01767 | south | Y | 0.013304 | 0.0020244 | 0.011984 | 0.018478 | 0.0020244 | south | N | 0.0020244 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.015646 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.0043659 | -0.015646 | -0.005686 | 0.00080781 | 0.00080781 | houston | Y | 0.015646 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.017638 | south | Y | 0.013272 | 0.0019924 | 0.011952 | 0.018446 | 0.0019924 | south | N | 0.0019924 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.017638 | south | Y | 0.013272 | 0.0019924 | 0.011952 | 0.018446 | 0.0019924 | south | N | 0.0019924 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.017654 | south | N | 0.013288 | 0.0020084 | 0.011968 | 0.018462 | 0.0020084 | south | N | 0.0020084 | 0
8506 | VAL #1 | 1 | 25 | 0.017658 | south | N | 0.013292 | 0.0020124 | 0.011972 | 0.018466 | 0.0020124 | south | N | 0.0020124 | 0
8507 | VAL #2 | 2 | 25 | 0.017658 | south | N | 0.013292 | 0.0020124 | 0.011972 | 0.018466 | 0.0020124 | south | N | 0.0020124 | 0
8511 | OXY_CC0A | 1 | 38 | 0.017636 | south | N | 0.01327 | 0.0019904 | 0.01195 | 0.018444 | 0.0019904 | south | N | 0.0019904 | 0
8517 | CELANEBI | 1 | 29 | 0.017543 | south | N | 0.013177 | 0.0018974 | 0.011857 | 0.018351 | 0.0018974 | south | N | 0.0018974 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.017669 | south | N | 0.013303 | 0.0020234 | 0.011983 | 0.018477 | 0.0020234 | south | N | 0.0020234 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.017669 | south | N | 0.013303 | 0.0020234 | 0.011983 | 0.018477 | 0.0020234 | south | N | 0.0020234 | 0
8562 | CNOPST1 | 3 | 153 | 0.017669 | south | N | 0.013303 | 0.0020234 | 0.011983 | 0.018477 | 0.0020234 | south | N | 0.0020234 | 0
8926 | LGE_GT10 | 1 | 158 | 0.017803 | south | N | 0.013437 | 0.0021574 | 0.012117 | 0.018611 | 0.0021574 | south | N | 0.0021574 | 0
8927 | LGE_GT20 | 2 | 153 | 0.017803 | south | N | 0.013437 | 0.0021574 | 0.012117 | 0.018611 | 0.0021574 | south | N | 0.0021574 | 0
8928 | LGE_STG0 | 3 | 100 | 0.017803 | south | N | 0.013437 | 0.0021574 | 0.012117 | 0.018611 | 0.0021574 | south | N | 0.0021574 | 0
8930 | ICPGN10A | 1 | 145 | 0.017803 | south | N | 0.013437 | 0.0021574 | 0.012117 | 0.018611 | 0.0021574 | south | N | 0.0021574 | 0
8931 | ICPGN20A | 2 | 147 | 0.017803 | south | N | 0.013437 | 0.0021574 | 0.012117 | 0.018611 | 0.0021574 | south | N | 0.0021574 | 0
8932 | ICPGN30A | 3 | 127 | 0.017803 | south | N | 0.013437 | 0.0021574 | 0.012117 | 0.018611 | 0.0021574 | south | N | 0.0021574 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.017398 | south | Y | 0.013032 | 0.0017524 | 0.011712 | 0.018206 | 0.0017524 | south | N | 0.0017524 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.017398 | south | Y | 0.013032 | 0.0017524 | 0.011712 | 0.018206 | 0.0017524 | south | N | 0.0017524 | 0
8935 | FGNTS201 | 3 | 173 | 0.017398 | south | Y | 0.013032 | 0.0017524 | 0.011712 | 0.018206 | 0.0017524 | south | N | 0.0017524 | 0
8936 | MVGN#1 | 1 | 207 | 0.017446 | south | Y | 0.01308 | 0.0018004 | 0.01176 | 0.018254 | 0.0018004 | south | N | 0.0018004 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.017446 | south | Y | 0.01308 | 0.0018004 | 0.01176 | 0.018254 | 0.0018004 | south | N | 0.0018004 | 0
8938 | MVGN#3 | 3 | 242 | 0.017446 | south | Y | 0.01308 | 0.0018004 | 0.01176 | 0.018254 | 0.0018004 | south | N | 0.0018004 | 0
8981 | HECN1 | 1 | 144 | 0.017447 | south | Y | 0.013081 | 0.0018014 | 0.011761 | 0.018255 | 0.0018014 | south | N | 0.0018014 | 0
8982 | HECN2 | 2 | 144 | 0.017447 | south | Y | 0.013081 | 0.0018014 | 0.011761 | 0.018255 | 0.0018014 | south | N | 0.0018014 | 0
8983 | HECN3 | 3 | 171 | 0.017447 | south | Y | 0.013081 | 0.0018014 | 0.011761 | 0.018255 | 0.0018014 | south | N | 0.0018014 | 0
9000 | DECKR_G1 | 1 | 310 | 0.01354 | south | Y | 0.0091741 | -0.0021056 | 0.007854 | 0.014348 | 0.0021056 | south | N | 0.0021056 | 0
9001 | DECKR_G2 | 2 | 413 | 0.01354 | south | Y | 0.0091741 | -0.0021056 | 0.007854 | 0.014348 | 0.0021056 | south | N | 0.0021056 | 0
9002 | DECKR_G3 | 3 | 42 | 0.013468 | south | Y | 0.0091021 | -0.0021776 | 0.007782 | 0.014276 | 0.0021776 | south | N | 0.0021776 | 0
9003 | DECKR_G4 | 4 | 44 | 0.013468 | south | Y | 0.0091021 | -0.0021776 | 0.007782 | 0.014276 | 0.0021776 | south | N | 0.0021776 | 0
9004 | DECKR_G5 | 5 | 44 | 0.013468 | south | Y | 0.0091021 | -0.0021776 | 0.007782 | 0.014276 | 0.0021776 | south | N | 0.0021776 | 0
9005 | DECKR_G6 | 6 | 47 | 0.013468 | south | Y | 0.0091021 | -0.0021776 | 0.007782 | 0.014276 | 0.0021776 | south | N | 0.0021776 | 0
9016 | SANDH_G1 | 1 | 49 | 0.013664 | south | Y | 0.0092981 | -0.0019816 | 0.007978 | 0.014472 | 0.0019816 | south | N | 0.0019816 | 0
9017 | SANDH_G2 | 2 | 46 | 0.013664 | south | Y | 0.0092981 | -0.0019816 | 0.007978 | 0.014472 | 0.0019816 | south | N | 0.0019816 | 0
9018 | SANDH_G3 | 3 | 46 | 0.013664 | south | Y | 0.0092981 | -0.0019816 | 0.007978 | 0.014472 | 0.0019816 | south | N | 0.0019816 | 0
9019 | SANDH_G4 | 4 | 47 | 0.013664 | south | Y | 0.0092981 | -0.0019816 | 0.007978 | 0.014472 | 0.0019816 | south | N | 0.0019816 | 0
9020 | SANDHG5A | 5A | 154 | 0.013664 | south | Y | 0.0092981 | -0.0019816 | 0.007978 | 0.014472 | 0.0019816 | south | N | 0.0019816 | 0
9021 | SANDHG5C | 5C | 148 | 0.013664 | south | Y | 0.0092981 | -0.0019816 | 0.007978 | 0.014472 | 0.0019816 | south | N | 0.0019816 | 0
9022 | SANDH_G6 | 6 | 48 | 0.013664 | south | Y | 0.0092981 | -0.0019816 | 0.007978 | 0.014472 | 0.0019816 | south | N | 0.0019816 | 0
9023 | SANDH_G7 | 7 | 48 | 0.013664 | south | Y | 0.0092981 | -0.0019816 | 0.007978 | 0.014472 | 0.0019816 | south | N | 0.0019816 | 0
11001 | NAV1CT | 1 | 70 | 0.005686 | west | Y | 0.0013201 | -0.0099596 | 1.532e-08 | 0.0064938 | 1.532e-08 | west | N | 1.532e-08 | 0
11009 | NAV2CT | 1 | 70 | 0.005686 | west | Y | 0.0013201 | -0.0099596 | 1.532e-08 | 0.0064938 | 1.532e-08 | west | N | 1.532e-08 | 0
11011 | NAV3ST | 1 | 92.8 | 0.005686 | west | Y | 0.0013201 | -0.0099596 | 1.532e-08 | 0.0064938 | 1.532e-08 | west | N | 1.532e-08 | 0
11012 | NAV4CT | 1 | 80 | 0.005686 | west | Y | 0.0013201 | -0.0099596 | 1.532e-08 | 0.0064938 | 1.532e-08 | west | N | 1.532e-08 | 0
11013 | NAV5CT | 1 | 80 | 0.005686 | west | Y | 0.0013201 | -0.0099596 | 1.532e-08 | 0.0064938 | 1.532e-08 | west | N | 1.532e-08 | 0
11014 | NAV6ST | 1 | 115 | 0.005686 | west | Y | 0.0013201 | -0.0099596 | 1.532e-08 | 0.0064938 | 1.532e-08 | west | N | 1.532e-08 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.005687 | west | Y | 0.0013211 | -0.0099586 | 1.0153e-06 | 0.0064948 | 1.0153e-06 | west | N | 1.0153e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.005687 | west | Y | 0.0013211 | -0.0099586 | 1.0153e-06 | 0.0064948 | 1.0153e-06 | west | N | 1.0153e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.005687 | west | Y | 0.0013211 | -0.0099586 | 1.0153e-06 | 0.0064948 | 1.0153e-06 | west | N | 1.0153e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.005687 | west | Y | 0.0013211 | -0.0099586 | 1.0153e-06 | 0.0064948 | 1.0153e-06 | west | N | 1.0153e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.005687 | west | Y | 0.0013211 | -0.0099586 | 1.0153e-06 | 0.0064948 | 1.0153e-06 | west | N | 1.0153e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.005687 | west | Y | 0.0013211 | -0.0099586 | 1.0153e-06 | 0.0064948 | 1.0153e-06 | west | N | 1.0153e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.005553 | west | Y | 0.0011871 | -0.010093 | -0.00013298 | 0.0063608 | 0.00013298 | west | N | 0.00013298 | 0
11057 | CHAMPION | 1 | 126.5 | 0.005553 | west | Y | 0.0011871 | -0.010093 | -0.00013298 | 0.0063608 | 0.00013298 | west | N | 0.00013298 | 0
11058 | PYRON_1G | 1 | 249 | 0.005553 | west | Y | 0.0011871 | -0.010093 | -0.00013298 | 0.0063608 | 0.00013298 | west | N | 0.00013298 | 0
11059 | INADALE_ | 1 | 197 | 0.005553 | west | Y | 0.0011871 | -0.010093 | -0.00013298 | 0.0063608 | 0.00013298 | west | N | 0.00013298 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.005621 | west | Y | 0.0012551 | -0.010025 | -6.4985e-05 | 0.0064288 | 6.4985e-05 | west | N | 6.4985e-05 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.005621 | west | Y | 0.0012551 | -0.010025 | -6.4985e-05 | 0.0064288 | 6.4985e-05 | west | N | 6.4985e-05 | 0
11147 | NOTREES_ | 1 | 149 | 0.005745 | west | Y | 0.0013791 | -0.0099006 | 5.9015e-05 | 0.0065528 | 5.9015e-05 | west | N | 5.9015e-05 | 0
11309 | BULLCREK | 1 | 180 | 0.005634 | west | Y | 0.0012681 | -0.010012 | -5.1985e-05 | 0.0064418 | 5.1985e-05 | west | N | 5.1985e-05 | 0
11310 | BULLCREK | 1 | 180 | 0.005634 | west | Y | 0.0012681 | -0.010012 | -5.1985e-05 | 0.0064418 | 5.1985e-05 | west | N | 5.1985e-05 | 0
11320 | COYOTE_1 | 1 | 225 | 0.005638 | west | Y | 0.0012721 | -0.010008 | -4.7985e-05 | 0.0064458 | 4.7985e-05 | west | N | 4.7985e-05 | 0
11415 | LORAINE_ | 1 | 125 | 0.005581 | west | Y | 0.0012151 | -0.010065 | -0.00010498 | 0.0063888 | 0.00010498 | west | N | 0.00010498 | 0
11416 | LORAINE_ | 1 | 125 | 0.005581 | west | Y | 0.0012151 | -0.010065 | -0.00010498 | 0.0063888 | 0.00010498 | west | N | 0.00010498 | 0
11691 | KMICHICT | 1 | 140 | 0.004656 | north | N | 0.00029006 | -0.01099 | -0.00103 | 0.0054638 | 0.00029006 | North | N | 0.00029006 | 0
11692 | KMICHICT | 2 | 141 | 0.004656 | north | N | 0.00029006 | -0.01099 | -0.00103 | 0.0054638 | 0.00029006 | North | N | 0.00029006 | 0
11693 | KMICHIST | 3 | 309 | 0.004656 | north | N | 0.00029006 | -0.01099 | -0.00103 | 0.0054638 | 0.00029006 | North | N | 0.00029006 | 0
11694 | KMICHICT | 4 | 143 | 0.004656 | north | N | 0.00029006 | -0.01099 | -0.00103 | 0.0054638 | 0.00029006 | North | N | 0.00029006 | 0
11695 | KMICHICT | 5 | 144 | 0.004656 | north | N | 0.00029006 | -0.01099 | -0.00103 | 0.0054638 | 0.00029006 | North | N | 0.00029006 | 0
11696 | KMICHIST | 6 | 310 | 0.004656 | north | N | 0.00029006 | -0.01099 | -0.00103 | 0.0054638 | 0.00029006 | North | N | 0.00029006 | 0
12322 | ENNSTRAC | 1 | 196 | 0.004772 | north | Y | 0.00040606 | -0.010874 | -0.00091398 | 0.0055798 | 0.00040606 | North | N | 0.00040606 | 0
12323 | ENNSTRAC | 2 | 111 | 0.004772 | north | Y | 0.00040606 | -0.010874 | -0.00091398 | 0.0055798 | 0.00040606 | North | N | 0.00040606 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.004704 | north | N | 0.00033806 | -0.010942 | -0.00098198 | 0.0055118 | 0.00033806 | North | N | 0.00033806 | 0
12411 | FPLEFR1A | 1 | 161 | 0.004553 | north | Y | 0.00018706 | -0.011093 | -0.001133 | 0.0053608 | 0.00018706 | North | N | 0.00018706 | 0
12412 | FPLEFR1B | 2 | 164 | 0.004553 | north | Y | 0.00018706 | -0.011093 | -0.001133 | 0.0053608 | 0.00018706 | North | N | 0.00018706 | 0
12413 | FPLEFR1C | 3 | 164 | 0.004553 | north | Y | 0.00018706 | -0.011093 | -0.001133 | 0.0053608 | 0.00018706 | North | N | 0.00018706 | 0
12414 | FPLEFR1S | 4 | 414 | 0.004553 | north | Y | 0.00018706 | -0.011093 | -0.001133 | 0.0053608 | 0.00018706 | North | N | 0.00018706 | 0
12421 | FPLEFR2A | 1 | 162 | 0.004553 | north | Y | 0.00018706 | -0.011093 | -0.001133 | 0.0053608 | 0.00018706 | North | N | 0.00018706 | 0
12422 | FPLEFR2B | 2 | 161 | 0.004553 | north | Y | 0.00018706 | -0.011093 | -0.001133 | 0.0053608 | 0.00018706 | North | N | 0.00018706 | 0
12423 | FPLEFR2C | 3 | 163 | 0.004553 | north | Y | 0.00018706 | -0.011093 | -0.001133 | 0.0053608 | 0.00018706 | North | N | 0.00018706 | 0
12424 | FPLEFR2S | 4 | 409 | 0.004553 | north | Y | 0.00018706 | -0.011093 | -0.001133 | 0.0053608 | 0.00018706 | North | N | 0.00018706 | 0
12440 | PARKD_1S | 1 | 0 | 0.004624 | north | N | 0.00025806 | -0.011022 | -0.001062 | 0.0054318 | 0.00025806 | North | N | 0.00025806 | 0
12449 | PARKD_2S | 1 | 0 | 0.004624 | north | N | 0.00025806 | -0.011022 | -0.001062 | 0.0054318 | 0.00025806 | North | N | 0.00025806 | 0
13116 | TGATEWAY | 1 | 148 | 0.004271 | north | N | -9.4938e-05 | -0.011375 | -0.001415 | 0.0050788 | 9.4938e-05 | North | N | 9.4938e-05 | 0
13117 | TGATEWAY | 2 | 130 | 0.004271 | north | N | -9.4938e-05 | -0.011375 | -0.001415 | 0.0050788 | 9.4938e-05 | North | N | 9.4938e-05 | 0
13118 | TGATEWAY | 3 | 145 | 0.004271 | north | N | -9.4938e-05 | -0.011375 | -0.001415 | 0.0050788 | 9.4938e-05 | North | N | 9.4938e-05 | 0
13119 | TGATEWAY | 4 | 399 | 0.004271 | north | N | -9.4938e-05 | -0.011375 | -0.001415 | 0.0050788 | 9.4938e-05 | North | N | 9.4938e-05 | 0
13131 | CALFREST | 1 | 150.7 | 0.003852 | north | Y | -0.00051394 | -0.011794 | -0.001834 | 0.0046598 | 0.00051394 | North | N | 0.00051394 | 0
13132 | CALFREST | 2 | 151 | 0.003852 | north | Y | -0.00051394 | -0.011794 | -0.001834 | 0.0046598 | 0.00051394 | North | N | 0.00051394 | 0
13133 | CALFREST | 3 | 177.4 | 0.003852 | north | Y | -0.00051394 | -0.011794 | -0.001834 | 0.0046598 | 0.00051394 | North | N | 0.00051394 | 0
13134 | CALFREST | 4 | 151.5 | 0.003868 | north | Y | -0.00049794 | -0.011778 | -0.001818 | 0.0046758 | 0.00049794 | North | N | 0.00049794 | 0
13135 | CALFREST | 5 | 152.3 | 0.003868 | north | Y | -0.00049794 | -0.011778 | -0.001818 | 0.0046758 | 0.00049794 | North | N | 0.00049794 | 0
13136 | CALFREST | 6 | 177.5 | 0.003868 | north | Y | -0.00049794 | -0.011778 | -0.001818 | 0.0046758 | 0.00049794 | North | N | 0.00049794 | 0
13432 | SANDOW_5 | 5 | 581 | 0.011213 | south | Y | 0.0068471 | -0.0044326 | 0.005527 | 0.012021 | 0.0044326 | south | N | 0.0044326 | 0
13691 | OAKGROVE | 1 | 855 | 0.002124 | north | Y | -0.0022419 | -0.013522 | -0.003562 | 0.0029318 | 0.0022419 | North | N | 0.0022419 | 0
13692 | OAKGROVE | 2 | 855 | 0.002124 | north | Y | -0.0022419 | -0.013522 | -0.003562 | 0.0029318 | 0.0022419 | North | N | 0.0022419 | 0
32798 | BRYN_TAM | 1 | 32 | 0.001354 | north | N | -0.0030119 | -0.014292 | -0.004332 | 0.0021618 | 0.0021618 | houston | Y | 0.0030119 | 0
32883 | BRYN_DNS | 1 | 48 | 0.001654 | north | Y | -0.0027119 | -0.013992 | -0.004032 | 0.0024618 | 0.0024618 | houston | Y | 0.0027119 | 0.012006
32884 | BRYN_DNS | 1 | 46 | 0.001654 | north | Y | -0.0027119 | -0.013992 | -0.004032 | 0.0024618 | 0.0024618 | houston | Y | 0.0027119 | 0.011506
32886 | BRYN_ATK | MB | 12 | 0.001381 | north | Y | -0.0029849 | -0.014265 | -0.004305 | 0.0021888 | 0.0021888 | houston | Y | 0.0029849 | 0
32887 | BRYN_ATK | MB | 51 | 0.001381 | north | Y | -0.0029849 | -0.014265 | -0.004305 | 0.0021888 | 0.0021888 | houston | Y | 0.0029849 | 0
32888 | BRYN_ATK | 1 | 17 | 0.001381 | north | Y | -0.0029849 | -0.014265 | -0.004305 | 0.0021888 | 0.0021888 | houston | Y | 0.0029849 | 0.013534
32890 | BRYN_ATK | MB | 22 | 0.001381 | north | Y | -0.0029849 | -0.014265 | -0.004305 | 0.0021888 | 0.0021888 | houston | Y | 0.0029849 | 0
32891 | BRYN_ATK | MB | 25 | 0.001381 | north | Y | -0.0029849 | -0.014265 | -0.004305 | 0.0021888 | 0.0021888 | houston | Y | 0.0029849 | 0
32892 | BRYN_DNS | 1 | 105 | 0.001654 | north | Y | -0.0027119 | -0.013992 | -0.004032 | 0.0024618 | 0.0024618 | houston | Y | 0.0027119 | 0.026264
36998 | RDCNYNG1 | 1 | 84 | 0.005595 | west | Y | 0.0012291 | -0.010051 | -9.0985e-05 | 0.0064028 | 9.0985e-05 | west | N | 9.0985e-05 | 0
38332 | WDWRDU2 | 1 | 80 | 0.006185 | west | Y | 0.0018191 | -0.0094606 | 0.00049902 | 0.0069928 | 0.00049902 | west | N | 0.00049902 | 0
38437 | TNSRBNMS | 1 | 150 | 0.006189 | west | Y | 0.0018231 | -0.0094566 | 0.00050302 | 0.0069968 | 0.00050302 | west | N | 0.00050302 | 0
38438 | TNSRBNMS | 1 | 150 | 0.006189 | west | Y | 0.0018231 | -0.0094566 | 0.00050302 | 0.0069968 | 0.00050302 | west | N | 0.00050302 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.044659 | houston | N | -0.049025 | -0.060305 | -0.050345 | -0.043851 | 0.043851 | houston | N | 0.043851 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.044659 | houston | N | -0.049025 | -0.060305 | -0.050345 | -0.043851 | 0.043851 | houston | N | 0.043851 | 0
38600 | TNBP_CGN | 5 | 53 | -0.044659 | houston | N | -0.049025 | -0.060305 | -0.050345 | -0.043851 | 0.043851 | houston | N | 0.043851 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.044659 | houston | N | -0.049025 | -0.060305 | -0.050345 | -0.043851 | 0.043851 | houston | N | 0.043851 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.044659 | houston | N | -0.049025 | -0.060305 | -0.050345 | -0.043851 | 0.043851 | houston | N | 0.043851 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.044659 | houston | N | -0.049025 | -0.060305 | -0.050345 | -0.043851 | 0.043851 | houston | N | 0.043851 | 0
38614 | TNBPAMCG | 4 | 96 | -0.044659 | houston | N | -0.049025 | -0.060305 | -0.050345 | -0.043851 | 0.043851 | houston | N | 0.043851 | 0
38615 | TNBPAMCG | 1 | 244 | -0.044659 | houston | N | -0.049025 | -0.060305 | -0.050345 | -0.043851 | 0.043851 | houston | N | 0.043851 | 0
38690 | TNBP_CGN | 3 | 40 | -0.044659 | houston | N | -0.049025 | -0.060305 | -0.050345 | -0.043851 | 0.043851 | houston | N | 0.043851 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.044492 | houston | N | -0.048858 | -0.060138 | -0.050178 | -0.043684 | 0.043684 | houston | N | 0.043684 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.044492 | houston | N | -0.048858 | -0.060138 | -0.050178 | -0.043684 | 0.043684 | houston | N | 0.043684 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.044492 | houston | N | -0.048858 | -0.060138 | -0.050178 | -0.043684 | 0.043684 | houston | N | 0.043684 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.044492 | houston | N | -0.048858 | -0.060138 | -0.050178 | -0.043684 | 0.043684 | houston | N | 0.043684 | 0
39470 | TNDOWCGN | 1 | 32 | -0.044497 | houston | N | -0.048863 | -0.060143 | -0.050183 | -0.043689 | 0.043689 | houston | N | 0.043689 | 0
39480 | TNDOWCGN | 1 | 30 | -0.044497 | houston | N | -0.048863 | -0.060143 | -0.050183 | -0.043689 | 0.043689 | houston | N | 0.043689 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.050756 | houston | N | 0.04639 | 0.03511 | 0.04507 | 0.051564 | 0.03511 | south | Y | 0.051564 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.050756 | houston | N | 0.04639 | 0.03511 | 0.04507 | 0.051564 | 0.03511 | south | Y | 0.051564 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.050756 | houston | N | 0.04639 | 0.03511 | 0.04507 | 0.051564 | 0.03511 | south | Y | 0.051564 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.050756 | houston | N | 0.04639 | 0.03511 | 0.04507 | 0.051564 | 0.03511 | south | Y | 0.051564 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.002124 | north | Y | -0.0022419 | -0.013522 | -0.003562 | 0.0029318 | 0.0022419 | North | N | 0.0022419 | 0
39970 | TNTNPONE | 1 | 153 | 0.002124 | north | Y | -0.0022419 | -0.013522 | -0.003562 | 0.0029318 | 0.0022419 | North | N | 0.0022419 | 0
48500 | APD_GT1_ | 1 | 136 | -0.074624 | houston | N | -0.07899 | -0.09027 | -0.08031 | -0.073816 | 0.073816 | houston | N | 0.073816 | 0
48510 | AK_GT1__ | 1 | 33 | 0.002243 | houston | N | -0.0021229 | -0.013403 | -0.003443 | 0.0030508 | 0.0021229 | North | Y | 0.0030508 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.0547 | houston | Y | -0.059066 | -0.070346 | -0.060386 | -0.053892 | 0.053892 | houston | N | 0.053892 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.0547 | houston | Y | -0.059066 | -0.070346 | -0.060386 | -0.053892 | 0.053892 | houston | N | 0.053892 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.0547 | houston | Y | -0.059066 | -0.070346 | -0.060386 | -0.053892 | 0.053892 | houston | N | 0.053892 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.0547 | houston | Y | -0.059066 | -0.070346 | -0.060386 | -0.053892 | 0.053892 | houston | N | 0.053892 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.032814 | houston | N | 0.028448 | 0.017168 | 0.027128 | 0.033622 | 0.017168 | south | Y | 0.033622 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.032814 | houston | N | 0.028448 | 0.017168 | 0.027128 | 0.033622 | 0.017168 | south | Y | 0.033622 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.022768 | houston | N | 0.018402 | 0.0071224 | 0.017082 | 0.023576 | 0.0071224 | south | Y | 0.023576 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.022768 | houston | N | 0.018402 | 0.0071224 | 0.017082 | 0.023576 | 0.0071224 | south | Y | 0.023576 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.022768 | houston | N | 0.018402 | 0.0071224 | 0.017082 | 0.023576 | 0.0071224 | south | Y | 0.023576 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.053563 | houston | N | -0.057929 | -0.069209 | -0.059249 | -0.052755 | 0.052755 | houston | N | 0.052755 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.053563 | houston | N | -0.057929 | -0.069209 | -0.059249 | -0.052755 | 0.052755 | houston | N | 0.052755 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.053563 | houston | N | -0.057929 | -0.069209 | -0.059249 | -0.052755 | 0.052755 | houston | N | 0.052755 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.053563 | houston | N | -0.057929 | -0.069209 | -0.059249 | -0.052755 | 0.052755 | houston | N | 0.052755 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.064213 | houston | N | -0.068579 | -0.079859 | -0.069899 | -0.063405 | 0.063405 | houston | N | 0.063405 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.064213 | houston | N | -0.068579 | -0.079859 | -0.069899 | -0.063405 | 0.063405 | houston | N | 0.063405 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.055996 | houston | N | -0.060362 | -0.071642 | -0.061682 | -0.055188 | 0.055188 | houston | N | 0.055188 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.055996 | houston | N | -0.060362 | -0.071642 | -0.061682 | -0.055188 | 0.055188 | houston | N | 0.055188 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.055996 | houston | N | -0.060362 | -0.071642 | -0.061682 | -0.055188 | 0.055188 | houston | N | 0.055188 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.055996 | houston | N | -0.060362 | -0.071642 | -0.061682 | -0.055188 | 0.055188 | houston | N | 0.055188 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.055996 | houston | N | -0.060362 | -0.071642 | -0.061682 | -0.055188 | 0.055188 | houston | N | 0.055188 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.031172 | houston | Y | -0.035538 | -0.046818 | -0.036858 | -0.030364 | 0.030364 | houston | N | 0.030364 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.039014 | houston | Y | -0.04338 | -0.05466 | -0.0447 | -0.038206 | 0.038206 | houston | N | 0.038206 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.026854 | houston | Y | -0.03122 | -0.0425 | -0.03254 | -0.026046 | 0.026046 | houston | N | 0.026046 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.026854 | houston | Y | -0.03122 | -0.0425 | -0.03254 | -0.026046 | 0.026046 | houston | N | 0.026046 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.026854 | houston | Y | -0.03122 | -0.0425 | -0.03254 | -0.026046 | 0.026046 | houston | N | 0.026046 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.023997 | houston | N | -0.028363 | -0.039643 | -0.029683 | -0.023189 | 0.023189 | houston | N | 0.023189 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.072883 | houston | N | -0.077249 | -0.088529 | -0.078569 | -0.072075 | 0.072075 | houston | N | 0.072075 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.072883 | houston | N | -0.077249 | -0.088529 | -0.078569 | -0.072075 | 0.072075 | houston | N | 0.072075 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.026075 | houston | N | -0.030441 | -0.041721 | -0.031761 | -0.025267 | 0.025267 | houston | N | 0.025267 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.026075 | houston | N | -0.030441 | -0.041721 | -0.031761 | -0.025267 | 0.025267 | houston | N | 0.025267 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.026075 | houston | N | -0.030441 | -0.041721 | -0.031761 | -0.025267 | 0.025267 | houston | N | 0.025267 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.026075 | houston | N | -0.030441 | -0.041721 | -0.031761 | -0.025267 | 0.025267 | houston | N | 0.025267 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.057996 | houston | N | -0.062362 | -0.073642 | -0.063682 | -0.057188 | 0.057188 | houston | N | 0.057188 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.057996 | houston | N | -0.062362 | -0.073642 | -0.063682 | -0.057188 | 0.057188 | houston | N | 0.057188 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.057996 | houston | N | -0.062362 | -0.073642 | -0.063682 | -0.057188 | 0.057188 | houston | N | 0.057188 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.057996 | houston | N | -0.062362 | -0.073642 | -0.063682 | -0.057188 | 0.057188 | houston | N | 0.057188 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.026904 | houston | N | -0.03127 | -0.04255 | -0.03259 | -0.026096 | 0.026096 | houston | N | 0.026096 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.026904 | houston | N | -0.03127 | -0.04255 | -0.03259 | -0.026096 | 0.026096 | houston | N | 0.026096 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.026904 | houston | N | -0.03127 | -0.04255 | -0.03259 | -0.026096 | 0.026096 | houston | N | 0.026096 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.026904 | houston | N | -0.03127 | -0.04255 | -0.03259 | -0.026096 | 0.026096 | houston | N | 0.026096 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.026904 | houston | N | -0.03127 | -0.04255 | -0.03259 | -0.026096 | 0.026096 | houston | N | 0.026096 | 0
48651 | EP_1_2 | 1 | 5 | -0.03515 | houston | N | -0.039516 | -0.050796 | -0.040836 | -0.034342 | 0.034342 | houston | N | 0.034342 | 0
48651 | EP_1_2 | 2 | 21 | -0.03515 | houston | N | -0.039516 | -0.050796 | -0.040836 | -0.034342 | 0.034342 | houston | N | 0.034342 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.001413 | north | N | -0.0057789 | -0.017059 | -0.007099 | -0.00060519 | 0.00060519 | houston | Y | 0.0057789 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.001413 | north | N | -0.0057789 | -0.017059 | -0.007099 | -0.00060519 | 0.00060519 | houston | Y | 0.0057789 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.001413 | north | N | -0.0057789 | -0.017059 | -0.007099 | -0.00060519 | 0.00060519 | houston | Y | 0.0057789 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.001413 | north | N | -0.0057789 | -0.017059 | -0.007099 | -0.00060519 | 0.00060519 | houston | Y | 0.0057789 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.042987 | houston | Y | -0.047353 | -0.058633 | -0.048673 | -0.042179 | 0.042179 | houston | N | 0.042179 | 0
48691 | GBY_7374 | A | 46 | -0.058753 | houston | Y | -0.063119 | -0.074399 | -0.064439 | -0.057945 | 0.057945 | houston | N | 0.057945 | 0
48691 | GBY_7374 | B | 46 | -0.058753 | houston | Y | -0.063119 | -0.074399 | -0.064439 | -0.057945 | 0.057945 | houston | N | 0.057945 | 0
48692 | GBY_8182 | C | 46 | -0.058753 | houston | Y | -0.063119 | -0.074399 | -0.064439 | -0.057945 | 0.057945 | houston | N | 0.057945 | 0
48692 | GBY_8182 | D | 55 | -0.058753 | houston | Y | -0.063119 | -0.074399 | -0.064439 | -0.057945 | 0.057945 | houston | N | 0.057945 | 0
48693 | GBY_8384 | E | 55 | -0.058753 | houston | Y | -0.063119 | -0.074399 | -0.064439 | -0.057945 | 0.057945 | houston | N | 0.057945 | 0
48693 | GBY_8384 | F | 54 | -0.058753 | houston | Y | -0.063119 | -0.074399 | -0.064439 | -0.057945 | 0.057945 | houston | N | 0.057945 | 0
48721 | LEG_1___ | 1 | 827 | 0.002771 | north | Y | -0.0015949 | -0.012875 | -0.002915 | 0.0035788 | 0.0015949 | North | N | 0.0015949 | 0
48722 | LEG_2___ | 2 | 819 | 0.002771 | north | Y | -0.0015949 | -0.012875 | -0.002915 | 0.0035788 | 0.0015949 | North | N | 0.0015949 | 0
48730 | MNS_GT | 1 | 46.1 | 0.009882 | houston | N | 0.0055161 | -0.0057636 | 0.004196 | 0.01069 | 0.004196 | west | Y | 0.01069 | 0
48731 | CBE_GT1 | 1 | 76 | 0.035407 | houston | Y | 0.031041 | 0.019761 | 0.029721 | 0.036215 | 0.019761 | south | Y | 0.036215 | 1.2505
48732 | CBE_GT2 | 1 | 76 | 0.035407 | houston | Y | 0.031041 | 0.019761 | 0.029721 | 0.036215 | 0.019761 | south | Y | 0.036215 | 1.2505
48733 | CBE_ST12 | 1 | 105 | 0.035407 | houston | Y | 0.031041 | 0.019761 | 0.029721 | 0.036215 | 0.019761 | south | Y | 0.036215 | 1.7276
48734 | CBE_GT3 | 1 | 74 | 0.035407 | houston | Y | 0.031041 | 0.019761 | 0.029721 | 0.036215 | 0.019761 | south | Y | 0.036215 | 1.2176
48735 | CBE_GT4 | 1 | 74 | 0.035407 | houston | Y | 0.031041 | 0.019761 | 0.029721 | 0.036215 | 0.019761 | south | Y | 0.036215 | 1.2176
48736 | CBE_ST34 | 1 | 102 | 0.035407 | houston | Y | 0.031041 | 0.019761 | 0.029721 | 0.036215 | 0.019761 | south | Y | 0.036215 | 1.6782
48740 | PSG_GN2_ | 1 | 180 | -0.068536 | houston | N | -0.072902 | -0.084182 | -0.074222 | -0.067728 | 0.067728 | houston | N | 0.067728 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.068536 | houston | N | -0.072902 | -0.084182 | -0.074222 | -0.067728 | 0.067728 | houston | N | 0.067728 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.068536 | houston | N | -0.072902 | -0.084182 | -0.074222 | -0.067728 | 0.067728 | houston | N | 0.067728 | 0
48761 | PR_GT1__ | 1 | 35 | -0.061627 | houston | N | -0.065993 | -0.077273 | -0.067313 | -0.060819 | 0.060819 | houston | N | 0.060819 | 0
48772 | PHR_GN2_ | MB | 459 | -0.048372 | houston | Y | -0.052738 | -0.064018 | -0.054058 | -0.047564 | 0.047564 | houston | N | 0.047564 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.044705 | houston | N | -0.049071 | -0.060351 | -0.050391 | -0.043897 | 0.043897 | houston | N | 0.043897 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.044705 | houston | N | -0.049071 | -0.060351 | -0.050391 | -0.043897 | 0.043897 | houston | N | 0.043897 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.044705 | houston | N | -0.049071 | -0.060351 | -0.050391 | -0.043897 | 0.043897 | houston | N | 0.043897 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.044705 | houston | N | -0.049071 | -0.060351 | -0.050391 | -0.043897 | 0.043897 | houston | N | 0.043897 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.044705 | houston | N | -0.049071 | -0.060351 | -0.050391 | -0.043897 | 0.043897 | houston | N | 0.043897 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.044705 | houston | N | -0.049071 | -0.060351 | -0.050391 | -0.043897 | 0.043897 | houston | N | 0.043897 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.044705 | houston | N | -0.049071 | -0.060351 | -0.050391 | -0.043897 | 0.043897 | houston | N | 0.043897 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.023997 | houston | N | -0.028363 | -0.039643 | -0.029683 | -0.023189 | 0.023189 | houston | N | 0.023189 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.023997 | houston | N | -0.028363 | -0.039643 | -0.029683 | -0.023189 | 0.023189 | houston | N | 0.023189 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.023997 | houston | N | -0.028363 | -0.039643 | -0.029683 | -0.023189 | 0.023189 | houston | N | 0.023189 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.023997 | houston | N | -0.028363 | -0.039643 | -0.029683 | -0.023189 | 0.023189 | houston | N | 0.023189 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.044403 | houston | N | -0.048769 | -0.060049 | -0.050089 | -0.043595 | 0.043595 | houston | N | 0.043595 | 0
48820 | SHELLG1_ | 1 | 71 | -0.061531 | houston | N | -0.065897 | -0.077177 | -0.067217 | -0.060723 | 0.060723 | houston | N | 0.060723 | 0
48821 | SHELLG2 | 2 | 72 | -0.061531 | houston | N | -0.065897 | -0.077177 | -0.067217 | -0.060723 | 0.060723 | houston | N | 0.060723 | 0
48822 | SHELLG3_ | 1 | 39 | -0.061531 | houston | N | -0.065897 | -0.077177 | -0.067217 | -0.060723 | 0.060723 | houston | N | 0.060723 | 0
48822 | SHELLG3_ | 2 | 30 | -0.061531 | houston | N | -0.065897 | -0.077177 | -0.067217 | -0.060723 | 0.060723 | houston | N | 0.060723 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.05407 | houston | N | -0.058436 | -0.069716 | -0.059756 | -0.053262 | 0.053262 | houston | N | 0.053262 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.05407 | houston | N | -0.058436 | -0.069716 | -0.059756 | -0.053262 | 0.053262 | houston | N | 0.053262 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.056902 | houston | N | -0.061268 | -0.072548 | -0.062588 | -0.056094 | 0.056094 | houston | N | 0.056094 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.05694 | houston | Y | -0.061306 | -0.072586 | -0.062626 | -0.056132 | 0.056132 | houston | N | 0.056132 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.056731 | houston | Y | -0.061097 | -0.072377 | -0.062417 | -0.055923 | 0.055923 | houston | N | 0.055923 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.055425 | houston | Y | -0.059791 | -0.071071 | -0.061111 | -0.054617 | 0.054617 | houston | N | 0.054617 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.060103 | houston | Y | -0.064469 | -0.075749 | -0.065789 | -0.059295 | 0.059295 | houston | N | 0.059295 | 0
48855 | SRB_GT21 | B2 | 12 | -0.056942 | houston | Y | -0.061308 | -0.072588 | -0.062628 | -0.056134 | 0.056134 | houston | N | 0.056134 | 0
48855 | SRB_GT21 | MB | 18 | -0.056942 | houston | Y | -0.061308 | -0.072588 | -0.062628 | -0.056134 | 0.056134 | houston | N | 0.056134 | 0
48865 | TECO_GT1 | 1 | 50 | -0.35953 | houston | Y | -0.36389 | -0.37517 | -0.36521 | -0.35872 | 0.35872 | houston | N | 0.35872 | 0
48873 | THW_ST3_ | 3 | 104 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.43845
48874 | THW_ST4_ | 4 | 104 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.43845
48875 | THW_3132 | A | 54 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.22766
48875 | THW_3132 | B | 53 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.22344
48877 | THW_3334 | C | 54 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.22766
48877 | THW_3334 | D | 57 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.2403
48879 | THW_4142 | E | 54 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.22766
48879 | THW_4142 | F | 54 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.22766
48881 | THW_4344 | G | 58 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.24452
48881 | THW_4344 | H | 58 | 0.003887 | houston | Y | -0.00047894 | -0.011759 | -0.001799 | 0.0046948 | 0.00047894 | North | Y | 0.0046948 | 0.24452
48883 | THW_GT1_ | B2 | 12 | -7.8e-05 | houston | Y | -0.0044439 | -0.015724 | -0.005764 | 0.00072981 | 0.00072981 | houston | N | 0.00072981 | 0
48885 | THW_5152 | A | 56 | 0.001008 | houston | Y | -0.0033579 | -0.014638 | -0.004678 | 0.0018158 | 0.0018158 | houston | N | 0.0018158 | 0
48885 | THW_5152 | B | 59 | 0.001008 | houston | Y | -0.0033579 | -0.014638 | -0.004678 | 0.0018158 | 0.0018158 | houston | N | 0.0018158 | 0
48886 | THW_5354 | C | 56 | 0.001008 | houston | Y | -0.0033579 | -0.014638 | -0.004678 | 0.0018158 | 0.0018158 | houston | N | 0.0018158 | 0
48886 | THW_5354 | D | 56 | 0.001008 | houston | Y | -0.0033579 | -0.014638 | -0.004678 | 0.0018158 | 0.0018158 | houston | N | 0.0018158 | 0
48887 | THW_5556 | E | 59 | 0.001008 | houston | Y | -0.0033579 | -0.014638 | -0.004678 | 0.0018158 | 0.0018158 | houston | N | 0.0018158 | 0
48887 | THW_5556 | F | 56 | 0.001008 | houston | Y | -0.0033579 | -0.014638 | -0.004678 | 0.0018158 | 0.0018158 | houston | N | 0.0018158 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.038104 | houston | Y | 0.033738 | 0.022458 | 0.032418 | 0.038912 | 0.022458 | south | Y | 0.038912 | 1.0859
48921 | WAP_GN1_ | 1 | 161 | 0.090029 | houston | Y | 0.085663 | 0.074383 | 0.084343 | 0.090837 | 0.074383 | south | Y | 0.090837 | 2.649
48922 | WAP_GN2_ | 2 | 166 | 0.090029 | houston | Y | 0.085663 | 0.074383 | 0.084343 | 0.090837 | 0.074383 | south | Y | 0.090837 | 2.7313
48923 | WAP_GN3_ | 3 | 248 | 0.090029 | houston | Y | 0.085663 | 0.074383 | 0.084343 | 0.090837 | 0.074383 | south | Y | 0.090837 | 4.0804
48924 | WAP_GN4_ | 4 | 546 | 0.090029 | houston | Y | 0.085663 | 0.074383 | 0.084343 | 0.090837 | 0.074383 | south | Y | 0.090837 | 8.9835
48925 | WAP_GN5_ | 5 | 643 | 0.090029 | houston | N | 0.085663 | 0.074383 | 0.084343 | 0.090837 | 0.074383 | south | Y | 0.090837 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.022463 | houston | Y | 0.018097 | 0.0068174 | 0.016777 | 0.023271 | 0.0068174 | south | Y | 0.023271 | 10.7112
48927 | WAP_GN7_ | 7 | 564 | 0.022463 | houston | Y | 0.018097 | 0.0068174 | 0.016777 | 0.023271 | 0.0068174 | south | Y | 0.023271 | 9.2797
48928 | WAP_GN8_ | 8 | 600 | 0.022463 | houston | Y | 0.018097 | 0.0068174 | 0.016777 | 0.023271 | 0.0068174 | south | Y | 0.023271 | 9.872
48929 | WAPGT21_ | B1 | 13 | 0.090029 | houston | Y | 0.085663 | 0.074383 | 0.084343 | 0.090837 | 0.074383 | south | Y | 0.090837 | 0.21389
48940 | WARVUE_G | G1 | 12 | -0.03325 | houston | Y | -0.037616 | -0.048896 | -0.038936 | -0.032442 | 0.032442 | houston | N | 0.032442 | 0
49803 | EXN_15GT | 1 | 34 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49826 | EXN938GT | 5 | 45.9 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49828 | EXN941GT | 10 | 17.7 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49829 | EXN942GT | 11 | 20.4 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49830 | EXN943GT | 12 | 19.9 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49831 | EXN944GT | 13 | 35 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49832 | EXN945GT | 9 | 18 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49837 | EXN_GT | 4 | 85.4 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49838 | EXN_14GT | 14 | 148 | -0.038526 | houston | N | -0.042892 | -0.054172 | -0.044212 | -0.037718 | 0.037718 | houston | N | 0.037718 | 0
49851 | DOW17000 | 37 | 62 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49858 | DOW38100 | 31 | 71.4 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49859 | DOW38200 | 33 | 45 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49860 | DOW38300 | 32 | 101 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49862 | DOW39100 | 36 | 86 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49863 | DOW39200 | 35 | 88 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49865 | DOW41000 | 41 | 50 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49866 | DOW42000 | 42 | 18 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49869 | DOW49000 | 45 | 94 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49870 | DOW61000 | 61 | 70 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49871 | DOW62000 | 62 | 63 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49872 | DOW63000 | 63 | 72 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49873 | DOW64000 | 64 | 64.8 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49876 | DOW65000 | 65 | 101 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49877 | DOW66000 | 66 | 97 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49878 | DOW67000 | 67 | 103 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49882 | DOW81000 | 81 | 76 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49884 | DOW82000 | 82 | 80 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49885 | DOW83000 | 83 | 80 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
49886 | DOW84000 | 84 | 171 | 0.015946 | houston | N | 0.01158 | 0.00030042 | 0.01026 | 0.016754 | 0.00030042 | south | Y | 0.016754 | 0
58909 | PEARSALL | 1 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58909 | PEARSALL | 2 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58909 | PEARSALL | 3 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58909 | PEARSALL | 4 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58909 | PEARSALL | 5 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58909 | PEARSALL | 6 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58919 | PEARSALL | 1 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58919 | PEARSALL | 2 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58919 | PEARSALL | 3 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58919 | PEARSALL | 4 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58919 | PEARSALL | 5 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58919 | PEARSALL | 6 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58929 | PEARSALL | 1 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58929 | PEARSALL | 2 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58929 | PEARSALL | 3 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58929 | PEARSALL | 4 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58929 | PEARSALL | 5 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58929 | PEARSALL | 6 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58949 | PEARSALL | 1 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58949 | PEARSALL | 2 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58949 | PEARSALL | 3 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58949 | PEARSALL | 4 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58949 | PEARSALL | 5 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
58949 | PEARSALL | 6 | 8.4 | 0.015871 | south | Y | 0.011505 | 0.00022542 | 0.010185 | 0.016679 | 0.00022542 | south | N | 0.00022542 | 0
60000 | DSKY2 | 1 | 76.5 | 0.006366 | west | Y | 0.0020001 | -0.0092796 | 0.00068002 | 0.0071738 | 0.00068002 | west | N | 0.00068002 | 0
60003 | KING_NE1 | 1 | 80 | 0.006177 | west | Y | 0.0018111 | -0.0094686 | 0.00049102 | 0.0069848 | 0.00049102 | west | N | 0.00049102 | 0
60005 | KING_SE1 | 1 | 40 | 0.006177 | west | Y | 0.0018111 | -0.0094686 | 0.00049102 | 0.0069848 | 0.00049102 | west | N | 0.00049102 | 0
60007 | KING_SW1 | 1 | 80 | 0.006147 | west | Y | 0.0017811 | -0.0094986 | 0.00046102 | 0.0069548 | 0.00046102 | west | N | 0.00046102 | 0
60016 | WOODWRD1 | 1 | 80 | 0.006184 | west | Y | 0.0018181 | -0.0094616 | 0.00049802 | 0.0069918 | 0.00049802 | west | N | 0.00049802 | 0
60017 | ORNNWP1 | 1 | 80 | 0.006341 | west | Y | 0.0019751 | -0.0093046 | 0.00065502 | 0.0071488 | 0.00065502 | west | N | 0.00065502 | 0
60018 | DSKY1 | 1 | 84 | 0.006392 | west | Y | 0.0020261 | -0.0092536 | 0.00070602 | 0.0071998 | 0.00070602 | west | N | 0.00070602 | 0
60019 | KING_NW1 | 1 | 80 | 0.006147 | west | Y | 0.0017811 | -0.0094986 | 0.00046102 | 0.0069548 | 0.00046102 | west | N | 0.00046102 | 0
60057 | CALLAHAN | 1 | 114 | 0.01524 | south | Y | 0.010874 | -0.00040558 | 0.009554 | 0.016048 | 0.00040558 | south | N | 0.00040558 | 0
60058 | BUFF_GAP | 1 | 120 | 0.005639 | west | Y | 0.0012731 | -0.010007 | -4.6985e-05 | 0.0064468 | 4.6985e-05 | west | N | 4.6985e-05 | 0
60060 | CIRELLO | 1 | 233 | 0.005639 | west | Y | 0.0012731 | -0.010007 | -4.6985e-05 | 0.0064468 | 4.6985e-05 | west | N | 4.6985e-05 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.005639 | west | Y | 0.0012731 | -0.010007 | -4.6985e-05 | 0.0064468 | 4.6985e-05 | west | N | 4.6985e-05 | 0
60066 | H_HOLLOW | 1 | 222 | 0.01524 | south | Y | 0.010874 | -0.00040558 | 0.009554 | 0.016048 | 0.00040558 | south | N | 0.00040558 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.01524 | south | Y | 0.010874 | -0.00040558 | 0.009554 | 0.016048 | 0.00040558 | south | N | 0.00040558 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.01524 | south | Y | 0.010874 | -0.00040558 | 0.009554 | 0.016048 | 0.00040558 | south | N | 0.00040558 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.01524 | south | Y | 0.010874 | -0.00040558 | 0.009554 | 0.016048 | 0.00040558 | south | N | 0.00040558 | 0
60074 | HORSH5 | 1 | 100 | 0.01524 | south | Y | 0.010874 | -0.00040558 | 0.009554 | 0.016048 | 0.00040558 | south | N | 0.00040558 | 0
60081 | WHRLWIND | 1 | 60 | 0.005496 | west | Y | 0.0011301 | -0.01015 | -0.00018998 | 0.0063038 | 0.00018998 | west | N | 0.00018998 | 0
60201 | RIO DRCS | F | 0 | 0.011423 | south | N | 0.0070571 | -0.0042226 | 0.005737 | 0.012231 | 0.0042226 | south | N | 0.0042226 | 0
60202 | FRIEND_R | F | 0 | 0.007212 | west | N | 0.0028461 | -0.0084336 | 0.001526 | 0.0080198 | 0.001526 | west | N | 0.001526 | 0
60203 | PRES0A | BT | 4.8 | 0.006034 | west | N | 0.0016681 | -0.0096116 | 0.00034802 | 0.0068418 | 0.00034802 | west | N | 0.00034802 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.00556 | west | Y | 0.0011941 | -0.010086 | -0.00012598 | 0.0063678 | 0.00012598 | west | N | 0.00012598 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.00556 | west | Y | 0.0011941 | -0.010086 | -0.00012598 | 0.0063678 | 0.00012598 | west | N | 0.00012598 | 0
71057 | L_SWEETW | W1 | 135 | 0.00556 | west | Y | 0.0011941 | -0.010086 | -0.00012598 | 0.0063678 | 0.00012598 | west | N | 0.00012598 | 0
71059 | L_SWEETW | W1 | 119 | 0.00556 | west | Y | 0.0011941 | -0.010086 | -0.00012598 | 0.0063678 | 0.00012598 | west | N | 0.00012598 | 0
71060 | L_SWEETW | W1 | 105 | 0.00556 | west | Y | 0.0011941 | -0.010086 | -0.00012598 | 0.0063678 | 0.00012598 | west | N | 0.00012598 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.00556 | west | Y | 0.0011941 | -0.010086 | -0.00012598 | 0.0063678 | 0.00012598 | west | N | 0.00012598 | 0
76031 | L_GASCCR | W1 | 150 | 0.005685 | west | Y | 0.0013191 | -0.0099606 | -9.8468e-07 | 0.0064928 | 9.8468e-07 | west | N | 9.8468e-07 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.005701 | west | Y | 0.0013351 | -0.0099446 | 1.5015e-05 | 0.0065088 | 1.5015e-05 | west | N | 1.5015e-05 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.005701 | west | Y | 0.0013351 | -0.0099446 | 1.5015e-05 | 0.0065088 | 1.5015e-05 | west | N | 1.5015e-05 | 0
76096 | L_CAPRSI | W1 | 186 | 0.005701 | west | Y | 0.0013351 | -0.0099446 | 1.5015e-05 | 0.0065088 | 1.5015e-05 | west | N | 1.5015e-05 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.005701 | west | Y | 0.0013351 | -0.0099446 | 1.5015e-05 | 0.0065088 | 1.5015e-05 | west | N | 1.5015e-05 | 0
80003 | MILHWYS | F | 0 | 0.017482 | south | N | 0.013116 | 0.0018364 | 0.011796 | 0.01829 | 0.0018364 | south | N | 0.0018364 | 0
80010 | EPLVT1 | F | 0 | 0.014331 | south | N | 0.0099651 | -0.0013146 | 0.008645 | 0.015139 | 0.0013146 | south | N | 0.0013146 | 0
80012 | LAR | F | 0 | 0.016388 | south | N | 0.012022 | 0.00074242 | 0.010702 | 0.017196 | 0.00074242 | south | N | 0.00074242 | 0
80051 | FORPVCM0 | 8 | 28 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
80053 | FOR69CG0 | 10 | 74 | 0.02018 | south | N | 0.015814 | 0.0045344 | 0.014494 | 0.020988 | 0.0045344 | south | N | 0.0045344 | 0
80080 | GWINDT11 | 1 | 94 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80080 | GWINDT11 | 2 | 41 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80080 | GWINDT11 | 3 | 38 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80080 | GWINDT11 | 4 | 19 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80081 | GWINDT21 | 1 | 94 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80081 | GWINDT21 | 2 | 36 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80081 | GWINDT21 | 3 | 43 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80081 | GWINDT21 | 4 | 22 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80137 | CSDR89 | 8 | 39 | 0.019609 | south | N | 0.015243 | 0.0039634 | 0.013923 | 0.020417 | 0.0039634 | south | N | 0.0039634 | 0
80137 | CSDR89 | 9 | 15 | 0.019609 | south | N | 0.015243 | 0.0039634 | 0.013923 | 0.020417 | 0.0039634 | south | N | 0.0039634 | 0
80138 | CSDR7 | 7 | 7 | 0.019609 | south | N | 0.015243 | 0.0039634 | 0.013923 | 0.020417 | 0.0039634 | south | N | 0.0039634 | 0
80139 | CSDR56 | 5 | 15 | 0.019609 | south | N | 0.015243 | 0.0039634 | 0.013923 | 0.020417 | 0.0039634 | south | N | 0.0039634 | 0
80139 | CSDR56 | 6 | 39 | 0.019609 | south | N | 0.015243 | 0.0039634 | 0.013923 | 0.020417 | 0.0039634 | south | N | 0.0039634 | 0
80140 | CSDR11 | 11 | 39 | 0.019609 | south | N | 0.015243 | 0.0039634 | 0.013923 | 0.020417 | 0.0039634 | south | N | 0.0039634 | 0
80180 | PNSCALT1 | 1 | 148 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80180 | PNSCALT1 | 2 | 50 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80181 | PNSCALT2 | 1 | 55 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80181 | PNSCALT2 | 2 | 50 | 0.017495 | south | Y | 0.013129 | 0.0018494 | 0.011809 | 0.018303 | 0.0018494 | south | N | 0.0018494 | 0
80223 | REYSHR G | 1 | 12 | 0.017803 | south | N | 0.013437 | 0.0021574 | 0.012117 | 0.018611 | 0.0021574 | south | N | 0.0021574 | 0
80224 | VISTRONG | 1 | 15 | 0.019464 | south | N | 0.015098 | 0.0038184 | 0.013778 | 0.020272 | 0.0038184 | south | N | 0.0038184 | 0
80225 | VISTRONG | 2 | 23 | 0.019464 | south | N | 0.015098 | 0.0038184 | 0.013778 | 0.020272 | 0.0038184 | south | N | 0.0038184 | 0
80226 | ALCOA G | 1 | 48 | 0.020056 | south | N | 0.01569 | 0.0044104 | 0.01437 | 0.020864 | 0.0044104 | south | N | 0.0044104 | 0
80227 | AIRCO G | 1 | 8 | 0.019468 | south | N | 0.015102 | 0.0038224 | 0.013782 | 0.020276 | 0.0038224 | south | N | 0.0038224 | 0
80261 | NBEC81A | 1 | 180 | 0.017667 | south | Y | 0.013301 | 0.0020214 | 0.011981 | 0.018475 | 0.0020214 | south | N | 0.0020214 | 0
80262 | NBEC91A | 1 | 180 | 0.01767 | south | Y | 0.013304 | 0.0020244 | 0.011984 | 0.018478 | 0.0020244 | south | N | 0.0020244 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.017638 | south | Y | 0.013272 | 0.0019924 | 0.011952 | 0.018446 | 0.0019924 | south | N | 0.0019924 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.017638 | south | Y | 0.013272 | 0.0019924 | 0.011952 | 0.018446 | 0.0019924 | south | N | 0.0019924 | 0
80265 | LARECU40 | 4 | 100 | 0.016388 | south | Y | 0.012022 | 0.00074242 | 0.010702 | 0.017196 | 0.00074242 | south | N | 0.00074242 | 0
80266 | LARECU50 | 5 | 100 | 0.016388 | south | Y | 0.012022 | 0.00074242 | 0.010702 | 0.017196 | 0.00074242 | south | N | 0.00074242 | 0
80291 | PAPALOTE | 1 | 25 | 0.017728 | south | Y | 0.013362 | 0.0020824 | 0.012042 | 0.018536 | 0.0020824 | south | N | 0.0020824 | 0
80291 | PAPALOTE | 2 | 25 | 0.017728 | south | Y | 0.013362 | 0.0020824 | 0.012042 | 0.018536 | 0.0020824 | south | N | 0.0020824 | 0
80291 | PAPALOTE | 3 | 25 | 0.017728 | south | Y | 0.013362 | 0.0020824 | 0.012042 | 0.018536 | 0.0020824 | south | N | 0.0020824 | 0
80291 | PAPALOTE | 4 | 16 | 0.017728 | south | Y | 0.013362 | 0.0020824 | 0.012042 | 0.018536 | 0.0020824 | south | N | 0.0020824 | 0
80294 | PAPALOTE | 5 | 25 | 0.017728 | south | Y | 0.013362 | 0.0020824 | 0.012042 | 0.018536 | 0.0020824 | south | N | 0.0020824 | 0
80294 | PAPALOTE | 6 | 25 | 0.017728 | south | Y | 0.013362 | 0.0020824 | 0.012042 | 0.018536 | 0.0020824 | south | N | 0.0020824 | 0
80294 | PAPALOTE | 7 | 25 | 0.017728 | south | Y | 0.013362 | 0.0020824 | 0.012042 | 0.018536 | 0.0020824 | south | N | 0.0020824 | 0
80294 | PAPALOTE | 8 | 15 | 0.017728 | south | Y | 0.013362 | 0.0020824 | 0.012042 | 0.018536 | 0.0020824 | south | N | 0.0020824 | 0
86104 | CID-138 | EQ | 0 | 0.016388 | south | N | 0.012022 | 0.00074242 | 0.010702 | 0.017196 | 0.00074242 | south | N | 0.00074242 | 0
86105 | CID-230 | EQ | 500 | 0.016388 | south | N | 0.012022 | 0.00074242 | 0.010702 | 0.017196 | 0.00074242 | south | N | 0.00074242 | 0
86106 | CUF-230 | EQ | 500 | 0.016388 | south | N | 0.012022 | 0.00074242 | 0.010702 | 0.017196 | 0.00074242 | south | N | 0.00074242 | 0
86107 | CUF-138 | EQ | 0 | 0.016388 | south | N | 0.012022 | 0.00074242 | 0.010702 | 0.017196 | 0.00074242 | south | N | 0.00074242 | 0
88198 | BEEVILLE | F | 0 | 0.017425 | south | N | 0.013059 | 0.0017794 | 0.011739 | 0.018233 | 0.0017794 | south | N | 0.0017794 | 0
88253 | HAMILTON | F | 0 | 0.013227 | south | N | 0.0088611 | -0.0024186 | 0.007541 | 0.014035 | 0.0024186 | south | N | 0.0024186 | 0
88299 | ZAPATA | F | 0 | 0.016818 | south | N | 0.012452 | 0.0011724 | 0.011132 | 0.017626 | 0.0011724 | south | N | 0.0011724 | 0
88508 | FALFURRI | F | 0 | 0.01729 | south | N | 0.012924 | 0.0016444 | 0.011604 | 0.018098 | 0.0016444 | south | N | 0.0016444 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:H_O_C - Knight 138kV 47150-47331 C:Bellaire - Garrot 138kV 47015-47320 & H_O_C - Garrot 138kV 47155-47660 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.090029 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 14.4947 | 161 | 0.085663 | 13.7918 | 161 | 13.7918
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.090029 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 14.9448 | 166 | 0.085663 | 14.2201 | 327 | 28.0118
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.090029 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 22.3272 | 248 | 0.085663 | 21.2444 | 575 | 49.2563
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.090029 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 49.1558 | 546 | 0.085663 | 46.772 |  |  | Weighted Shift Factors
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.090029 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 57.8886 | 0 | 0.085663 | 0 |  |  | North | 0.0043659
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.090029 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.1704 | 13 | 0.085663 | 1.1136 |  |  | Houston | -0.0073444
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.6339 | 0 | 0.04639 | 0 |  |  |  | 0.01171
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.6339 | 0 | 0.04639 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.04 | 0 | 0.04639 | 0 |  |  | Line Rating | 378
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.5578 | 0 | 0.04639 | 0 |  |  | Conc Gen | 575
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.038104 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.5149 | 66 | 0.033738 | 2.2267 |  |  | Weighted Imp. | 49.2563
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.6909 | 76 | 0.031041 | 2.3591 |  |  | PTDF | 0.085663
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.6909 | 76 | 0.031041 | 2.3591
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.7177 | 105 | 0.031041 | 3.2593 |  |  | Concentration | 7.3152
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.6201 | 74 | 0.031041 | 2.297
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.6201 | 74 | 0.031041 | 2.297
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.6115 | 102 | 0.031041 | 3.1662
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.032814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.3298 | 0 | 0.028448 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.032814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32814 | 0 | 0.028448 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 1.524 | 100 | 0.022584 | 2.2584
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.011423 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.018767 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.022768 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7112 | 0 | 0.018402 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.022768 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7112 | 0 | 0.018402 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.022768 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.5782 | 0 | 0.018402 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.022463 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 14.6234 | 651 | 0.018097 | 11.7812
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.022463 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 12.6691 | 564 | 0.018097 | 10.2067
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.022463 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 13.4778 | 600 | 0.018097 | 10.8582
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5942 | 0 | 0.015814 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6346 | 0 | 0.015814 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5942 | 0 | 0.015814 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6144 | 0 | 0.015814 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5821 | 0 | 0.015814 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5045 | 0 | 0.015814 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.92828 | 0 | 0.015814 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.56504 | 0 | 0.015814 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87985 | 0 | 0.015814 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4933 | 0 | 0.015814 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.020056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.96269 | 0 | 0.01569 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.54905 | 0 | 0.015243 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13726 | 0 | 0.015243 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.76475 | 0 | 0.015243 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29413 | 0 | 0.015243 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13726 | 0 | 0.015243 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29413 | 0 | 0.015243 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.76475 | 0 | 0.015243 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.76475 | 0 | 0.015243 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.007791 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1686 | 150 | 0.015135 | 2.2703
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.019468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15574 | 0 | 0.015102 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.019464 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29196 | 0 | 0.015098 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.019464 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44767 | 0 | 0.015098 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.019346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4123 | 0 | 0.01498 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.019255 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.42361 | 22 | 0.014889 | 0.32756
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.019255 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2118 | 11 | 0.014889 | 0.16378
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.019255 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2118 | 11 | 0.014889 | 0.16378
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.91846 | 47.7 | 0.014889 | 0.71021
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71821 | 37.3 | 0.014889 | 0.55536
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.88573 | 46 | 0.014889 | 0.6849
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.92424 | 48 | 0.014889 | 0.71467
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.019237 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.7701 | 144 | 0.014871 | 2.1414
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.019237 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6166 | 188 | 0.014871 | 2.7958
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.007212 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.014556 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.018783 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 25.0377 | 0 | 0.014417 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.018783 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 24.9438 | 0 | 0.014417 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006997 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.014341 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006997 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.014341 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.006902 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.014246 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.006902 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.4319 | 787 | 0.014246 | 11.2119
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.006761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7241 | 255 | 0.014105 | 3.5969
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.006761 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0074 | 149 | 0.014105 | 2.1017
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.006761 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0344 | 153 | 0.014105 | 2.1581
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.006638 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9957 | 150 | 0.013982 | 2.0974
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.006638 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.53104 | 80 | 0.013982 | 1.1186
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.006392 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.53693 | 84 | 0.013736 | 1.1539
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.006366 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.487 | 76.5 | 0.01371 | 1.0488
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.006358 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.09537 | 0 | 0.013702 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.006358 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.09537 | 0 | 0.013702 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006341 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.50728 | 80 | 0.013685 | 1.0948
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.017987 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.3138 | 629 | 0.013621 | 8.5676
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.006189 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.92835 | 150 | 0.013533 | 2.03
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.006189 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.92835 | 150 | 0.013533 | 2.03
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.006185 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.4948 | 80 | 0.013529 | 1.0824
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006184 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49472 | 80 | 0.013528 | 1.0823
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.006177 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.46327 | 75 | 0.013521 | 1.0141
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006177 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49416 | 80 | 0.013521 | 1.0817
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.006177 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.24708 | 40 | 0.013521 | 0.54086
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006147 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49176 | 80 | 0.013491 | 1.0793
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006147 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49176 | 80 | 0.013491 | 1.0793
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.8129 | 0 | 0.013437 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7239 | 0 | 0.013437 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 1.7803 | 0 | 0.013437 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.5814 | 0 | 0.013437 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.617 | 0 | 0.013437 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.261 | 0 | 0.013437 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.017803 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.21364 | 0 | 0.013437 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.006034 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.028963 | 0 | 0.013378 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 25 | 0.013362 | 0.33405
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 25 | 0.013362 | 0.33405
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 25 | 0.013362 | 0.33405
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.28365 | 16 | 0.013362 | 0.21379
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 25 | 0.013362 | 0.33405
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 25 | 0.013362 | 0.33405
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 25 | 0.013362 | 0.33405
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26592 | 15 | 0.013362 | 0.20043
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.01767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.9371 | 336 | 0.013304 | 4.4702
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.01767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1806 | 180 | 0.013304 | 2.3947
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.017669 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6203 | 0 | 0.013303 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.017669 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6256 | 0 | 0.013303 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.017669 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7034 | 0 | 0.013303 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.017667 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1801 | 180 | 0.013301 | 2.3942
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.017658 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44145 | 0 | 0.013292 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.017658 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44145 | 0 | 0.013292 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.017654 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67085 | 0 | 0.013288 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.017638 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.8911 | 334 | 0.013272 | 4.4329
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.017638 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.9969 | 340 | 0.013272 | 4.5125
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.017638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1748 | 180 | 0.013272 | 2.389
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.017638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1748 | 180 | 0.013272 | 2.389
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.017636 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67017 | 0 | 0.01327 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.017543 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.50875 | 0 | 0.013177 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6445 | 94 | 0.013129 | 1.2341
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.7173 | 41 | 0.013129 | 0.53829
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66481 | 38 | 0.013129 | 0.4989
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.33241 | 19 | 0.013129 | 0.24945
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6445 | 94 | 0.013129 | 1.2341
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.62982 | 36 | 0.013129 | 0.47265
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.75228 | 43 | 0.013129 | 0.56455
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.38489 | 22 | 0.013129 | 0.28884
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5893 | 148 | 0.013129 | 1.9431
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.87475 | 50 | 0.013129 | 0.65645
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.96222 | 55 | 0.013129 | 0.7221
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.87475 | 50 | 0.013129 | 0.65645
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.017482 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013116 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.017482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.66432 | 38 | 0.013116 | 0.49841
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.017482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.3374 | 19.3 | 0.013116 | 0.25314
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.017482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.26223 | 15 | 0.013116 | 0.19674
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.017482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.82165 | 47 | 0.013116 | 0.61645
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38023 | 66 | 0.013105 | 0.86496
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.37446 | 65 | 0.013105 | 0.85185
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38599 | 67 | 0.013105 | 0.87806
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38599 | 67 | 0.013105 | 0.87806
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38599 | 67 | 0.013105 | 0.87806
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.005761 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.013105 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.005761 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.013105 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.005757 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.2015 | 35 | 0.013101 | 0.45855
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.005757 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.17271 | 30 | 0.013101 | 0.39304
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.00575 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.97462 | 169.5 | 0.013094 | 2.2195
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.005745 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.85601 | 149 | 0.013089 | 1.9503
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.017447 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5124 | 144 | 0.013081 | 1.8837
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.017447 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5124 | 144 | 0.013081 | 1.8837
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.017447 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.9834 | 171 | 0.013081 | 2.2369
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.017446 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6113 | 207 | 0.01308 | 2.7076
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.017446 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.7805 | 216.7 | 0.01308 | 2.8344
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.017446 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2219 | 242 | 0.01308 | 3.1654
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.005722 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.037765 | 6.6 | 0.013066 | 0.086238
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.005722 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.19626 | 34.3 | 0.013066 | 0.44818
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.017425 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013059 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.64136 | 112.5 | 0.013045 | 1.4676
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8523 | 149.5 | 0.013045 | 1.9503
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0604 | 186 | 0.013045 | 2.4264
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2229 | 214.5 | 0.013045 | 2.7982
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.017398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5488 | 146.5 | 0.013032 | 1.9092
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.017398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5732 | 147.9 | 0.013032 | 1.9274
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.017398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0099 | 173 | 0.013032 | 2.2545
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.184 | 208.2 | 0.013031 | 2.7131
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.80812 | 142.1 | 0.013031 | 1.8518
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.75296 | 132.4 | 0.013031 | 1.7254
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.77343 | 136 | 0.013031 | 1.7723
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.83599 | 147 | 0.013031 | 1.9156
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1943 | 210 | 0.013031 | 2.7366
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.39802 | 70 | 0.01303 | 0.91213
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.39802 | 70 | 0.01303 | 0.91213
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.52766 | 92.8 | 0.01303 | 1.2092
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.45488 | 80 | 0.01303 | 1.0424
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.45488 | 80 | 0.01303 | 1.0424
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.65389 | 115 | 0.01303 | 1.4985
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.005685 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.85275 | 150 | 0.013029 | 1.9544
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.005684 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.32967 | 58 | 0.013028 | 0.75565
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.005683 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57114 | 100.5 | 0.013027 | 1.3093
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.005674 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2154 | 214.2 | 0.013018 | 2.7885
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.00567 | west | 8 | N | N | Nwest | Nwest | 1 | 0.14629 | 0 | 0.013014 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.005646 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67752 | 120 | 0.01299 | 1.5588
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.005645 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6774 | 120 | 0.012989 | 1.5587
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.005639 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67668 | 120 | 0.012983 | 1.558
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.005639 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3139 | 233 | 0.012983 | 3.0251
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.005639 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.95976 | 170.2 | 0.012983 | 2.2098
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.005638 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2686 | 225 | 0.012982 | 2.921
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0141 | 180 | 0.012978 | 2.3361
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0141 | 180 | 0.012978 | 2.3361
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.005633 | west | 8 | N | N | Nwest | Nwest | 1 | 0.39431 | 0 | 0.012977 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.005633 | west | 8 | N | N | Nwest | Nwest | 1 | 0.41346 | 0 | 0.012977 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.005633 | west | 8 | N | N | Nwest | Nwest | 1 | 0.39656 | 0 | 0.012977 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.84315 | 150 | 0.012965 | 1.9448
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2366 | 220 | 0.012965 | 2.8524
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1242 | 200 | 0.012965 | 2.5931
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6852 | 121.9 | 0.012965 | 1.5805
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.37039 | 66 | 0.012956 | 0.85512
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38723 | 69 | 0.012956 | 0.89399
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38723 | 69 | 0.012956 | 0.89399
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.376 | 67 | 0.012956 | 0.86808
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.376 | 67 | 0.012956 | 0.86808
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.36478 | 65 | 0.012956 | 0.84217
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.005609 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.35337 | 63 | 0.012953 | 0.81606
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.005606 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.79045 | 141 | 0.01295 | 1.826
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.005606 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67272 | 120 | 0.01295 | 1.554
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.005605 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.5549 | 99 | 0.012949 | 1.282
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.005605 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34191 | 61 | 0.012949 | 0.78991
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.005605 | west | 7 | N | N | Nwest | Nwest | 1 | 0.14012 | 0 | 0.012949 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.005605 | west | 7 | N | N | Nwest | Nwest | 1 | 0.25615 | 0 | 0.012949 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.005605 | west | 7 | N | N | Nwest | Nwest | 1 | 0.25615 | 0 | 0.012949 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.005595 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.46998 | 84 | 0.012939 | 1.0869
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.005591 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.83865 | 150 | 0.012935 | 1.9403
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.005591 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.56469 | 101 | 0.012935 | 1.3065
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005581 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69763 | 125 | 0.012925 | 1.6157
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005581 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69763 | 125 | 0.012925 | 1.6157
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.01729 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012924 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.2085 | 37.5 | 0.012904 | 0.48391
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.5977 | 107.5 | 0.012904 | 1.3872
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.7506 | 135 | 0.012904 | 1.7421
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.66164 | 119 | 0.012904 | 1.5356
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.5838 | 105 | 0.012904 | 1.355
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.44758 | 80.5 | 0.012904 | 1.0388
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.005554 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.33324 | 60 | 0.012898 | 0.7739
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1606 | 209 | 0.012897 | 2.6956
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.70245 | 126.5 | 0.012897 | 1.6315
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3827 | 249 | 0.012897 | 3.2115
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0939 | 197 | 0.012897 | 2.5408
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.005552 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8328 | 150 | 0.012896 | 1.9345
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.005496 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.32976 | 60 | 0.01284 | 0.77042
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.005415 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.166 | 400 | 0.012759 | 5.1038
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.005415 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2779 | 236 | 0.012759 | 3.0112
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.017101 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20521 | 0 | 0.012735 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.017101 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18811 | 0 | 0.012735 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.017101 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20521 | 0 | 0.012735 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.005368 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.88572 | 165 | 0.012712 | 2.0975
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.005328 | west | 4 | Y | N | Ywest | Nwest | 1 | 3.4616 | 649.7 | 0.012672 | 8.2333
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.005301 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.38697 | 73 | 0.012645 | 0.92311
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.005301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.63082 | 119 | 0.012645 | 1.5048
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.005301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.0867 | 205 | 0.012645 | 2.5923
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.005301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5407 | 102 | 0.012645 | 1.2898
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.005301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5089 | 96 | 0.012645 | 1.214
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.005265 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.2741 | 242 | 0.012609 | 3.0515
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.005249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.88183 | 168 | 0.012593 | 2.1157
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.005249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.47241 | 90 | 0.012593 | 1.1334
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.005227 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.62724 | 120 | 0.012571 | 1.5086
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.005219 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.9102 | 366 | 0.012563 | 4.5982
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.005216 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.062592 | 0 | 0.01256 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.005216 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.062592 | 0 | 0.01256 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.1042 | 20 | 0.012554 | 0.25109
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.1042 | 20 | 0.012554 | 0.25109
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.1042 | 20 | 0.012554 | 0.25109
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.08857 | 17 | 0.012554 | 0.21342
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36365 | 70 | 0.012539 | 0.87776
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35846 | 69 | 0.012539 | 0.86522
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35846 | 69 | 0.012539 | 0.86522
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35326 | 68 | 0.012539 | 0.85268
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.016895 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20274 | 0 | 0.012529 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.005147 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.092646 | 18 | 0.012491 | 0.22485
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.005147 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.092646 | 18 | 0.012491 | 0.22485
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.005147 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.19559 | 38 | 0.012491 | 0.47467
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.005124 | north | 3 | N | N | Nnorth | Nnorth | 1 | 5.9285 | 0 | 0.012468 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.005124 | north | 3 | N | N | Nnorth | Nnorth | 1 | 5.9336 | 0 | 0.012468 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.016818 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012452 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.005104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1091 | 217.3 | 0.012448 | 2.705
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.005104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0463 | 205 | 0.012448 | 2.5519
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.005104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3903 | 272.4 | 0.012448 | 3.3909
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.005097 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0398 | 204 | 0.012441 | 2.538
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.005097 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0245 | 201 | 0.012441 | 2.5007
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.005097 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2335 | 242 | 0.012441 | 3.0108
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.005086 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.01243 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.005051 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4547 | 288 | 0.012395 | 3.5699
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.005051 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7425 | 147 | 0.012395 | 1.8221
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.005051 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7425 | 147 | 0.012395 | 1.8221
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.131 | 224 | 0.012393 | 2.7761
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1411 | 226 | 0.012393 | 2.8009
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0704 | 212 | 0.012393 | 2.6274
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0653 | 211 | 0.012393 | 2.615
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.004968 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012312 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.004968 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012312 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.004968 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012312 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.004965 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0744 | 216.4 | 0.012309 | 2.6638
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.004965 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0729 | 216.1 | 0.012309 | 2.6601
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.00495 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.9552 | 395 | 0.012294 | 4.8563
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.00495 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1532 | 435 | 0.012294 | 5.3481
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.004938 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.55553 | 112.5 | 0.012282 | 1.3818
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.004933 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1459 | 435 | 0.012277 | 5.3407
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.004852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.29112 | 60 | 0.012196 | 0.73178
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.004852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.30568 | 63 | 0.012196 | 0.76837
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.004772 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.93531 | 196 | 0.012116 | 2.3748
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.004772 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.52969 | 111 | 0.012116 | 1.3449
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.004723 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012067 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.004704 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.012048 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.004702 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.55484 | 118 | 0.012046 | 1.4215
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.004702 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.54073 | 115 | 0.012046 | 1.3853
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.004702 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.6143 | 556 | 0.012046 | 6.6978
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.004685 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.1874 | 0 | 0.012029 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.004685 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.1874 | 0 | 0.012029 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.016388 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6388 | 100 | 0.012022 | 1.2022
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.016388 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6388 | 100 | 0.012022 | 1.2022
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.004672 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.79424 | 170 | 0.012016 | 2.0428
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.004672 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.4294 | 520 | 0.012016 | 6.2485
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.004656 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7227 | 370 | 0.012 | 4.4401
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.65184 | 0 | 0.012 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.6565 | 0 | 0.012 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4387 | 0 | 0.012 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.66581 | 0 | 0.012 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.67046 | 0 | 0.012 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4434 | 0 | 0.012 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.016365 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.4805 | 396 | 0.011999 | 4.7516
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74384 | 160 | 0.011993 | 1.9189
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.72524 | 156 | 0.011993 | 1.871
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9112 | 196 | 0.011993 | 2.3507
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.72524 | 156 | 0.011993 | 1.871
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.72989 | 157 | 0.011993 | 1.883
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9205 | 198 | 0.011993 | 2.3747
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.004644 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.3483 | 0 | 0.011988 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.004644 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.36966 | 0 | 0.011988 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.004644 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.41053 | 0 | 0.011988 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.004637 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.5874 | 558 | 0.011981 | 6.6856
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.004637 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6848 | 579 | 0.011981 | 6.9372
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.004637 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.7467 | 808 | 0.011981 | 9.681
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.18512 | 40 | 0.011972 | 0.4789
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.36561 | 79 | 0.011972 | 0.94582
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.49057 | 106 | 0.011972 | 1.2691
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.67569 | 146 | 0.011972 | 1.748
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.004628 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35173 | 76 | 0.011972 | 0.9099
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004624 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.011968 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004624 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.011968 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.004617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.09234 | 20 | 0.011961 | 0.23923
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.004617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.11542 | 25 | 0.011961 | 0.29903
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.004617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1893 | 41 | 0.011961 | 0.49042
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.004607 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7875 | 388 | 0.011951 | 4.6371
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.004607 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.3726 | 515 | 0.011951 | 6.155
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.73303 | 161 | 0.011897 | 1.9155
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74669 | 164 | 0.011897 | 1.9512
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74669 | 164 | 0.011897 | 1.9512
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8849 | 414 | 0.011897 | 4.9255
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.73759 | 162 | 0.011897 | 1.9274
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.73303 | 161 | 0.011897 | 1.9155
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74214 | 163 | 0.011897 | 1.9393
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8622 | 409 | 0.011897 | 4.866
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.004542 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.0174 | 224 | 0.011886 | 2.6626
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.004306 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.3802 | 785 | 0.01165 | 9.1456
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.004306 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4233 | 795 | 0.01165 | 9.2621
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.004306 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.3587 | 780 | 0.01165 | 9.0873
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015998 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.038395 | 0 | 0.011632 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015998 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.038395 | 0 | 0.011632 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.015992 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.38381 | 24 | 0.011626 | 0.27903
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.015992 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.38381 | 24 | 0.011626 | 0.27903
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.015992 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.36782 | 23 | 0.011626 | 0.2674
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.63211 | 0 | 0.011615 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.55523 | 0 | 0.011615 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.6193 | 0 | 0.011615 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7041 | 0 | 0.011615 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.004239 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.011583 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98865 | 0 | 0.01158 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1385 | 0 | 0.01158 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71757 | 0 | 0.01158 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6105 | 0 | 0.01158 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3714 | 0 | 0.01158 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4032 | 0 | 0.01158 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7973 | 0 | 0.01158 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28703 | 0 | 0.01158 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4989 | 0 | 0.01158 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1162 | 0 | 0.01158 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0046 | 0 | 0.01158 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1481 | 0 | 0.01158 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0333 | 0 | 0.01158 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6105 | 0 | 0.01158 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5468 | 0 | 0.01158 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6424 | 0 | 0.01158 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2119 | 0 | 0.01158 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2757 | 0 | 0.01158 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2757 | 0 | 0.01158 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.7268 | 0 | 0.01158 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.004235 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.21175 | 50 | 0.011579 | 0.57897
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.004231 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.77004 | 182 | 0.011575 | 2.1067
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.004231 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0478 | 484 | 0.011575 | 5.6025
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.015917 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.6907 | 546 | 0.011551 | 6.3069
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.015917 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.9377 | 750 | 0.011551 | 8.6633
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.01585 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4567 | 155 | 0.011484 | 1.78
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.01585 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6945 | 170 | 0.011484 | 1.9523
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.01585 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4567 | 155 | 0.011484 | 1.78
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.015807 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.3037 | 209 | 0.011441 | 2.3912
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.015807 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.4143 | 216 | 0.011441 | 2.4713
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72712 | 46 | 0.011441 | 0.52629
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.74293 | 47 | 0.011441 | 0.53773
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72712 | 46 | 0.011441 | 0.52629
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72712 | 46 | 0.011441 | 0.52629
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.01579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.91582 | 58 | 0.011424 | 0.6626
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.01579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.4053 | 89 | 0.011424 | 1.0167
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69476 | 44 | 0.011424 | 0.50266
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69476 | 44 | 0.011424 | 0.50266
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.67897 | 43 | 0.011424 | 0.49123
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.71055 | 45 | 0.011424 | 0.51408
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.015786 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.5038 | 412 | 0.01142 | 4.7051
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.015786 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.3144 | 400 | 0.01142 | 4.568
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.015773 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011407 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.015773 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011407 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.015773 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011407 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.015768 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.4176 | 407 | 0.011402 | 4.6406
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.015767 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.6852 | 424 | 0.011401 | 4.8341
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.015767 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.701 | 425 | 0.011401 | 4.8455
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3005 | 147 | 0.011284 | 1.6588
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1597 | 138 | 0.011284 | 1.5572
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.191 | 140 | 0.011284 | 1.5798
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3005 | 147 | 0.011284 | 1.6588
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.8483 | 182 | 0.011284 | 2.0537
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0987 | 198 | 0.011284 | 2.2342
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.003868 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.586 | 151.5 | 0.011212 | 1.6987
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.003868 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.5891 | 152.3 | 0.011212 | 1.7076
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.003868 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.68657 | 177.5 | 0.011212 | 1.9902
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.003852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.5805 | 150.7 | 0.011196 | 1.6873
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.003852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.58165 | 151 | 0.011196 | 1.6907
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.003852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.68334 | 177.4 | 0.011196 | 1.9862
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037279 | 0 | 0.011167 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037279 | 0 | 0.011167 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.015533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.043492 | 0 | 0.011167 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7761 | 50 | 0.011156 | 0.5578
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7761 | 50 | 0.011156 | 0.5578
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7761 | 50 | 0.011156 | 0.5578
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7761 | 50 | 0.011156 | 0.5578
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.003767 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.3167 | 615 | 0.011111 | 6.8335
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.003767 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2112 | 587 | 0.011111 | 6.5224
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.015471 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.061884 | 0 | 0.011105 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.01542 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.6769 | 433 | 0.011054 | 4.7864
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.015415 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 9.0024 | 584 | 0.011049 | 6.4527
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.015415 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 9.1719 | 595 | 0.011049 | 6.5742
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1871 | 142 | 0.011036 | 1.5671
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2333 | 145 | 0.011036 | 1.6002
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3257 | 151 | 0.011036 | 1.6664
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.4666 | 290 | 0.011036 | 3.2005
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7374 | 114 | 0.010874 | 1.2396
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3833 | 222 | 0.010874 | 2.414
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.8042 | 184 | 0.010874 | 2.0008
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.4138 | 224 | 0.010874 | 2.4358
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7526 | 115 | 0.010874 | 1.2505
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3894 | 223.9 | 0.010772 | 2.4119
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4061 | 225 | 0.010772 | 2.4237
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4 | 224.6 | 0.010772 | 2.4194
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4318 | 226.7 | 0.010772 | 2.442
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.014824 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.088944 | 0 | 0.010458 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.002771 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2916 | 827 | 0.010115 | 8.3654
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.002771 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2694 | 819 | 0.010115 | 8.2845
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.014331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0099651 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.014258 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8821 | 132 | 0.0098921 | 1.3058
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.014258 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.9106 | 134 | 0.0098921 | 1.3255
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.014258 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.6053 | 323 | 0.0098921 | 3.1951
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.014258 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2528 | 158 | 0.0098921 | 1.5629
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.014258 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2813 | 160 | 0.0098921 | 1.5827
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.014258 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4952 | 175 | 0.0098921 | 1.7311
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.014123 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084738 | 0 | 0.0097571 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.014068 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1454 | 152.5 | 0.0097021 | 1.4796
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.014068 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1032 | 149.5 | 0.0097021 | 1.4505
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.014068 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2722 | 232.6 | 0.0097021 | 2.2567
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.816 | 855 | 0.0094684 | 8.0955
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.816 | 855 | 0.0094684 | 8.0955
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32349 | 152.3 | 0.0094684 | 1.442
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32497 | 153 | 0.0094684 | 1.4487
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.66954 | 49 | 0.0092981 | 0.45561
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.62854 | 46 | 0.0092981 | 0.42771
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.62854 | 46 | 0.0092981 | 0.42771
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.64221 | 47 | 0.0092981 | 0.43701
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.013664 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1043 | 154 | 0.0092981 | 1.4319
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.013664 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0223 | 148 | 0.0092981 | 1.3761
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.65587 | 48 | 0.0092981 | 0.44631
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.65587 | 48 | 0.0092981 | 0.44631
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.01354 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.1974 | 310 | 0.0091741 | 2.844
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.01354 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.592 | 413 | 0.0091741 | 3.7889
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.013525 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1082 | 0 | 0.0091591 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.013525 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1082 | 0 | 0.0091591 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.56566 | 42 | 0.0091021 | 0.38229
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.59259 | 44 | 0.0091021 | 0.40049
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.59259 | 44 | 0.0091021 | 0.40049
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.633 | 47 | 0.0091021 | 0.4278
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.001654 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.079392 | 48 | 0.0089984 | 0.43192
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.001654 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.076084 | 46 | 0.0089984 | 0.41393
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.001654 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.17367 | 105 | 0.0089984 | 0.94483
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.013358 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46753 | 0 | 0.0089921 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.013358 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.45417 | 0 | 0.0089921 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.013358 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46753 | 0 | 0.0089921 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.013227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.43649 | 0 | 0.0088611 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.013227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.33067 | 0 | 0.0088611 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.013227 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0088611 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.013143 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23657 | 0 | 0.0087771 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.013143 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23657 | 0 | 0.0087771 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0087254 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0087254 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.001381 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.023477 | 17 | 0.0087254 | 0.14833
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0087254 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0087254 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.001354 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.043328 | 0 | 0.0086984 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.013048 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.5063 | 422 | 0.0086821 | 3.6638
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.013026 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.36473 | 0 | 0.0086601 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.013026 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37775 | 0 | 0.0086601 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.012591 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1725 | 0 | 0.0082251 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.012494 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22489 | 0 | 0.0081281 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.012494 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22489 | 0 | 0.0081281 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.012494 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18741 | 0 | 0.0081281 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.000472 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.21854 | 463 | 0.0078164 | 3.619
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0073444 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0073444 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.011213 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3802 | 569 | 0.0068471 | 3.896
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.011213 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.5148 | 581 | 0.0068471 | 3.9781
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.21788 | 0 | 0.0059314 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.22043 | 0 | 0.0059314 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.22043 | 0 | 0.0059314 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.53694 | 0 | 0.0059314 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.009882 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.45556 | 0 | 0.0055161 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.40425 | 104 | -0.00047894 | -0.04981
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.40425 | 104 | -0.00047894 | -0.04981
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2099 | 54 | -0.00047894 | -0.025863
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20601 | 53 | -0.00047894 | -0.025384
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2099 | 54 | -0.00047894 | -0.025863
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.22156 | 57 | -0.00047894 | -0.027299
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2099 | 54 | -0.00047894 | -0.025863
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2099 | 54 | -0.00047894 | -0.025863
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.22545 | 58 | -0.00047894 | -0.027778
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.22545 | 58 | -0.00047894 | -0.027778
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.002243 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.074019 | 0 | -0.0021229 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.056448 | 56 | -0.0033579 | -0.18804
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.059472 | 59 | -0.0033579 | -0.19812
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.056448 | 56 | -0.0033579 | -0.18804
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.056448 | 56 | -0.0033579 | -0.18804
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.059472 | 59 | -0.0033579 | -0.19812
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.056448 | 56 | -0.0033579 | -0.18804
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0043659 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0043659 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -7.8e-05 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.000936 | 12 | -0.0044439 | -0.053327
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1515 | 0 | -0.028363 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7435 | 0 | -0.028363 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6955 | 0 | -0.028363 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6955 | 0 | -0.028363 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.023997 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8875 | 0 | -0.028363 | 0
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.245 | 0 | -0.030441 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2085 | 0 | -0.030441 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1433 | 0 | -0.030441 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0194 | 0 | -0.030441 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.026854 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.6189 | 172 | -0.03122 | -5.3698
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.026854 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.6189 | 172 | -0.03122 | -5.3698
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.026854 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.6189 | 172 | -0.03122 | -5.3698
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3907 | 0 | -0.03127 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2266 | 0 | -0.03127 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2374 | 0 | -0.03127 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2239 | 0 | -0.03127 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2372 | 0 | -0.03127 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.031172 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -23.1608 | 743 | -0.035538 | -26.4047
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.03325 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.399 | 12 | -0.037616 | -0.45139
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.03515 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17575 | 0 | -0.039516 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.03515 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73815 | 0 | -0.039516 | 0
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3099 | 0 | -0.042892 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3369 | 0 | -0.042892 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2598 | 0 | -0.042892 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7683 | 0 | -0.042892 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68191 | 0 | -0.042892 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78593 | 0 | -0.042892 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76667 | 0 | -0.042892 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3484 | 0 | -0.042892 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69347 | 0 | -0.042892 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2901 | 0 | -0.042892 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.7018 | 0 | -0.042892 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.039014 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -28.6753 | 735 | -0.04338 | -31.8843
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.042987 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -17.1088 | 398 | -0.047353 | -18.8465
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.044403 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.9713 | 0 | -0.048769 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.4625 | 0 | -0.048858 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1333 | 0 | -0.048858 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.5693 | 0 | -0.048858 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.5382 | 0 | -0.048858 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.044497 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4239 | 0 | -0.048863 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.044497 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3349 | 0 | -0.048863 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1619 | 0 | -0.049025 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9788 | 0 | -0.049025 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3669 | 0 | -0.049025 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8418 | 0 | -0.049025 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8552 | 0 | -0.049025 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8016 | 0 | -0.049025 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2873 | 0 | -0.049025 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.8968 | 0 | -0.049025 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7864 | 0 | -0.049025 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9058 | 0 | -0.049071 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9505 | 0 | -0.049071 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1294 | 0 | -0.049071 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8164 | 0 | -0.049071 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7717 | 0 | -0.049071 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6493 | 0 | -0.049071 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6376 | 0 | -0.049071 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.048372 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.052738 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.4816 | 0 | -0.057929 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2138 | 0 | -0.057929 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.4816 | 0 | -0.057929 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.4816 | 0 | -0.057929 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.05407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2175 | 0 | -0.058436 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.05407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3256 | 0 | -0.058436 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2974 | 42 | -0.059066 | -2.4808
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2974 | 42 | -0.059066 | -2.4808
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0786 | 38 | -0.059066 | -2.2445
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0786 | 38 | -0.059066 | -2.2445
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.055425 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.8055 | 213 | -0.059791 | -12.7355
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0956 | 0 | -0.060362 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9052 | 0 | -0.060362 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8717 | 0 | -0.060362 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0518 | 0 | -0.060362 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68315 | 0 | -0.060362 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.056731 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.5875 | 169 | -0.061097 | -10.3254
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.056902 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92181 | 0 | -0.061268 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.05694 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.3951 | 165 | -0.061306 | -10.1155
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.056942 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6833 | 12 | -0.061308 | -0.7357
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.056942 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.061308 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7117 | 0 | -0.062362 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6653 | 0 | -0.062362 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7905 | 0 | -0.062362 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2685 | 0 | -0.062362 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.7026 | 46 | -0.063119 | -2.9035
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.7026 | 46 | -0.063119 | -2.9035
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.7026 | 46 | -0.063119 | -2.9035
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.2314 | 55 | -0.063119 | -3.4715
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.2314 | 55 | -0.063119 | -3.4715
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.1727 | 54 | -0.063119 | -3.4084
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.060103 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.7035 | 228 | -0.064469 | -14.6989
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3687 | 0 | -0.065897 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4302 | 0 | -0.065897 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3997 | 0 | -0.065897 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8459 | 0 | -0.065897 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.061627 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1569 | 0 | -0.065993 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.064213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5677 | 0 | -0.068579 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.064213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1803 | 0 | -0.068579 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.068536 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.3365 | 0 | -0.072902 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.068536 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.8698 | 0 | -0.072902 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.068536 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.7602 | 0 | -0.072902 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.072883 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6088 | 0 | -0.077249 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.072883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.8392 | 0 | -0.077249 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.074624 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1489 | 0 | -0.07899 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.35953 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -17.9763 | 50 | -0.36389 | -18.1946

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:H_O_C - Knight 138kV 47150-47331 C:Bellaire - Garrot 138kV 47015-47320 & H_O_C - Garrot 138kV 47155-47660 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.35953 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -17.9763 | 50 | -0.36389 | -18.1946 | 50 | 18.1946
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.074624 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1489 | 0 | -0.07899 | 0 | 50 | 18.1946
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.072883 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6088 | 0 | -0.077249 | 0 | 50 | 18.1946
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.072883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.8392 | 0 | -0.077249 | 0 | 50 | 18.1946 | Weighted Shift Factors
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.068536 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.3365 | 0 | -0.072902 | 0 | 50 | 18.1946 | North | 0.0043659
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.068536 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.8698 | 0 | -0.072902 | 0 | 50 | 18.1946 | Houston | -0.0073444
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.068536 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.7602 | 0 | -0.072902 | 0 | 50 | 18.1946 |  | 0.01171
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.064213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5677 | 0 | -0.068579 | 0 | 50 | 18.1946
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.064213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1803 | 0 | -0.068579 | 0 | 50 | 18.1946 | Line Rating | 378
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.061627 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1569 | 0 | -0.065993 | 0 | 50 | 18.1946 | Conc Gen | 592
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3687 | 0 | -0.065897 | 0 | 50 | 18.1946 | Weighted Imp. | 52.6911
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4302 | 0 | -0.065897 | 0 | 50 | 18.1946 | PTDF | 0.089005
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3997 | 0 | -0.065897 | 0 | 50 | 18.1946
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.061531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8459 | 0 | -0.065897 | 0 | 50 | 18.1946 | Concentration | 7.6006
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.060103 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.7035 | 228 | -0.064469 | -14.6989 | 278 | 32.8935
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.7026 | 46 | -0.063119 | -2.9035 | 324 | 35.797
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.7026 | 46 | -0.063119 | -2.9035 | 370 | 38.7005
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.7026 | 46 | -0.063119 | -2.9035 | 416 | 41.6039
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.2314 | 55 | -0.063119 | -3.4715 | 471 | 45.0755
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.2314 | 55 | -0.063119 | -3.4715 | 526 | 48.547
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.058753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.1727 | 54 | -0.063119 | -3.4084 | 580 | 51.9554
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7117 | 0 | -0.062362 | 0 | 580 | 51.9554
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6653 | 0 | -0.062362 | 0 | 580 | 51.9554
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7905 | 0 | -0.062362 | 0 | 580 | 51.9554
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.057996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2685 | 0 | -0.062362 | 0 | 580 | 51.9554
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.056942 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6833 | 12 | -0.061308 | -0.7357 | 592 | 52.6911
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.056942 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.061308 | 0 | 592 | 52.6911
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.05694 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.3951 | 165 | -0.061306 | -10.1155
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.056902 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92181 | 0 | -0.061268 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.056731 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.5875 | 169 | -0.061097 | -10.3254
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0956 | 0 | -0.060362 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9052 | 0 | -0.060362 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8717 | 0 | -0.060362 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0518 | 0 | -0.060362 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.055996 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68315 | 0 | -0.060362 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.055425 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.8055 | 213 | -0.059791 | -12.7355
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2974 | 42 | -0.059066 | -2.4808
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2974 | 42 | -0.059066 | -2.4808
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0786 | 38 | -0.059066 | -2.2445
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.0547 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0786 | 38 | -0.059066 | -2.2445
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.05407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2175 | 0 | -0.058436 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.05407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3256 | 0 | -0.058436 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.4816 | 0 | -0.057929 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2138 | 0 | -0.057929 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.4816 | 0 | -0.057929 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.053563 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.4816 | 0 | -0.057929 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.048372 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.052738 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9058 | 0 | -0.049071 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9505 | 0 | -0.049071 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1294 | 0 | -0.049071 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8164 | 0 | -0.049071 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7717 | 0 | -0.049071 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6493 | 0 | -0.049071 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.044705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6376 | 0 | -0.049071 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1619 | 0 | -0.049025 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9788 | 0 | -0.049025 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3669 | 0 | -0.049025 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8418 | 0 | -0.049025 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8552 | 0 | -0.049025 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8016 | 0 | -0.049025 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2873 | 0 | -0.049025 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.044659 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.8968 | 0 | -0.049025 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.044659 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7864 | 0 | -0.049025 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.044497 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4239 | 0 | -0.048863 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.044497 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3349 | 0 | -0.048863 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.4625 | 0 | -0.048858 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1333 | 0 | -0.048858 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.5693 | 0 | -0.048858 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.044492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.5382 | 0 | -0.048858 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.044403 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.9713 | 0 | -0.048769 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.042987 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -17.1088 | 398 | -0.047353 | -18.8465
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.039014 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -28.6753 | 735 | -0.04338 | -31.8843
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3099 | 0 | -0.042892 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3369 | 0 | -0.042892 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2598 | 0 | -0.042892 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7683 | 0 | -0.042892 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68191 | 0 | -0.042892 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78593 | 0 | -0.042892 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76667 | 0 | -0.042892 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3484 | 0 | -0.042892 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69347 | 0 | -0.042892 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2901 | 0 | -0.042892 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.038526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.7018 | 0 | -0.042892 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.03515 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17575 | 0 | -0.039516 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.03515 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73815 | 0 | -0.039516 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.03325 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.399 | 0 | -0.037616 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.031172 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -23.1608 | 743 | -0.035538 | -26.4047
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3907 | 0 | -0.03127 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2266 | 0 | -0.03127 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2374 | 0 | -0.03127 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2239 | 0 | -0.03127 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.026904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2372 | 0 | -0.03127 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.026854 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.6189 | 172 | -0.03122 | -5.3698
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.026854 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.6189 | 172 | -0.03122 | -5.3698
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.026854 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.6189 | 172 | -0.03122 | -5.3698
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.245 | 0 | -0.030441 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2085 | 0 | -0.030441 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1433 | 0 | -0.030441 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.026075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0194 | 0 | -0.030441 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1515 | 0 | -0.028363 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7435 | 0 | -0.028363 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6955 | 0 | -0.028363 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.023997 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6955 | 0 | -0.028363 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.023997 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8875 | 0 | -0.028363 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -7.8e-05 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.000936 | 12 | -0.0044439 | -0.053327
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0043659 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0043659 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0043659 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.056448 | 56 | -0.0033579 | -0.18804
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.059472 | 59 | -0.0033579 | -0.19812
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.056448 | 56 | -0.0033579 | -0.18804
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.056448 | 56 | -0.0033579 | -0.18804
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.059472 | 59 | -0.0033579 | -0.19812
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.001008 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.056448 | 56 | -0.0033579 | -0.18804
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.002243 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.074019 | 0 | -0.0021229 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.40425 | 104 | -0.00047894 | -0.04981
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.40425 | 104 | -0.00047894 | -0.04981
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2099 | 54 | -0.00047894 | -0.025863
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20601 | 53 | -0.00047894 | -0.025384
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2099 | 54 | -0.00047894 | -0.025863
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.22156 | 57 | -0.00047894 | -0.027299
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2099 | 54 | -0.00047894 | -0.025863
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2099 | 54 | -0.00047894 | -0.025863
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.22545 | 58 | -0.00047894 | -0.027778
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.003887 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.22545 | 58 | -0.00047894 | -0.027778
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.009882 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.45556 | 0 | 0.0055161 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.21788 | 0 | 0.0059314 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.22043 | 0 | 0.0059314 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.22043 | 0 | 0.0059314 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.001413 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.53694 | 0 | 0.0059314 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.011213 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3802 | 0 | 0.0068471 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.011213 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.5148 | 0 | 0.0068471 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0073444 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0073444 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.000472 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.21854 | 0 | 0.0078164 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.012494 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22489 | 0 | 0.0081281 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.012494 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22489 | 0 | 0.0081281 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.012494 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18741 | 0 | 0.0081281 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.012591 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1725 | 0 | 0.0082251 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.013026 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.36473 | 0 | 0.0086601 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.013026 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37775 | 0 | 0.0086601 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.013048 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.5063 | 422 | 0.0086821 | 3.6638
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.001354 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.043328 | 0 | 0.0086984 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0087254 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0087254 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.001381 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.023477 | 17 | 0.0087254 | 0.14833
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0087254 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.001381 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0087254 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.013143 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23657 | 0 | 0.0087771 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.013143 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23657 | 0 | 0.0087771 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.013227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.43649 | 0 | 0.0088611 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.013227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.33067 | 0 | 0.0088611 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.013227 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0088611 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.013358 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46753 | 0 | 0.0089921 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.013358 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.45417 | 0 | 0.0089921 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.013358 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46753 | 0 | 0.0089921 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.001654 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.079392 | 48 | 0.0089984 | 0.43192
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.001654 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.076084 | 46 | 0.0089984 | 0.41393
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.001654 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.17367 | 105 | 0.0089984 | 0.94483
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.56566 | 42 | 0.0091021 | 0.38229
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.59259 | 44 | 0.0091021 | 0.40049
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.59259 | 44 | 0.0091021 | 0.40049
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.013468 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.633 | 47 | 0.0091021 | 0.4278
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.013525 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1082 | 0 | 0.0091591 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.013525 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1082 | 0 | 0.0091591 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.01354 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.1974 | 310 | 0.0091741 | 2.844
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.01354 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.592 | 413 | 0.0091741 | 3.7889
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.66954 | 49 | 0.0092981 | 0.45561
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.62854 | 46 | 0.0092981 | 0.42771
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.62854 | 46 | 0.0092981 | 0.42771
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.64221 | 47 | 0.0092981 | 0.43701
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.013664 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1043 | 154 | 0.0092981 | 1.4319
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.013664 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0223 | 148 | 0.0092981 | 1.3761
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.65587 | 48 | 0.0092981 | 0.44631
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.013664 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.65587 | 48 | 0.0092981 | 0.44631
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.816 | 0 | 0.0094684 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.816 | 0 | 0.0094684 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32349 | 0 | 0.0094684 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.002124 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32497 | 0 | 0.0094684 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.014068 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1454 | 152.5 | 0.0097021 | 1.4796
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.014068 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1032 | 149.5 | 0.0097021 | 1.4505
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.014068 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2722 | 232.6 | 0.0097021 | 2.2567
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.014123 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084738 | 0 | 0.0097571 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.014258 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2528 | 158 | 0.0098921 | 1.5629
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.014258 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2813 | 160 | 0.0098921 | 1.5827
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.014258 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4952 | 175 | 0.0098921 | 1.7311
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.014258 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8821 | 132 | 0.0098921 | 1.3058
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.014258 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.9106 | 134 | 0.0098921 | 1.3255
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.014258 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.6053 | 323 | 0.0098921 | 3.1951
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.014331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0099651 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.002771 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2916 | 0 | 0.010115 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.002771 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2694 | 0 | 0.010115 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.014824 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.088944 | 0 | 0.010458 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3894 | 223.9 | 0.010772 | 2.4119
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4061 | 225 | 0.010772 | 2.4237
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4 | 224.6 | 0.010772 | 2.4194
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.015138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4318 | 226.7 | 0.010772 | 2.442
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7374 | 0 | 0.010874 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3833 | 0 | 0.010874 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.8042 | 0 | 0.010874 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.4138 | 0 | 0.010874 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7526 | 0 | 0.010874 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1871 | 142 | 0.011036 | 1.5671
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2333 | 145 | 0.011036 | 1.6002
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3257 | 151 | 0.011036 | 1.6664
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.015402 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.4666 | 290 | 0.011036 | 3.2005
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.015415 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 9.0024 | 0 | 0.011049 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.015415 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 9.1719 | 0 | 0.011049 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.01542 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.6769 | 0 | 0.011054 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.015471 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.061884 | 0 | 0.011105 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.003767 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.3167 | 0 | 0.011111 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.003767 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.2112 | 0 | 0.011111 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7761 | 50 | 0.011156 | 0.5578
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7761 | 50 | 0.011156 | 0.5578
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7761 | 50 | 0.011156 | 0.5578
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.015522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.7761 | 50 | 0.011156 | 0.5578
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037279 | 0 | 0.011167 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037279 | 0 | 0.011167 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.015533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.043492 | 0 | 0.011167 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.003852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.5805 | 150.7 | 0.011196 | 1.6873
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.003852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.58165 | 151 | 0.011196 | 1.6907
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.003852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.68334 | 177.4 | 0.011196 | 1.9862
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.003868 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.586 | 151.5 | 0.011212 | 1.6987
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.003868 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.5891 | 152.3 | 0.011212 | 1.7076
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.003868 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.68657 | 177.5 | 0.011212 | 1.9902
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3005 | 147 | 0.011284 | 1.6588
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1597 | 138 | 0.011284 | 1.5572
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.191 | 140 | 0.011284 | 1.5798
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3005 | 147 | 0.011284 | 1.6588
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.8483 | 182 | 0.011284 | 2.0537
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.01565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0987 | 198 | 0.011284 | 2.2342
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.015767 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.6852 | 0 | 0.011401 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.015767 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.701 | 0 | 0.011401 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.015768 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.4176 | 407 | 0.011402 | 4.6406
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.015773 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011407 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.015773 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011407 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.015773 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.011407 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.015786 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.5038 | 412 | 0.01142 | 4.7051
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.015786 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.3144 | 400 | 0.01142 | 4.568
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.01579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.91582 | 58 | 0.011424 | 0.6626
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.01579 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.4053 | 89 | 0.011424 | 1.0167
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69476 | 44 | 0.011424 | 0.50266
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69476 | 44 | 0.011424 | 0.50266
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.67897 | 43 | 0.011424 | 0.49123
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.01579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.71055 | 45 | 0.011424 | 0.51408
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.015807 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.3037 | 209 | 0.011441 | 2.3912
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.015807 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.4143 | 216 | 0.011441 | 2.4713
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72712 | 46 | 0.011441 | 0.52629
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.74293 | 47 | 0.011441 | 0.53773
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72712 | 46 | 0.011441 | 0.52629
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.015807 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72712 | 46 | 0.011441 | 0.52629
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.01585 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4567 | 155 | 0.011484 | 1.78
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.01585 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6945 | 170 | 0.011484 | 1.9523
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.01585 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4567 | 155 | 0.011484 | 1.78
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015871 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13332 | 8.4 | 0.011505 | 0.096643
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.015917 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.6907 | 0 | 0.011551 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.015917 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.9377 | 0 | 0.011551 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.004231 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.77004 | 182 | 0.011575 | 2.1067
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.004231 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0478 | 484 | 0.011575 | 5.6025
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.004235 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.21175 | 0 | 0.011579 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98865 | 0 | 0.01158 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1385 | 0 | 0.01158 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71757 | 0 | 0.01158 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6105 | 0 | 0.01158 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3714 | 0 | 0.01158 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4032 | 0 | 0.01158 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7973 | 0 | 0.01158 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28703 | 0 | 0.01158 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4989 | 0 | 0.01158 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1162 | 0 | 0.01158 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0046 | 0 | 0.01158 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1481 | 0 | 0.01158 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0333 | 0 | 0.01158 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6105 | 0 | 0.01158 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5468 | 0 | 0.01158 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6424 | 0 | 0.01158 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2119 | 0 | 0.01158 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2757 | 0 | 0.01158 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2757 | 0 | 0.01158 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.015946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.7268 | 0 | 0.01158 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.004239 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.011583 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.63211 | 0 | 0.011615 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.55523 | 0 | 0.011615 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.6193 | 0 | 0.011615 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.004271 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7041 | 0 | 0.011615 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.015992 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.38381 | 24 | 0.011626 | 0.27903
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.015992 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.38381 | 24 | 0.011626 | 0.27903
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.015992 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.36782 | 23 | 0.011626 | 0.2674
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015998 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.038395 | 0 | 0.011632 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015998 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.038395 | 0 | 0.011632 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.004306 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.3802 | 0 | 0.01165 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.004306 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4233 | 0 | 0.01165 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.004306 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.3587 | 0 | 0.01165 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.004542 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.0174 | 224 | 0.011886 | 2.6626
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.73303 | 161 | 0.011897 | 1.9155
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74669 | 164 | 0.011897 | 1.9512
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74669 | 164 | 0.011897 | 1.9512
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8849 | 414 | 0.011897 | 4.9255
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.73759 | 162 | 0.011897 | 1.9274
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.73303 | 161 | 0.011897 | 1.9155
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74214 | 163 | 0.011897 | 1.9393
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.004553 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8622 | 409 | 0.011897 | 4.866
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.004607 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7875 | 388 | 0.011951 | 4.6371
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.004607 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.3726 | 515 | 0.011951 | 6.155
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.004617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.09234 | 20 | 0.011961 | 0.23923
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.004617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.11542 | 25 | 0.011961 | 0.29903
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.004617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1893 | 41 | 0.011961 | 0.49042
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004624 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.011968 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004624 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.011968 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.36561 | 79 | 0.011972 | 0.94582
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.49057 | 106 | 0.011972 | 1.2691
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.67569 | 146 | 0.011972 | 1.748
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.004628 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35173 | 76 | 0.011972 | 0.9099
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.004628 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.18512 | 40 | 0.011972 | 0.4789
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.004637 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.5874 | 0 | 0.011981 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.004637 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6848 | 0 | 0.011981 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.004637 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.7467 | 0 | 0.011981 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.004644 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.3483 | 0 | 0.011988 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.004644 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.36966 | 0 | 0.011988 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.004644 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.41053 | 0 | 0.011988 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74384 | 160 | 0.011993 | 1.9189
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.72524 | 156 | 0.011993 | 1.871
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9112 | 196 | 0.011993 | 2.3507
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.72524 | 156 | 0.011993 | 1.871
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.72989 | 157 | 0.011993 | 1.883
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.004649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9205 | 198 | 0.011993 | 2.3747
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.016365 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.4805 | 0 | 0.011999 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.004656 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7227 | 370 | 0.012 | 4.4401
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.65184 | 0 | 0.012 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.6565 | 0 | 0.012 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4387 | 0 | 0.012 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.66581 | 0 | 0.012 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.67046 | 0 | 0.012 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.004656 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4434 | 0 | 0.012 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.004672 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.79424 | 170 | 0.012016 | 2.0428
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.004672 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.4294 | 520 | 0.012016 | 6.2485
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.016388 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6388 | 100 | 0.012022 | 1.2022
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.016388 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6388 | 100 | 0.012022 | 1.2022
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.016388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012022 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.004685 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.1874 | 0 | 0.012029 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.004685 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.1874 | 0 | 0.012029 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.004702 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.55484 | 118 | 0.012046 | 1.4215
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.004702 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.54073 | 115 | 0.012046 | 1.3853
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.004702 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.6143 | 556 | 0.012046 | 6.6978
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.004704 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.012048 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.004723 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012067 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.004772 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.93531 | 196 | 0.012116 | 2.3748
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.004772 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.52969 | 111 | 0.012116 | 1.3449
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.004852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.29112 | 60 | 0.012196 | 0.73178
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.004852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.30568 | 63 | 0.012196 | 0.76837
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.004933 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1459 | 435 | 0.012277 | 5.3407
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.004938 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.55553 | 0 | 0.012282 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.00495 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.9552 | 395 | 0.012294 | 4.8563
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.00495 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1532 | 435 | 0.012294 | 5.3481
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.004965 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0744 | 216.4 | 0.012309 | 2.6638
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.004965 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0729 | 216.1 | 0.012309 | 2.6601
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.004968 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012312 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.004968 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012312 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.004968 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012312 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.131 | 224 | 0.012393 | 2.7761
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1411 | 226 | 0.012393 | 2.8009
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0704 | 212 | 0.012393 | 2.6274
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.005049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0653 | 211 | 0.012393 | 2.615
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.005051 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4547 | 288 | 0.012395 | 3.5699
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.005051 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7425 | 147 | 0.012395 | 1.8221
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.005051 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7425 | 147 | 0.012395 | 1.8221
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.005086 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.01243 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.005097 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0398 | 204 | 0.012441 | 2.538
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.005097 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0245 | 201 | 0.012441 | 2.5007
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.005097 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2335 | 242 | 0.012441 | 3.0108
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.005104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1091 | 217.3 | 0.012448 | 2.705
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.005104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0463 | 205 | 0.012448 | 2.5519
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.005104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3903 | 272.4 | 0.012448 | 3.3909
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.016818 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012452 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.005124 | north | 3 | N | N | Nnorth | Nnorth | 1 | 5.9285 | 0 | 0.012468 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.005124 | north | 3 | N | N | Nnorth | Nnorth | 1 | 5.9336 | 0 | 0.012468 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.005147 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.092646 | 18 | 0.012491 | 0.22485
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.005147 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.092646 | 18 | 0.012491 | 0.22485
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.005147 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.19559 | 38 | 0.012491 | 0.47467
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.016895 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20274 | 0 | 0.012529 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36365 | 70 | 0.012539 | 0.87776
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35846 | 69 | 0.012539 | 0.86522
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35846 | 69 | 0.012539 | 0.86522
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.005195 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35326 | 68 | 0.012539 | 0.85268
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.1042 | 20 | 0.012554 | 0.25109
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.1042 | 20 | 0.012554 | 0.25109
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.1042 | 20 | 0.012554 | 0.25109
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.00521 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.08857 | 17 | 0.012554 | 0.21342
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.005216 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.062592 | 0 | 0.01256 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.005216 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.062592 | 0 | 0.01256 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.005219 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.9102 | 366 | 0.012563 | 4.5982
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.005227 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.62724 | 0 | 0.012571 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.005249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.88183 | 168 | 0.012593 | 2.1157
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.005249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.47241 | 90 | 0.012593 | 1.1334
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.005265 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.2741 | 242 | 0.012609 | 3.0515
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.005301 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.38697 | 73 | 0.012645 | 0.92311
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.005301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.63082 | 119 | 0.012645 | 1.5048
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.005301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.0867 | 205 | 0.012645 | 2.5923
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.005301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5407 | 102 | 0.012645 | 1.2898
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.005301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5089 | 96 | 0.012645 | 1.214
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.005328 | west | 4 | Y | N | Ywest | Nwest | 1 | 3.4616 | 0 | 0.012672 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.005368 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.88572 | 0 | 0.012712 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.017101 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20521 | 0 | 0.012735 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.017101 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18811 | 0 | 0.012735 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.017101 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20521 | 0 | 0.012735 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.005415 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2779 | 0 | 0.012759 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.005415 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.166 | 0 | 0.012759 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.005496 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.32976 | 0 | 0.01284 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.005552 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8328 | 0 | 0.012896 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1606 | 0 | 0.012897 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.70245 | 0 | 0.012897 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3827 | 0 | 0.012897 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.005553 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0939 | 0 | 0.012897 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.005554 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.33324 | 0 | 0.012898 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.2085 | 0 | 0.012904 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.5977 | 0 | 0.012904 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.7506 | 0 | 0.012904 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.66164 | 0 | 0.012904 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.5838 | 0 | 0.012904 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.00556 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.44758 | 0 | 0.012904 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.01729 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012924 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005581 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69763 | 0 | 0.012925 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005581 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69763 | 0 | 0.012925 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.005591 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.83865 | 0 | 0.012935 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.005591 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.56469 | 0 | 0.012935 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.005595 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.46998 | 0 | 0.012939 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.005605 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.5549 | 0 | 0.012949 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.005605 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34191 | 0 | 0.012949 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.005605 | west | 7 | N | N | Nwest | Nwest | 1 | 0.14012 | 0 | 0.012949 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.005605 | west | 7 | N | N | Nwest | Nwest | 1 | 0.25615 | 0 | 0.012949 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.005605 | west | 7 | N | N | Nwest | Nwest | 1 | 0.25615 | 0 | 0.012949 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.005606 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.79045 | 0 | 0.01295 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.005606 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67272 | 0 | 0.01295 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.005609 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.35337 | 0 | 0.012953 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.37039 | 66 | 0.012956 | 0.85512
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38723 | 69 | 0.012956 | 0.89399
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38723 | 69 | 0.012956 | 0.89399
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.376 | 67 | 0.012956 | 0.86808
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.376 | 67 | 0.012956 | 0.86808
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.005612 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.36478 | 65 | 0.012956 | 0.84217
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.84315 | 0 | 0.012965 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2366 | 0 | 0.012965 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1242 | 0 | 0.012965 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.005621 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6852 | 0 | 0.012965 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.005633 | west | 8 | N | N | Nwest | Nwest | 1 | 0.39431 | 0 | 0.012977 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.005633 | west | 8 | N | N | Nwest | Nwest | 1 | 0.41346 | 0 | 0.012977 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.005633 | west | 8 | N | N | Nwest | Nwest | 1 | 0.39656 | 0 | 0.012977 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0141 | 0 | 0.012978 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0141 | 0 | 0.012978 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.005638 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2686 | 0 | 0.012982 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.005639 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67668 | 0 | 0.012983 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.005639 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3139 | 0 | 0.012983 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.005639 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.95976 | 0 | 0.012983 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.005645 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6774 | 0 | 0.012989 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.005646 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67752 | 0 | 0.01299 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.00567 | west | 8 | N | N | Nwest | Nwest | 1 | 0.14629 | 0 | 0.013014 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.005674 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2154 | 0 | 0.013018 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.005683 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57114 | 0 | 0.013027 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.005684 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.32967 | 0 | 0.013028 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.005685 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.85275 | 0 | 0.013029 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.39802 | 70 | 0.01303 | 0.91213
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.39802 | 70 | 0.01303 | 0.91213
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.52766 | 92.8 | 0.01303 | 1.2092
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.45488 | 80 | 0.01303 | 1.0424
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.45488 | 80 | 0.01303 | 1.0424
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.005686 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.65389 | 115 | 0.01303 | 1.4985
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.184 | 208.2 | 0.013031 | 2.7131
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.80812 | 142.1 | 0.013031 | 1.8518
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.75296 | 132.4 | 0.013031 | 1.7254
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.77343 | 136 | 0.013031 | 1.7723
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.83599 | 147 | 0.013031 | 1.9156
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.005687 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1943 | 210 | 0.013031 | 2.7366
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.017398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5488 | 146.5 | 0.013032 | 1.9092
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.017398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5732 | 147.9 | 0.013032 | 1.9274
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.017398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0099 | 173 | 0.013032 | 2.2545
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.64136 | 0 | 0.013045 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8523 | 0 | 0.013045 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0604 | 0 | 0.013045 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.005701 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2229 | 0 | 0.013045 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.017425 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013059 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.005722 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.037765 | 0 | 0.013066 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.005722 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.19626 | 0 | 0.013066 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.017446 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6113 | 207 | 0.01308 | 2.7076
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.017446 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.7805 | 216.7 | 0.01308 | 2.8344
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.017446 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2219 | 242 | 0.01308 | 3.1654
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.017447 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5124 | 144 | 0.013081 | 1.8837
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.017447 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5124 | 144 | 0.013081 | 1.8837
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.017447 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.9834 | 171 | 0.013081 | 2.2369
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.005745 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.85601 | 0 | 0.013089 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.00575 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.97462 | 0 | 0.013094 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.005757 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.2015 | 0 | 0.013101 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.005757 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.17271 | 0 | 0.013101 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38023 | 66 | 0.013105 | 0.86496
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.37446 | 65 | 0.013105 | 0.85185
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38599 | 67 | 0.013105 | 0.87806
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38599 | 67 | 0.013105 | 0.87806
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.005761 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38599 | 67 | 0.013105 | 0.87806
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.005761 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.013105 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.005761 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.013105 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.017482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.66432 | 38 | 0.013116 | 0.49841
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.017482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.3374 | 19.3 | 0.013116 | 0.25314
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.017482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.26223 | 15 | 0.013116 | 0.19674
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.017482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.82165 | 47 | 0.013116 | 0.61645
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.017482 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013116 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6445 | 0 | 0.013129 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.7173 | 0 | 0.013129 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66481 | 0 | 0.013129 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.33241 | 0 | 0.013129 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6445 | 0 | 0.013129 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.62982 | 0 | 0.013129 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.75228 | 0 | 0.013129 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.38489 | 0 | 0.013129 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5893 | 0 | 0.013129 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.87475 | 0 | 0.013129 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.96222 | 0 | 0.013129 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.017495 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.87475 | 0 | 0.013129 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.017543 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.50875 | 0 | 0.013177 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.017636 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67017 | 0 | 0.01327 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.017638 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.8911 | 334 | 0.013272 | 4.4329
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.017638 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.9969 | 340 | 0.013272 | 4.5125
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.017638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1748 | 180 | 0.013272 | 2.389
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.017638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1748 | 180 | 0.013272 | 2.389
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.017654 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67085 | 0 | 0.013288 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.017658 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44145 | 0 | 0.013292 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.017658 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44145 | 0 | 0.013292 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.017667 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1801 | 180 | 0.013301 | 2.3942
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.017669 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6203 | 0 | 0.013303 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.017669 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6256 | 0 | 0.013303 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.017669 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7034 | 0 | 0.013303 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.01767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.9371 | 336 | 0.013304 | 4.4702
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.01767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1806 | 180 | 0.013304 | 2.3947
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 0 | 0.013362 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 0 | 0.013362 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 0 | 0.013362 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.28365 | 0 | 0.013362 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 0 | 0.013362 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 0 | 0.013362 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4432 | 0 | 0.013362 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.017728 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26592 | 0 | 0.013362 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.006034 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.028963 | 0 | 0.013378 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.8129 | 0 | 0.013437 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7239 | 0 | 0.013437 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 1.7803 | 0 | 0.013437 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.5814 | 0 | 0.013437 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.617 | 0 | 0.013437 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.017803 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.261 | 0 | 0.013437 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.017803 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.21364 | 0 | 0.013437 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006147 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49176 | 0 | 0.013491 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006147 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49176 | 0 | 0.013491 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.006177 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.46327 | 0 | 0.013521 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006177 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49416 | 0 | 0.013521 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.006177 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.24708 | 0 | 0.013521 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006184 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49472 | 0 | 0.013528 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.006185 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.4948 | 0 | 0.013529 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.006189 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.92835 | 0 | 0.013533 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.006189 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.92835 | 0 | 0.013533 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.017987 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.3138 | 0 | 0.013621 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006341 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.50728 | 0 | 0.013685 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.006358 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.09537 | 0 | 0.013702 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.006358 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.09537 | 0 | 0.013702 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.006366 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.487 | 0 | 0.01371 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.006392 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.53693 | 0 | 0.013736 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.006638 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9957 | 150 | 0.013982 | 2.0974
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.006638 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.53104 | 80 | 0.013982 | 1.1186
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.006761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7241 | 255 | 0.014105 | 3.5969
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.006761 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0074 | 149 | 0.014105 | 2.1017
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.006761 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0344 | 153 | 0.014105 | 2.1581
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.006902 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.014246 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.006902 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.4319 | 787 | 0.014246 | 11.2119
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006997 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.014341 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006997 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.014341 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.018783 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 25.0377 | 0 | 0.014417 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.018783 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 24.9438 | 0 | 0.014417 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.007212 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.014556 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.019237 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.7701 | 144 | 0.014871 | 2.1414
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.019237 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6166 | 188 | 0.014871 | 2.7958
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.91846 | 47.7 | 0.014889 | 0.71021
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71821 | 37.3 | 0.014889 | 0.55536
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.88573 | 46 | 0.014889 | 0.6849
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.019255 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.92424 | 48 | 0.014889 | 0.71467
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.019255 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.42361 | 22 | 0.014889 | 0.32756
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.019255 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2118 | 11 | 0.014889 | 0.16378
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.019255 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2118 | 11 | 0.014889 | 0.16378
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.019346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4123 | 0 | 0.01498 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.019464 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29196 | 0 | 0.015098 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.019464 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44767 | 0 | 0.015098 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.019468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15574 | 0 | 0.015102 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.007791 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1686 | 0 | 0.015135 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.54905 | 0 | 0.015243 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13726 | 0 | 0.015243 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.76475 | 0 | 0.015243 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29413 | 0 | 0.015243 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13726 | 0 | 0.015243 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29413 | 0 | 0.015243 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.76475 | 0 | 0.015243 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.019609 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.76475 | 0 | 0.015243 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.020056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.96269 | 0 | 0.01569 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5942 | 0 | 0.015814 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6346 | 0 | 0.015814 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5942 | 0 | 0.015814 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6144 | 0 | 0.015814 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5821 | 0 | 0.015814 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5045 | 0 | 0.015814 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.92828 | 0 | 0.015814 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.56504 | 0 | 0.015814 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87985 | 0 | 0.015814 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.02018 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4933 | 0 | 0.015814 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.022463 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 14.6234 | 0 | 0.018097 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.022463 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 12.6691 | 0 | 0.018097 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.022463 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 13.4778 | 0 | 0.018097 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.022768 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7112 | 0 | 0.018402 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.022768 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7112 | 0 | 0.018402 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.022768 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.5782 | 0 | 0.018402 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.011423 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.018767 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.01524 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 1.524 | 0 | 0.022584 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.032814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.3298 | 0 | 0.028448 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.032814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32814 | 0 | 0.028448 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.6909 | 76 | 0.031041 | 2.3591
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.6909 | 76 | 0.031041 | 2.3591
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.7177 | 105 | 0.031041 | 3.2593
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.6201 | 74 | 0.031041 | 2.297
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.6201 | 74 | 0.031041 | 2.297
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.035407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.6115 | 102 | 0.031041 | 3.1662
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.038104 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.5149 | 66 | 0.033738 | 2.2267
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.6339 | 0 | 0.04639 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.6339 | 0 | 0.04639 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.04 | 0 | 0.04639 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.050756 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.5578 | 0 | 0.04639 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.090029 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 14.4947 | 161 | 0.085663 | 13.7918
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.090029 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 14.9448 | 166 | 0.085663 | 14.2201
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.090029 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 22.3272 | 248 | 0.085663 | 21.2444
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.090029 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 49.1558 | 546 | 0.085663 | 46.772
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.090029 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 57.8886 | 0 | 0.085663 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.090029 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.1704 | 13 | 0.085663 | 1.1136

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 461
| 25 | 461
| 30 | 461
| 35 | 457
| 40 | 447
| 45 | 437
| 50 | 427
| 55 | 416
| 60 | 405
| 65 | 394
| 70 | 382
| 75 | 370
| 80 | 357
| 85 | 344
| 90 | 330
| 95 | 315
| 100 | 300
| 105 | 283
| 110 | 266
| 115 | 247
| Max | 461
| Min | 247
| Avg | 378