## test results
CRE test for: |  | Singleton - TH Wharton 345kV 44645-45500 | [5 empty] | PASS
Line Rating: |  | 1450
Direction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Singleton - TH Wharton 345kV 44645-45500
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.1431
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.035014
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.12213
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.17006
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Singleton - TH Wharton 345kV 44645-45500
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.13439
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.037261
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.12241
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.17699
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Singleton - TH Wharton 345kV 44645-45500
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.18036
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.020686
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.32008
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.15743
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.13505
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.29912
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.32008 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.32008 | 0.18036
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.36076
[6 empty] | Concentration |  | 1.1271 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.33828
[6 empty] | Concentration |  | 1.0569 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 51.7899
| Percent of line rating => | [6 empty] | 3.572% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.0746
[7 empty] | B1(N-S) | 0.034542 | 0.22835 | 0.19381 | 0.034542
[7 empty] | B2 (N-W) | 0.0039043 | 0.026133 | 0.022228 | 0.0039043
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.030121 | -0.19929 | -0.16917 | -0.030121
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.026585 | 0.11854 | 0.14512 | -0.026585
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0039581 | 0.31747 | 0.32143 | -0.0039581
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 10.04%
Deployment Error Percent | [6 empty] | B2 | 1.135%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -8.757%
[7 empty] | B5 | -7.729%
[7 empty] | B6 | -1.151%
[7 empty] | Max Abs Error | 10.04% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-H
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:Singleton - TH Wharton 345kV 44645-45500 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45872 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:Singleton - TH Wharton 345kV 44645-45500 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45872
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.10514 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 26.8107
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.10514 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 15.6659
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.11152 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.6728
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.11152 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.6728
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.10514 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 16.0864
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.10708 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 16.0628
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.10708 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 8.5668
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12827 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 9.3637
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12827 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 15.2641
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12827 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 26.2953
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12827 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 13.0835
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.12827 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 12.3139
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.12961 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.5553
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.12961 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.5553
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.12909 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 21.6878
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.12909 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 11.6185
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.13071 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.3527
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.13071 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.3527
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.13071 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 4.9668
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13222 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 38.0796
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13222 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 19.4365
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13222 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 19.4365
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.13402 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 15.0777
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 5.5578
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 10.9762
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 14.7275
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 20.2851
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.13894 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 10.5594
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.13538 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 8.1229
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.13538 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 8.5291
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.13911 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.7822
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.13911 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.4778
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.13911 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 5.7036
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.20485 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 94.8437
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 7.9819
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 7.861
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.1028
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.1028
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.1028
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12094 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 13.7869
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12094 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 62.2831
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 8.1381
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.508
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.508
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.2614
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.2614
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 8.0148
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12297 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 8.608
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12297 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 9.0261
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12297 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 8.6572
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 18.4745
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 27.0959
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12341 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 12.2181
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12341 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 7.5283
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.1234 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 17.399
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12341 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 3.0854
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12341 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.6401
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12341 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.6401
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.1234 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 14.8076
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.12239 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 3.1577
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.12218 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 12.2792
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.12276 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 14.7312
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.12216 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 7.0853
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.12232 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 26.2012
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 18.5467
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12155 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.80224
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12155 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 4.1692
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 12.4881
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.12279 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 14.7343
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.12956 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 47.4182
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.12882 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 31.174
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.12644 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 50.5748
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.12644 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 29.8401
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.12719 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 20.9862
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13149 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 26.8242
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13149 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 26.4297
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13149 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 31.8208
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.5939
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.5939
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.5939
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 2.2048
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.12944 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 15.5328
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.12425 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 7.4548
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.13869 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 10.4014
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.13869 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 11.0393
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.13869 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 12.2598
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 22.1768
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 21.6224
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 27.1666
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 21.6224
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 21.761
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 27.4438
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.13824 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 23.5015
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.13824 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 71.8869
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1385 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 51.2435
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.1388 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 77.4493
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.1388 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 80.364
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.1388 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 112.1488
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13354 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 14.9565
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13354 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 13.354
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13354 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 50.4781
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.13139 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 28.5513
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.13139 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 26.9352
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.13139 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 35.7909
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.13168 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 101.3944
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 9.0961
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 8.9662
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 8.9662
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 8.8363
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.13107 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 151.6457
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.13107 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 151.7767
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 29.6287
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 29.8932
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.13359 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 28.91
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.13359 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 28.8699
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 28.0415
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 27.9092
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.13383 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 52.8617
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.1341 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 58.3352
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.13383 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 58.2147
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.13744 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 18.9664
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.13776 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 16.2562
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.13776 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 15.8429
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.13776 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 76.5968
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.13927 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 54.0383
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.13927 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 71.7261
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.14404 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 113.0714
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.14404 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 114.5118
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.14404 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 112.3512
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.14524 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 26.4344
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.14524 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 70.2981
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.14031 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 31.429
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.14517 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 7.2584
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.14511 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 6.0946
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.1526 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 93.8502
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.1526 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 89.5774
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.1029 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 55.2594
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.1029 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 80.9854
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.10141 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 7.6055
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.10141 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 22.5121
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.034628 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 19.7033
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.03991 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -8.3412
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.03991 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -8.6206
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.0397 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -16.1579
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.8359
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -1.8758
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.8359
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.8359
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.039777 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -16.8654
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.039777 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -16.9052
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.03973 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -2.3043
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.03973 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -3.536
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.7481
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.7481
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -1.7084
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.7878
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.039757 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -16.3799
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.039757 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -15.9028
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.041972 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -22.9167
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.041972 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -31.479
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.039955 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -2.4373
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.039955 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -3.7957
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.039955 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -6.0332
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.041008 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -6.3562
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.041008 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -6.9714
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.041008 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -6.3562
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.069414 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.5271
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.069414 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.76355
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.069414 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.76355
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -3.2772
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -2.5627
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -3.1604
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -3.2978
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.058095 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.69714
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.058095 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.63904
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.040888 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.98131
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.040888 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.98131
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.040888 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.94042
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.048122 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -19.0563
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.11379 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -151.6834
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.11379 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -151.1144
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.063721 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -2.4214
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.063721 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -1.2298
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.063721 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.95581
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.063721 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -2.9949
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11432 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 8.5744
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.12426 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 18.6393
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.1211 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 20.5265
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.088642 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 13.2963
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.12335 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 7.7709
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.12783 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 83.0499
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.13804 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.5217
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.13804 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.5217
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.005038 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 2.126
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.011476 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -1.5148
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.011476 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -1.5378
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.011476 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -3.7067
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.01345 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -2.1251
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.01345 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -2.152
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.01345 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -2.3537
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.031004 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -18.1063
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.031004 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -18.4474
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.031142 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -13.4845
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -6.6122
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -6.6447
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -6.6329
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -6.6949
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.002012 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.016096
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.002012 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.016096
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.01396 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.25128
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.01396 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.25128
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.01396 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.2094
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.012386 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.16969
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.003637 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.065466
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.003637 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.065466
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000462 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.01617
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000462 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.015708
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000462 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.01617
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.005409 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.15145
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.005409 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.15686
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.121 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 4.2349
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.121 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.6299
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.3926
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.3926
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.3926
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.3926
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.023695 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.14217
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.033369 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.080086
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.033369 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.080086
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.033369 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.093433
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.034783 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.13913
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.03598 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.086352
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.03598 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.086352
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -5.6929
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -5.3443
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -5.4218
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -5.6929
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -7.0483
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -7.6679
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.01098 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -1.6744
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.01098 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -1.6415
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.01098 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -2.5539
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -4.8648
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -4.9676
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -5.1731
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -9.9351
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.002535 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.083655
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.002535 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.063375
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.058095 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.69714
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.068744 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -5.0183
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -6.0787
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -6.2326
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -2.0288
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.5072
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -6.0787
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -6.1557
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -6.0326
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.9237
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -3.5395
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.060781 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -38.2312
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.067371 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -9.7014
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.067371 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -12.6657
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.044582 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.53498
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.011636 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.069816
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.065466 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -21.9966
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.065154 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -21.7614
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.065154 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -22.1524
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.064926 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -2.4672
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.065081 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.627
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.065081 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.627
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.064966 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -2.4687
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.064239 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -1.8629
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.06545 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -9.7062
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.06545 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -9.7259
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.06545 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -10.0138
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -10.5713
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -10.2368
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -6.6907
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -9.7015
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -9.8353
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -8.4972
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.062481 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -9.1535
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.062481 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -9.2409
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.062481 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -10.8092
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.063202 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -13.0828
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.063202 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -13.6959
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.063202 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -15.2949
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.063207 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -9.1018
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.063207 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -9.1018
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.063207 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -10.8084
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.002188 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -0.67828
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.002188 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -0.90364
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.037506
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.039292
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.039292
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.041971
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.20791
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.19518
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.19518
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.19942
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.004243 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.65342
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.004243 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.62796
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.20366
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.20366
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.549
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.549
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 11.3336
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.7703
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.7703
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 14.0448
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 25.4248
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 17.3528
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 16.1683
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 16.6079
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 17.9512
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 25.6446
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 25.9653
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 15.7159
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 30.9348
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 24.4745
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 24.6326
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 15.0136
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.1212 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 18.0585
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12296 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.1328
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12296 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.1328
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.1229 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 27.6523
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12379 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.474
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12379 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.474
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 19.3894
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 19.5279
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 42.7953
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 19.8049
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 19.9434
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 42.9338
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.13666 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 26.7852
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.13666 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 15.1691
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.13773 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 22.5613
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 22.9816
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 22.9816
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 58.0146
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 22.7014
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 22.5613
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 22.8415
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 57.314
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.13901 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.13901 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 21.4021
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 18.7992
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 20.9683
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 57.699
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.15125 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 22.7935
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.15125 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 22.8389
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.15125 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 26.8319
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.151 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 22.876
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.151 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 22.9968
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.151 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 26.802
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.034628 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 20.1189
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 152.7457
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 152.7457
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.19085 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 6.1073
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.1861 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 8.9327
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.1861 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 8.5605
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 2.2852
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 9.7122
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.19043 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 3.2374
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 4.1896
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 4.7609
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.1861 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 19.5403
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.12357 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 10.38
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.11421 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 9.1364
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.11414 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 17.1216
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.11414 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 17.1216
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -11.6396
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -10.9655
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -8.7133
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -25.1862
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -25.2356
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -25.0383
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -15.7825
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -40.1138
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -6.576
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -16.4843
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -15.2681
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -16.8787
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -16.7637
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.16435 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -5.2593
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.16435 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -4.9306
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -15.8218
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -15.8218
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -16.9621
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -15.608
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 27.2084
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 27.3334
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.18242 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -24.8095
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.1576 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -5.2008
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -7.6549
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -7.6549
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.9258
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.9258
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.13858 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -9.839
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.13858 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -1.3858
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.14571 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -23.7507
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.14571 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -23.7507
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.14571 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -35.699
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -11.3996
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -10.5227
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -11.3996
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -11.3996
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.17968 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -26.7717
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.17968 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -11.6969
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -15.8513
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -15.259
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -15.1545
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -9.4934
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -2.1251
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.1881 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -139.759
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.18573 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -136.513
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.18905 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -32.5171
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.18905 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -32.5171
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.18905 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -32.5171
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -33.9402
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.18274 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -31.6135
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.18274 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -24.6695
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -30.9315
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -30.6655
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -30.1905
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -51.1472
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -11.5103
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -11.3664
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -14.8554
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -13.2368
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -29.1986
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -28.1072
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -28.1788
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -28.0893
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -48.1276
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.18761 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.93807
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.18761 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -3.9399
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 32.5498
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 32.9297
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 32.9297
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 80.2134
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.18894 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -75.1977
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.2758
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.2758
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.2758
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.895
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.895
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -9.7151
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.16839 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 139.2618
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.16839 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 137.9147
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.15556 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -7.1714
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -8.7751
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -8.7751
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -12.1235
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -8.5442
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -8.5442
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -11.7771
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.17985 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -32.3723
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.17985 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -28.5236
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.17985 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -28.2358
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.17909 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -6.2682
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.17078 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -78.3866
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -12.125
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -12.3116
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -13.0577
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -11.752
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -11.5654
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -19.4001
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -11.0058
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -30.605
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -30.2126
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -30.2126
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.19619 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -31.7821
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.18696 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -29.3529
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -12.833
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -13.0138
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -7.0491
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -5.4224
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.17772 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -13.8626
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.17772 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -14.218
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.17984 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -2.9134
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.17968 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -29.6479
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.17964 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -30.3595
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.17983 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -38.3038
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.17986 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -41.0085
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.17961 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -2.1553
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.17961 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -3.233
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.16972 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -8.486
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -20.6613
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -20.6613
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -10.728
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -10.5293
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -10.728
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -11.324
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -10.728
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -10.728
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -11.5226
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -11.5226
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.19895 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -2.3874
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -12.3402
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -13.0012
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -12.3402
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -12.3402
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -13.0012
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -12.3402
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.12068 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -7.9647
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.15627 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -25.1591
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.15627 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -25.9405
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.15627 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -38.7545
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.15627 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -85.3223
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.15627 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -100.4803
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.14552 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -94.7355
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.14552 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -82.075
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.14552 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -87.3138
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.15627 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -2.0315
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.18785 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -2.2542
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -6.3253
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -6.4555
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -6.0834
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -8.5391
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -3.2929
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -3.7952
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -3.7022
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -6.5113
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -3.3487
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -15.8876
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -27.5336
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -8.2813
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -9.5369
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -6.0107
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -13.4906
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -11.487
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -11.7542
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -6.6785
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -2.4043
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -12.5556
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -9.3499
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -8.4149
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -9.617
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -8.6553
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -13.4906
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -12.9563
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -13.7577
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -10.1513
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -10.6856
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -10.6856
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -22.8405
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.32994
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.11132 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 8.516
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11432 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 9.146
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11432 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 4.573
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11481 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 9.1847
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.11422 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 9.1375
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.11172 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 8.9379
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.11091 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 9.3163
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11481 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 9.1847
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -3.5528
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12287 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 14.7448
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12287 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 28.6294
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12287 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 20.913
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -6.9186
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -5.7344
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -6.981
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -3.584
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -3.1165
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.12515 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.5091
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.03057 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.097892 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.1166 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.55969
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.6551
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 13.3445
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 16.7582
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 14.7721
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 13.0342
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 9.9929
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.12215 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 18.3219
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 13.7131
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 18.2232
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 22.6723
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 26.1463
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.063721 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.014933 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.047631 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -2.1545
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -3.3548
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -5.694
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.0081
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -2.6206
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -2.4288
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -1.2144
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.0081
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -2.301
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -2.7484
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.4062
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.8258
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0869
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.5072
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0869
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.8258
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.072456 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.8258
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -9.4596
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.1958
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -3.5154
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.1958
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066907 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.80288
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.071081 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.0662
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.071081 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.6349
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.075904 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -3.6434
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.071905 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.57524
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.065422 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -11.776
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.065466 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -11.7839
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.065154 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -11.7277
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.065154 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -11.7277
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.047627 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -4.7627
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.047627 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -4.7627
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6582
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6582
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6582
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -1.0612
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6582
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6582
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6582
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.99491
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.047627 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.047627 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -23.8135
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.047627 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -23.8135
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.047627 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.057473 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.002535 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.053899 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.060469 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:Singleton - TH Wharton 345kV 44645-45500 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45872 | [7 empty] | 51.7899
Number of Bus | Name of Bus | ID | Max MW | L:Singleton - TH Wharton 345kV 44645-45500 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45872 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.10514 | north | Y | -0.037957 | 0.14015 | -0.01699 | 0.2752 | 0.01699 | west | Y | 0.037957 | 5.3466
239 | BOSQUESW | 1 | 149 | 0.10514 | north | Y | -0.037957 | 0.14015 | -0.01699 | 0.2752 | 0.01699 | west | Y | 0.037957 | 3.1241
244 | WHITNYDM | 1 | 15 | 0.11152 | north | N | -0.031577 | 0.14653 | -0.01061 | 0.28158 | 0.01061 | west | Y | 0.031577 | 0
245 | WHITNYDM | 2 | 15 | 0.11152 | north | N | -0.031577 | 0.14653 | -0.01061 | 0.28158 | 0.01061 | west | Y | 0.031577 | 0
247 | BOSQUESW | 2 | 153 | 0.10514 | north | Y | -0.037957 | 0.14015 | -0.01699 | 0.2752 | 0.01699 | west | Y | 0.037957 | 3.2079
251 | BOSQUESW | 2 | 150 | 0.10708 | north | Y | -0.036012 | 0.1421 | -0.015045 | 0.27715 | 0.015045 | west | Y | 0.036012 | 3.145
253 | BOSQUESW | 2 | 80 | 0.10708 | north | Y | -0.036012 | 0.1421 | -0.015045 | 0.27715 | 0.015045 | west | Y | 0.036012 | 1.6774
332 | RWMILLER | 1 | 73 | 0.12827 | north | Y | -0.014827 | 0.16328 | 0.0061397 | 0.29833 | 0.0061397 | west | Y | 0.014827 | 0.63419
333 | RWMILLER | 2 | 119 | 0.12827 | north | Y | -0.014827 | 0.16328 | 0.0061397 | 0.29833 | 0.0061397 | west | Y | 0.014827 | 1.0338
334 | RWMILLER | 3 | 205 | 0.12827 | north | Y | -0.014827 | 0.16328 | 0.0061397 | 0.29833 | 0.0061397 | west | Y | 0.014827 | 1.7809
335 | RWMILLER | 4 | 102 | 0.12827 | north | Y | -0.014827 | 0.16328 | 0.0061397 | 0.29833 | 0.0061397 | west | Y | 0.014827 | 0.88613
336 | RWMILLER | 5 | 96 | 0.12827 | north | Y | -0.014827 | 0.16328 | 0.0061397 | 0.29833 | 0.0061397 | west | Y | 0.014827 | 0.834
344 | MRSSHPRD | 1 | 12 | 0.12961 | north | N | -0.01349 | 0.16462 | 0.0074767 | 0.29967 | 0.0074767 | west | Y | 0.01349 | 0
345 | MRSSHPRD | 2 | 12 | 0.12961 | north | N | -0.01349 | 0.16462 | 0.0074767 | 0.29967 | 0.0074767 | west | Y | 0.01349 | 0
366 | JNSNCNTY | 1 | 168 | 0.12909 | north | Y | -0.014003 | 0.16411 | 0.0069637 | 0.29916 | 0.0069637 | west | Y | 0.014003 | 1.1826
367 | JNSNCNTY | 2 | 90 | 0.12909 | north | Y | -0.014003 | 0.16411 | 0.0069637 | 0.29916 | 0.0069637 | west | Y | 0.014003 | 0.63356
503 | NTHTEXAS | 1 | 18 | 0.13071 | north | Y | -0.012391 | 0.16572 | 0.0085757 | 0.30077 | 0.0085757 | west | Y | 0.012391 | 0.06868
504 | NTHTEXAS | 2 | 18 | 0.13071 | north | Y | -0.012391 | 0.16572 | 0.0085757 | 0.30077 | 0.0085757 | west | Y | 0.012391 | 0.06868
505 | NTHTEXAS | 3 | 38 | 0.13071 | north | Y | -0.012391 | 0.16572 | 0.0085757 | 0.30077 | 0.0085757 | west | Y | 0.012391 | 0.14499
580 | JCKCNTY8 | 1 | 288 | 0.13222 | north | Y | -0.010876 | 0.16724 | 0.010091 | 0.30228 | 0.010091 | west | Y | 0.010876 | 0.22623
581 | JCKCNTY8 | 2 | 147 | 0.13222 | north | Y | -0.010876 | 0.16724 | 0.010091 | 0.30228 | 0.010091 | west | Y | 0.010876 | 0.11547
582 | JCKCNTY8 | 3 | 147 | 0.13222 | north | Y | -0.010876 | 0.16724 | 0.010091 | 0.30228 | 0.010091 | west | Y | 0.010876 | 0.11547
728 | WOLFRIDG | 1 | 112.5 | 0.13402 | north | Y | -0.0090732 | 0.16904 | 0.011894 | 0.30409 | 0.0090732 | North | N | 0.0090732 | 0
837 | NEWMAN_G | 1 | 40 | 0.13894 | north | Y | -0.0041532 | 0.17396 | 0.016814 | 0.30901 | 0.0041532 | North | N | 0.0041532 | 0
842 | OLINGER_ | 1 | 79 | 0.13894 | north | Y | -0.0041582 | 0.17395 | 0.016809 | 0.309 | 0.0041582 | North | N | 0.0041582 | 0
843 | OLINGER_ | 1 | 106 | 0.13894 | north | Y | -0.0041582 | 0.17395 | 0.016809 | 0.309 | 0.0041582 | North | N | 0.0041582 | 0
844 | OLINGER_ | 1 | 146 | 0.13894 | north | Y | -0.0041582 | 0.17395 | 0.016809 | 0.309 | 0.0041582 | North | N | 0.0041582 | 0
845 | OLINGER_ | 1 | 76 | 0.13894 | north | Y | -0.0041582 | 0.17395 | 0.016809 | 0.309 | 0.0041582 | North | N | 0.0041582 | 0
923 | SPENCER_ | 1 | 60 | 0.13538 | north | Y | -0.0077152 | 0.1704 | 0.013252 | 0.30545 | 0.0077152 | North | N | 0.0077152 | 0
924 | SPENCER_ | 1 | 63 | 0.13538 | north | Y | -0.0077152 | 0.1704 | 0.013252 | 0.30545 | 0.0077152 | North | N | 0.0077152 | 0
948 | STEAM1 | 1 | 20 | 0.13911 | north | Y | -0.0039862 | 0.17413 | 0.016981 | 0.30917 | 0.0039862 | North | N | 0.0039862 | 0
949 | STEAM2 | 1 | 25 | 0.13911 | north | Y | -0.0039862 | 0.17413 | 0.016981 | 0.30917 | 0.0039862 | North | N | 0.0039862 | 0
950 | STEAM3 | 1 | 41 | 0.13911 | north | Y | -0.0039862 | 0.17413 | 0.016981 | 0.30917 | 0.0039862 | North | N | 0.0039862 | 0
990 | GIBN_CRE | 1 | 463 | 0.20485 | north | Y | 0.061749 | 0.23986 | 0.082716 | 0.37491 | 0.061749 | North | N | 0.061749 | 0
1002 | PBCTAGE_ | A | 66 | 0.12094 | west | Y | -0.022159 | 0.15595 | -0.0011923 | 0.291 | 0.0011923 | west | N | 0.0011923 | 0
1003 | PBCTBGE_ | B | 65 | 0.12094 | west | Y | -0.022159 | 0.15595 | -0.0011923 | 0.291 | 0.0011923 | west | N | 0.0011923 | 0
1004 | PBCTCGE_ | C | 67 | 0.12094 | west | Y | -0.022159 | 0.15595 | -0.0011923 | 0.291 | 0.0011923 | west | N | 0.0011923 | 0
1005 | PBCTDGE_ | D | 67 | 0.12094 | west | Y | -0.022159 | 0.15595 | -0.0011923 | 0.291 | 0.0011923 | west | N | 0.0011923 | 0
1006 | PBCTEGE_ | E | 67 | 0.12094 | west | Y | -0.022159 | 0.15595 | -0.0011923 | 0.291 | 0.0011923 | west | N | 0.0011923 | 0
1007 | PB5GEN_6 | MB | 114 | 0.12094 | west | Y | -0.022159 | 0.15595 | -0.0011923 | 0.291 | 0.0011923 | west | N | 0.0011923 | 0
1008 | PB6GEN_7 | MB | 515 | 0.12094 | west | Y | -0.022159 | 0.15595 | -0.0011923 | 0.291 | 0.0011923 | west | N | 0.0011923 | 0
1039 | MRGNAG_1 | A | 66 | 0.1233 | west | Y | -0.019793 | 0.15832 | 0.0011737 | 0.29337 | 0.0011737 | west | N | 0.0011737 | 0
1040 | MRGNBG_2 | B | 69 | 0.1233 | west | Y | -0.019793 | 0.15832 | 0.0011737 | 0.29337 | 0.0011737 | west | N | 0.0011737 | 0
1041 | MRGNCG_3 | C | 69 | 0.1233 | west | Y | -0.019793 | 0.15832 | 0.0011737 | 0.29337 | 0.0011737 | west | N | 0.0011737 | 0
1042 | MRGNDG_4 | D | 67 | 0.1233 | west | Y | -0.019793 | 0.15832 | 0.0011737 | 0.29337 | 0.0011737 | west | N | 0.0011737 | 0
1043 | MRGNEG_5 | E | 67 | 0.1233 | west | Y | -0.019793 | 0.15832 | 0.0011737 | 0.29337 | 0.0011737 | west | N | 0.0011737 | 0
1044 | MRGNFG_6 | F | 65 | 0.1233 | west | Y | -0.019793 | 0.15832 | 0.0011737 | 0.29337 | 0.0011737 | west | N | 0.0011737 | 0
1045 | CALENG1G | 1 | 70 | 0.12297 | west | N | -0.020125 | 0.15799 | 0.00084167 | 0.29304 | 0.00084167 | west | N | 0.00084167 | 0
1046 | CALENG2G | 2 | 73.4 | 0.12297 | west | N | -0.020125 | 0.15799 | 0.00084167 | 0.29304 | 0.00084167 | west | N | 0.00084167 | 0
1047 | CALENG3G | 3 | 70.4 | 0.12297 | west | N | -0.020125 | 0.15799 | 0.00084167 | 0.29304 | 0.00084167 | west | N | 0.00084167 | 0
1058 | LONGSHOR | 1 | 150 | 0.12316 | west | Y | -0.019934 | 0.15818 | 0.0010327 | 0.29323 | 0.0010327 | west | N | 0.0010327 | 0
1058 | LONGSHOR | 2 | 220 | 0.12316 | west | Y | -0.019934 | 0.15818 | 0.0010327 | 0.29323 | 0.0010327 | west | N | 0.0010327 | 0
1061 | CIELOGEN | 1 | 99 | 0.12341 | west | Y | -0.019682 | 0.15843 | 0.0012847 | 0.29348 | 0.0012847 | west | N | 0.0012847 | 0
1062 | CIELOGEN | 1 | 61 | 0.12341 | west | Y | -0.019682 | 0.15843 | 0.0012847 | 0.29348 | 0.0012847 | west | N | 0.0012847 | 0
1068 | SCURRYCW | 1 | 141 | 0.1234 | west | Y | -0.0197 | 0.15841 | 0.0012667 | 0.29346 | 0.0012667 | west | N | 0.0012667 | 0
1069 | KINDERMG | 1 | 25 | 0.12341 | west | N | -0.019682 | 0.15843 | 0.0012847 | 0.29348 | 0.0012847 | west | N | 0.0012847 | 0
1070 | KINDERMG | 1 | 45.7 | 0.12341 | west | N | -0.019682 | 0.15843 | 0.0012847 | 0.29348 | 0.0012847 | west | N | 0.0012847 | 0
1071 | KINDERMG | 1 | 45.7 | 0.12341 | west | N | -0.019682 | 0.15843 | 0.0012847 | 0.29348 | 0.0012847 | west | N | 0.0012847 | 0
1073 | SCURRYCW | 2 | 120 | 0.1234 | west | Y | -0.0197 | 0.15841 | 0.0012667 | 0.29346 | 0.0012667 | west | N | 0.0012667 | 0
1320 | BSP 1 | 1 | 25.8 | 0.12239 | west | N | -0.020706 | 0.15741 | 0.00026067 | 0.29245 | 0.00026067 | west | N | 0.00026067 | 0
1326 | STANTONW | 1 | 100.5 | 0.12218 | west | Y | -0.020916 | 0.1572 | 5.0674e-05 | 0.29224 | 5.0674e-05 | west | N | 5.0674e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.12276 | west | Y | -0.020337 | 0.15777 | 0.00062967 | 0.29282 | 0.00062967 | west | N | 0.00062967 | 0
1328 | OCOTILLO | 1 | 58 | 0.12216 | west | Y | -0.020936 | 0.15718 | 3.0674e-05 | 0.29222 | 3.0674e-05 | west | N | 3.0674e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.12232 | west | Y | -0.020776 | 0.15734 | 0.00019067 | 0.29238 | 0.00019067 | west | N | 0.00019067 | 0
1343 | TRENTIPP | 1 | 150 | 0.12365 | west | Y | -0.019452 | 0.15866 | 0.0015147 | 0.29371 | 0.0015147 | west | N | 0.0015147 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.12155 | west | Y | -0.021545 | 0.15657 | -0.00057833 | 0.29162 | 0.00057833 | west | N | 0.00057833 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.12155 | west | Y | -0.021545 | 0.15657 | -0.00057833 | 0.29162 | 0.00057833 | west | N | 0.00057833 | 0
1354 | AEPWIND_ | 1 | 101 | 0.12365 | west | Y | -0.019452 | 0.15866 | 0.0015147 | 0.29371 | 0.0015147 | west | N | 0.0015147 | 0
1360 | GUNSIGHT | 1 | 120 | 0.12279 | west | Y | -0.020311 | 0.1578 | 0.00065567 | 0.29285 | 0.00065567 | west | N | 0.00065567 | 0
1432 | GRHAMSES | 2 | 366 | 0.12956 | north | Y | -0.013539 | 0.16457 | 0.0074277 | 0.29962 | 0.0074277 | west | Y | 0.013539 | 2.2368
1433 | GRHAMSES | 1 | 242 | 0.12882 | north | Y | -0.014279 | 0.16383 | 0.0066877 | 0.29888 | 0.0066877 | west | Y | 0.014279 | 1.8372
1437 | MESQUITW | 1 | 400 | 0.12644 | west | Y | -0.01666 | 0.16145 | 0.0043067 | 0.2965 | 0.0043067 | west | N | 0.0043067 | 0
1438 | MESQUITW | 1 | 236 | 0.12644 | west | Y | -0.016656 | 0.16146 | 0.0043107 | 0.2965 | 0.0043107 | west | N | 0.0043107 | 0
1442 | COKFIELD | 1 | 165 | 0.12719 | west | Y | -0.015908 | 0.1622 | 0.0050587 | 0.29725 | 0.0050587 | west | N | 0.0050587 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.13149 | north | Y | -0.011606 | 0.16651 | 0.0093607 | 0.30155 | 0.0093607 | west | Y | 0.011606 | 0.45809
1454 | WCPWRCO_ | 2 | 201 | 0.13149 | north | Y | -0.011606 | 0.16651 | 0.0093607 | 0.30155 | 0.0093607 | west | Y | 0.011606 | 0.45135
1455 | WCPWRCO_ | 3 | 242 | 0.13149 | north | Y | -0.011606 | 0.16651 | 0.0093607 | 0.30155 | 0.0093607 | west | Y | 0.011606 | 0.54342
1479 | WFCOGEN_ | 1 | 20 | 0.12969 | west | Y | -0.013403 | 0.16471 | 0.0075637 | 0.29976 | 0.0075637 | west | N | 0.0075637 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.12969 | west | Y | -0.013403 | 0.16471 | 0.0075637 | 0.29976 | 0.0075637 | west | N | 0.0075637 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.12969 | west | Y | -0.013403 | 0.16471 | 0.0075637 | 0.29976 | 0.0075637 | west | N | 0.0075637 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.12969 | west | Y | -0.013403 | 0.16471 | 0.0075637 | 0.29976 | 0.0075637 | west | N | 0.0075637 | 0
1600 | BARTNWND | 1 | 120 | 0.12944 | north | Y | -0.013657 | 0.16445 | 0.0073097 | 0.2995 | 0.0073097 | west | Y | 0.013657 | 0.7617
1643 | SLSTR1PP | 1 | 60 | 0.12425 | north | Y | -0.018851 | 0.15926 | 0.0021157 | 0.29431 | 0.0021157 | west | Y | 0.018851 | 1.0041
1675 | PEC_1G | 1 | 75 | 0.13869 | north | N | -0.0044122 | 0.1737 | 0.016555 | 0.30875 | 0.0044122 | North | N | 0.0044122 | 0
1676 | PEC_2G | 2 | 79.6 | 0.13869 | north | N | -0.0044122 | 0.1737 | 0.016555 | 0.30875 | 0.0044122 | North | N | 0.0044122 | 0
1677 | PEC_3G | 3 | 88.4 | 0.13869 | north | N | -0.0044122 | 0.1737 | 0.016555 | 0.30875 | 0.0044122 | North | N | 0.0044122 | 0
1678 | LAMARPWR | 1 | 160 | 0.13861 | north | Y | -0.0044922 | 0.17362 | 0.016475 | 0.30867 | 0.0044922 | North | N | 0.0044922 | 0
1679 | LAMARPWR | 2 | 156 | 0.13861 | north | Y | -0.0044922 | 0.17362 | 0.016475 | 0.30867 | 0.0044922 | North | N | 0.0044922 | 0
1680 | LAMARPWR | 3 | 196 | 0.13861 | north | Y | -0.0044922 | 0.17362 | 0.016475 | 0.30867 | 0.0044922 | North | N | 0.0044922 | 0
1681 | LAMARPWR | 4 | 156 | 0.13861 | north | Y | -0.0044922 | 0.17362 | 0.016475 | 0.30867 | 0.0044922 | North | N | 0.0044922 | 0
1682 | LAMARPWR | 5 | 157 | 0.13861 | north | Y | -0.0044922 | 0.17362 | 0.016475 | 0.30867 | 0.0044922 | North | N | 0.0044922 | 0
1683 | LAMARPWR | 6 | 198 | 0.13861 | north | Y | -0.0044922 | 0.17362 | 0.016475 | 0.30867 | 0.0044922 | North | N | 0.0044922 | 0
1687 | VALLEY_1 | 1 | 170 | 0.13824 | north | Y | -0.0048532 | 0.17326 | 0.016114 | 0.30831 | 0.0048532 | North | N | 0.0048532 | 0
1688 | VALLEY_2 | 2 | 520 | 0.13824 | north | Y | -0.0048532 | 0.17326 | 0.016114 | 0.30831 | 0.0048532 | North | N | 0.0048532 | 0
1689 | VALLEY_3 | 3 | 370 | 0.1385 | north | Y | -0.0046012 | 0.17351 | 0.016366 | 0.30856 | 0.0046012 | North | N | 0.0046012 | 0
1701 | MOSES_1G | 1 | 558 | 0.1388 | north | Y | -0.0042992 | 0.17381 | 0.016668 | 0.30886 | 0.0042992 | North | N | 0.0042992 | 0
1702 | MOSES_2G | 2 | 579 | 0.1388 | north | Y | -0.0042992 | 0.17381 | 0.016668 | 0.30886 | 0.0042992 | North | N | 0.0042992 | 0
1703 | MOSES_3G | 3 | 808 | 0.1388 | north | Y | -0.0042992 | 0.17381 | 0.016668 | 0.30886 | 0.0042992 | North | N | 0.0042992 | 0
1861 | EAGLEMNT | MB | 112 | 0.13354 | north | Y | -0.0095572 | 0.16855 | 0.01141 | 0.3036 | 0.0095572 | North | N | 0.0095572 | 0
1862 | EAGLEMNT | MB | 100 | 0.13354 | north | Y | -0.0095572 | 0.16855 | 0.01141 | 0.3036 | 0.0095572 | North | N | 0.0095572 | 0
1863 | EAGLEMNT | MB | 378 | 0.13354 | north | Y | -0.0095572 | 0.16855 | 0.01141 | 0.3036 | 0.0095572 | North | N | 0.0095572 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.13139 | north | Y | -0.011706 | 0.16641 | 0.0092607 | 0.30145 | 0.0092607 | west | Y | 0.011706 | 0.53141
1878 | WLFHOLW_ | 2 | 205 | 0.13139 | north | Y | -0.011706 | 0.16641 | 0.0092607 | 0.30145 | 0.0092607 | west | Y | 0.011706 | 0.50133
1879 | WLFHOLW_ | 3 | 272.4 | 0.13139 | north | Y | -0.011706 | 0.16641 | 0.0092607 | 0.30145 | 0.0092607 | west | Y | 0.011706 | 0.66616
1889 | DECRDOVA | MB | 770 | 0.13168 | north | Y | -0.011416 | 0.1667 | 0.0095507 | 0.30174 | 0.0095507 | west | Y | 0.011416 | 0
1892 | DECRDOVA | A | 70 | 0.12995 | north | Y | -0.013152 | 0.16496 | 0.0078147 | 0.30001 | 0.0078147 | west | Y | 0.013152 | 0.37363
1893 | DECRDOVA | B | 69 | 0.12995 | north | Y | -0.013152 | 0.16496 | 0.0078147 | 0.30001 | 0.0078147 | west | Y | 0.013152 | 0.36829
1894 | DECRDOVA | C | 69 | 0.12995 | north | Y | -0.013152 | 0.16496 | 0.0078147 | 0.30001 | 0.0078147 | west | Y | 0.013152 | 0.36829
1895 | DECRDOVA | D | 68 | 0.12995 | north | Y | -0.013152 | 0.16496 | 0.0078147 | 0.30001 | 0.0078147 | west | Y | 0.013152 | 0.36295
1898 | COMCHEPK | 1 | 1157 | 0.13107 | north | N | -0.012029 | 0.16608 | 0.0089377 | 0.30113 | 0.0089377 | west | Y | 0.012029 | 0
1899 | COMCHEPK | 2 | 1158 | 0.13107 | north | N | -0.012029 | 0.16608 | 0.0089377 | 0.30113 | 0.0089377 | west | Y | 0.012029 | 0
1937 | MDLTHELP | 5 | 224 | 0.13227 | north | Y | -0.010826 | 0.16729 | 0.010141 | 0.30233 | 0.010141 | west | Y | 0.010826 | 0.15356
1938 | MDLTHELP | 6 | 226 | 0.13227 | north | Y | -0.010826 | 0.16729 | 0.010141 | 0.30233 | 0.010141 | west | Y | 0.010826 | 0.15493
1941 | MDLTHELP | 1 | 216.4 | 0.13359 | north | Y | -0.0095022 | 0.16861 | 0.011465 | 0.30366 | 0.0095022 | North | N | 0.0095022 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.13359 | north | Y | -0.0095022 | 0.16861 | 0.011465 | 0.30366 | 0.0095022 | North | N | 0.0095022 | 0
1943 | MDLTHELP | 3 | 212 | 0.13227 | north | Y | -0.010826 | 0.16729 | 0.010141 | 0.30233 | 0.010141 | west | Y | 0.010826 | 0.14533
1944 | MDLTHELP | 4 | 211 | 0.13227 | north | Y | -0.010826 | 0.16729 | 0.010141 | 0.30233 | 0.010141 | west | Y | 0.010826 | 0.14465
1947 | HANDLEY_ | 3 | 395 | 0.13383 | north | Y | -0.0092702 | 0.16884 | 0.011697 | 0.30389 | 0.0092702 | North | N | 0.0092702 | 0
1948 | HANDLEY_ | 4 | 435 | 0.1341 | north | Y | -0.0089932 | 0.16912 | 0.011974 | 0.30417 | 0.0089932 | North | N | 0.0089932 | 0
1949 | HANDLEY_ | 5 | 435 | 0.13383 | north | Y | -0.0092702 | 0.16884 | 0.011697 | 0.30389 | 0.0092702 | North | N | 0.0092702 | 0
2371 | COLLIN_1 | MB | 138 | 0.13744 | north | Y | -0.0056592 | 0.17245 | 0.015308 | 0.3075 | 0.0056592 | North | N | 0.0056592 | 0
2413 | MTCK6_G | 6 | 118 | 0.13776 | north | Y | -0.0053332 | 0.17278 | 0.015634 | 0.30783 | 0.0053332 | North | N | 0.0053332 | 0
2414 | MTCK7_G | 7 | 115 | 0.13776 | north | Y | -0.0053332 | 0.17278 | 0.015634 | 0.30783 | 0.0053332 | North | N | 0.0053332 | 0
2417 | MTCK8_G | 8 | 556 | 0.13776 | north | Y | -0.0053332 | 0.17278 | 0.015634 | 0.30783 | 0.0053332 | North | N | 0.0053332 | 0
2451 | LKHB1_G | 1 | 388 | 0.13927 | north | Y | -0.0038232 | 0.17429 | 0.017144 | 0.30934 | 0.0038232 | North | N | 0.0038232 | 0
2452 | LKHB2_G | 2 | 515 | 0.13927 | north | Y | -0.0038232 | 0.17429 | 0.017144 | 0.30934 | 0.0038232 | North | N | 0.0038232 | 0
3097 | MARTLAKE | 1 | 785 | 0.14404 | north | Y | 0.00094279 | 0.17905 | 0.02191 | 0.3141 | 0.00094279 | North | N | 0.00094279 | 0
3098 | MARTLAKE | 2 | 795 | 0.14404 | north | Y | 0.00094279 | 0.17905 | 0.02191 | 0.3141 | 0.00094279 | North | N | 0.00094279 | 0
3099 | MARTLAKE | 3 | 780 | 0.14404 | north | Y | 0.00094279 | 0.17905 | 0.02191 | 0.3141 | 0.00094279 | North | N | 0.00094279 | 0
3107 | STRYKER_ | 1 | 182 | 0.14524 | north | Y | 0.0021468 | 0.18026 | 0.023114 | 0.31531 | 0.0021468 | North | N | 0.0021468 | 0
3108 | STRYKER_ | 2 | 484 | 0.14524 | north | Y | 0.0021468 | 0.18026 | 0.023114 | 0.31531 | 0.0021468 | North | N | 0.0021468 | 0
3126 | TRINIDAD | 1 | 224 | 0.14031 | north | Y | -0.0027892 | 0.17532 | 0.018178 | 0.31037 | 0.0027892 | North | N | 0.0027892 | 0
3309 | ASPN_G | 1 | 50 | 0.14517 | north | Y | 0.0020698 | 0.18018 | 0.023037 | 0.31523 | 0.0020698 | North | N | 0.0020698 | 0
3348 | CHAMPION | MB | 42 | 0.14511 | north | N | 0.0020118 | 0.18012 | 0.022979 | 0.31517 | 0.0020118 | North | N | 0.0020118 | 0
3381 | BBRN_1G | 1 | 615 | 0.1526 | north | Y | 0.0095048 | 0.18762 | 0.030472 | 0.32267 | 0.0095048 | North | N | 0.0095048 | 0
3382 | BBRN_2G | 2 | 587 | 0.1526 | north | Y | 0.0095048 | 0.18762 | 0.030472 | 0.32267 | 0.0095048 | North | N | 0.0095048 | 0
3403 | THOUSE_1 | MB | 537 | 0.1029 | north | Y | -0.040193 | 0.13792 | -0.019226 | 0.27297 | 0.019226 | west | Y | 0.040193 | 0
3404 | THOUSE_2 | 2 | 787 | 0.1029 | north | Y | -0.040193 | 0.13792 | -0.019226 | 0.27297 | 0.019226 | west | Y | 0.040193 | 16.5009
3416 | LAKE_CRK | MB | 75 | 0.10141 | north | Y | -0.041691 | 0.13642 | -0.020724 | 0.27147 | 0.020724 | west | Y | 0.041691 | 0
3417 | LAKE_CRK | MB | 222 | 0.10141 | north | Y | -0.041691 | 0.13642 | -0.020724 | 0.27147 | 0.020724 | west | Y | 0.041691 | 0
3432 | SANDOW_4 | 4 | 569 | 0.034628 | south | Y | -0.10847 | 0.069642 | -0.087502 | 0.20469 | 0.069642 | south | N | 0.069642 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.03991 | south | Y | -0.18301 | -0.0048958 | -0.16204 | 0.13015 | 0.0048958 | south | N | 0.0048958 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.03991 | south | Y | -0.18301 | -0.0048958 | -0.16204 | 0.13015 | 0.0048958 | south | N | 0.0048958 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.0397 | south | Y | -0.1828 | -0.0046858 | -0.16183 | 0.13036 | 0.0046858 | south | N | 0.0046858 | 0
5031 | BRA_VHBC | 1 | 46 | -0.03991 | south | Y | -0.18301 | -0.0048958 | -0.16204 | 0.13015 | 0.0048958 | south | N | 0.0048958 | 0
5032 | BRA_VHBC | 2 | 47 | -0.03991 | south | Y | -0.18301 | -0.0048958 | -0.16204 | 0.13015 | 0.0048958 | south | N | 0.0048958 | 0
5033 | BRA_VHBC | 3 | 46 | -0.03991 | south | Y | -0.18301 | -0.0048958 | -0.16204 | 0.13015 | 0.0048958 | south | N | 0.0048958 | 0
5034 | BRA_VHBC | 4 | 46 | -0.03991 | south | Y | -0.18301 | -0.0048958 | -0.16204 | 0.13015 | 0.0048958 | south | N | 0.0048958 | 0
5111 | CALAVER_ | 1 | 424 | -0.039777 | south | Y | -0.18287 | -0.0047628 | -0.16191 | 0.13029 | 0.0047628 | south | N | 0.0047628 | 0
5112 | CALAVER_ | 2 | 425 | -0.039777 | south | Y | -0.18287 | -0.0047628 | -0.16191 | 0.13029 | 0.0047628 | south | N | 0.0047628 | 0
5264 | LEON_LCP | 3 | 58 | -0.03973 | south | Y | -0.18283 | -0.0047158 | -0.16186 | 0.13033 | 0.0047158 | south | N | 0.0047158 | 0
5265 | LEON_LCP | 4 | 89 | -0.03973 | south | Y | -0.18283 | -0.0047158 | -0.16186 | 0.13033 | 0.0047158 | south | N | 0.0047158 | 0
5266 | LEON_LCP | 1 | 44 | -0.03973 | south | Y | -0.18283 | -0.0047158 | -0.16186 | 0.13033 | 0.0047158 | south | N | 0.0047158 | 0
5267 | LEON_LCP | 2 | 44 | -0.03973 | south | Y | -0.18283 | -0.0047158 | -0.16186 | 0.13033 | 0.0047158 | south | N | 0.0047158 | 0
5268 | LEON_LCP | 3 | 43 | -0.03973 | south | Y | -0.18283 | -0.0047158 | -0.16186 | 0.13033 | 0.0047158 | south | N | 0.0047158 | 0
5269 | LEON_LCP | 4 | 45 | -0.03973 | south | Y | -0.18283 | -0.0047158 | -0.16186 | 0.13033 | 0.0047158 | south | N | 0.0047158 | 0
5396 | CALAVER_ | 1 | 412 | -0.039757 | south | Y | -0.18285 | -0.0047428 | -0.16189 | 0.13031 | 0.0047428 | south | N | 0.0047428 | 0
5397 | CALAVER_ | 2 | 400 | -0.039757 | south | Y | -0.18285 | -0.0047428 | -0.16189 | 0.13031 | 0.0047428 | south | N | 0.0047428 | 0
5401 | CALAVER_ | 1 | 546 | -0.041972 | south | Y | -0.18507 | -0.0069578 | -0.1641 | 0.12809 | 0.0069578 | south | N | 0.0069578 | 0
5402 | CALAVER_ | 2 | 750 | -0.041972 | south | Y | -0.18507 | -0.0069578 | -0.1641 | 0.12809 | 0.0069578 | south | N | 0.0069578 | 0
5436 | TUTTL_WB | MB | 61 | -0.039955 | south | Y | -0.18305 | -0.0049408 | -0.16209 | 0.13011 | 0.0049408 | south | N | 0.0049408 | 0
5438 | TUTTL_WB | MB | 95 | -0.039955 | south | Y | -0.18305 | -0.0049408 | -0.16209 | 0.13011 | 0.0049408 | south | N | 0.0049408 | 0
5439 | TUTTL_WB | MB | 151 | -0.039955 | south | Y | -0.18305 | -0.0049408 | -0.16209 | 0.13011 | 0.0049408 | south | N | 0.0049408 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.041008 | south | Y | -0.18411 | -0.0059938 | -0.16314 | 0.12906 | 0.0059938 | south | N | 0.0059938 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.041008 | south | Y | -0.18411 | -0.0059938 | -0.16314 | 0.12906 | 0.0059938 | south | N | 0.0059938 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.041008 | south | Y | -0.18411 | -0.0059938 | -0.16314 | 0.12906 | 0.0059938 | south | N | 0.0059938 | 0
5503 | RAYBURNG | 1 | 22 | -0.069414 | south | Y | -0.21251 | -0.0344 | -0.19154 | 0.10065 | 0.0344 | south | N | 0.0344 | 0
5505 | RAYBURNG | 1 | 11 | -0.069414 | south | Y | -0.21251 | -0.0344 | -0.19154 | 0.10065 | 0.0344 | south | N | 0.0344 | 0
5506 | RAYBURNG | 1 | 11 | -0.069414 | south | Y | -0.21251 | -0.0344 | -0.19154 | 0.10065 | 0.0344 | south | N | 0.0344 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.068705 | south | Y | -0.2118 | -0.033691 | -0.19084 | 0.10136 | 0.033691 | south | N | 0.033691 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.068705 | south | Y | -0.2118 | -0.033691 | -0.19084 | 0.10136 | 0.033691 | south | N | 0.033691 | 0
5511 | RAYBURNC | 1 | 46 | -0.068705 | south | Y | -0.2118 | -0.033691 | -0.19084 | 0.10136 | 0.033691 | south | N | 0.033691 | 0
5512 | RAYBURNC | 1 | 48 | -0.068705 | south | Y | -0.2118 | -0.033691 | -0.19084 | 0.10136 | 0.033691 | south | N | 0.033691 | 0
5728 | FALCONHY | 2 | 12 | -0.058095 | south | N | -0.20119 | -0.023081 | -0.18023 | 0.11197 | 0.023081 | south | N | 0.023081 | 0
5729 | FALCONHY | 3 | 11 | -0.058095 | south | N | -0.20119 | -0.023081 | -0.18023 | 0.11197 | 0.023081 | south | N | 0.023081 | 0
5890 | PEARSALL | 1 | 24 | -0.040888 | south | Y | -0.18399 | -0.0058738 | -0.16302 | 0.12918 | 0.0058738 | south | N | 0.0058738 | 0
5891 | PEARSALL | 1 | 24 | -0.040888 | south | Y | -0.18399 | -0.0058738 | -0.16302 | 0.12918 | 0.0058738 | south | N | 0.0058738 | 0
5892 | PEARSALL | 1 | 23 | -0.040888 | south | Y | -0.18399 | -0.0058738 | -0.16302 | 0.12918 | 0.0058738 | south | N | 0.0058738 | 0
5903 | SANMIGUE | 1 | 396 | -0.048122 | south | Y | -0.19122 | -0.013108 | -0.17025 | 0.12194 | 0.013108 | south | N | 0.013108 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.11379 | houston | N | -0.25689 | -0.078777 | -0.23592 | 0.056272 | 0.056272 | houston | N | 0.056272 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.11379 | houston | N | -0.25689 | -0.078777 | -0.23592 | 0.056272 | 0.056272 | houston | N | 0.056272 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | Y | 0.1431 | 0
5932 | SI_RAY9 | 9 | 38 | -0.063721 | south | Y | -0.20682 | -0.028707 | -0.18585 | 0.10634 | 0.028707 | south | N | 0.028707 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.063721 | south | Y | -0.20682 | -0.028707 | -0.18585 | 0.10634 | 0.028707 | south | N | 0.028707 | 0
5934 | SI_RAY5 | 5 | 15 | -0.063721 | south | Y | -0.20682 | -0.028707 | -0.18585 | 0.10634 | 0.028707 | south | N | 0.028707 | 0
5935 | SI_RAY10 | 10 | 47 | -0.063721 | south | Y | -0.20682 | -0.028707 | -0.18585 | 0.10634 | 0.028707 | south | N | 0.028707 | 0
6016 | SWMESA | 1 | 75 | 0.11432 | west | Y | -0.028772 | 0.14934 | -0.0078053 | 0.28439 | 0.0078053 | west | N | 0.0078053 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | Y | 0.12213 | 0
6144 | MCADOO1A | 1 | 150 | 0.12426 | west | Y | -0.018835 | 0.15928 | 0.0021317 | 0.29433 | 0.0021317 | west | N | 0.0021317 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.1211 | west | Y | -0.021997 | 0.15611 | -0.0010303 | 0.29116 | 0.0010303 | west | N | 0.0010303 | 0
6476 | LANGFORD | 1 | 150 | 0.088642 | west | Y | -0.054455 | 0.12366 | -0.033488 | 0.25871 | 0.033488 | west | N | 0.033488 | 0
6637 | SNYDERW1 | 1 | 63 | 0.12335 | west | Y | -0.019749 | 0.15836 | 0.0012177 | 0.29341 | 0.0012177 | west | N | 0.0012177 | 0
6752 | OKLA0A | 1 | 649.7 | 0.12783 | west | Y | -0.015269 | 0.16284 | 0.0056977 | 0.29789 | 0.0056977 | west | N | 0.0056977 | 0
6948 | DENISNDM | 1 | 40 | 0.13804 | north | N | -0.0050542 | 0.17306 | 0.015913 | 0.30811 | 0.0050542 | North | N | 0.0050542 | 0
6948 | DENISNDM | 2 | 40 | 0.13804 | north | N | -0.0050542 | 0.17306 | 0.015913 | 0.30811 | 0.0050542 | North | N | 0.0050542 | 0
7000 | L_FERGUS | 1 | 422 | 0.005038 | south | Y | -0.13806 | 0.040052 | -0.11709 | 0.1751 | 0.040052 | south | N | 0.040052 | 0
7004 | L_SIMGID | 1 | 132 | -0.011476 | south | Y | -0.15457 | 0.023538 | -0.13361 | 0.15859 | 0.023538 | south | N | 0.023538 | 0
7005 | L_SIMGID | 2 | 134 | -0.011476 | south | Y | -0.15457 | 0.023538 | -0.13361 | 0.15859 | 0.023538 | south | N | 0.023538 | 0
7006 | L_SIMGID | 3 | 323 | -0.011476 | south | Y | -0.15457 | 0.023538 | -0.13361 | 0.15859 | 0.023538 | south | N | 0.023538 | 0
7007 | L_LOSTPI | 1 | 158 | -0.01345 | south | Y | -0.15655 | 0.021564 | -0.13558 | 0.15661 | 0.021564 | south | N | 0.021564 | 0
7008 | L_LOSTPI | 2 | 160 | -0.01345 | south | Y | -0.15655 | 0.021564 | -0.13558 | 0.15661 | 0.021564 | south | N | 0.021564 | 0
7009 | L_LOSTPI | 3 | 175 | -0.01345 | south | Y | -0.15655 | 0.021564 | -0.13558 | 0.15661 | 0.021564 | south | N | 0.021564 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.031004 | south | Y | -0.1741 | 0.0040102 | -0.15313 | 0.13906 | 0.0040102 | south | N | 0.0040102 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.031004 | south | Y | -0.1741 | 0.0040102 | -0.15313 | 0.13906 | 0.0040102 | south | N | 0.0040102 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.031142 | south | Y | -0.17424 | 0.0038722 | -0.15327 | 0.13892 | 0.0038722 | south | N | 0.0038722 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.029532 | south | Y | -0.17263 | 0.0054822 | -0.15166 | 0.14053 | 0.0054822 | south | N | 0.0054822 | 0
7015 | L_HAYSEN | 2 | 225 | -0.029532 | south | Y | -0.17263 | 0.0054822 | -0.15166 | 0.14053 | 0.0054822 | south | N | 0.0054822 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.029532 | south | Y | -0.17263 | 0.0054822 | -0.15166 | 0.14053 | 0.0054822 | south | N | 0.0054822 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.029532 | south | Y | -0.17263 | 0.0054822 | -0.15166 | 0.14053 | 0.0054822 | south | N | 0.0054822 | 0
7020 | L_AUSTPL | 1 | 8 | -0.002012 | south | N | -0.14511 | 0.033002 | -0.12414 | 0.16805 | 0.033002 | south | N | 0.033002 | 0
7020 | L_AUSTPL | 2 | 8 | -0.002012 | south | N | -0.14511 | 0.033002 | -0.12414 | 0.16805 | 0.033002 | south | N | 0.033002 | 0
7022 | L_BUCHAN | 1 | 18 | 0.01396 | south | N | -0.12914 | 0.048974 | -0.10817 | 0.18402 | 0.048974 | south | N | 0.048974 | 0
7023 | L_BUCHAN | 2 | 18 | 0.01396 | south | N | -0.12914 | 0.048974 | -0.10817 | 0.18402 | 0.048974 | south | N | 0.048974 | 0
7024 | L_BUCHAN | 3 | 15 | 0.01396 | south | N | -0.12914 | 0.048974 | -0.10817 | 0.18402 | 0.048974 | south | N | 0.048974 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.012386 | south | N | -0.13071 | 0.0474 | -0.10974 | 0.18245 | 0.0474 | south | N | 0.0474 | 0
7028 | L_MARBFA | 1 | 18 | 0.003637 | south | N | -0.13946 | 0.038651 | -0.11849 | 0.1737 | 0.038651 | south | N | 0.038651 | 0
7029 | L_MARBFA | 2 | 18 | 0.003637 | south | N | -0.13946 | 0.038651 | -0.11849 | 0.1737 | 0.038651 | south | N | 0.038651 | 0
7031 | L_MARSFO | 1 | 35 | 0.000462 | south | N | -0.14264 | 0.035476 | -0.12167 | 0.17053 | 0.035476 | south | N | 0.035476 | 0
7032 | L_MARSFO | 2 | 34 | 0.000462 | south | N | -0.14264 | 0.035476 | -0.12167 | 0.17053 | 0.035476 | south | N | 0.035476 | 0
7033 | L_MARSFO | 3 | 35 | 0.000462 | south | N | -0.14264 | 0.035476 | -0.12167 | 0.17053 | 0.035476 | south | N | 0.035476 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.005409 | south | N | -0.13769 | 0.040423 | -0.11672 | 0.17547 | 0.040423 | south | N | 0.040423 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.005409 | south | N | -0.13769 | 0.040423 | -0.11672 | 0.17547 | 0.040423 | south | N | 0.040423 | 0
7038 | L_DELAWA | 1 | 35 | 0.121 | west | Y | -0.022101 | 0.15601 | -0.0011343 | 0.29106 | 0.0011343 | west | N | 0.0011343 | 0
7038 | L_DELAWA | 2 | 30 | 0.121 | west | Y | -0.022101 | 0.15601 | -0.0011343 | 0.29106 | 0.0011343 | west | N | 0.0011343 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.027852 | south | Y | -0.17095 | 0.0071622 | -0.14998 | 0.14221 | 0.0071622 | south | N | 0.0071622 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.027852 | south | Y | -0.17095 | 0.0071622 | -0.14998 | 0.14221 | 0.0071622 | south | N | 0.0071622 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.027852 | south | Y | -0.17095 | 0.0071622 | -0.14998 | 0.14221 | 0.0071622 | south | N | 0.0071622 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.027852 | south | Y | -0.17095 | 0.0071622 | -0.14998 | 0.14221 | 0.0071622 | south | N | 0.0071622 | 0
7487 | L_CANYHY | 1 | 6 | -0.023695 | south | N | -0.16679 | 0.011319 | -0.14583 | 0.14637 | 0.011319 | south | N | 0.011319 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.033369 | south | N | -0.17647 | 0.0016452 | -0.1555 | 0.13669 | 0.0016452 | south | N | 0.0016452 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.033369 | south | N | -0.17647 | 0.0016452 | -0.1555 | 0.13669 | 0.0016452 | south | N | 0.0016452 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.033369 | south | N | -0.17647 | 0.0016452 | -0.1555 | 0.13669 | 0.0016452 | south | N | 0.0016452 | 0
7609 | L_SCHUMA | 1 | 4 | -0.034783 | south | N | -0.17788 | 0.00023124 | -0.15691 | 0.13528 | 0.00023124 | south | N | 0.00023124 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.03598 | south | N | -0.17908 | -0.00096576 | -0.15811 | 0.13408 | 0.00096576 | south | N | 0.00096576 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.03598 | south | N | -0.17908 | -0.00096576 | -0.15811 | 0.13408 | 0.00096576 | south | N | 0.00096576 | 0
7800 | L_GUADGE | 1 | 147 | -0.038727 | south | Y | -0.18182 | -0.0037128 | -0.16086 | 0.13134 | 0.0037128 | south | N | 0.0037128 | 0
7801 | L_GUADGE | 2 | 138 | -0.038727 | south | Y | -0.18182 | -0.0037128 | -0.16086 | 0.13134 | 0.0037128 | south | N | 0.0037128 | 0
7802 | L_GUADGE | 3 | 140 | -0.038727 | south | Y | -0.18182 | -0.0037128 | -0.16086 | 0.13134 | 0.0037128 | south | N | 0.0037128 | 0
7803 | L_GUADGE | 4 | 147 | -0.038727 | south | Y | -0.18182 | -0.0037128 | -0.16086 | 0.13134 | 0.0037128 | south | N | 0.0037128 | 0
7804 | L_GUADGE | 5 | 182 | -0.038727 | south | Y | -0.18182 | -0.0037128 | -0.16086 | 0.13134 | 0.0037128 | south | N | 0.0037128 | 0
7805 | L_GUADGE | 6 | 198 | -0.038727 | south | Y | -0.18182 | -0.0037128 | -0.16086 | 0.13134 | 0.0037128 | south | N | 0.0037128 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.01098 | south | Y | -0.15408 | 0.024034 | -0.13311 | 0.15908 | 0.024034 | south | N | 0.024034 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.01098 | south | Y | -0.15408 | 0.024034 | -0.13311 | 0.15908 | 0.024034 | south | N | 0.024034 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.01098 | south | Y | -0.15408 | 0.024034 | -0.13311 | 0.15908 | 0.024034 | south | N | 0.024034 | 0
7810 | L_RIONOG | 1 | 142 | -0.034259 | south | Y | -0.17736 | 0.00075524 | -0.15639 | 0.1358 | 0.00075524 | south | N | 0.00075524 | 0
7811 | L_RIONOG | 2 | 145 | -0.034259 | south | Y | -0.17736 | 0.00075524 | -0.15639 | 0.1358 | 0.00075524 | south | N | 0.00075524 | 0
7812 | L_RIONOG | 3 | 151 | -0.034259 | south | Y | -0.17736 | 0.00075524 | -0.15639 | 0.1358 | 0.00075524 | south | N | 0.00075524 | 0
7813 | L_RIONOG | 4 | 290 | -0.034259 | south | Y | -0.17736 | 0.00075524 | -0.15639 | 0.1358 | 0.00075524 | south | N | 0.00075524 | 0
8032 | AMISTADH | 1 | 33 | 0.002535 | south | N | -0.14056 | 0.037549 | -0.1196 | 0.1726 | 0.037549 | south | N | 0.037549 | 0
8033 | AMISTADH | 2 | 25 | 0.002535 | south | N | -0.14056 | 0.037549 | -0.1196 | 0.1726 | 0.037549 | south | N | 0.037549 | 0
8048 | FALCONHY | 1 | 12 | -0.058095 | south | N | -0.20119 | -0.023081 | -0.18023 | 0.11197 | 0.023081 | south | N | 0.023081 | 0
8066 | DUP1V#1 | 1 | 73 | -0.068744 | south | N | -0.21184 | -0.03373 | -0.19087 | 0.10132 | 0.03373 | south | N | 0.03373 | 0
8134 | FOR69CG0 | 1 | 79 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
8138 | FOR69CG0 | 2 | 81 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | N | 0.035014 | 0
8147 | UCAR #2 | 10 | 28 | -0.072457 | south | N | -0.21555 | -0.037443 | -0.19459 | 0.097606 | 0.037443 | south | N | 0.037443 | 0
8148 | UCAR #1 | 2 | 7 | -0.072457 | south | N | -0.21555 | -0.037443 | -0.19459 | 0.097606 | 0.037443 | south | N | 0.037443 | 0
8153 | FOR69CG0 | 3 | 79 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
8154 | FOR69CG0 | 4 | 80 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
8156 | FOR69CG0 | 6 | 25 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
8157 | FOR69CG0 | 7 | 46 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
8161 | COLETOU1 | 1 | 629 | -0.060781 | south | Y | -0.20388 | -0.025767 | -0.18291 | 0.10928 | 0.025767 | south | N | 0.025767 | 0
8173 | VICEC51A | 5 | 144 | -0.067371 | south | Y | -0.21047 | -0.032357 | -0.1895 | 0.10269 | 0.032357 | south | N | 0.032357 | 0
8174 | VICEC61A | 6 | 188 | -0.067371 | south | Y | -0.21047 | -0.032357 | -0.1895 | 0.10269 | 0.032357 | south | N | 0.032357 | 0
8189 | CUERO 2 | 1 | 12 | -0.044582 | south | N | -0.18768 | -0.0095678 | -0.16671 | 0.12548 | 0.0095678 | south | N | 0.0095678 | 0
8262 | ELPS | 1 | 6 | -0.011636 | south | N | -0.15473 | 0.023378 | -0.13377 | 0.15843 | 0.023378 | south | N | 0.023378 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | N | 0.035014 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | N | 0.035014 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | N | 0.035014 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | N | 0.035014 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | N | 0.035014 | 0
8442 | NBEC71A | 1 | 336 | -0.065466 | south | Y | -0.20856 | -0.030452 | -0.1876 | 0.1046 | 0.030452 | south | N | 0.030452 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | N | 0.035014 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.1431 | 0.035014 | -0.12213 | 0.17006 | 0.035014 | south | N | 0.035014 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.065154 | south | Y | -0.20825 | -0.03014 | -0.18728 | 0.10491 | 0.03014 | south | N | 0.03014 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.065154 | south | Y | -0.20825 | -0.03014 | -0.18728 | 0.10491 | 0.03014 | south | N | 0.03014 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.064926 | south | N | -0.20802 | -0.029912 | -0.18706 | 0.10514 | 0.029912 | south | N | 0.029912 | 0
8506 | VAL #1 | 1 | 25 | -0.065081 | south | N | -0.20818 | -0.030067 | -0.18721 | 0.10498 | 0.030067 | south | N | 0.030067 | 0
8507 | VAL #2 | 2 | 25 | -0.065081 | south | N | -0.20818 | -0.030067 | -0.18721 | 0.10498 | 0.030067 | south | N | 0.030067 | 0
8511 | OXY_CC0A | 1 | 38 | -0.064966 | south | N | -0.20806 | -0.029952 | -0.1871 | 0.1051 | 0.029952 | south | N | 0.029952 | 0
8517 | CELANEBI | 1 | 29 | -0.064239 | south | N | -0.20734 | -0.029225 | -0.18637 | 0.10582 | 0.029225 | south | N | 0.029225 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.06545 | south | N | -0.20855 | -0.030436 | -0.18758 | 0.10461 | 0.030436 | south | N | 0.030436 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.06545 | south | N | -0.20855 | -0.030436 | -0.18758 | 0.10461 | 0.030436 | south | N | 0.030436 | 0
8562 | CNOPST1 | 3 | 153 | -0.06545 | south | N | -0.20855 | -0.030436 | -0.18758 | 0.10461 | 0.030436 | south | N | 0.030436 | 0
8926 | LGE_GT10 | 1 | 158 | -0.066907 | south | N | -0.21 | -0.031893 | -0.18904 | 0.10316 | 0.031893 | south | N | 0.031893 | 0
8927 | LGE_GT20 | 2 | 153 | -0.066907 | south | N | -0.21 | -0.031893 | -0.18904 | 0.10316 | 0.031893 | south | N | 0.031893 | 0
8928 | LGE_STG0 | 3 | 100 | -0.066907 | south | N | -0.21 | -0.031893 | -0.18904 | 0.10316 | 0.031893 | south | N | 0.031893 | 0
8930 | ICPGN10A | 1 | 145 | -0.066907 | south | N | -0.21 | -0.031893 | -0.18904 | 0.10316 | 0.031893 | south | N | 0.031893 | 0
8931 | ICPGN20A | 2 | 147 | -0.066907 | south | N | -0.21 | -0.031893 | -0.18904 | 0.10316 | 0.031893 | south | N | 0.031893 | 0
8932 | ICPGN30A | 3 | 127 | -0.066907 | south | N | -0.21 | -0.031893 | -0.18904 | 0.10316 | 0.031893 | south | N | 0.031893 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.062481 | south | Y | -0.20558 | -0.027467 | -0.18461 | 0.10758 | 0.027467 | south | N | 0.027467 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.062481 | south | Y | -0.20558 | -0.027467 | -0.18461 | 0.10758 | 0.027467 | south | N | 0.027467 | 0
8935 | FGNTS201 | 3 | 173 | -0.062481 | south | Y | -0.20558 | -0.027467 | -0.18461 | 0.10758 | 0.027467 | south | N | 0.027467 | 0
8936 | MVGN#1 | 1 | 207 | -0.063202 | south | Y | -0.2063 | -0.028188 | -0.18533 | 0.10686 | 0.028188 | south | N | 0.028188 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.063202 | south | Y | -0.2063 | -0.028188 | -0.18533 | 0.10686 | 0.028188 | south | N | 0.028188 | 0
8938 | MVGN#3 | 3 | 242 | -0.063202 | south | Y | -0.2063 | -0.028188 | -0.18533 | 0.10686 | 0.028188 | south | N | 0.028188 | 0
8981 | HECN1 | 1 | 144 | -0.063207 | south | Y | -0.2063 | -0.028193 | -0.18534 | 0.10686 | 0.028193 | south | N | 0.028193 | 0
8982 | HECN2 | 2 | 144 | -0.063207 | south | Y | -0.2063 | -0.028193 | -0.18534 | 0.10686 | 0.028193 | south | N | 0.028193 | 0
8983 | HECN3 | 3 | 171 | -0.063207 | south | Y | -0.2063 | -0.028193 | -0.18534 | 0.10686 | 0.028193 | south | N | 0.028193 | 0
9000 | DECKR_G1 | 1 | 310 | -0.002188 | south | Y | -0.14529 | 0.032826 | -0.12432 | 0.16788 | 0.032826 | south | N | 0.032826 | 0
9001 | DECKR_G2 | 2 | 413 | -0.002188 | south | Y | -0.14529 | 0.032826 | -0.12432 | 0.16788 | 0.032826 | south | N | 0.032826 | 0
9002 | DECKR_G3 | 3 | 42 | -0.000893 | south | Y | -0.14399 | 0.034121 | -0.12302 | 0.16917 | 0.034121 | south | N | 0.034121 | 0
9003 | DECKR_G4 | 4 | 44 | -0.000893 | south | Y | -0.14399 | 0.034121 | -0.12302 | 0.16917 | 0.034121 | south | N | 0.034121 | 0
9004 | DECKR_G5 | 5 | 44 | -0.000893 | south | Y | -0.14399 | 0.034121 | -0.12302 | 0.16917 | 0.034121 | south | N | 0.034121 | 0
9005 | DECKR_G6 | 6 | 47 | -0.000893 | south | Y | -0.14399 | 0.034121 | -0.12302 | 0.16917 | 0.034121 | south | N | 0.034121 | 0
9016 | SANDH_G1 | 1 | 49 | -0.004243 | south | Y | -0.14734 | 0.030771 | -0.12637 | 0.16582 | 0.030771 | south | N | 0.030771 | 0
9017 | SANDH_G2 | 2 | 46 | -0.004243 | south | Y | -0.14734 | 0.030771 | -0.12637 | 0.16582 | 0.030771 | south | N | 0.030771 | 0
9018 | SANDH_G3 | 3 | 46 | -0.004243 | south | Y | -0.14734 | 0.030771 | -0.12637 | 0.16582 | 0.030771 | south | N | 0.030771 | 0
9019 | SANDH_G4 | 4 | 47 | -0.004243 | south | Y | -0.14734 | 0.030771 | -0.12637 | 0.16582 | 0.030771 | south | N | 0.030771 | 0
9020 | SANDHG5A | 5A | 154 | -0.004243 | south | Y | -0.14734 | 0.030771 | -0.12637 | 0.16582 | 0.030771 | south | N | 0.030771 | 0
9021 | SANDHG5C | 5C | 148 | -0.004243 | south | Y | -0.14734 | 0.030771 | -0.12637 | 0.16582 | 0.030771 | south | N | 0.030771 | 0
9022 | SANDH_G6 | 6 | 48 | -0.004243 | south | Y | -0.14734 | 0.030771 | -0.12637 | 0.16582 | 0.030771 | south | N | 0.030771 | 0
9023 | SANDH_G7 | 7 | 48 | -0.004243 | south | Y | -0.14734 | 0.030771 | -0.12637 | 0.16582 | 0.030771 | south | N | 0.030771 | 0
11001 | NAV1CT | 1 | 70 | 0.12213 | west | Y | -0.020968 | 0.15714 | -1.3255e-06 | 0.29219 | 1.3255e-06 | west | N | 1.3255e-06 | 0
11009 | NAV2CT | 1 | 70 | 0.12213 | west | Y | -0.020968 | 0.15714 | -1.3255e-06 | 0.29219 | 1.3255e-06 | west | N | 1.3255e-06 | 0
11011 | NAV3ST | 1 | 92.8 | 0.12213 | west | Y | -0.020968 | 0.15714 | -1.3255e-06 | 0.29219 | 1.3255e-06 | west | N | 1.3255e-06 | 0
11012 | NAV4CT | 1 | 80 | 0.12213 | west | Y | -0.020968 | 0.15714 | -1.3255e-06 | 0.29219 | 1.3255e-06 | west | N | 1.3255e-06 | 0
11013 | NAV5CT | 1 | 80 | 0.12213 | west | Y | -0.020968 | 0.15714 | -1.3255e-06 | 0.29219 | 1.3255e-06 | west | N | 1.3255e-06 | 0
11014 | NAV6ST | 1 | 115 | 0.12213 | west | Y | -0.020968 | 0.15714 | -1.3255e-06 | 0.29219 | 1.3255e-06 | west | N | 1.3255e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.12212 | west | Y | -0.02098 | 0.15713 | -1.3326e-05 | 0.29218 | 1.3326e-05 | west | N | 1.3326e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.12212 | west | Y | -0.02098 | 0.15713 | -1.3326e-05 | 0.29218 | 1.3326e-05 | west | N | 1.3326e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.12212 | west | Y | -0.02098 | 0.15713 | -1.3326e-05 | 0.29218 | 1.3326e-05 | west | N | 1.3326e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.12212 | west | Y | -0.02098 | 0.15713 | -1.3326e-05 | 0.29218 | 1.3326e-05 | west | N | 1.3326e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.12212 | west | Y | -0.02098 | 0.15713 | -1.3326e-05 | 0.29218 | 1.3326e-05 | west | N | 1.3326e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.12212 | west | Y | -0.02098 | 0.15713 | -1.3326e-05 | 0.29218 | 1.3326e-05 | west | N | 1.3326e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.12424 | west | Y | -0.018861 | 0.15925 | 0.0021057 | 0.2943 | 0.0021057 | west | N | 0.0021057 | 0
11057 | CHAMPION | 1 | 126.5 | 0.12424 | west | Y | -0.018861 | 0.15925 | 0.0021057 | 0.2943 | 0.0021057 | west | N | 0.0021057 | 0
11058 | PYRON_1G | 1 | 249 | 0.12424 | west | Y | -0.018861 | 0.15925 | 0.0021057 | 0.2943 | 0.0021057 | west | N | 0.0021057 | 0
11059 | INADALE_ | 1 | 197 | 0.12424 | west | Y | -0.018861 | 0.15925 | 0.0021057 | 0.2943 | 0.0021057 | west | N | 0.0021057 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.12316 | west | Y | -0.019934 | 0.15818 | 0.0010327 | 0.29323 | 0.0010327 | west | N | 0.0010327 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.12316 | west | Y | -0.019934 | 0.15818 | 0.0010327 | 0.29323 | 0.0010327 | west | N | 0.0010327 | 0
11147 | NOTREES_ | 1 | 149 | 0.1212 | west | Y | -0.021899 | 0.15621 | -0.00093233 | 0.29126 | 0.00093233 | west | N | 0.00093233 | 0
11309 | BULLCREK | 1 | 180 | 0.12296 | west | Y | -0.020137 | 0.15797 | 0.00082967 | 0.29302 | 0.00082967 | west | N | 0.00082967 | 0
11310 | BULLCREK | 1 | 180 | 0.12296 | west | Y | -0.020137 | 0.15797 | 0.00082967 | 0.29302 | 0.00082967 | west | N | 0.00082967 | 0
11320 | COYOTE_1 | 1 | 225 | 0.1229 | west | Y | -0.020198 | 0.15791 | 0.00076867 | 0.29296 | 0.00076867 | west | N | 0.00076867 | 0
11415 | LORAINE_ | 1 | 125 | 0.12379 | west | Y | -0.019305 | 0.15881 | 0.0016617 | 0.29386 | 0.0016617 | west | N | 0.0016617 | 0
11416 | LORAINE_ | 1 | 125 | 0.12379 | west | Y | -0.019305 | 0.15881 | 0.0016617 | 0.29386 | 0.0016617 | west | N | 0.0016617 | 0
11691 | KMICHICT | 1 | 140 | 0.1385 | north | N | -0.0046012 | 0.17351 | 0.016366 | 0.30856 | 0.0046012 | North | N | 0.0046012 | 0
11692 | KMICHICT | 2 | 141 | 0.1385 | north | N | -0.0046012 | 0.17351 | 0.016366 | 0.30856 | 0.0046012 | North | N | 0.0046012 | 0
11693 | KMICHIST | 3 | 309 | 0.1385 | north | N | -0.0046012 | 0.17351 | 0.016366 | 0.30856 | 0.0046012 | North | N | 0.0046012 | 0
11694 | KMICHICT | 4 | 143 | 0.1385 | north | N | -0.0046012 | 0.17351 | 0.016366 | 0.30856 | 0.0046012 | North | N | 0.0046012 | 0
11695 | KMICHICT | 5 | 144 | 0.1385 | north | N | -0.0046012 | 0.17351 | 0.016366 | 0.30856 | 0.0046012 | North | N | 0.0046012 | 0
11696 | KMICHIST | 6 | 310 | 0.1385 | north | N | -0.0046012 | 0.17351 | 0.016366 | 0.30856 | 0.0046012 | North | N | 0.0046012 | 0
12322 | ENNSTRAC | 1 | 196 | 0.13666 | north | Y | -0.0064382 | 0.17167 | 0.014529 | 0.30672 | 0.0064382 | North | N | 0.0064382 | 0
12323 | ENNSTRAC | 2 | 111 | 0.13666 | north | Y | -0.0064382 | 0.17167 | 0.014529 | 0.30672 | 0.0064382 | North | N | 0.0064382 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.13773 | north | N | -0.0053682 | 0.17274 | 0.015599 | 0.30779 | 0.0053682 | North | N | 0.0053682 | 0
12411 | FPLEFR1A | 1 | 161 | 0.14013 | north | Y | -0.0029652 | 0.17515 | 0.018002 | 0.3102 | 0.0029652 | North | N | 0.0029652 | 0
12412 | FPLEFR1B | 2 | 164 | 0.14013 | north | Y | -0.0029652 | 0.17515 | 0.018002 | 0.3102 | 0.0029652 | North | N | 0.0029652 | 0
12413 | FPLEFR1C | 3 | 164 | 0.14013 | north | Y | -0.0029652 | 0.17515 | 0.018002 | 0.3102 | 0.0029652 | North | N | 0.0029652 | 0
12414 | FPLEFR1S | 4 | 414 | 0.14013 | north | Y | -0.0029652 | 0.17515 | 0.018002 | 0.3102 | 0.0029652 | North | N | 0.0029652 | 0
12421 | FPLEFR2A | 1 | 162 | 0.14013 | north | Y | -0.0029652 | 0.17515 | 0.018002 | 0.3102 | 0.0029652 | North | N | 0.0029652 | 0
12422 | FPLEFR2B | 2 | 161 | 0.14013 | north | Y | -0.0029652 | 0.17515 | 0.018002 | 0.3102 | 0.0029652 | North | N | 0.0029652 | 0
12423 | FPLEFR2C | 3 | 163 | 0.14013 | north | Y | -0.0029652 | 0.17515 | 0.018002 | 0.3102 | 0.0029652 | North | N | 0.0029652 | 0
12424 | FPLEFR2S | 4 | 409 | 0.14013 | north | Y | -0.0029652 | 0.17515 | 0.018002 | 0.3102 | 0.0029652 | North | N | 0.0029652 | 0
12440 | PARKD_1S | 1 | 0 | 0.13901 | north | N | -0.0040852 | 0.17403 | 0.016882 | 0.30908 | 0.0040852 | North | N | 0.0040852 | 0
12449 | PARKD_2S | 1 | 0 | 0.13901 | north | N | -0.0040852 | 0.17403 | 0.016882 | 0.30908 | 0.0040852 | North | N | 0.0040852 | 0
13116 | TGATEWAY | 1 | 148 | 0.14461 | north | N | 0.0015118 | 0.17962 | 0.022479 | 0.31467 | 0.0015118 | North | N | 0.0015118 | 0
13117 | TGATEWAY | 2 | 130 | 0.14461 | north | N | 0.0015118 | 0.17962 | 0.022479 | 0.31467 | 0.0015118 | North | N | 0.0015118 | 0
13118 | TGATEWAY | 3 | 145 | 0.14461 | north | N | 0.0015118 | 0.17962 | 0.022479 | 0.31467 | 0.0015118 | North | N | 0.0015118 | 0
13119 | TGATEWAY | 4 | 399 | 0.14461 | north | N | 0.0015118 | 0.17962 | 0.022479 | 0.31467 | 0.0015118 | North | N | 0.0015118 | 0
13131 | CALFREST | 1 | 150.7 | 0.15125 | north | Y | 0.0081538 | 0.18627 | 0.029121 | 0.32131 | 0.0081538 | North | N | 0.0081538 | 0
13132 | CALFREST | 2 | 151 | 0.15125 | north | Y | 0.0081538 | 0.18627 | 0.029121 | 0.32131 | 0.0081538 | North | N | 0.0081538 | 0
13133 | CALFREST | 3 | 177.4 | 0.15125 | north | Y | 0.0081538 | 0.18627 | 0.029121 | 0.32131 | 0.0081538 | North | N | 0.0081538 | 0
13134 | CALFREST | 4 | 151.5 | 0.151 | north | Y | 0.0078998 | 0.18601 | 0.028867 | 0.32106 | 0.0078998 | North | N | 0.0078998 | 0
13135 | CALFREST | 5 | 152.3 | 0.151 | north | Y | 0.0078998 | 0.18601 | 0.028867 | 0.32106 | 0.0078998 | North | N | 0.0078998 | 0
13136 | CALFREST | 6 | 177.5 | 0.151 | north | Y | 0.0078998 | 0.18601 | 0.028867 | 0.32106 | 0.0078998 | North | N | 0.0078998 | 0
13432 | SANDOW_5 | 5 | 581 | 0.034628 | south | Y | -0.10847 | 0.069642 | -0.087502 | 0.20469 | 0.069642 | south | N | 0.069642 | 0
13691 | OAKGROVE | 1 | 855 | 0.17865 | north | Y | 0.035553 | 0.21366 | 0.05652 | 0.34871 | 0.035553 | North | N | 0.035553 | 0
13692 | OAKGROVE | 2 | 855 | 0.17865 | north | Y | 0.035553 | 0.21366 | 0.05652 | 0.34871 | 0.035553 | North | N | 0.035553 | 0
32798 | BRYN_TAM | 1 | 32 | 0.19085 | north | N | 0.047756 | 0.22587 | 0.068723 | 0.36092 | 0.047756 | North | N | 0.047756 | 0
32883 | BRYN_DNS | 1 | 48 | 0.1861 | north | Y | 0.043001 | 0.22111 | 0.063968 | 0.35616 | 0.043001 | North | N | 0.043001 | 0
32884 | BRYN_DNS | 1 | 46 | 0.1861 | north | Y | 0.043001 | 0.22111 | 0.063968 | 0.35616 | 0.043001 | North | N | 0.043001 | 0
32886 | BRYN_ATK | MB | 12 | 0.19043 | north | Y | 0.047338 | 0.22545 | 0.068305 | 0.3605 | 0.047338 | North | N | 0.047338 | 0
32887 | BRYN_ATK | MB | 51 | 0.19043 | north | Y | 0.047338 | 0.22545 | 0.068305 | 0.3605 | 0.047338 | North | N | 0.047338 | 0
32888 | BRYN_ATK | 1 | 17 | 0.19043 | north | Y | 0.047338 | 0.22545 | 0.068305 | 0.3605 | 0.047338 | North | N | 0.047338 | 0
32890 | BRYN_ATK | MB | 22 | 0.19043 | north | Y | 0.047338 | 0.22545 | 0.068305 | 0.3605 | 0.047338 | North | N | 0.047338 | 0
32891 | BRYN_ATK | MB | 25 | 0.19043 | north | Y | 0.047338 | 0.22545 | 0.068305 | 0.3605 | 0.047338 | North | N | 0.047338 | 0
32892 | BRYN_DNS | 1 | 105 | 0.1861 | north | Y | 0.043001 | 0.22111 | 0.063968 | 0.35616 | 0.043001 | North | N | 0.043001 | 0
36998 | RDCNYNG1 | 1 | 84 | 0.12357 | west | Y | -0.019525 | 0.15859 | 0.0014417 | 0.29364 | 0.0014417 | west | N | 0.0014417 | 0
38332 | WDWRDU2 | 1 | 80 | 0.11421 | west | Y | -0.028892 | 0.14922 | -0.0079253 | 0.28427 | 0.0079253 | west | N | 0.0079253 | 0
38437 | TNSRBNMS | 1 | 150 | 0.11414 | west | Y | -0.028953 | 0.14916 | -0.0079863 | 0.28421 | 0.0079863 | west | N | 0.0079863 | 0
38438 | TNSRBNMS | 1 | 150 | 0.11414 | west | Y | -0.028953 | 0.14916 | -0.0079863 | 0.28421 | 0.0079863 | west | N | 0.0079863 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.1644 | houston | N | -0.3075 | -0.12939 | -0.28653 | 0.0056622 | 0.0056622 | houston | N | 0.0056622 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.1644 | houston | N | -0.3075 | -0.12939 | -0.28653 | 0.0056622 | 0.0056622 | houston | N | 0.0056622 | 0
38600 | TNBP_CGN | 5 | 53 | -0.1644 | houston | N | -0.3075 | -0.12939 | -0.28653 | 0.0056622 | 0.0056622 | houston | N | 0.0056622 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.1644 | houston | N | -0.3075 | -0.12939 | -0.28653 | 0.0056622 | 0.0056622 | houston | N | 0.0056622 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.1644 | houston | N | -0.3075 | -0.12939 | -0.28653 | 0.0056622 | 0.0056622 | houston | N | 0.0056622 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.1644 | houston | N | -0.3075 | -0.12939 | -0.28653 | 0.0056622 | 0.0056622 | houston | N | 0.0056622 | 0
38614 | TNBPAMCG | 4 | 96 | -0.1644 | houston | N | -0.3075 | -0.12939 | -0.28653 | 0.0056622 | 0.0056622 | houston | N | 0.0056622 | 0
38615 | TNBPAMCG | 1 | 244 | -0.1644 | houston | N | -0.3075 | -0.12939 | -0.28653 | 0.0056622 | 0.0056622 | houston | N | 0.0056622 | 0
38690 | TNBP_CGN | 3 | 40 | -0.1644 | houston | N | -0.3075 | -0.12939 | -0.28653 | 0.0056622 | 0.0056622 | houston | N | 0.0056622 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.16435 | houston | N | -0.30745 | -0.12934 | -0.28648 | 0.0057132 | 0.0057132 | houston | N | 0.0057132 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.16435 | houston | N | -0.30745 | -0.12934 | -0.28648 | 0.0057132 | 0.0057132 | houston | N | 0.0057132 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.16435 | houston | N | -0.30745 | -0.12934 | -0.28648 | 0.0057132 | 0.0057132 | houston | N | 0.0057132 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.16435 | houston | N | -0.30745 | -0.12934 | -0.28648 | 0.0057132 | 0.0057132 | houston | N | 0.0057132 | 0
39470 | TNDOWCGN | 1 | 32 | -0.16435 | houston | N | -0.30745 | -0.12934 | -0.28648 | 0.0057112 | 0.0057112 | houston | N | 0.0057112 | 0
39480 | TNDOWCGN | 1 | 30 | -0.16435 | houston | N | -0.30745 | -0.12934 | -0.28648 | 0.0057112 | 0.0057112 | houston | N | 0.0057112 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.14254 | houston | N | -0.28564 | -0.10752 | -0.26467 | 0.027524 | 0.027524 | houston | N | 0.027524 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.14254 | houston | N | -0.28564 | -0.10752 | -0.26467 | 0.027524 | 0.027524 | houston | N | 0.027524 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.14254 | houston | N | -0.28564 | -0.10752 | -0.26467 | 0.027524 | 0.027524 | houston | N | 0.027524 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.14254 | houston | N | -0.28564 | -0.10752 | -0.26467 | 0.027524 | 0.027524 | houston | N | 0.027524 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.17865 | north | Y | 0.035553 | 0.21366 | 0.05652 | 0.34871 | 0.035553 | North | N | 0.035553 | 0
39970 | TNTNPONE | 1 | 153 | 0.17865 | north | Y | 0.035553 | 0.21366 | 0.05652 | 0.34871 | 0.035553 | North | N | 0.035553 | 0
48500 | APD_GT1_ | 1 | 136 | -0.18242 | houston | N | -0.32552 | -0.14741 | -0.30455 | -0.01236 | 0.01236 | houston | N | 0.01236 | 0
48510 | AK_GT1__ | 1 | 33 | -0.1576 | houston | N | -0.3007 | -0.12259 | -0.27973 | 0.012462 | 0.012462 | houston | N | 0.012462 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.18226 | houston | Y | -0.32536 | -0.14724 | -0.30439 | -0.012196 | 0.012196 | houston | N | 0.012196 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.18226 | houston | Y | -0.32536 | -0.14724 | -0.30439 | -0.012196 | 0.012196 | houston | N | 0.012196 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.18226 | houston | Y | -0.32536 | -0.14724 | -0.30439 | -0.012196 | 0.012196 | houston | N | 0.012196 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.18226 | houston | Y | -0.32536 | -0.14724 | -0.30439 | -0.012196 | 0.012196 | houston | N | 0.012196 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.13858 | houston | N | -0.28167 | -0.10356 | -0.26071 | 0.031486 | 0.031486 | houston | N | 0.031486 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.13858 | houston | N | -0.28167 | -0.10356 | -0.26071 | 0.031486 | 0.031486 | houston | N | 0.031486 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.14571 | houston | N | -0.28881 | -0.1107 | -0.26784 | 0.024353 | 0.024353 | houston | N | 0.024353 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.14571 | houston | N | -0.28881 | -0.1107 | -0.26784 | 0.024353 | 0.024353 | houston | N | 0.024353 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.14571 | houston | N | -0.28881 | -0.1107 | -0.26784 | 0.024353 | 0.024353 | houston | N | 0.024353 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.17538 | houston | N | -0.31848 | -0.14036 | -0.29751 | -0.0053158 | 0.0053158 | houston | N | 0.0053158 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.17538 | houston | N | -0.31848 | -0.14036 | -0.29751 | -0.0053158 | 0.0053158 | houston | N | 0.0053158 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.17538 | houston | N | -0.31848 | -0.14036 | -0.29751 | -0.0053158 | 0.0053158 | houston | N | 0.0053158 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.17538 | houston | N | -0.31848 | -0.14036 | -0.29751 | -0.0053158 | 0.0053158 | houston | N | 0.0053158 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.17968 | houston | N | -0.32277 | -0.14466 | -0.30181 | -0.0096128 | 0.0096128 | houston | N | 0.0096128 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.17968 | houston | N | -0.32277 | -0.14466 | -0.30181 | -0.0096128 | 0.0096128 | houston | N | 0.0096128 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.17419 | houston | N | -0.31729 | -0.13918 | -0.29632 | -0.0041268 | 0.0041268 | houston | N | 0.0041268 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.17419 | houston | N | -0.31729 | -0.13918 | -0.29632 | -0.0041268 | 0.0041268 | houston | N | 0.0041268 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.17419 | houston | N | -0.31729 | -0.13918 | -0.29632 | -0.0041268 | 0.0041268 | houston | N | 0.0041268 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.17419 | houston | N | -0.31729 | -0.13918 | -0.29632 | -0.0041268 | 0.0041268 | houston | N | 0.0041268 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.17419 | houston | N | -0.31729 | -0.13918 | -0.29632 | -0.0041268 | 0.0041268 | houston | N | 0.0041268 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.1881 | houston | Y | -0.3312 | -0.15309 | -0.31023 | -0.018038 | 0.018038 | houston | N | 0.018038 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.18573 | houston | Y | -0.32883 | -0.15072 | -0.30786 | -0.015669 | 0.015669 | houston | N | 0.015669 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.18905 | houston | Y | -0.33215 | -0.15404 | -0.31118 | -0.01899 | 0.01899 | houston | N | 0.01899 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.18905 | houston | Y | -0.33215 | -0.15404 | -0.31118 | -0.01899 | 0.01899 | houston | N | 0.01899 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.18905 | houston | Y | -0.33215 | -0.15404 | -0.31118 | -0.01899 | 0.01899 | houston | N | 0.01899 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.19619 | houston | N | -0.33928 | -0.16117 | -0.31832 | -0.026123 | 0.026123 | houston | N | 0.026123 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.18274 | houston | N | -0.32583 | -0.14772 | -0.30487 | -0.012674 | 0.012674 | houston | N | 0.012674 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.18274 | houston | N | -0.32583 | -0.14772 | -0.30487 | -0.012674 | 0.012674 | houston | N | 0.012674 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.19 | houston | N | -0.33309 | -0.15498 | -0.31213 | -0.019934 | 0.019934 | houston | N | 0.019934 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.19 | houston | N | -0.33309 | -0.15498 | -0.31213 | -0.019934 | 0.019934 | houston | N | 0.019934 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.19 | houston | N | -0.33309 | -0.15498 | -0.31213 | -0.019934 | 0.019934 | houston | N | 0.019934 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.19 | houston | N | -0.33309 | -0.15498 | -0.31213 | -0.019934 | 0.019934 | houston | N | 0.019934 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.17985 | houston | N | -0.32295 | -0.14483 | -0.30198 | -0.0097848 | 0.0097848 | houston | N | 0.0097848 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.17985 | houston | N | -0.32295 | -0.14483 | -0.30198 | -0.0097848 | 0.0097848 | houston | N | 0.0097848 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.17985 | houston | N | -0.32295 | -0.14483 | -0.30198 | -0.0097848 | 0.0097848 | houston | N | 0.0097848 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.17985 | houston | N | -0.32295 | -0.14483 | -0.30198 | -0.0097848 | 0.0097848 | houston | N | 0.0097848 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.17891 | houston | N | -0.32201 | -0.1439 | -0.30104 | -0.0088498 | 0.0088498 | houston | N | 0.0088498 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.17891 | houston | N | -0.32201 | -0.1439 | -0.30104 | -0.0088498 | 0.0088498 | houston | N | 0.0088498 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.17891 | houston | N | -0.32201 | -0.1439 | -0.30104 | -0.0088498 | 0.0088498 | houston | N | 0.0088498 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.17891 | houston | N | -0.32201 | -0.1439 | -0.30104 | -0.0088498 | 0.0088498 | houston | N | 0.0088498 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.17891 | houston | N | -0.32201 | -0.1439 | -0.30104 | -0.0088498 | 0.0088498 | houston | N | 0.0088498 | 0
48651 | EP_1_2 | 1 | 5 | -0.18761 | houston | N | -0.33071 | -0.1526 | -0.30974 | -0.017551 | 0.017551 | houston | N | 0.017551 | 0
48651 | EP_1_2 | 2 | 21 | -0.18761 | houston | N | -0.33071 | -0.1526 | -0.30974 | -0.017551 | 0.017551 | houston | N | 0.017551 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.21109 | north | N | 0.067991 | 0.2461 | 0.088958 | 0.38115 | 0.067991 | North | N | 0.067991 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.21109 | north | N | 0.067991 | 0.2461 | 0.088958 | 0.38115 | 0.067991 | North | N | 0.067991 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.21109 | north | N | 0.067991 | 0.2461 | 0.088958 | 0.38115 | 0.067991 | North | N | 0.067991 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.21109 | north | N | 0.067991 | 0.2461 | 0.088958 | 0.38115 | 0.067991 | North | N | 0.067991 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.18894 | houston | Y | -0.33204 | -0.15392 | -0.31107 | -0.018876 | 0.018876 | houston | N | 0.018876 | 0
48691 | GBY_7374 | A | 46 | -0.17991 | houston | Y | -0.32301 | -0.14489 | -0.30204 | -0.0098458 | 0.0098458 | houston | N | 0.0098458 | 0
48691 | GBY_7374 | B | 46 | -0.17991 | houston | Y | -0.32301 | -0.14489 | -0.30204 | -0.0098458 | 0.0098458 | houston | N | 0.0098458 | 0
48692 | GBY_8182 | C | 46 | -0.17991 | houston | Y | -0.32301 | -0.14489 | -0.30204 | -0.0098458 | 0.0098458 | houston | N | 0.0098458 | 0
48692 | GBY_8182 | D | 55 | -0.17991 | houston | Y | -0.32301 | -0.14489 | -0.30204 | -0.0098458 | 0.0098458 | houston | N | 0.0098458 | 0
48693 | GBY_8384 | E | 55 | -0.17991 | houston | Y | -0.32301 | -0.14489 | -0.30204 | -0.0098458 | 0.0098458 | houston | N | 0.0098458 | 0
48693 | GBY_8384 | F | 54 | -0.17991 | houston | Y | -0.32301 | -0.14489 | -0.30204 | -0.0098458 | 0.0098458 | houston | N | 0.0098458 | 0
48721 | LEG_1___ | 1 | 827 | 0.16839 | north | Y | 0.025297 | 0.20341 | 0.046264 | 0.33846 | 0.025297 | North | N | 0.025297 | 0
48722 | LEG_2___ | 2 | 819 | 0.16839 | north | Y | 0.025297 | 0.20341 | 0.046264 | 0.33846 | 0.025297 | North | N | 0.025297 | 0
48730 | MNS_GT | 1 | 46.1 | -0.15556 | houston | N | -0.29866 | -0.12055 | -0.27769 | 0.014502 | 0.014502 | houston | N | 0.014502 | 0
48731 | CBE_GT1 | 1 | 76 | -0.11546 | houston | Y | -0.25856 | -0.080448 | -0.23759 | 0.054601 | 0.054601 | houston | N | 0.054601 | 0
48732 | CBE_GT2 | 1 | 76 | -0.11546 | houston | Y | -0.25856 | -0.080448 | -0.23759 | 0.054601 | 0.054601 | houston | N | 0.054601 | 0
48733 | CBE_ST12 | 1 | 105 | -0.11546 | houston | Y | -0.25856 | -0.080448 | -0.23759 | 0.054601 | 0.054601 | houston | N | 0.054601 | 0
48734 | CBE_GT3 | 1 | 74 | -0.11546 | houston | Y | -0.25856 | -0.080448 | -0.23759 | 0.054601 | 0.054601 | houston | N | 0.054601 | 0
48735 | CBE_GT4 | 1 | 74 | -0.11546 | houston | Y | -0.25856 | -0.080448 | -0.23759 | 0.054601 | 0.054601 | houston | N | 0.054601 | 0
48736 | CBE_ST34 | 1 | 102 | -0.11546 | houston | Y | -0.25856 | -0.080448 | -0.23759 | 0.054601 | 0.054601 | houston | N | 0.054601 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.17985 | houston | N | -0.32294 | -0.14483 | -0.30198 | -0.0097828 | 0.0097828 | houston | N | 0.0097828 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.17985 | houston | N | -0.32294 | -0.14483 | -0.30198 | -0.0097828 | 0.0097828 | houston | N | 0.0097828 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.17985 | houston | N | -0.32294 | -0.14483 | -0.30198 | -0.0097828 | 0.0097828 | houston | N | 0.0097828 | 0
48761 | PR_GT1__ | 1 | 35 | -0.17909 | houston | N | -0.32219 | -0.14408 | -0.30122 | -0.0090278 | 0.0090278 | houston | N | 0.0090278 | 0
48772 | PHR_GN2_ | MB | 459 | -0.17078 | houston | Y | -0.31387 | -0.13576 | -0.29291 | -0.00071385 | 0.00071385 | houston | N | 0.00071385 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.18654 | houston | N | -0.32964 | -0.15152 | -0.30867 | -0.016476 | 0.016476 | houston | N | 0.016476 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.18654 | houston | N | -0.32964 | -0.15152 | -0.30867 | -0.016476 | 0.016476 | houston | N | 0.016476 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.18654 | houston | N | -0.32964 | -0.15152 | -0.30867 | -0.016476 | 0.016476 | houston | N | 0.016476 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.18654 | houston | N | -0.32964 | -0.15152 | -0.30867 | -0.016476 | 0.016476 | houston | N | 0.016476 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.18654 | houston | N | -0.32964 | -0.15152 | -0.30867 | -0.016476 | 0.016476 | houston | N | 0.016476 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.18654 | houston | N | -0.32964 | -0.15152 | -0.30867 | -0.016476 | 0.016476 | houston | N | 0.016476 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.18654 | houston | N | -0.32964 | -0.15152 | -0.30867 | -0.016476 | 0.016476 | houston | N | 0.016476 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.19619 | houston | N | -0.33928 | -0.16117 | -0.31832 | -0.026123 | 0.026123 | houston | N | 0.026123 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.19619 | houston | N | -0.33928 | -0.16117 | -0.31832 | -0.026123 | 0.026123 | houston | N | 0.026123 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.19619 | houston | N | -0.33928 | -0.16117 | -0.31832 | -0.026123 | 0.026123 | houston | N | 0.026123 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.19619 | houston | N | -0.33928 | -0.16117 | -0.31832 | -0.026123 | 0.026123 | houston | N | 0.026123 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.18696 | houston | N | -0.33006 | -0.15195 | -0.30909 | -0.016898 | 0.016898 | houston | N | 0.016898 | 0
48820 | SHELLG1_ | 1 | 71 | -0.18075 | houston | N | -0.32384 | -0.14573 | -0.30288 | -0.010684 | 0.010684 | houston | N | 0.010684 | 0
48821 | SHELLG2 | 2 | 72 | -0.18075 | houston | N | -0.32384 | -0.14573 | -0.30288 | -0.010684 | 0.010684 | houston | N | 0.010684 | 0
48822 | SHELLG3_ | 1 | 39 | -0.18075 | houston | N | -0.32384 | -0.14573 | -0.30288 | -0.010684 | 0.010684 | houston | N | 0.010684 | 0
48822 | SHELLG3_ | 2 | 30 | -0.18075 | houston | N | -0.32384 | -0.14573 | -0.30288 | -0.010684 | 0.010684 | houston | N | 0.010684 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.17772 | houston | N | -0.32082 | -0.14271 | -0.29986 | -0.0076618 | 0.0076618 | houston | N | 0.0076618 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.17772 | houston | N | -0.32082 | -0.14271 | -0.29986 | -0.0076618 | 0.0076618 | houston | N | 0.0076618 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.17984 | houston | N | -0.32294 | -0.14483 | -0.30197 | -0.0097768 | 0.0097768 | houston | N | 0.0097768 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.17968 | houston | Y | -0.32278 | -0.14467 | -0.30181 | -0.0096208 | 0.0096208 | houston | N | 0.0096208 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.17964 | houston | Y | -0.32274 | -0.14463 | -0.30177 | -0.0095788 | 0.0095788 | houston | N | 0.0095788 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.17983 | houston | Y | -0.32293 | -0.14482 | -0.30196 | -0.0097668 | 0.0097668 | houston | N | 0.0097668 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.17986 | houston | Y | -0.32296 | -0.14485 | -0.30199 | -0.0097988 | 0.0097988 | houston | N | 0.0097988 | 0
48855 | SRB_GT21 | B2 | 12 | -0.17961 | houston | Y | -0.32271 | -0.1446 | -0.30174 | -0.0095478 | 0.0095478 | houston | N | 0.0095478 | 0
48855 | SRB_GT21 | MB | 18 | -0.17961 | houston | Y | -0.32271 | -0.1446 | -0.30174 | -0.0095478 | 0.0095478 | houston | N | 0.0095478 | 0
48865 | TECO_GT1 | 1 | 50 | -0.16972 | houston | Y | -0.31282 | -0.1347 | -0.29185 | 0.00034415 | 0.00034415 | houston | N | 0.00034415 | 0
48873 | THW_ST3_ | 3 | 104 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48874 | THW_ST4_ | 4 | 104 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48875 | THW_3132 | A | 54 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48875 | THW_3132 | B | 53 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48877 | THW_3334 | C | 54 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48877 | THW_3334 | D | 57 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48879 | THW_4142 | E | 54 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48879 | THW_4142 | F | 54 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48881 | THW_4344 | G | 58 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48881 | THW_4344 | H | 58 | -0.19867 | houston | Y | -0.34176 | -0.16365 | -0.3208 | -0.028603 | 0.028603 | houston | N | 0.028603 | 0
48883 | THW_GT1_ | B2 | 12 | -0.19895 | houston | Y | -0.34205 | -0.16393 | -0.32108 | -0.028886 | 0.028886 | houston | N | 0.028886 | 0
48885 | THW_5152 | A | 56 | -0.22036 | houston | Y | -0.36346 | -0.18535 | -0.34249 | -0.050297 | 0.050297 | houston | N | 0.050297 | 0
48885 | THW_5152 | B | 59 | -0.22036 | houston | Y | -0.36346 | -0.18535 | -0.34249 | -0.050297 | 0.050297 | houston | N | 0.050297 | 0
48886 | THW_5354 | C | 56 | -0.22036 | houston | Y | -0.36346 | -0.18535 | -0.34249 | -0.050297 | 0.050297 | houston | N | 0.050297 | 0
48886 | THW_5354 | D | 56 | -0.22036 | houston | Y | -0.36346 | -0.18535 | -0.34249 | -0.050297 | 0.050297 | houston | N | 0.050297 | 0
48887 | THW_5556 | E | 59 | -0.22036 | houston | Y | -0.36346 | -0.18535 | -0.34249 | -0.050297 | 0.050297 | houston | N | 0.050297 | 0
48887 | THW_5556 | F | 56 | -0.22036 | houston | Y | -0.36346 | -0.18535 | -0.34249 | -0.050297 | 0.050297 | houston | N | 0.050297 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.12068 | houston | Y | -0.26377 | -0.085663 | -0.24281 | 0.049386 | 0.049386 | houston | N | 0.049386 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.15627 | houston | Y | -0.29937 | -0.12125 | -0.2784 | 0.013795 | 0.013795 | houston | N | 0.013795 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.15627 | houston | Y | -0.29937 | -0.12125 | -0.2784 | 0.013795 | 0.013795 | houston | N | 0.013795 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.15627 | houston | Y | -0.29937 | -0.12125 | -0.2784 | 0.013795 | 0.013795 | houston | N | 0.013795 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.15627 | houston | Y | -0.29937 | -0.12125 | -0.2784 | 0.013795 | 0.013795 | houston | N | 0.013795 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.15627 | houston | N | -0.29937 | -0.12125 | -0.2784 | 0.013795 | 0.013795 | houston | N | 0.013795 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.14552 | houston | Y | -0.28862 | -0.11051 | -0.26765 | 0.02454 | 0.02454 | houston | N | 0.02454 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.14552 | houston | Y | -0.28862 | -0.11051 | -0.26765 | 0.02454 | 0.02454 | houston | N | 0.02454 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.14552 | houston | Y | -0.28862 | -0.11051 | -0.26765 | 0.02454 | 0.02454 | houston | N | 0.02454 | 0
48929 | WAPGT21_ | B1 | 13 | -0.15627 | houston | Y | -0.29937 | -0.12125 | -0.2784 | 0.013795 | 0.013795 | houston | N | 0.013795 | 0
48940 | WARVUE_G | G1 | 12 | -0.18785 | houston | Y | -0.33094 | -0.15283 | -0.30998 | -0.017784 | 0.017784 | houston | N | 0.017784 | 0
49803 | EXN_15GT | 1 | 34 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49826 | EXN938GT | 5 | 45.9 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49828 | EXN941GT | 10 | 17.7 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49829 | EXN942GT | 11 | 20.4 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49830 | EXN943GT | 12 | 19.9 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49831 | EXN944GT | 13 | 35 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49832 | EXN945GT | 9 | 18 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49837 | EXN_GT | 4 | 85.4 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49838 | EXN_14GT | 14 | 148 | -0.18604 | houston | N | -0.32914 | -0.15102 | -0.30817 | -0.015975 | 0.015975 | houston | N | 0.015975 | 0
49851 | DOW17000 | 37 | 62 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49858 | DOW38100 | 31 | 71.4 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49859 | DOW38200 | 33 | 45 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49860 | DOW38300 | 32 | 101 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49862 | DOW39100 | 36 | 86 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49863 | DOW39200 | 35 | 88 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49865 | DOW41000 | 41 | 50 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49866 | DOW42000 | 42 | 18 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49869 | DOW49000 | 45 | 94 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49870 | DOW61000 | 61 | 70 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49871 | DOW62000 | 62 | 63 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49872 | DOW63000 | 63 | 72 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49873 | DOW64000 | 64 | 64.8 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49876 | DOW65000 | 65 | 101 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49877 | DOW66000 | 66 | 97 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49878 | DOW67000 | 67 | 103 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49882 | DOW81000 | 81 | 76 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49884 | DOW82000 | 82 | 80 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49885 | DOW83000 | 83 | 80 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
49886 | DOW84000 | 84 | 171 | -0.13357 | houston | N | -0.27667 | -0.098556 | -0.2557 | 0.036493 | 0.036493 | houston | N | 0.036493 | 0
58909 | PEARSALL | 1 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58909 | PEARSALL | 2 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58909 | PEARSALL | 3 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58909 | PEARSALL | 4 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58909 | PEARSALL | 5 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58909 | PEARSALL | 6 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58919 | PEARSALL | 1 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58919 | PEARSALL | 2 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58919 | PEARSALL | 3 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58919 | PEARSALL | 4 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58919 | PEARSALL | 5 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58919 | PEARSALL | 6 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58929 | PEARSALL | 1 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58929 | PEARSALL | 2 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58929 | PEARSALL | 3 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58929 | PEARSALL | 4 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58929 | PEARSALL | 5 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58929 | PEARSALL | 6 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58949 | PEARSALL | 1 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58949 | PEARSALL | 2 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58949 | PEARSALL | 3 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58949 | PEARSALL | 4 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58949 | PEARSALL | 5 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
58949 | PEARSALL | 6 | 8.4 | -0.039279 | south | Y | -0.18238 | -0.0042648 | -0.16141 | 0.13078 | 0.0042648 | south | N | 0.0042648 | 0
60000 | DSKY2 | 1 | 76.5 | 0.11132 | west | Y | -0.031777 | 0.14633 | -0.01081 | 0.28138 | 0.01081 | west | N | 0.01081 | 0
60003 | KING_NE1 | 1 | 80 | 0.11432 | west | Y | -0.028772 | 0.14934 | -0.0078053 | 0.28439 | 0.0078053 | west | N | 0.0078053 | 0
60005 | KING_SE1 | 1 | 40 | 0.11432 | west | Y | -0.028772 | 0.14934 | -0.0078053 | 0.28439 | 0.0078053 | west | N | 0.0078053 | 0
60007 | KING_SW1 | 1 | 80 | 0.11481 | west | Y | -0.028288 | 0.14982 | -0.0073213 | 0.28487 | 0.0073213 | west | N | 0.0073213 | 0
60016 | WOODWRD1 | 1 | 80 | 0.11422 | west | Y | -0.028878 | 0.14923 | -0.0079113 | 0.28428 | 0.0079113 | west | N | 0.0079113 | 0
60017 | ORNNWP1 | 1 | 80 | 0.11172 | west | Y | -0.031373 | 0.14674 | -0.010406 | 0.28179 | 0.010406 | west | N | 0.010406 | 0
60018 | DSKY1 | 1 | 84 | 0.11091 | west | Y | -0.032189 | 0.14592 | -0.011222 | 0.28097 | 0.011222 | west | N | 0.011222 | 0
60019 | KING_NW1 | 1 | 80 | 0.11481 | west | Y | -0.028288 | 0.14982 | -0.0073213 | 0.28487 | 0.0073213 | west | N | 0.0073213 | 0
60057 | CALLAHAN | 1 | 114 | -0.031165 | south | Y | -0.17426 | 0.0038492 | -0.1533 | 0.1389 | 0.0038492 | south | N | 0.0038492 | 0
60058 | BUFF_GAP | 1 | 120 | 0.12287 | west | Y | -0.020224 | 0.15789 | 0.00074267 | 0.29294 | 0.00074267 | west | N | 0.00074267 | 0
60060 | CIRELLO | 1 | 233 | 0.12287 | west | Y | -0.020224 | 0.15789 | 0.00074267 | 0.29294 | 0.00074267 | west | N | 0.00074267 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.12287 | west | Y | -0.020224 | 0.15789 | 0.00074267 | 0.29294 | 0.00074267 | west | N | 0.00074267 | 0
60066 | H_HOLLOW | 1 | 222 | -0.031165 | south | Y | -0.17426 | 0.0038492 | -0.1533 | 0.1389 | 0.0038492 | south | N | 0.0038492 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.031165 | south | Y | -0.17426 | 0.0038492 | -0.1533 | 0.1389 | 0.0038492 | south | N | 0.0038492 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.031165 | south | Y | -0.17426 | 0.0038492 | -0.1533 | 0.1389 | 0.0038492 | south | N | 0.0038492 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.031165 | south | Y | -0.17426 | 0.0038492 | -0.1533 | 0.1389 | 0.0038492 | south | N | 0.0038492 | 0
60074 | HORSH5 | 1 | 100 | -0.031165 | south | Y | -0.17426 | 0.0038492 | -0.1533 | 0.1389 | 0.0038492 | south | N | 0.0038492 | 0
60081 | WHRLWIND | 1 | 60 | 0.12515 | west | Y | -0.017946 | 0.16017 | 0.0030207 | 0.29521 | 0.0030207 | west | N | 0.0030207 | 0
60201 | RIO DRCS | F | 0 | 0.03057 | south | N | -0.11253 | 0.065584 | -0.09156 | 0.20063 | 0.065584 | south | N | 0.065584 | 0
60202 | FRIEND_R | F | 0 | 0.097892 | west | N | -0.045205 | 0.13291 | -0.024238 | 0.26796 | 0.024238 | west | N | 0.024238 | 0
60203 | PRES0A | BT | 4.8 | 0.1166 | west | N | -0.026495 | 0.15162 | -0.0055283 | 0.28667 | 0.0055283 | west | N | 0.0055283 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.12413 | west | Y | -0.018962 | 0.15915 | 0.0020047 | 0.2942 | 0.0020047 | west | N | 0.0020047 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.12413 | west | Y | -0.018962 | 0.15915 | 0.0020047 | 0.2942 | 0.0020047 | west | N | 0.0020047 | 0
71057 | L_SWEETW | W1 | 135 | 0.12413 | west | Y | -0.018962 | 0.15915 | 0.0020047 | 0.2942 | 0.0020047 | west | N | 0.0020047 | 0
71059 | L_SWEETW | W1 | 119 | 0.12413 | west | Y | -0.018962 | 0.15915 | 0.0020047 | 0.2942 | 0.0020047 | west | N | 0.0020047 | 0
71060 | L_SWEETW | W1 | 105 | 0.12413 | west | Y | -0.018962 | 0.15915 | 0.0020047 | 0.2942 | 0.0020047 | west | N | 0.0020047 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.12413 | west | Y | -0.018962 | 0.15915 | 0.0020047 | 0.2942 | 0.0020047 | west | N | 0.0020047 | 0
76031 | L_GASCCR | W1 | 150 | 0.12215 | west | Y | -0.020951 | 0.15716 | 1.5674e-05 | 0.29221 | 1.5674e-05 | west | N | 1.5674e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.12189 | west | Y | -0.021203 | 0.15691 | -0.00023633 | 0.29196 | 0.00023633 | west | N | 0.00023633 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.12189 | west | Y | -0.021203 | 0.15691 | -0.00023633 | 0.29196 | 0.00023633 | west | N | 0.00023633 | 0
76096 | L_CAPRSI | W1 | 186 | 0.12189 | west | Y | -0.021203 | 0.15691 | -0.00023633 | 0.29196 | 0.00023633 | west | N | 0.00023633 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.12189 | west | Y | -0.021203 | 0.15691 | -0.00023633 | 0.29196 | 0.00023633 | west | N | 0.00023633 | 0
80003 | MILHWYS | F | 0 | -0.063721 | south | N | -0.20682 | -0.028707 | -0.18585 | 0.10634 | 0.028707 | south | N | 0.028707 | 0
80010 | EPLVT1 | F | 0 | -0.014933 | south | N | -0.15803 | 0.020081 | -0.13706 | 0.15513 | 0.020081 | south | N | 0.020081 | 0
80012 | LAR | F | 0 | -0.047631 | south | N | -0.19073 | -0.012617 | -0.16976 | 0.12243 | 0.012617 | south | N | 0.012617 | 0
80051 | FORPVCM0 | 8 | 28 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
80053 | FOR69CG0 | 10 | 74 | -0.076946 | south | N | -0.22004 | -0.041932 | -0.19908 | 0.093117 | 0.041932 | south | N | 0.041932 | 0
80080 | GWINDT11 | 1 | 94 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80080 | GWINDT11 | 2 | 41 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80080 | GWINDT11 | 3 | 38 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80080 | GWINDT11 | 4 | 19 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80081 | GWINDT21 | 1 | 94 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80081 | GWINDT21 | 2 | 36 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80081 | GWINDT21 | 3 | 43 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80081 | GWINDT21 | 4 | 22 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80137 | CSDR89 | 8 | 39 | -0.072457 | south | N | -0.21555 | -0.037443 | -0.19459 | 0.097606 | 0.037443 | south | N | 0.037443 | 0
80137 | CSDR89 | 9 | 15 | -0.072457 | south | N | -0.21555 | -0.037443 | -0.19459 | 0.097606 | 0.037443 | south | N | 0.037443 | 0
80138 | CSDR7 | 7 | 7 | -0.072457 | south | N | -0.21555 | -0.037443 | -0.19459 | 0.097606 | 0.037443 | south | N | 0.037443 | 0
80139 | CSDR56 | 5 | 15 | -0.072457 | south | N | -0.21555 | -0.037443 | -0.19459 | 0.097606 | 0.037443 | south | N | 0.037443 | 0
80139 | CSDR56 | 6 | 39 | -0.072457 | south | N | -0.21555 | -0.037443 | -0.19459 | 0.097606 | 0.037443 | south | N | 0.037443 | 0
80140 | CSDR11 | 11 | 39 | -0.072456 | south | N | -0.21555 | -0.037442 | -0.19459 | 0.097607 | 0.037442 | south | N | 0.037442 | 0
80180 | PNSCALT1 | 1 | 148 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80180 | PNSCALT1 | 2 | 50 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80181 | PNSCALT2 | 1 | 55 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80181 | PNSCALT2 | 2 | 50 | -0.063916 | south | Y | -0.20701 | -0.028902 | -0.18605 | 0.10615 | 0.028902 | south | N | 0.028902 | 0
80223 | REYSHR G | 1 | 12 | -0.066907 | south | N | -0.21 | -0.031893 | -0.18904 | 0.10316 | 0.031893 | south | N | 0.031893 | 0
80224 | VISTRONG | 1 | 15 | -0.071081 | south | N | -0.21418 | -0.036067 | -0.19321 | 0.098982 | 0.036067 | south | N | 0.036067 | 0
80225 | VISTRONG | 2 | 23 | -0.071081 | south | N | -0.21418 | -0.036067 | -0.19321 | 0.098982 | 0.036067 | south | N | 0.036067 | 0
80226 | ALCOA G | 1 | 48 | -0.075904 | south | N | -0.219 | -0.04089 | -0.19803 | 0.094159 | 0.04089 | south | N | 0.04089 | 0
80227 | AIRCO G | 1 | 8 | -0.071905 | south | N | -0.215 | -0.036891 | -0.19404 | 0.098158 | 0.036891 | south | N | 0.036891 | 0
80261 | NBEC81A | 1 | 180 | -0.065422 | south | Y | -0.20852 | -0.030408 | -0.18755 | 0.10464 | 0.030408 | south | N | 0.030408 | 0
80262 | NBEC91A | 1 | 180 | -0.065466 | south | Y | -0.20856 | -0.030452 | -0.1876 | 0.1046 | 0.030452 | south | N | 0.030452 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.065154 | south | Y | -0.20825 | -0.03014 | -0.18728 | 0.10491 | 0.03014 | south | N | 0.03014 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.065154 | south | Y | -0.20825 | -0.03014 | -0.18728 | 0.10491 | 0.03014 | south | N | 0.03014 | 0
80265 | LARECU40 | 4 | 100 | -0.047627 | south | Y | -0.19072 | -0.012613 | -0.16976 | 0.12244 | 0.012613 | south | N | 0.012613 | 0
80266 | LARECU50 | 5 | 100 | -0.047627 | south | Y | -0.19072 | -0.012613 | -0.16976 | 0.12244 | 0.012613 | south | N | 0.012613 | 0
80291 | PAPALOTE | 1 | 25 | -0.066327 | south | Y | -0.20942 | -0.031313 | -0.18846 | 0.10374 | 0.031313 | south | N | 0.031313 | 0
80291 | PAPALOTE | 2 | 25 | -0.066327 | south | Y | -0.20942 | -0.031313 | -0.18846 | 0.10374 | 0.031313 | south | N | 0.031313 | 0
80291 | PAPALOTE | 3 | 25 | -0.066327 | south | Y | -0.20942 | -0.031313 | -0.18846 | 0.10374 | 0.031313 | south | N | 0.031313 | 0
80291 | PAPALOTE | 4 | 16 | -0.066327 | south | Y | -0.20942 | -0.031313 | -0.18846 | 0.10374 | 0.031313 | south | N | 0.031313 | 0
80294 | PAPALOTE | 5 | 25 | -0.066327 | south | Y | -0.20942 | -0.031313 | -0.18846 | 0.10374 | 0.031313 | south | N | 0.031313 | 0
80294 | PAPALOTE | 6 | 25 | -0.066327 | south | Y | -0.20942 | -0.031313 | -0.18846 | 0.10374 | 0.031313 | south | N | 0.031313 | 0
80294 | PAPALOTE | 7 | 25 | -0.066327 | south | Y | -0.20942 | -0.031313 | -0.18846 | 0.10374 | 0.031313 | south | N | 0.031313 | 0
80294 | PAPALOTE | 8 | 15 | -0.066327 | south | Y | -0.20942 | -0.031313 | -0.18846 | 0.10374 | 0.031313 | south | N | 0.031313 | 0
86104 | CID-138 | EQ | 0 | -0.047627 | south | N | -0.19072 | -0.012613 | -0.16976 | 0.12244 | 0.012613 | south | N | 0.012613 | 0
86105 | CID-230 | EQ | 500 | -0.047627 | south | N | -0.19072 | -0.012613 | -0.16976 | 0.12244 | 0.012613 | south | N | 0.012613 | 0
86106 | CUF-230 | EQ | 500 | -0.047627 | south | N | -0.19072 | -0.012613 | -0.16976 | 0.12244 | 0.012613 | south | N | 0.012613 | 0
86107 | CUF-138 | EQ | 0 | -0.047627 | south | N | -0.19072 | -0.012613 | -0.16976 | 0.12244 | 0.012613 | south | N | 0.012613 | 0
88198 | BEEVILLE | F | 0 | -0.057473 | south | N | -0.20057 | -0.022459 | -0.1796 | 0.11259 | 0.022459 | south | N | 0.022459 | 0
88253 | HAMILTON | F | 0 | 0.002535 | south | N | -0.14056 | 0.037549 | -0.1196 | 0.1726 | 0.037549 | south | N | 0.037549 | 0
88299 | ZAPATA | F | 0 | -0.053899 | south | N | -0.197 | -0.018885 | -0.17603 | 0.11616 | 0.018885 | south | N | 0.018885 | 0
88508 | FALFURRI | F | 0 | -0.060469 | south | N | -0.20357 | -0.025455 | -0.1826 | 0.10959 | 0.025455 | south | N | 0.025455 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:Singleton - TH Wharton 345kV 44645-45500 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45872 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.5498 | 0 | 0.38808 | 0 | 0 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.9297 | 0 | 0.38808 | 0 | 0 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.9297 | 0 | 0.38808 | 0 | 0 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | 1 | 80.2134 | 0 | 0.38808 | 0 | 0 | 0 | Weighted Shift Factors
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.20485 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 94.8437 | 463 | 0.38183 | 176.7887 | 463 | 176.7887 | North | 0.1431
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.19085 | north | 7 | N | N | Nnorth | Nnorth | 1 | 6.1073 | 0 | 0.36784 | 0 | 463 | 176.7887 | Houston | -0.17699
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.36742 | 0 | 463 | 176.7887 |  | 0.32008
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.36742 | 0 | 463 | 176.7887
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.19043 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.2374 | 17 | 0.36742 | 6.2462 | 480 | 183.0349 | Line Rating | 1450
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.36742 | 0 | 480 | 183.0349 | Conc Gen | 2694.3
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.36742 | 0 | 480 | 183.0349 | Weighted Imp. | 972.0042
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.1861 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.9327 | 48 | 0.36309 | 17.4281 | 528 | 200.463 | PTDF | 0.36076
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.1861 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.5605 | 46 | 0.36309 | 16.7019 | 574 | 217.1649
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.1861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 19.5403 | 105 | 0.36309 | 38.1239 | 679 | 255.2888 | Concentration | 1.1271
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 152.7457 | 855 | 0.35564 | 304.0697 | 1534 | 559.3585
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 152.7457 | 855 | 0.35564 | 304.0697 | 2389 | 863.4282
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 27.2084 | 152.3 | 0.35564 | 54.1635 | 2541.3 | 917.5918
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 27.3334 | 153 | 0.35564 | 54.4125 | 2694.3 | 972.0042
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.16839 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 139.2618 | 827 | 0.34538 | 285.6302
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.16839 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 137.9147 | 819 | 0.34538 | 282.8671
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.1526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 93.8502 | 615 | 0.32959 | 202.6973
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.1526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 89.5774 | 587 | 0.32959 | 193.4688
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.15125 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7935 | 150.7 | 0.32824 | 49.4655
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.15125 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8389 | 151 | 0.32824 | 49.564
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.15125 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.8319 | 177.4 | 0.32824 | 58.2294
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.876 | 151.5 | 0.32798 | 49.6896
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9968 | 152.3 | 0.32798 | 49.952
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.802 | 177.5 | 0.32798 | 58.2172
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.14524 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.4344 | 182 | 0.32223 | 58.6461
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.14524 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 70.2981 | 484 | 0.32223 | 155.9598
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.14517 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.2584 | 50 | 0.32215 | 16.1077
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.14511 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.3221 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.4021 | 0 | 0.3216 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.7992 | 0 | 0.3216 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.9683 | 0 | 0.3216 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | 1 | 57.699 | 0 | 0.3216 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.14404 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 113.0714 | 785 | 0.32103 | 252.0063
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.14404 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 114.5118 | 795 | 0.32103 | 255.2165
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.14404 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 112.3512 | 780 | 0.32103 | 250.4011
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.14031 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.429 | 224 | 0.3173 | 71.0741
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5613 | 161 | 0.31712 | 51.0562
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9816 | 164 | 0.31712 | 52.0075
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9816 | 164 | 0.31712 | 52.0075
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.0146 | 414 | 0.31712 | 131.2873
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7014 | 162 | 0.31712 | 51.3733
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5613 | 161 | 0.31712 | 51.0562
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8415 | 163 | 0.31712 | 51.6904
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 57.314 | 409 | 0.31712 | 129.7017
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.13927 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 54.0383 | 388 | 0.31626 | 122.7093
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.13927 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 71.7261 | 515 | 0.31626 | 162.8745
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.13911 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.7822 | 20 | 0.3161 | 6.322
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.13911 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.4778 | 25 | 0.3161 | 7.9025
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.13911 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7036 | 41 | 0.3161 | 12.96
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13901 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.316 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13901 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.316 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.5578 | 40 | 0.31593 | 12.6372
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.9762 | 79 | 0.31593 | 24.9582
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.7275 | 106 | 0.31593 | 33.4882
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.2851 | 146 | 0.31593 | 46.1252
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.13894 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.5594 | 76 | 0.31593 | 24.0104
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.1388 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.4493 | 558 | 0.31579 | 176.2081
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.1388 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.364 | 579 | 0.31579 | 182.8396
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.1388 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 112.1488 | 808 | 0.31579 | 255.1543
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.13869 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.4014 | 0 | 0.31567 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.13869 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.0393 | 0 | 0.31567 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.13869 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.2598 | 0 | 0.31567 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1768 | 160 | 0.31559 | 50.4947
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.6224 | 156 | 0.31559 | 49.2324
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.1666 | 196 | 0.31559 | 61.856
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.6224 | 156 | 0.31559 | 49.2324
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.761 | 157 | 0.31559 | 49.548
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.4438 | 198 | 0.31559 | 62.4872
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.1385 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 51.2435 | 370 | 0.31548 | 116.7287
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.3894 | 0 | 0.31548 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.5279 | 0 | 0.31548 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 42.7953 | 0 | 0.31548 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.8049 | 0 | 0.31548 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.9434 | 0 | 0.31548 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 42.9338 | 0 | 0.31548 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.13824 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 23.5015 | 170 | 0.31523 | 53.5893
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.13824 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 71.8869 | 520 | 0.31523 | 163.9202
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.13804 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.5217 | 0 | 0.31503 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.13804 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.5217 | 0 | 0.31503 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.13776 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.2562 | 118 | 0.31475 | 37.1406
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.13776 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.8429 | 115 | 0.31475 | 36.1964
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.13776 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 76.5968 | 556 | 0.31475 | 175.0016
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.13773 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31472 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.13744 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31443 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.13666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.7852 | 196 | 0.31365 | 61.4746
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.13666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.1691 | 111 | 0.31365 | 34.8147
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.13538 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.1229 | 60 | 0.31237 | 18.7421
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.13538 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.5291 | 63 | 0.31237 | 19.6793
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.1341 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 58.3352 | 435 | 0.31109 | 135.3246
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.13402 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.0777 | 112.5 | 0.31101 | 34.9887
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.13383 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 52.8617 | 395 | 0.31081 | 122.7716
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.13383 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 58.2147 | 435 | 0.31081 | 135.2041
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.13359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.91 | 216.4 | 0.31058 | 67.21
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.13359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8699 | 216.1 | 0.31058 | 67.1168
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.13354 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31053 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.13354 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31053 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.13354 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31053 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.6287 | 224 | 0.30926 | 69.2738
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8932 | 226 | 0.30926 | 69.8923
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0415 | 212 | 0.30926 | 65.5627
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.9092 | 211 | 0.30926 | 65.2535
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.13222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 38.0796 | 288 | 0.30921 | 89.0519
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.13222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.4365 | 147 | 0.30921 | 45.4536
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.13222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.4365 | 147 | 0.30921 | 45.4536
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.13168 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30867 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.13149 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.8242 | 204 | 0.30848 | 62.9295
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.13149 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.4297 | 201 | 0.30848 | 62.0041
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.13149 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.8208 | 242 | 0.30848 | 74.6517
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.13139 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.5513 | 217.3 | 0.30838 | 67.0106
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.13139 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.9352 | 205 | 0.30838 | 63.2175
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.13139 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.7909 | 272.4 | 0.30838 | 84.0022
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.13107 | north | 3 | N | N | Nnorth | Nnorth | 1 | 151.6457 | 0 | 0.30806 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.13107 | north | 3 | N | N | Nnorth | Nnorth | 1 | 151.7767 | 0 | 0.30806 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.13071 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3527 | 18 | 0.30769 | 5.5385
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.13071 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3527 | 18 | 0.30769 | 5.5385
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.13071 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.9668 | 38 | 0.30769 | 11.6923
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.0961 | 70 | 0.30693 | 21.4852
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.9662 | 69 | 0.30693 | 21.1783
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.9662 | 69 | 0.30693 | 21.1783
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.8363 | 68 | 0.30693 | 20.8714
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5939 | 20 | 0.30668 | 6.1336
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5939 | 20 | 0.30668 | 6.1336
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5939 | 20 | 0.30668 | 6.1336
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2048 | 17 | 0.30668 | 5.2136
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.12961 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5553 | 0 | 0.30659 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.12961 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5553 | 0 | 0.30659 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.12956 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 47.4182 | 366 | 0.30655 | 112.1955
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.12944 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.5328 | 120 | 0.30643 | 36.7712
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.12909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.6878 | 168 | 0.30608 | 51.4216
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.12909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6185 | 90 | 0.30608 | 27.5473
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.12882 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.174 | 242 | 0.30581 | 74.0048
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.12827 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.3637 | 73 | 0.30526 | 22.2838
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.12827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.2641 | 119 | 0.30526 | 36.3256
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.12827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.2953 | 205 | 0.30526 | 62.5777
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.12827 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.0835 | 102 | 0.30526 | 31.1362
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.12827 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.3139 | 96 | 0.30526 | 29.3047
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.12783 | west | 4 | Y | N | Ywest | Nwest | 1 | 83.0499 | 649.7 | 0.30482 | 198.0384
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.12719 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9862 | 165 | 0.30418 | 50.1891
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.12644 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.8401 | 236 | 0.30343 | 71.609
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.12644 | west | 6 | Y | N | Ywest | Nwest | 1 | 50.5748 | 400 | 0.30342 | 121.3696
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.12515 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5091 | 60 | 0.30214 | 18.1283
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12426 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.6393 | 150 | 0.30125 | 45.1874
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.12425 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.4548 | 60 | 0.30123 | 18.074
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.9653 | 209 | 0.30122 | 62.9556
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7159 | 126.5 | 0.30122 | 38.1047
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.9348 | 249 | 0.30122 | 75.0045
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.4745 | 197 | 0.30122 | 59.3409
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6551 | 37.5 | 0.30112 | 11.2921
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3445 | 107.5 | 0.30112 | 32.3706
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.7582 | 135 | 0.30112 | 40.6515
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7721 | 119 | 0.30112 | 35.8335
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.0342 | 105 | 0.30112 | 31.6178
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9929 | 80.5 | 0.30112 | 24.2403
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12379 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.474 | 125 | 0.30078 | 37.5974
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12379 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.474 | 125 | 0.30078 | 37.5974
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5467 | 150 | 0.30063 | 45.0948
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4881 | 101 | 0.30063 | 30.3638
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12357 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.38 | 84 | 0.30056 | 25.247
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12341 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2181 | 99 | 0.3004 | 29.7398
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12341 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5283 | 61 | 0.3004 | 18.3245
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12341 | west | 7 | N | N | Nwest | Nwest | 1 | 3.0854 | 0 | 0.3004 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12341 | west | 7 | N | N | Nwest | Nwest | 1 | 5.6401 | 0 | 0.3004 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12341 | west | 7 | N | N | Nwest | Nwest | 1 | 5.6401 | 0 | 0.3004 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.1234 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.399 | 141 | 0.30038 | 42.3542
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.1234 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8076 | 120 | 0.30038 | 36.0461
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12335 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7709 | 63 | 0.30034 | 18.9211
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1381 | 66 | 0.30029 | 19.8192
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.508 | 69 | 0.30029 | 20.7201
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.508 | 69 | 0.30029 | 20.7201
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2614 | 67 | 0.30029 | 20.1195
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2614 | 67 | 0.30029 | 20.1195
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0148 | 65 | 0.30029 | 19.5189
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.4745 | 150 | 0.30015 | 45.0225
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.0959 | 220 | 0.30015 | 66.033
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.6326 | 200 | 0.30015 | 60.03
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0136 | 121.9 | 0.30015 | 36.5883
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12297 | west | 8 | N | N | Nwest | Nwest | 1 | 8.608 | 0 | 0.29996 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12297 | west | 8 | N | N | Nwest | Nwest | 1 | 9.0261 | 0 | 0.29996 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12297 | west | 8 | N | N | Nwest | Nwest | 1 | 8.6572 | 0 | 0.29996 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12296 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.1328 | 180 | 0.29995 | 53.9905
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12296 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.1328 | 180 | 0.29995 | 53.9905
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.1229 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.6523 | 225 | 0.29989 | 67.4744
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12287 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7448 | 120 | 0.29986 | 35.9832
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12287 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.6294 | 233 | 0.29986 | 69.8674
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12287 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.913 | 170.2 | 0.29986 | 51.0362
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12279 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7343 | 120 | 0.29977 | 35.9728
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12276 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7312 | 120 | 0.29975 | 35.9696
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12239 | west | 8 | N | N | Nwest | Nwest | 1 | 3.1577 | 0 | 0.29938 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12232 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.2012 | 214.2 | 0.29931 | 64.1118
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12218 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2792 | 100.5 | 0.29917 | 30.0664
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12216 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.0853 | 58 | 0.29915 | 17.3506
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12215 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.3219 | 150 | 0.29913 | 44.87
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.549 | 70 | 0.29912 | 20.9381
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.549 | 70 | 0.29912 | 20.9381
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.3336 | 92.8 | 0.29912 | 27.758
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.7703 | 80 | 0.29912 | 23.9293
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.7703 | 80 | 0.29912 | 23.9293
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.0448 | 115 | 0.29912 | 34.3983
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.4248 | 208.2 | 0.2991 | 62.2735
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.3528 | 142.1 | 0.2991 | 42.5027
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.1683 | 132.4 | 0.2991 | 39.6014
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.6079 | 136 | 0.2991 | 40.6782
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.9512 | 147 | 0.2991 | 43.9683
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.6446 | 210 | 0.2991 | 62.8119
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7131 | 112.5 | 0.29888 | 33.6241
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.2232 | 149.5 | 0.29888 | 44.6827
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6723 | 186 | 0.29888 | 55.5919
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.1463 | 214.5 | 0.29888 | 64.11
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12155 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.80224 | 6.6 | 0.29854 | 1.9704
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12155 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1692 | 34.3 | 0.29854 | 10.2399
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.1212 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.0585 | 149 | 0.29819 | 44.4296
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.1211 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5265 | 169.5 | 0.29809 | 50.5258
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.121 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2349 | 35 | 0.29798 | 10.4294
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.121 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6299 | 30 | 0.29798 | 8.9395
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.9819 | 66 | 0.29793 | 19.6631
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.861 | 65 | 0.29793 | 19.3651
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1028 | 67 | 0.29793 | 19.961
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1028 | 67 | 0.29793 | 19.961
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1028 | 67 | 0.29793 | 19.961
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12094 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29793 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12094 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29793 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.1166 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.55969 | 0 | 0.29359 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11481 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1847 | 80 | 0.2918 | 23.3437
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11481 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1847 | 80 | 0.2918 | 23.3437
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11432 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5744 | 75 | 0.29131 | 21.8484
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11432 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.146 | 80 | 0.29131 | 23.305
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11432 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.573 | 40 | 0.29131 | 11.6525
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11422 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1375 | 80 | 0.29121 | 23.2965
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11421 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1364 | 80 | 0.29119 | 23.2954
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.11414 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.1216 | 150 | 0.29113 | 43.6697
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.11414 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.1216 | 150 | 0.29113 | 43.6697
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11172 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9379 | 80 | 0.28871 | 23.0969
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.11152 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6728 | 0 | 0.28851 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.11152 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6728 | 0 | 0.28851 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.11132 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.516 | 76.5 | 0.28831 | 22.0555
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.11091 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3163 | 84 | 0.2879 | 24.1832
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.10708 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.0628 | 150 | 0.28407 | 42.6108
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.10708 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.5668 | 80 | 0.28407 | 22.7258
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.10514 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.8107 | 255 | 0.28213 | 71.9424
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.10514 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 15.6659 | 149 | 0.28213 | 42.0369
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.10514 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 16.0864 | 153 | 0.28213 | 43.1654
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.1029 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27989 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.1029 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 80.9854 | 787 | 0.27989 | 220.2743
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.10141 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27839 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.10141 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27839 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.097892 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.27488 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.088642 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2963 | 150 | 0.26563 | 39.8444
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.03057 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.20756 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17699 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17699 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.1165 | 100 | 0.14582 | 14.5822
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.034628 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 19.7033 | 569 | -0.10847 | -61.719
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.034628 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 20.1189 | 581 | -0.10847 | -63.0206
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.01396 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25128 | 0 | -0.12914 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.01396 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25128 | 0 | -0.12914 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.01396 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2094 | 0 | -0.12914 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.012386 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16969 | 0 | -0.13071 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.005409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15145 | 0 | -0.13769 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.005409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15686 | 0 | -0.13769 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.005038 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.126 | 422 | -0.13806 | -58.261
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.003637 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.065466 | 0 | -0.13946 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.003637 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.065466 | 0 | -0.13946 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.002535 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.083655 | 0 | -0.14056 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.002535 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.063375 | 0 | -0.14056 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.002535 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14056 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01617 | 0 | -0.14264 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.015708 | 0 | -0.14264 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01617 | 0 | -0.14264 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1431 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1431 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.037506 | 42 | -0.14399 | -6.0476
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.039292 | 44 | -0.14399 | -6.3356
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.039292 | 44 | -0.14399 | -6.3356
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.041971 | 47 | -0.14399 | -6.7675
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.002012 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.016096 | 0 | -0.14511 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.002012 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.016096 | 0 | -0.14511 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.002188 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.67828 | 310 | -0.14529 | -45.0384
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.002188 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.90364 | 413 | -0.14529 | -60.0028
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20791 | 49 | -0.14734 | -7.2197
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19518 | 46 | -0.14734 | -6.7776
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19518 | 46 | -0.14734 | -6.7776
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19942 | 47 | -0.14734 | -6.925
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.004243 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.65342 | 154 | -0.14734 | -22.6904
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.004243 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.62796 | 148 | -0.14734 | -21.8064
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20366 | 48 | -0.14734 | -7.0723
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20366 | 48 | -0.14734 | -7.0723
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.01098 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.6744 | 152.5 | -0.15408 | -23.4968
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.01098 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.6415 | 149.5 | -0.15408 | -23.0345
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.01098 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5539 | 232.6 | -0.15408 | -35.8384
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.011476 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5148 | 132 | -0.15457 | -20.4037
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.011476 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5378 | 134 | -0.15457 | -20.7128
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.011476 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.7067 | 323 | -0.15457 | -49.9271
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.011636 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.069816 | 0 | -0.15473 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.01345 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1251 | 158 | -0.15655 | -24.7345
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.01345 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.152 | 160 | -0.15655 | -25.0476
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.01345 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3537 | 175 | -0.15655 | -27.3958
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.014933 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.15803 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.023695 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14217 | 0 | -0.16679 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3926 | 50 | -0.17095 | -8.5475
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3926 | 50 | -0.17095 | -8.5475
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3926 | 50 | -0.17095 | -8.5475
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3926 | 50 | -0.17095 | -8.5475
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6122 | 223.9 | -0.17263 | -38.6517
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6447 | 225 | -0.17263 | -38.8416
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6329 | 224.6 | -0.17263 | -38.7725
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6949 | 226.7 | -0.17263 | -39.135
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.031004 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.1063 | 584 | -0.1741 | -101.6751
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.031004 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.4474 | 595 | -0.1741 | -103.5902
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.031142 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.4845 | 433 | -0.17424 | -75.4456
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5528 | 114 | -0.17426 | -19.8659
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9186 | 222 | -0.17426 | -38.6862
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7344 | 184 | -0.17426 | -32.0642
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.981 | 224 | -0.17426 | -39.0347
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.584 | 115 | -0.17426 | -20.0402
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.033369 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.080086 | 0 | -0.17647 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.033369 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.080086 | 0 | -0.17647 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.033369 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.093433 | 0 | -0.17647 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8648 | 142 | -0.17736 | -25.1846
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.9676 | 145 | -0.17736 | -25.7166
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1731 | 151 | -0.17736 | -26.7808
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.9351 | 290 | -0.17736 | -51.4333
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.034783 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13913 | 0 | -0.17788 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.03598 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086352 | 0 | -0.17908 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.03598 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086352 | 0 | -0.17908 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6929 | 147 | -0.18182 | -26.7282
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3443 | 138 | -0.18182 | -25.0917
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4218 | 140 | -0.18182 | -25.4554
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6929 | 147 | -0.18182 | -26.7282
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0483 | 182 | -0.18182 | -33.092
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6679 | 198 | -0.18182 | -36.0012
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.0397 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.1579 | 407 | -0.1828 | -74.3985
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.03973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.3043 | 58 | -0.18283 | -10.604
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.03973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.536 | 89 | -0.18283 | -16.2716
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7481 | 44 | -0.18283 | -8.0444
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7481 | 44 | -0.18283 | -8.0444
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7084 | 43 | -0.18283 | -7.8616
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7878 | 45 | -0.18283 | -8.2272
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.039757 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.3799 | 412 | -0.18285 | -75.3359
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.039757 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.9028 | 400 | -0.18285 | -73.1417
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.039777 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.8654 | 424 | -0.18287 | -77.5387
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.039777 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.9052 | 425 | -0.18287 | -77.7215
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.03991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.3412 | 209 | -0.18301 | -38.2485
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.03991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.6206 | 216 | -0.18301 | -39.5296
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8359 | 46 | -0.18301 | -8.4183
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8758 | 47 | -0.18301 | -8.6013
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8359 | 46 | -0.18301 | -8.4183
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8359 | 46 | -0.18301 | -8.4183
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.039955 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18305 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.039955 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18305 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.039955 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18305 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.040888 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.98131 | 24 | -0.18399 | -4.4156
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.040888 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.98131 | 24 | -0.18399 | -4.4156
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.040888 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.94042 | 23 | -0.18399 | -4.2317
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.041008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3562 | 155 | -0.18411 | -28.5363
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.041008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9714 | 170 | -0.18411 | -31.2979
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.041008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3562 | 155 | -0.18411 | -28.5363
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.041972 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -22.9167 | 546 | -0.18507 | -101.0478
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.041972 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -31.479 | 750 | -0.18507 | -138.8019
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.044582 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.53498 | 0 | -0.18768 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.047627 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.7627 | 100 | -0.19072 | -19.0724
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.047627 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.7627 | 100 | -0.19072 | -19.0724
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.047627 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19072 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.047627 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19072 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.047627 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19072 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.047627 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19072 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.047631 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19073 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.048122 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.0563 | 396 | -0.19122 | -75.7228
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.053899 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.197 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.057473 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20057 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.058095 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69714 | 0 | -0.20119 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.058095 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.63904 | 0 | -0.20119 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.058095 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69714 | 0 | -0.20119 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.060469 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20357 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.060781 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -38.2312 | 629 | -0.20388 | -128.2394
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.062481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.1535 | 146.5 | -0.20558 | -30.1172
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.062481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2409 | 147.9 | -0.20558 | -30.405
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.062481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8092 | 173 | -0.20558 | -35.565
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.063202 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0828 | 207 | -0.2063 | -42.7039
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.063202 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6959 | 216.7 | -0.2063 | -44.705
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.063202 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.2949 | 242 | -0.2063 | -49.9244
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.063207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.1018 | 144 | -0.2063 | -29.7078
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.063207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.1018 | 144 | -0.2063 | -29.7078
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.063207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8084 | 171 | -0.2063 | -35.278
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.063721 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20682 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.063721 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.4214 | 38 | -0.20682 | -7.8591
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.063721 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2298 | 19.3 | -0.20682 | -3.9916
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.063721 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.95581 | 15 | -0.20682 | -3.1023
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.063721 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9949 | 47 | -0.20682 | -9.7205
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.0081 | 94 | -0.20701 | -19.4592
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6206 | 41 | -0.20701 | -8.4875
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4288 | 38 | -0.20701 | -7.8665
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2144 | 19 | -0.20701 | -3.9333
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.0081 | 94 | -0.20701 | -19.4592
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.301 | 36 | -0.20701 | -7.4525
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7484 | 43 | -0.20701 | -8.9016
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4062 | 22 | -0.20701 | -4.5543
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.4596 | 148 | -0.20701 | -30.638
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1958 | 50 | -0.20701 | -10.3507
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5154 | 55 | -0.20701 | -11.3857
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1958 | 50 | -0.20701 | -10.3507
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.064239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8629 | 0 | -0.20734 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.064926 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4672 | 0 | -0.20802 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.064966 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4687 | 0 | -0.20806 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.065081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.627 | 0 | -0.20818 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.065081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.627 | 0 | -0.20818 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.065154 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -21.7614 | 334 | -0.20825 | -69.5559
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.065154 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.1524 | 340 | -0.20825 | -70.8054
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.065154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7277 | 180 | -0.20825 | -37.4852
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.065154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7277 | 180 | -0.20825 | -37.4852
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.065422 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.776 | 180 | -0.20852 | -37.5335
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.06545 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7062 | 0 | -0.20855 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.06545 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7259 | 0 | -0.20855 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.06545 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.0138 | 0 | -0.20855 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.065466 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9966 | 336 | -0.20856 | -70.0772
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.065466 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7839 | 180 | -0.20856 | -37.5414
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 25 | -0.20942 | -5.2356
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 25 | -0.20942 | -5.2356
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 25 | -0.20942 | -5.2356
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0612 | 16 | -0.20942 | -3.3508
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 25 | -0.20942 | -5.2356
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 25 | -0.20942 | -5.2356
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 25 | -0.20942 | -5.2356
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.99491 | 15 | -0.20942 | -3.1414
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5713 | 0 | -0.21 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.2368 | 0 | -0.21 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.6907 | 0 | -0.21 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7015 | 0 | -0.21 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.8353 | 0 | -0.21 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.4972 | 0 | -0.21 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.066907 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.80288 | 0 | -0.21 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.067371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.7014 | 144 | -0.21047 | -30.3074
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.067371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6657 | 188 | -0.21047 | -39.568
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2772 | 47.7 | -0.2118 | -10.103
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5627 | 37.3 | -0.2118 | -7.9002
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1604 | 46 | -0.2118 | -9.7429
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2978 | 48 | -0.2118 | -10.1665
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.068744 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0183 | 0 | -0.21184 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.069414 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5271 | 22 | -0.21251 | -4.6752
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.069414 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.76355 | 11 | -0.21251 | -2.3376
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.069414 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.76355 | 11 | -0.21251 | -2.3376
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.071081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0662 | 0 | -0.21418 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.071081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6349 | 0 | -0.21418 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.071905 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.57524 | 0 | -0.215 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.072456 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8258 | 0 | -0.21555 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0288 | 0 | -0.21555 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5072 | 0 | -0.21555 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8258 | 0 | -0.21555 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0869 | 0 | -0.21555 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5072 | 0 | -0.21555 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0869 | 0 | -0.21555 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8258 | 0 | -0.21555 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.075904 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6434 | 0 | -0.219 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0787 | 0 | -0.22004 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.2326 | 0 | -0.22004 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0787 | 0 | -0.22004 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1557 | 0 | -0.22004 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0326 | 0 | -0.22004 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9237 | 0 | -0.22004 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5395 | 0 | -0.22004 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1545 | 0 | -0.22004 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3548 | 0 | -0.22004 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.694 | 0 | -0.22004 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.11379 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -151.6834 | 0 | -0.25689 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.11379 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -151.1144 | 0 | -0.25689 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.7751 | 76 | -0.25856 | -19.6505
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.7751 | 76 | -0.25856 | -19.6505
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -12.1235 | 105 | -0.25856 | -27.1487
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5442 | 74 | -0.25856 | -19.1334
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5442 | 74 | -0.25856 | -19.1334
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.7771 | 102 | -0.25856 | -26.373
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.12068 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.9647 | 66 | -0.26377 | -17.4091
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2813 | 0 | -0.27667 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5369 | 0 | -0.27667 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0107 | 0 | -0.27667 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4906 | 0 | -0.27667 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.487 | 0 | -0.27667 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7542 | 0 | -0.27667 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6785 | 0 | -0.27667 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4043 | 0 | -0.27667 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5556 | 0 | -0.27667 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3499 | 0 | -0.27667 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.4149 | 0 | -0.27667 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.617 | 0 | -0.27667 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.6553 | 0 | -0.27667 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4906 | 0 | -0.27667 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.9563 | 0 | -0.27667 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.7577 | 0 | -0.27667 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.1513 | 0 | -0.27667 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6856 | 0 | -0.27667 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6856 | 0 | -0.27667 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.8405 | 0 | -0.27667 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.13858 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.839 | 0 | -0.28167 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.13858 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3858 | 0 | -0.28167 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.8218 | 0 | -0.28564 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.8218 | 0 | -0.28564 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.9621 | 0 | -0.28564 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.608 | 0 | -0.28564 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.14552 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -94.7355 | 651 | -0.28862 | -187.8918
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.14552 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -82.075 | 564 | -0.28862 | -162.7818
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.14552 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -87.3138 | 600 | -0.28862 | -173.1721
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.14571 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.7507 | 0 | -0.28881 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.14571 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.7507 | 0 | -0.28881 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.14571 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -35.699 | 0 | -0.28881 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.15556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1714 | 0 | -0.29866 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.15627 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.1591 | 161 | -0.29937 | -48.1978
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.15627 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.9405 | 166 | -0.29937 | -49.6946
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.15627 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -38.7545 | 248 | -0.29937 | -74.2426
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.15627 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -85.3223 | 546 | -0.29937 | -163.4534
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.15627 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -100.4803 | 0 | -0.29937 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.15627 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0315 | 13 | -0.29937 | -3.8917
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.1576 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2008 | 0 | -0.3007 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.4843 | 0 | -0.30745 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.2681 | 0 | -0.30745 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.8787 | 0 | -0.30745 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.7637 | 0 | -0.30745 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.16435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2593 | 0 | -0.30745 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.16435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9306 | 0 | -0.30745 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.6396 | 0 | -0.3075 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9655 | 0 | -0.3075 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.7133 | 0 | -0.3075 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.1862 | 0 | -0.3075 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.2356 | 0 | -0.3075 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.0383 | 0 | -0.3075 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.7825 | 0 | -0.3075 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -40.1138 | 0 | -0.3075 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.576 | 0 | -0.3075 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.16972 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.486 | 50 | -0.31282 | -15.6408
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.17078 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.31387 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.8513 | 0 | -0.31729 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.259 | 0 | -0.31729 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.1545 | 0 | -0.31729 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4934 | 0 | -0.31729 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1251 | 0 | -0.31729 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3996 | 0 | -0.31848 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.5227 | 0 | -0.31848 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3996 | 0 | -0.31848 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3996 | 0 | -0.31848 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.17772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.8626 | 0 | -0.32082 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.17772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.218 | 0 | -0.32082 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.1986 | 0 | -0.32201 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.1072 | 0 | -0.32201 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.1788 | 0 | -0.32201 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.0893 | 0 | -0.32201 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -48.1276 | 0 | -0.32201 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.17909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2682 | 0 | -0.32219 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.17961 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1553 | 12 | -0.32271 | -3.8725
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.17961 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32271 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.17964 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -30.3595 | 169 | -0.32274 | -54.5429
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.17968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.7717 | 0 | -0.32277 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.17968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.6969 | 0 | -0.32277 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.17968 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.6479 | 165 | -0.32278 | -53.2589
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.17983 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -38.3038 | 213 | -0.32293 | -68.7835
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.17984 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9134 | 0 | -0.32294 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.17985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.3723 | 0 | -0.32294 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.17985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.5236 | 0 | -0.32294 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.17985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.2358 | 0 | -0.32294 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5103 | 0 | -0.32295 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3664 | 0 | -0.32295 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.8554 | 0 | -0.32295 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.2368 | 0 | -0.32295 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.17986 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -41.0085 | 228 | -0.32296 | -73.6347
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2758 | 46 | -0.32301 | -14.8583
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2758 | 46 | -0.32301 | -14.8583
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2758 | 46 | -0.32301 | -14.8583
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.895 | 55 | -0.32301 | -17.7653
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.895 | 55 | -0.32301 | -17.7653
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.7151 | 54 | -0.32301 | -17.4423
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.833 | 0 | -0.32384 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.0138 | 0 | -0.32384 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0491 | 0 | -0.32384 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4224 | 0 | -0.32384 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.6549 | 42 | -0.32536 | -13.665
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.6549 | 42 | -0.32536 | -13.665
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.9258 | 38 | -0.32536 | -12.3635
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.9258 | 38 | -0.32536 | -12.3635
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.18242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.8095 | 0 | -0.32552 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.18274 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -31.6135 | 0 | -0.32583 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.18274 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6695 | 0 | -0.32583 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.18573 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -136.513 | 735 | -0.32883 | -241.6895
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3253 | 0 | -0.32914 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4555 | 0 | -0.32914 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0834 | 0 | -0.32914 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.5391 | 0 | -0.32914 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2929 | 0 | -0.32914 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7952 | 0 | -0.32914 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7022 | 0 | -0.32914 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5113 | 0 | -0.32914 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3487 | 0 | -0.32914 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.8876 | 0 | -0.32914 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.5336 | 0 | -0.32914 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.125 | 0 | -0.32964 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.3116 | 0 | -0.32964 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.0577 | 0 | -0.32964 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.752 | 0 | -0.32964 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5654 | 0 | -0.32964 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -19.4001 | 0 | -0.32964 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0058 | 0 | -0.32964 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.18696 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.3529 | 0 | -0.33006 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.18761 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93807 | 0 | -0.33071 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.18761 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9399 | 0 | -0.33071 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.18785 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -2.2542 | 12 | -0.33094 | -3.9713
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.1881 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -139.759 | 743 | -0.3312 | -246.0803
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.18894 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -75.1977 | 398 | -0.33204 | -132.1504
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.18905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -32.5171 | 172 | -0.33215 | -57.1298
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.18905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -32.5171 | 172 | -0.33215 | -57.1298
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.18905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -32.5171 | 172 | -0.33215 | -57.1298
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.9315 | 0 | -0.33309 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.6655 | 0 | -0.33309 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.1905 | 0 | -0.33309 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -51.1472 | 0 | -0.33309 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -33.9402 | 0 | -0.33928 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -30.605 | 0 | -0.33928 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -30.2126 | 0 | -0.33928 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -30.2126 | 0 | -0.33928 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.19619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -31.7821 | 0 | -0.33928 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -20.6613 | 104 | -0.34176 | -35.5434
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -20.6613 | 104 | -0.34176 | -35.5434
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.728 | 54 | -0.34176 | -18.4552
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.5293 | 53 | -0.34176 | -18.1134
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.728 | 54 | -0.34176 | -18.4552
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.324 | 57 | -0.34176 | -19.4805
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.728 | 54 | -0.34176 | -18.4552
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.728 | 54 | -0.34176 | -18.4552
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.5226 | 58 | -0.34176 | -19.8223
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.5226 | 58 | -0.34176 | -19.8223
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.19895 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.3874 | 12 | -0.34205 | -4.1046
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -12.3402 | 56 | -0.36346 | -20.3536
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -13.0012 | 59 | -0.36346 | -21.444
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -12.3402 | 56 | -0.36346 | -20.3536
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -12.3402 | 56 | -0.36346 | -20.3536
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -13.0012 | 59 | -0.36346 | -21.444
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -12.3402 | 56 | -0.36346 | -20.3536

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:Singleton - TH Wharton 345kV 44645-45500 C:Singleton - Tomball 345kV 44645-46500 & Roans - King 345kV 40600-45872 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -12.3402 | 56 | -0.36346 | -20.3536 | 56 | 20.3536
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -13.0012 | 59 | -0.36346 | -21.444 | 115 | 41.7976
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -12.3402 | 56 | -0.36346 | -20.3536 | 171 | 62.1512
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -12.3402 | 56 | -0.36346 | -20.3536 | 227 | 82.5048 | Weighted Shift Factors
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -13.0012 | 59 | -0.36346 | -21.444 | 286 | 103.9488 | North | 0.1431
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.22036 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -12.3402 | 56 | -0.36346 | -20.3536 | 342 | 124.3024 | Houston | -0.17699
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.19895 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.3874 | 12 | -0.34205 | -4.1046 | 354 | 128.4069 |  | 0.32008
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -20.6613 | 104 | -0.34176 | -35.5434 | 458 | 163.9503
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -20.6613 | 104 | -0.34176 | -35.5434 | 562 | 199.4937 | Line Rating | 1450
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.728 | 54 | -0.34176 | -18.4552 | 616 | 217.9489 | Conc Gen | 2661
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.5293 | 53 | -0.34176 | -18.1134 | 669 | 236.0623 | Weighted Imp. | 900.1732
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.728 | 54 | -0.34176 | -18.4552 | 723 | 254.5175 | PTDF | 0.33828
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.324 | 57 | -0.34176 | -19.4805 | 780 | 273.998
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.728 | 54 | -0.34176 | -18.4552 | 834 | 292.4533 | Concentration | 1.0569
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.728 | 54 | -0.34176 | -18.4552 | 888 | 310.9085
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.5226 | 58 | -0.34176 | -19.8223 | 946 | 330.7307
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.19867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.5226 | 58 | -0.34176 | -19.8223 | 1004 | 350.553
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -33.9402 | 0 | -0.33928 | 0 | 1004 | 350.553
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -30.605 | 0 | -0.33928 | 0 | 1004 | 350.553
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -30.2126 | 0 | -0.33928 | 0 | 1004 | 350.553
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.19619 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -30.2126 | 0 | -0.33928 | 0 | 1004 | 350.553
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.19619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -31.7821 | 0 | -0.33928 | 0 | 1004 | 350.553
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.9315 | 0 | -0.33309 | 0 | 1004 | 350.553
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.6655 | 0 | -0.33309 | 0 | 1004 | 350.553
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.1905 | 0 | -0.33309 | 0 | 1004 | 350.553
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.19 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -51.1472 | 0 | -0.33309 | 0 | 1004 | 350.553
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.18905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -32.5171 | 172 | -0.33215 | -57.1298 | 1176 | 407.6828
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.18905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -32.5171 | 172 | -0.33215 | -57.1298 | 1348 | 464.8127
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.18905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -32.5171 | 172 | -0.33215 | -57.1298 | 1520 | 521.9425
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.18894 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -75.1977 | 398 | -0.33204 | -132.1504 | 1918 | 654.0929
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.1881 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -139.759 | 743 | -0.3312 | -246.0803 | 2661 | 900.1732
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.18785 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -2.2542 | 0 | -0.33094 | 0 | 2661 | 900.1732
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.18761 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93807 | 0 | -0.33071 | 0 | 2661 | 900.1732
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.18761 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9399 | 0 | -0.33071 | 0 | 2661 | 900.1732
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.18696 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.3529 | 0 | -0.33006 | 0 | 2661 | 900.1732
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.125 | 0 | -0.32964 | 0 | 2661 | 900.1732
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.3116 | 0 | -0.32964 | 0 | 2661 | 900.1732
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.0577 | 0 | -0.32964 | 0 | 2661 | 900.1732
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.752 | 0 | -0.32964 | 0 | 2661 | 900.1732
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5654 | 0 | -0.32964 | 0 | 2661 | 900.1732
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -19.4001 | 0 | -0.32964 | 0 | 2661 | 900.1732
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.18654 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0058 | 0 | -0.32964 | 0 | 2661 | 900.1732
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3253 | 0 | -0.32914 | 0 | 2661 | 900.1732
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4555 | 0 | -0.32914 | 0 | 2661 | 900.1732
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0834 | 0 | -0.32914 | 0 | 2661 | 900.1732
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.5391 | 0 | -0.32914 | 0 | 2661 | 900.1732
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2929 | 0 | -0.32914 | 0 | 2661 | 900.1732
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7952 | 0 | -0.32914 | 0 | 2661 | 900.1732
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7022 | 0 | -0.32914 | 0 | 2661 | 900.1732
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5113 | 0 | -0.32914 | 0 | 2661 | 900.1732
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3487 | 0 | -0.32914 | 0 | 2661 | 900.1732
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.8876 | 0 | -0.32914 | 0 | 2661 | 900.1732
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.18604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.5336 | 0 | -0.32914 | 0 | 2661 | 900.1732
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.18573 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -136.513 | 735 | -0.32883 | -241.6895
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.18274 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -31.6135 | 0 | -0.32583 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.18274 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6695 | 0 | -0.32583 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.18242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.8095 | 0 | -0.32552 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.6549 | 42 | -0.32536 | -13.665
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.6549 | 42 | -0.32536 | -13.665
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.9258 | 38 | -0.32536 | -12.3635
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.18226 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.9258 | 38 | -0.32536 | -12.3635
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.833 | 0 | -0.32384 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.0138 | 0 | -0.32384 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0491 | 0 | -0.32384 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.18075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4224 | 0 | -0.32384 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2758 | 46 | -0.32301 | -14.8583
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2758 | 46 | -0.32301 | -14.8583
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2758 | 46 | -0.32301 | -14.8583
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.895 | 55 | -0.32301 | -17.7653
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.895 | 55 | -0.32301 | -17.7653
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.17991 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.7151 | 54 | -0.32301 | -17.4423
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.17986 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -41.0085 | 228 | -0.32296 | -73.6347
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5103 | 0 | -0.32295 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3664 | 0 | -0.32295 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.8554 | 0 | -0.32295 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.17985 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.2368 | 0 | -0.32295 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.17985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.3723 | 0 | -0.32294 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.17985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.5236 | 0 | -0.32294 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.17985 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.2358 | 0 | -0.32294 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.17984 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9134 | 0 | -0.32294 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.17983 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -38.3038 | 213 | -0.32293 | -68.7835
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.17968 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.6479 | 165 | -0.32278 | -53.2589
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.17968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.7717 | 0 | -0.32277 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.17968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.6969 | 0 | -0.32277 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.17964 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -30.3595 | 169 | -0.32274 | -54.5429
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.17961 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1553 | 12 | -0.32271 | -3.8725
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.17961 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32271 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.17909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2682 | 0 | -0.32219 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.1986 | 0 | -0.32201 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.1072 | 0 | -0.32201 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.1788 | 0 | -0.32201 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.0893 | 0 | -0.32201 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.17891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -48.1276 | 0 | -0.32201 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.17772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.8626 | 0 | -0.32082 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.17772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.218 | 0 | -0.32082 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3996 | 0 | -0.31848 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.5227 | 0 | -0.31848 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3996 | 0 | -0.31848 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.17538 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.3996 | 0 | -0.31848 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.8513 | 0 | -0.31729 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.259 | 0 | -0.31729 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.1545 | 0 | -0.31729 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4934 | 0 | -0.31729 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.17419 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1251 | 0 | -0.31729 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.17078 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.31387 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.16972 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.486 | 50 | -0.31282 | -15.6408
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.6396 | 0 | -0.3075 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9655 | 0 | -0.3075 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.7133 | 0 | -0.3075 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.1862 | 0 | -0.3075 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.2356 | 0 | -0.3075 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.0383 | 0 | -0.3075 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.7825 | 0 | -0.3075 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.1644 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -40.1138 | 0 | -0.3075 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.1644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.576 | 0 | -0.3075 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.16435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2593 | 0 | -0.30745 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.16435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9306 | 0 | -0.30745 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.4843 | 0 | -0.30745 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.2681 | 0 | -0.30745 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.8787 | 0 | -0.30745 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.16435 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.7637 | 0 | -0.30745 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.1576 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2008 | 0 | -0.3007 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.15627 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.1591 | 161 | -0.29937 | -48.1978
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.15627 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.9405 | 166 | -0.29937 | -49.6946
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.15627 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -38.7545 | 248 | -0.29937 | -74.2426
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.15627 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -85.3223 | 546 | -0.29937 | -163.4534
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.15627 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -100.4803 | 0 | -0.29937 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.15627 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0315 | 13 | -0.29937 | -3.8917
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.15556 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1714 | 0 | -0.29866 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.14571 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.7507 | 0 | -0.28881 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.14571 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.7507 | 0 | -0.28881 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.14571 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -35.699 | 0 | -0.28881 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.14552 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -94.7355 | 0 | -0.28862 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.14552 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -82.075 | 0 | -0.28862 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.14552 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -87.3138 | 0 | -0.28862 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.8218 | 0 | -0.28564 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.8218 | 0 | -0.28564 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.9621 | 0 | -0.28564 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.14254 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.608 | 0 | -0.28564 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.13858 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.839 | 0 | -0.28167 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.13858 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3858 | 0 | -0.28167 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2813 | 0 | -0.27667 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.5369 | 0 | -0.27667 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0107 | 0 | -0.27667 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4906 | 0 | -0.27667 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.487 | 0 | -0.27667 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7542 | 0 | -0.27667 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6785 | 0 | -0.27667 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4043 | 0 | -0.27667 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5556 | 0 | -0.27667 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3499 | 0 | -0.27667 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.4149 | 0 | -0.27667 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.617 | 0 | -0.27667 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.6553 | 0 | -0.27667 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4906 | 0 | -0.27667 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.9563 | 0 | -0.27667 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.7577 | 0 | -0.27667 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.1513 | 0 | -0.27667 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6856 | 0 | -0.27667 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6856 | 0 | -0.27667 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.13357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -22.8405 | 0 | -0.27667 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.12068 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.9647 | 66 | -0.26377 | -17.4091
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.7751 | 76 | -0.25856 | -19.6505
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.7751 | 76 | -0.25856 | -19.6505
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -12.1235 | 105 | -0.25856 | -27.1487
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5442 | 74 | -0.25856 | -19.1334
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5442 | 74 | -0.25856 | -19.1334
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.11546 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.7771 | 102 | -0.25856 | -26.373
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.11379 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -151.6834 | 0 | -0.25689 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.11379 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -151.1144 | 0 | -0.25689 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0787 | 0 | -0.22004 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.2326 | 0 | -0.22004 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0787 | 0 | -0.22004 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1557 | 0 | -0.22004 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0326 | 0 | -0.22004 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9237 | 0 | -0.22004 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5395 | 0 | -0.22004 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1545 | 0 | -0.22004 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3548 | 0 | -0.22004 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.076946 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.694 | 0 | -0.22004 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.075904 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6434 | 0 | -0.219 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0288 | 0 | -0.21555 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5072 | 0 | -0.21555 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8258 | 0 | -0.21555 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0869 | 0 | -0.21555 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5072 | 0 | -0.21555 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0869 | 0 | -0.21555 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.072457 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8258 | 0 | -0.21555 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.072456 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8258 | 0 | -0.21555 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.071905 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.57524 | 0 | -0.215 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.071081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0662 | 0 | -0.21418 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.071081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6349 | 0 | -0.21418 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.069414 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5271 | 22 | -0.21251 | -4.6752
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.069414 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.76355 | 11 | -0.21251 | -2.3376
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.069414 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.76355 | 11 | -0.21251 | -2.3376
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.068744 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0183 | 0 | -0.21184 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2772 | 47.7 | -0.2118 | -10.103
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5627 | 37.3 | -0.2118 | -7.9002
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1604 | 46 | -0.2118 | -9.7429
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.068705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2978 | 48 | -0.2118 | -10.1665
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.067371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.7014 | 144 | -0.21047 | -30.3074
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.067371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6657 | 188 | -0.21047 | -39.568
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5713 | 0 | -0.21 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.2368 | 0 | -0.21 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.6907 | 0 | -0.21 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7015 | 0 | -0.21 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.8353 | 0 | -0.21 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.066907 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.4972 | 0 | -0.21 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.066907 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.80288 | 0 | -0.21 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 0 | -0.20942 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 0 | -0.20942 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 0 | -0.20942 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0612 | 0 | -0.20942 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 0 | -0.20942 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 0 | -0.20942 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6582 | 0 | -0.20942 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.066327 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.99491 | 0 | -0.20942 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.065466 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9966 | 336 | -0.20856 | -70.0772
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.065466 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7839 | 180 | -0.20856 | -37.5414
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.06545 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7062 | 0 | -0.20855 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.06545 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7259 | 0 | -0.20855 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.06545 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.0138 | 0 | -0.20855 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.065422 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.776 | 180 | -0.20852 | -37.5335
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.065154 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -21.7614 | 334 | -0.20825 | -69.5559
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.065154 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.1524 | 340 | -0.20825 | -70.8054
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.065154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7277 | 180 | -0.20825 | -37.4852
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.065154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7277 | 180 | -0.20825 | -37.4852
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.065081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.627 | 0 | -0.20818 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.065081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.627 | 0 | -0.20818 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.064966 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4687 | 0 | -0.20806 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.064926 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4672 | 0 | -0.20802 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.064239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8629 | 0 | -0.20734 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.0081 | 0 | -0.20701 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6206 | 0 | -0.20701 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4288 | 0 | -0.20701 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2144 | 0 | -0.20701 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.0081 | 0 | -0.20701 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.301 | 0 | -0.20701 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7484 | 0 | -0.20701 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4062 | 0 | -0.20701 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.4596 | 0 | -0.20701 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1958 | 0 | -0.20701 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5154 | 0 | -0.20701 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.063916 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1958 | 0 | -0.20701 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.063721 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.4214 | 38 | -0.20682 | -7.8591
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.063721 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2298 | 19.3 | -0.20682 | -3.9916
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.063721 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.95581 | 15 | -0.20682 | -3.1023
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.063721 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9949 | 47 | -0.20682 | -9.7205
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.063721 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20682 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.063207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.1018 | 144 | -0.2063 | -29.7078
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.063207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.1018 | 144 | -0.2063 | -29.7078
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.063207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8084 | 171 | -0.2063 | -35.278
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.063202 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0828 | 207 | -0.2063 | -42.7039
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.063202 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6959 | 216.7 | -0.2063 | -44.705
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.063202 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.2949 | 242 | -0.2063 | -49.9244
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.062481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.1535 | 146.5 | -0.20558 | -30.1172
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.062481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2409 | 147.9 | -0.20558 | -30.405
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.062481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8092 | 173 | -0.20558 | -35.565
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.060781 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -38.2312 | 0 | -0.20388 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.060469 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20357 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.058095 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69714 | 0 | -0.20119 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.058095 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.63904 | 0 | -0.20119 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.058095 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69714 | 0 | -0.20119 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.057473 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20057 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.053899 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.197 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.048122 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.0563 | 0 | -0.19122 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.047631 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19073 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.047627 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.7627 | 100 | -0.19072 | -19.0724
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.047627 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.7627 | 100 | -0.19072 | -19.0724
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.047627 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19072 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.047627 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19072 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.047627 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19072 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.047627 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19072 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.044582 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.53498 | 0 | -0.18768 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.041972 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -22.9167 | 0 | -0.18507 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.041972 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -31.479 | 0 | -0.18507 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.041008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3562 | 155 | -0.18411 | -28.5363
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.041008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9714 | 170 | -0.18411 | -31.2979
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.041008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3562 | 155 | -0.18411 | -28.5363
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.040888 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.98131 | 24 | -0.18399 | -4.4156
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.040888 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.98131 | 24 | -0.18399 | -4.4156
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.040888 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.94042 | 23 | -0.18399 | -4.2317
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.039955 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18305 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.039955 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18305 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.039955 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18305 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.03991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.3412 | 209 | -0.18301 | -38.2485
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.03991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.6206 | 216 | -0.18301 | -39.5296
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8359 | 46 | -0.18301 | -8.4183
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8758 | 47 | -0.18301 | -8.6013
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8359 | 46 | -0.18301 | -8.4183
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.03991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8359 | 46 | -0.18301 | -8.4183
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.039777 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.8654 | 0 | -0.18287 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.039777 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.9052 | 0 | -0.18287 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.039757 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.3799 | 412 | -0.18285 | -75.3359
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.039757 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.9028 | 400 | -0.18285 | -73.1417
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.03973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.3043 | 58 | -0.18283 | -10.604
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.03973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.536 | 89 | -0.18283 | -16.2716
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7481 | 44 | -0.18283 | -8.0444
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7481 | 44 | -0.18283 | -8.0444
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7084 | 43 | -0.18283 | -7.8616
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.03973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7878 | 45 | -0.18283 | -8.2272
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.0397 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.1579 | 407 | -0.1828 | -74.3985
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.039279 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.32994 | 8.4 | -0.18238 | -1.532
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6929 | 147 | -0.18182 | -26.7282
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3443 | 138 | -0.18182 | -25.0917
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4218 | 140 | -0.18182 | -25.4554
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6929 | 147 | -0.18182 | -26.7282
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0483 | 182 | -0.18182 | -33.092
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.038727 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6679 | 198 | -0.18182 | -36.0012
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.03598 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086352 | 0 | -0.17908 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.03598 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086352 | 0 | -0.17908 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.034783 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13913 | 0 | -0.17788 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8648 | 142 | -0.17736 | -25.1846
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.9676 | 145 | -0.17736 | -25.7166
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1731 | 151 | -0.17736 | -26.7808
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.034259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.9351 | 290 | -0.17736 | -51.4333
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.033369 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.080086 | 0 | -0.17647 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.033369 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.080086 | 0 | -0.17647 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.033369 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.093433 | 0 | -0.17647 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5528 | 0 | -0.17426 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9186 | 0 | -0.17426 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7344 | 0 | -0.17426 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.981 | 0 | -0.17426 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.584 | 0 | -0.17426 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.031142 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.4845 | 0 | -0.17424 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.031004 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.1063 | 0 | -0.1741 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.031004 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.4474 | 0 | -0.1741 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6122 | 223.9 | -0.17263 | -38.6517
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6447 | 225 | -0.17263 | -38.8416
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6329 | 224.6 | -0.17263 | -38.7725
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.029532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6949 | 226.7 | -0.17263 | -39.135
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3926 | 50 | -0.17095 | -8.5475
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3926 | 50 | -0.17095 | -8.5475
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3926 | 50 | -0.17095 | -8.5475
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027852 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3926 | 50 | -0.17095 | -8.5475
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.023695 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14217 | 0 | -0.16679 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.014933 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.15803 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.01345 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1251 | 158 | -0.15655 | -24.7345
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.01345 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.152 | 160 | -0.15655 | -25.0476
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.01345 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3537 | 175 | -0.15655 | -27.3958
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.011636 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.069816 | 0 | -0.15473 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.011476 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5148 | 132 | -0.15457 | -20.4037
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.011476 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5378 | 134 | -0.15457 | -20.7128
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.011476 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.7067 | 323 | -0.15457 | -49.9271
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.01098 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.6744 | 152.5 | -0.15408 | -23.4968
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.01098 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.6415 | 149.5 | -0.15408 | -23.0345
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.01098 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5539 | 232.6 | -0.15408 | -35.8384
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20791 | 49 | -0.14734 | -7.2197
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19518 | 46 | -0.14734 | -6.7776
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19518 | 46 | -0.14734 | -6.7776
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19942 | 47 | -0.14734 | -6.925
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.004243 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.65342 | 154 | -0.14734 | -22.6904
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.004243 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.62796 | 148 | -0.14734 | -21.8064
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20366 | 48 | -0.14734 | -7.0723
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.004243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20366 | 48 | -0.14734 | -7.0723
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.002188 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.67828 | 310 | -0.14529 | -45.0384
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.002188 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.90364 | 413 | -0.14529 | -60.0028
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.002012 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.016096 | 0 | -0.14511 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.002012 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.016096 | 0 | -0.14511 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.037506 | 42 | -0.14399 | -6.0476
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.039292 | 44 | -0.14399 | -6.3356
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.039292 | 44 | -0.14399 | -6.3356
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.000893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.041971 | 47 | -0.14399 | -6.7675
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1431 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1431 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1431 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01617 | 0 | -0.14264 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.015708 | 0 | -0.14264 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01617 | 0 | -0.14264 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.002535 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.083655 | 0 | -0.14056 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.002535 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.063375 | 0 | -0.14056 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.002535 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14056 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.003637 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.065466 | 0 | -0.13946 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.003637 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.065466 | 0 | -0.13946 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.005038 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.126 | 422 | -0.13806 | -58.261
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.005409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15145 | 0 | -0.13769 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.005409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15686 | 0 | -0.13769 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.012386 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16969 | 0 | -0.13071 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.01396 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25128 | 0 | -0.12914 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.01396 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25128 | 0 | -0.12914 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.01396 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2094 | 0 | -0.12914 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.034628 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 19.7033 | 0 | -0.10847 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.034628 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 20.1189 | 0 | -0.10847 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.031165 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.1165 | 0 | 0.14582 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17699 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17699 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.03057 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.20756 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.088642 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2963 | 0 | 0.26563 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.097892 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.27488 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.10141 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27839 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.10141 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27839 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.1029 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27989 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.1029 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 80.9854 | 787 | 0.27989 | 220.2743
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.10514 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.8107 | 255 | 0.28213 | 71.9424
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.10514 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 15.6659 | 149 | 0.28213 | 42.0369
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.10514 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 16.0864 | 153 | 0.28213 | 43.1654
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.10708 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.0628 | 150 | 0.28407 | 42.6108
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.10708 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.5668 | 80 | 0.28407 | 22.7258
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.11091 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3163 | 0 | 0.2879 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.11132 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.516 | 0 | 0.28831 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.11152 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6728 | 0 | 0.28851 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.11152 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6728 | 0 | 0.28851 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11172 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9379 | 0 | 0.28871 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.11414 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.1216 | 0 | 0.29113 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.11414 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.1216 | 0 | 0.29113 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11421 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1364 | 0 | 0.29119 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11422 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1375 | 0 | 0.29121 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11432 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5744 | 0 | 0.29131 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11432 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.146 | 0 | 0.29131 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11432 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.573 | 0 | 0.29131 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11481 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1847 | 0 | 0.2918 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11481 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1847 | 0 | 0.2918 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.1166 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.55969 | 0 | 0.29359 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.9819 | 66 | 0.29793 | 19.6631
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.861 | 65 | 0.29793 | 19.3651
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1028 | 67 | 0.29793 | 19.961
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1028 | 67 | 0.29793 | 19.961
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12094 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1028 | 67 | 0.29793 | 19.961
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12094 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29793 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12094 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29793 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.121 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2349 | 0 | 0.29798 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.121 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6299 | 0 | 0.29798 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.1211 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5265 | 0 | 0.29809 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.1212 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.0585 | 0 | 0.29819 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12155 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.80224 | 0 | 0.29854 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12155 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1692 | 0 | 0.29854 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7131 | 0 | 0.29888 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.2232 | 0 | 0.29888 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6723 | 0 | 0.29888 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12189 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.1463 | 0 | 0.29888 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.4248 | 208.2 | 0.2991 | 62.2735
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.3528 | 142.1 | 0.2991 | 42.5027
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.1683 | 132.4 | 0.2991 | 39.6014
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.6079 | 136 | 0.2991 | 40.6782
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.9512 | 147 | 0.2991 | 43.9683
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12212 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.6446 | 210 | 0.2991 | 62.8119
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.549 | 70 | 0.29912 | 20.9381
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.549 | 70 | 0.29912 | 20.9381
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.3336 | 92.8 | 0.29912 | 27.758
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.7703 | 80 | 0.29912 | 23.9293
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.7703 | 80 | 0.29912 | 23.9293
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12213 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.0448 | 115 | 0.29912 | 34.3983
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12215 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.3219 | 0 | 0.29913 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12216 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.0853 | 0 | 0.29915 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12218 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2792 | 0 | 0.29917 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12232 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.2012 | 0 | 0.29931 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12239 | west | 8 | N | N | Nwest | Nwest | 1 | 3.1577 | 0 | 0.29938 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12276 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7312 | 0 | 0.29975 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12279 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7343 | 0 | 0.29977 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12287 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7448 | 0 | 0.29986 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12287 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.6294 | 0 | 0.29986 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12287 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.913 | 0 | 0.29986 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.1229 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.6523 | 0 | 0.29989 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12296 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.1328 | 0 | 0.29995 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12296 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.1328 | 0 | 0.29995 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12297 | west | 8 | N | N | Nwest | Nwest | 1 | 8.608 | 0 | 0.29996 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12297 | west | 8 | N | N | Nwest | Nwest | 1 | 9.0261 | 0 | 0.29996 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12297 | west | 8 | N | N | Nwest | Nwest | 1 | 8.6572 | 0 | 0.29996 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.4745 | 0 | 0.30015 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.0959 | 0 | 0.30015 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.6326 | 0 | 0.30015 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12316 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0136 | 0 | 0.30015 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1381 | 66 | 0.30029 | 19.8192
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.508 | 69 | 0.30029 | 20.7201
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.508 | 69 | 0.30029 | 20.7201
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2614 | 67 | 0.30029 | 20.1195
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2614 | 67 | 0.30029 | 20.1195
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.1233 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0148 | 65 | 0.30029 | 19.5189
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12335 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7709 | 0 | 0.30034 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.1234 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.399 | 0 | 0.30038 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.1234 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8076 | 0 | 0.30038 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12341 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2181 | 0 | 0.3004 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12341 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5283 | 0 | 0.3004 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12341 | west | 7 | N | N | Nwest | Nwest | 1 | 3.0854 | 0 | 0.3004 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12341 | west | 7 | N | N | Nwest | Nwest | 1 | 5.6401 | 0 | 0.3004 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12341 | west | 7 | N | N | Nwest | Nwest | 1 | 5.6401 | 0 | 0.3004 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12357 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.38 | 0 | 0.30056 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5467 | 0 | 0.30063 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4881 | 0 | 0.30063 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12379 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.474 | 0 | 0.30078 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12379 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.474 | 0 | 0.30078 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6551 | 0 | 0.30112 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3445 | 0 | 0.30112 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.7582 | 0 | 0.30112 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7721 | 0 | 0.30112 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.0342 | 0 | 0.30112 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12413 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9929 | 0 | 0.30112 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.9653 | 0 | 0.30122 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7159 | 0 | 0.30122 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.9348 | 0 | 0.30122 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12424 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.4745 | 0 | 0.30122 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.12425 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.4548 | 0 | 0.30123 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12426 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.6393 | 0 | 0.30125 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.12515 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5091 | 0 | 0.30214 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.12644 | west | 6 | Y | N | Ywest | Nwest | 1 | 50.5748 | 0 | 0.30342 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.12644 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.8401 | 0 | 0.30343 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.12719 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9862 | 0 | 0.30418 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.12783 | west | 4 | Y | N | Ywest | Nwest | 1 | 83.0499 | 0 | 0.30482 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.12827 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.3637 | 73 | 0.30526 | 22.2838
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.12827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.2641 | 119 | 0.30526 | 36.3256
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.12827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.2953 | 205 | 0.30526 | 62.5777
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.12827 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.0835 | 102 | 0.30526 | 31.1362
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.12827 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.3139 | 96 | 0.30526 | 29.3047
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.12882 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.174 | 242 | 0.30581 | 74.0048
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.12909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.6878 | 168 | 0.30608 | 51.4216
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.12909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.6185 | 90 | 0.30608 | 27.5473
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.12944 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.5328 | 0 | 0.30643 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.12956 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 47.4182 | 366 | 0.30655 | 112.1955
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.12961 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5553 | 0 | 0.30659 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.12961 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5553 | 0 | 0.30659 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5939 | 20 | 0.30668 | 6.1336
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5939 | 20 | 0.30668 | 6.1336
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5939 | 20 | 0.30668 | 6.1336
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.12969 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2048 | 17 | 0.30668 | 5.2136
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.0961 | 70 | 0.30693 | 21.4852
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.9662 | 69 | 0.30693 | 21.1783
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.9662 | 69 | 0.30693 | 21.1783
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.12995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.8363 | 68 | 0.30693 | 20.8714
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.13071 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3527 | 18 | 0.30769 | 5.5385
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.13071 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3527 | 18 | 0.30769 | 5.5385
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.13071 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.9668 | 38 | 0.30769 | 11.6923
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.13107 | north | 3 | N | N | Nnorth | Nnorth | 1 | 151.6457 | 0 | 0.30806 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.13107 | north | 3 | N | N | Nnorth | Nnorth | 1 | 151.7767 | 0 | 0.30806 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.13139 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.5513 | 217.3 | 0.30838 | 67.0106
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.13139 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.9352 | 205 | 0.30838 | 63.2175
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.13139 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.7909 | 272.4 | 0.30838 | 84.0022
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.13149 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.8242 | 204 | 0.30848 | 62.9295
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.13149 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.4297 | 201 | 0.30848 | 62.0041
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.13149 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.8208 | 242 | 0.30848 | 74.6517
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.13168 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30867 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.13222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 38.0796 | 288 | 0.30921 | 89.0519
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.13222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.4365 | 147 | 0.30921 | 45.4536
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.13222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.4365 | 147 | 0.30921 | 45.4536
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.6287 | 224 | 0.30926 | 69.2738
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8932 | 226 | 0.30926 | 69.8923
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0415 | 212 | 0.30926 | 65.5627
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.13227 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.9092 | 211 | 0.30926 | 65.2535
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.13354 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31053 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.13354 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31053 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.13354 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31053 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.13359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.91 | 216.4 | 0.31058 | 67.21
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.13359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8699 | 216.1 | 0.31058 | 67.1168
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.13383 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 52.8617 | 395 | 0.31081 | 122.7716
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.13383 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 58.2147 | 435 | 0.31081 | 135.2041
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.13402 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.0777 | 0 | 0.31101 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.1341 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 58.3352 | 435 | 0.31109 | 135.3246
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.13538 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.1229 | 60 | 0.31237 | 18.7421
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.13538 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.5291 | 63 | 0.31237 | 19.6793
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.13666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.7852 | 196 | 0.31365 | 61.4746
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.13666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.1691 | 111 | 0.31365 | 34.8147
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.13744 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31443 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.13773 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31472 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.13776 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.2562 | 118 | 0.31475 | 37.1406
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.13776 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.8429 | 115 | 0.31475 | 36.1964
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.13776 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 76.5968 | 556 | 0.31475 | 175.0016
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.13804 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.5217 | 0 | 0.31503 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.13804 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.5217 | 0 | 0.31503 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.13824 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 23.5015 | 170 | 0.31523 | 53.5893
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.13824 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 71.8869 | 520 | 0.31523 | 163.9202
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.1385 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 51.2435 | 370 | 0.31548 | 116.7287
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.3894 | 0 | 0.31548 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.5279 | 0 | 0.31548 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 42.7953 | 0 | 0.31548 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.8049 | 0 | 0.31548 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.9434 | 0 | 0.31548 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.1385 | north | 1 | N | N | Nnorth | Nnorth | 1 | 42.9338 | 0 | 0.31548 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1768 | 160 | 0.31559 | 50.4947
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.6224 | 156 | 0.31559 | 49.2324
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.1666 | 196 | 0.31559 | 61.856
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.6224 | 156 | 0.31559 | 49.2324
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.761 | 157 | 0.31559 | 49.548
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.13861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.4438 | 198 | 0.31559 | 62.4872
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.13869 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.4014 | 0 | 0.31567 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.13869 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.0393 | 0 | 0.31567 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.13869 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.2598 | 0 | 0.31567 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.1388 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.4493 | 0 | 0.31579 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.1388 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.364 | 0 | 0.31579 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.1388 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 112.1488 | 0 | 0.31579 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.9762 | 79 | 0.31593 | 24.9582
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.7275 | 106 | 0.31593 | 33.4882
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.2851 | 146 | 0.31593 | 46.1252
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.13894 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.5594 | 76 | 0.31593 | 24.0104
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.13894 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.5578 | 40 | 0.31593 | 12.6372
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13901 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.316 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13901 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.316 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.13911 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.7822 | 20 | 0.3161 | 6.322
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.13911 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.4778 | 25 | 0.3161 | 7.9025
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.13911 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7036 | 41 | 0.3161 | 12.96
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.13927 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 54.0383 | 388 | 0.31626 | 122.7093
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.13927 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 71.7261 | 515 | 0.31626 | 162.8745
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5613 | 161 | 0.31712 | 51.0562
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9816 | 164 | 0.31712 | 52.0075
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9816 | 164 | 0.31712 | 52.0075
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.0146 | 414 | 0.31712 | 131.2873
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7014 | 162 | 0.31712 | 51.3733
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5613 | 161 | 0.31712 | 51.0562
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8415 | 163 | 0.31712 | 51.6904
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 57.314 | 409 | 0.31712 | 129.7017
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.14031 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.429 | 224 | 0.3173 | 71.0741
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.14404 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 113.0714 | 0 | 0.32103 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.14404 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 114.5118 | 0 | 0.32103 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.14404 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 112.3512 | 0 | 0.32103 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.4021 | 0 | 0.3216 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.7992 | 0 | 0.3216 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.9683 | 0 | 0.3216 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.14461 | north | 1 | N | N | Nnorth | Nnorth | 1 | 57.699 | 0 | 0.3216 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.14511 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.3221 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.14517 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.2584 | 0 | 0.32215 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.14524 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.4344 | 182 | 0.32223 | 58.6461
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.14524 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 70.2981 | 484 | 0.32223 | 155.9598
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.876 | 151.5 | 0.32798 | 49.6896
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9968 | 152.3 | 0.32798 | 49.952
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.802 | 177.5 | 0.32798 | 58.2172
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.15125 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7935 | 150.7 | 0.32824 | 49.4655
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.15125 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8389 | 151 | 0.32824 | 49.564
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.15125 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.8319 | 177.4 | 0.32824 | 58.2294
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.1526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 93.8502 | 0 | 0.32959 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.1526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 89.5774 | 0 | 0.32959 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.16839 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 139.2618 | 0 | 0.34538 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.16839 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 137.9147 | 0 | 0.34538 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 152.7457 | 0 | 0.35564 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 152.7457 | 0 | 0.35564 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 27.2084 | 0 | 0.35564 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.17865 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 27.3334 | 0 | 0.35564 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.1861 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.9327 | 48 | 0.36309 | 17.4281
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.1861 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.5605 | 46 | 0.36309 | 16.7019
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.1861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 19.5403 | 105 | 0.36309 | 38.1239
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.36742 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.36742 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.19043 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.2374 | 17 | 0.36742 | 6.2462
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.36742 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.19043 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.36742 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.19085 | north | 7 | N | N | Nnorth | Nnorth | 1 | 6.1073 | 0 | 0.36784 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.20485 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 94.8437 | 0 | 0.38183 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.5498 | 0 | 0.38808 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.9297 | 0 | 0.38808 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.9297 | 0 | 0.38808 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.21109 | north | 1 | N | N | Nnorth | Nnorth | 1 | 80.2134 | 0 | 0.38808 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
20
25
30
35
40
45
50
55
60
65
70
75
80
85
90
95
100
105
110
| 115 | 0
| Max | 1450
| Min | 1450
| Avg | 1450