## test results
CRE test for: |  | 3415 TEMP_SS - 3420 TEMP_PEC | [5 empty] | PASS
Line Rating: |  | 532.85
Direction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3415 TEMP_SS - 3420 TEMP_PEC
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.074128
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.10347
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.066969
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.023461
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3415 TEMP_SS - 3420 TEMP_PEC
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.080759
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.10121
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.06729
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.021944
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3415 TEMP_SS - 3420 TEMP_PEC
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.17534
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.0068378
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.096072
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.17076
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.08001
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.088913
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.17534 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.17534 | -0.17534
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.23619
[6 empty] | Concentration |  | -1.347 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.22543
[6 empty] | Concentration |  | -1.2857 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 46.893
| Percent of line rating => | [6 empty] | 8.8% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -2.2923
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | 0.00093986 | 0.016614 | 0.015674 | 0.00093986
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.0010712 | 0.21915 | 0.22022 | -0.0010712
[7 empty] | B4 (S-W) | 0.0018462 | -0.38958 | -0.39143 | 0.0018462
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.0036406 | -0.18705 | -0.18341 | -0.0036406
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0020189 | 0.20179 | 0.20381 | -0.0020189
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | 0.2338%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -0.2665%
[7 empty] | B4 | 0.4594%
[7 empty] | B5 | -0.9058%
[7 empty] | B6 | -0.5023%
[7 empty] | Max Abs Error | 0.9058% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3415 TEMP_SS - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3415 TEMP_SS - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.11412 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -29.1011
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.11412 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -17.0042
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.098341 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -1.4751
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.098341 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -1.4751
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.11412 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -17.4607
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.10289 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -15.4338
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.10289 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -8.2314
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.07783 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -5.6816
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.07783 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -9.2618
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.07783 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -15.9551
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.07783 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -7.9387
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.07783 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -7.4717
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.076534 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.91841
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.076534 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.91841
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.082839 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -13.917
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.082839 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -7.4555
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.078248 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -1.4085
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.078248 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -1.4085
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.078248 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -2.9734
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.078033 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -22.4735
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.078033 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -11.4709
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.078033 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -11.4709
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.077671 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -8.738
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.077054 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -3.0822
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.077038 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -6.086
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.077038 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -8.166
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.077038 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -11.2475
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.077038 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -5.8549
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.077968 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -4.6781
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.077968 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -4.912
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.07694 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -1.5388
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.07694 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -1.9235
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.07694 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -3.1545
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.02606 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -12.0658
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -4.3402
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -4.2744
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -4.4059
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -4.4059
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -4.4059
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.06576 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -7.4966
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.06576 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -33.8664
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -4.5015
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -4.7061
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -4.7061
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -4.5697
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -4.5697
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -4.4333
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.067852 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -4.7496
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.067852 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -4.9803
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.067852 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -4.7768
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -10.2073
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -14.9708
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.068346 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -6.7663
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.068346 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -4.1691
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.068326 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -9.634
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.068346 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -1.7087
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.068346 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -3.1234
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.068346 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -3.1234
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.068326 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -8.1991
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.067203 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -1.7338
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.067031 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -6.7366
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.067626 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -8.1151
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.067019 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -3.8871
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.067185 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -14.391
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.068616 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -10.2924
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.066217 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -0.43703
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.066217 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -2.2712
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.068616 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -6.9302
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.067655 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -8.1186
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.075068 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -27.4749
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.074826 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -18.1079
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.071609 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -28.6436
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.071613 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -16.9007
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.072442 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -11.9529
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.077019 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -15.7119
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.077019 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -15.4808
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.077019 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -18.6386
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -1.503
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -1.503
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -1.503
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -1.2775
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.076464 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -9.1757
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.074975 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -4.4985
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.077047 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -5.7785
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.077047 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -6.1329
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.077047 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -6.811
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -12.3362
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -12.0278
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -15.1118
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -12.0278
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -12.1049
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -15.266
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.077228 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -13.1288
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.077228 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -40.1586
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.077156 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -28.5477
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.077016 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -42.9749
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.077016 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -44.5923
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.077016 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -62.2289
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.078947 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -8.8421
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.078947 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -7.8947
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.078947 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -29.842
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.079447 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -17.2638
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.079447 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -16.2866
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.079447 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -21.6414
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.079733 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -61.3944
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -5.6162
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -5.5359
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -5.5359
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -5.4557
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.079151 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -91.5777
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.079151 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -91.6569
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -18.8348
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -19.003
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.084027 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -18.1834
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.084027 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -18.1582
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -17.8258
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -17.7417
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.080517 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -31.8042
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.080371 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -34.9614
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.080517 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -35.0249
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.077666 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -10.7179
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.078454 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -9.2576
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.078454 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -9.0222
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.078454 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -43.6204
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.077025 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -29.8857
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.077025 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -39.6679
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.073665 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -57.827
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.073665 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -58.5637
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.073665 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -57.4587
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.072564 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -13.2066
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.072564 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -35.121
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.076654 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -17.1705
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.072848 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -3.6424
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.07288 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -3.061
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.068167 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -41.9227
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.068167 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -40.014
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.12749 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -68.4621
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.12749 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -100.3346
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.13417 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -10.0629
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.13417 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -29.7862
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.16206 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 92.2116
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.098085 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 20.4998
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.098085 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 21.1864
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.098024 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 39.8958
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 4.5119
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 4.61
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 4.5119
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 4.5119
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.098252 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 41.6588
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.098252 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 41.7571
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.097481 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 5.6539
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.097481 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 8.6758
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 4.2892
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 4.2892
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 4.1917
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 4.3866
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.09819 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 40.4543
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.09819 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 39.276
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.097356 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 53.1564
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.097356 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 73.017
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.09854 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 6.0109
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.09854 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 9.3613
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.09854 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 14.8795
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.097835 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 15.1644
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.097835 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 16.6319
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.097835 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 15.1644
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.079072 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 1.7396
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.079072 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.86979
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.079072 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.86979
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 3.8063
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 2.9764
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 3.6707
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 3.8303
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.083269 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.99923
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.083269 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.91596
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.086878 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 2.0851
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.086878 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 2.0851
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.086878 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 1.9982
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.092154 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 36.493
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.05126 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 68.3296
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.05126 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 68.0733
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.081993 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 3.1157
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.081993 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 1.5825
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.081993 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 1.2299
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.081993 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 3.8537
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.058968 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -4.4226
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.069312 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -10.3968
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.065509 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -11.1038
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.029953 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -4.493
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.068268 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -4.3009
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.073078 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -47.4788
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.077295 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -3.0918
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.077295 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -3.0918
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.10701 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 45.1561
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.12475 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 16.4671
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.12475 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 16.7166
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.12475 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 40.2946
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.12372 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 19.5473
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.12372 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 19.7947
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.12372 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 21.6505
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.11061 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 64.5957
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.11061 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 65.8124
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.1105 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 47.8474
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 24.2269
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 24.3459
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 24.3026
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 24.5298
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.13092 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 1.0474
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.13092 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 1.0474
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.10263 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 1.8474
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.10263 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 1.8474
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.10263 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 1.5395
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.10359 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 1.4191
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.11284 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 2.0311
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.11284 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 2.0311
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.12607 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 4.4123
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.12607 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 4.2863
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.12607 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 4.4123
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.10778 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 3.0178
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.10778 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 3.1256
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.065821 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -2.3037
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.065821 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -1.9746
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 5.6418
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 5.6418
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 5.6418
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 5.6418
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.11137 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.6682
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.10502 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.25205
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.10502 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.25205
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.10502 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.29405
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.10339 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.41356
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.10378 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.24907
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.10378 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.24907
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 14.8055
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 13.8991
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 14.1005
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 14.8055
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 18.3307
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 19.9422
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.12491 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 19.0495
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.12491 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 18.6748
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.12491 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 29.0552
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 14.821
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 15.1341
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 15.7603
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 30.2682
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.047114 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 1.5548
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.047114 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 1.1779
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.083269 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.99923
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.079981 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 5.8386
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 5.9071
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 6.0566
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 2.1708
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.5427
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 5.9071
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 5.9818
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 5.8622
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 1.8693
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 3.4396
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.084633 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 53.2342
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.080874 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 11.6459
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.080874 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 15.2043
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.097502 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 1.17
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.059484 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.3569
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.081135 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 27.2614
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.081319 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 27.1605
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.081319 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 27.6485
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.081434 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 3.0945
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.081349 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 2.0337
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.081349 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 2.0337
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.081428 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 3.0943
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.081814 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 2.3726
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.081145 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 12.0338
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.081145 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 12.0581
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.081145 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 12.4152
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 12.6888
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 12.2873
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 8.0309
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 11.6448
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 11.8054
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 10.1992
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.082303 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 12.0574
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.082303 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 12.1726
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.082303 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 14.2384
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.082148 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 17.0046
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.082148 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 17.8015
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.082148 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 19.8798
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.082145 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 11.8289
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.082145 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 11.8289
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.082145 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 14.0468
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.1312 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 40.6732
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.1312 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 54.1873
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 5.566
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 5.831
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 5.831
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 6.2286
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 6.3386
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 5.9506
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 5.9506
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 6.0799
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.12936 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 19.9214
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.12936 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 19.1453
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 6.2093
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 6.2093
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -4.6889
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -4.6889
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -6.2161
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -5.3587
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -5.3587
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -7.7032
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -13.9436
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -9.5167
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -8.8671
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -9.1082
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -9.8449
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -14.0641
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -14.4651
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -8.7552
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -17.2335
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -13.6346
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -13.6098
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -8.2952
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.066029 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -9.8383
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.067861 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -12.215
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.067861 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -12.215
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.067797 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -15.2543
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.068719 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -8.5899
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.068719 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -8.5899
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -10.8018
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -10.879
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -23.8412
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -11.0333
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -11.1105
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -23.9184
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.079414 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -15.5651
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.079414 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -8.815
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.077697 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -12.2943
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -12.5234
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -12.5234
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -31.6139
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -12.3706
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -12.2943
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -12.447
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -31.2321
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.077316 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.077316 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -10.8497
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -9.5302
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -10.6298
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -29.2503
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.069081 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -10.4105
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.069081 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -10.4312
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.069081 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -12.255
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.069241 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -10.49
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.069241 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -10.5454
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.069241 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -12.2903
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.16206 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 94.1563
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -40.1046
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -40.1046
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.020344 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.65101
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.017807 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.85474
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.017807 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.81912
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.24448
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -1.039
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.020373 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.34634
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.44821
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.50933
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.017807 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -1.8697
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.068525 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -5.7561
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.058846 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -4.7077
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.058783 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -8.8174
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.058783 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -8.8174
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 1.7416
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 1.6408
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 1.3037
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 3.7686
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 3.7759
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 3.7464
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 2.3615
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 6.0022
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.98396
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 2.4691
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 2.2869
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 2.5282
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 2.5109
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.024616 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.78771
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.024616 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.73848
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 3.9169
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 3.9169
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 4.1992
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 3.8639
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -7.1438
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -7.1766
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.018101 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 2.4617
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.028159 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.92925
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.75865
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.75865
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.68639
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.68639
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.036994 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 2.6266
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.036994 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.36994
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.028806 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 4.6954
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.028806 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 4.6954
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.028806 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 7.0575
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 1.3343
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 1.2316
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 1.3343
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 1.3343
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.018945 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 2.8228
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.018945 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 1.2333
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 1.9114
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 1.84
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 1.8273
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 1.1447
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.25625
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.016076 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 11.9445
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.016882 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 12.4083
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.015833 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 2.7233
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.015833 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 2.7233
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.015833 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 2.7233
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 1.9655
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.017941 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 3.1038
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.017941 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 2.422
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 2.485
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 2.4636
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 2.4254
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 4.1091
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 1.2091
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 1.194
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 1.5605
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 1.3905
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 3.1656
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 3.0473
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 3.055
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 3.0453
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 5.2178
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.016119 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.080595
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.016119 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.3385
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -3.111
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -3.1473
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -3.1473
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -7.6665
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.015067 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 5.9967
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.91167
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.91167
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.91167
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 1.09
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 1.09
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 1.0702
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.055778 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -46.1284
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.055778 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -45.6822
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.029085 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 1.3408
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 3.874
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 3.874
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 5.3523
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 3.7721
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 3.7721
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 5.1993
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.018877 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 3.3979
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.018877 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 2.9939
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.018877 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 2.9637
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.019199 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.67197
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.02222 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 10.199
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 1.0474
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 1.0635
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 1.128
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 1.0152
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.99907
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 1.6759
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.95073
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 1.7723
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.7496
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.7496
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011361 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 1.8405
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.01593 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 2.501
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 1.319
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 1.3375
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.7245
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.55731
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.019641 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 1.532
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.019641 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 1.5713
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.018896 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.30612
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.018957 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 3.1279
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.018974 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 3.2066
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.018901 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 4.0259
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.018884 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 4.3056
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.018986 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.22783
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.018986 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.34175
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.023264 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 1.1632
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 1.7864
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 1.7864
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.92756
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.91038
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.92756
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.97909
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.92756
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.92756
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.99627
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.99627
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.016437 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.19724
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.82426
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.86842
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.82426
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.82426
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.86842
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.82426
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.048127 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 3.1764
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.027884 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 4.4893
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.027884 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 4.6287
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.027884 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 6.9152
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.027884 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 15.2247
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.027884 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 17.9294
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.028858 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 18.7866
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.028858 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 16.2759
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.028858 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 17.3148
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.027884 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.36249
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.016099 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.19319
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.56736
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.57904
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.54566
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.76593
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.29536
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.34041
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.33207
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.58405
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.30037
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 1.4251
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 2.4697
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 2.4276
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 2.7957
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 1.762
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 3.9547
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 3.3673
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 3.4456
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 1.9578
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.70479
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 3.6806
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 2.7409
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 2.4668
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 2.8192
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 2.5372
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 3.9547
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 3.798
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 4.033
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 2.9758
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 3.1324
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 3.1324
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 6.6955
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.72143
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.055879 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -4.2747
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.058968 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -4.7174
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.058968 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -2.3587
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.059463 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -4.757
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.05886 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -4.7088
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.056308 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -4.5046
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.055473 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -4.6597
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.059463 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -4.757
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 11.6917
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.067599 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -8.1119
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.067599 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -15.7506
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.067599 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -11.5053
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 22.7681
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 18.8709
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 22.9732
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 11.7943
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 10.2559
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.070297 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -4.2178
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.052992 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.042162 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.061307 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.29427
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -2.5903
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -7.4256
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -9.3251
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -8.2199
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -7.2529
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -5.5605
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.066829 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -10.0244
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -7.4853
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -9.9471
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -12.3757
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -14.272
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.081993 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.062361 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.086311 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 2.0936
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 3.2601
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 5.5332
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 7.7023
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 3.3595
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 3.1137
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 1.5568
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 7.7023
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 2.9498
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 3.5234
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 1.8027
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 3.0236
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 1.1629
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.5427
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 1.1629
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 3.0236
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 3.0236
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 12.127
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 4.0969
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 4.5066
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 4.0969
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.080309 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.96371
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.078415 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 1.1762
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.078415 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 1.8035
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.075423 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 3.6203
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.077839 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.62271
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.081161 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 14.609
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.081135 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 14.6043
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.081319 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 14.6374
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.081319 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 14.6374
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.086318 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 8.6318
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.086318 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 8.6318
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0158
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0158
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0158
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 1.2901
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0158
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0158
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0158
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 1.2095
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.086318 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.086318 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 43.159
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.086318 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 43.159
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.086318 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.085737 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.047114 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.084193 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.083306 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:3415 TEMP_SS - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | [7 empty] | 46.893
Number of Bus | Name of Bus | ID | Max MW | L:3415 TEMP_SS - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.11412 | north | Y | -0.039994 | -0.21759 | -0.047153 | -0.13758 | 0.039994 | North | N | 0.039994 | 0
239 | BOSQUESW | 1 | 149 | -0.11412 | north | Y | -0.039994 | -0.21759 | -0.047153 | -0.13758 | 0.039994 | North | N | 0.039994 | 0
244 | WHITNYDM | 1 | 15 | -0.098341 | north | N | -0.024213 | -0.20181 | -0.031372 | -0.1218 | 0.024213 | North | N | 0.024213 | 0
245 | WHITNYDM | 2 | 15 | -0.098341 | north | N | -0.024213 | -0.20181 | -0.031372 | -0.1218 | 0.024213 | North | N | 0.024213 | 0
247 | BOSQUESW | 2 | 153 | -0.11412 | north | Y | -0.039994 | -0.21759 | -0.047153 | -0.13758 | 0.039994 | North | N | 0.039994 | 0
251 | BOSQUESW | 2 | 150 | -0.10289 | north | Y | -0.028764 | -0.20636 | -0.035923 | -0.12635 | 0.028764 | North | N | 0.028764 | 0
253 | BOSQUESW | 2 | 80 | -0.10289 | north | Y | -0.028764 | -0.20636 | -0.035923 | -0.12635 | 0.028764 | North | N | 0.028764 | 0
332 | RWMILLER | 1 | 73 | -0.07783 | north | Y | -0.0037023 | -0.1813 | -0.010861 | -0.10129 | 0.0037023 | North | N | 0.0037023 | 0
333 | RWMILLER | 2 | 119 | -0.07783 | north | Y | -0.0037023 | -0.1813 | -0.010861 | -0.10129 | 0.0037023 | North | N | 0.0037023 | 0
334 | RWMILLER | 3 | 205 | -0.07783 | north | Y | -0.0037023 | -0.1813 | -0.010861 | -0.10129 | 0.0037023 | North | N | 0.0037023 | 0
335 | RWMILLER | 4 | 102 | -0.07783 | north | Y | -0.0037023 | -0.1813 | -0.010861 | -0.10129 | 0.0037023 | North | N | 0.0037023 | 0
336 | RWMILLER | 5 | 96 | -0.07783 | north | Y | -0.0037023 | -0.1813 | -0.010861 | -0.10129 | 0.0037023 | North | N | 0.0037023 | 0
344 | MRSSHPRD | 1 | 12 | -0.076534 | north | N | -0.0024063 | -0.18001 | -0.0095652 | -0.099995 | 0.0024063 | North | N | 0.0024063 | 0
345 | MRSSHPRD | 2 | 12 | -0.076534 | north | N | -0.0024063 | -0.18001 | -0.0095652 | -0.099995 | 0.0024063 | North | N | 0.0024063 | 0
366 | JNSNCNTY | 1 | 168 | -0.082839 | north | Y | -0.0087113 | -0.18631 | -0.01587 | -0.1063 | 0.0087113 | North | N | 0.0087113 | 0
367 | JNSNCNTY | 2 | 90 | -0.082839 | north | Y | -0.0087113 | -0.18631 | -0.01587 | -0.1063 | 0.0087113 | North | N | 0.0087113 | 0
503 | NTHTEXAS | 1 | 18 | -0.078248 | north | Y | -0.0041203 | -0.18172 | -0.011279 | -0.10171 | 0.0041203 | North | N | 0.0041203 | 0
504 | NTHTEXAS | 2 | 18 | -0.078248 | north | Y | -0.0041203 | -0.18172 | -0.011279 | -0.10171 | 0.0041203 | North | N | 0.0041203 | 0
505 | NTHTEXAS | 3 | 38 | -0.078248 | north | Y | -0.0041203 | -0.18172 | -0.011279 | -0.10171 | 0.0041203 | North | N | 0.0041203 | 0
580 | JCKCNTY8 | 1 | 288 | -0.078033 | north | Y | -0.0039053 | -0.1815 | -0.011064 | -0.10149 | 0.0039053 | North | N | 0.0039053 | 0
581 | JCKCNTY8 | 2 | 147 | -0.078033 | north | Y | -0.0039053 | -0.1815 | -0.011064 | -0.10149 | 0.0039053 | North | N | 0.0039053 | 0
582 | JCKCNTY8 | 3 | 147 | -0.078033 | north | Y | -0.0039053 | -0.1815 | -0.011064 | -0.10149 | 0.0039053 | North | N | 0.0039053 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.077671 | north | Y | -0.0035433 | -0.18114 | -0.010702 | -0.10113 | 0.0035433 | North | N | 0.0035433 | 0
837 | NEWMAN_G | 1 | 40 | -0.077054 | north | Y | -0.0029263 | -0.18053 | -0.010085 | -0.10051 | 0.0029263 | North | N | 0.0029263 | 0
842 | OLINGER_ | 1 | 79 | -0.077038 | north | Y | -0.0029103 | -0.18051 | -0.010069 | -0.1005 | 0.0029103 | North | N | 0.0029103 | 0
843 | OLINGER_ | 1 | 106 | -0.077038 | north | Y | -0.0029103 | -0.18051 | -0.010069 | -0.1005 | 0.0029103 | North | N | 0.0029103 | 0
844 | OLINGER_ | 1 | 146 | -0.077038 | north | Y | -0.0029103 | -0.18051 | -0.010069 | -0.1005 | 0.0029103 | North | N | 0.0029103 | 0
845 | OLINGER_ | 1 | 76 | -0.077038 | north | Y | -0.0029103 | -0.18051 | -0.010069 | -0.1005 | 0.0029103 | North | N | 0.0029103 | 0
923 | SPENCER_ | 1 | 60 | -0.077968 | north | Y | -0.0038403 | -0.18144 | -0.010999 | -0.10143 | 0.0038403 | North | N | 0.0038403 | 0
924 | SPENCER_ | 1 | 63 | -0.077968 | north | Y | -0.0038403 | -0.18144 | -0.010999 | -0.10143 | 0.0038403 | North | N | 0.0038403 | 0
948 | STEAM1 | 1 | 20 | -0.07694 | north | Y | -0.0028123 | -0.18041 | -0.0099712 | -0.1004 | 0.0028123 | North | N | 0.0028123 | 0
949 | STEAM2 | 1 | 25 | -0.07694 | north | Y | -0.0028123 | -0.18041 | -0.0099712 | -0.1004 | 0.0028123 | North | N | 0.0028123 | 0
950 | STEAM3 | 1 | 41 | -0.07694 | north | Y | -0.0028123 | -0.18041 | -0.0099712 | -0.1004 | 0.0028123 | North | N | 0.0028123 | 0
990 | GIBN_CRE | 1 | 463 | -0.02606 | north | Y | 0.048068 | -0.12953 | 0.040909 | -0.049521 | 0.040909 | west | Y | 0.048068 | 3.3146
1002 | PBCTAGE_ | A | 66 | -0.06576 | west | Y | 0.0083677 | -0.16923 | 0.0012088 | -0.089221 | 0.0012088 | west | N | 0.0012088 | 0
1003 | PBCTBGE_ | B | 65 | -0.06576 | west | Y | 0.0083677 | -0.16923 | 0.0012088 | -0.089221 | 0.0012088 | west | N | 0.0012088 | 0
1004 | PBCTCGE_ | C | 67 | -0.06576 | west | Y | 0.0083677 | -0.16923 | 0.0012088 | -0.089221 | 0.0012088 | west | N | 0.0012088 | 0
1005 | PBCTDGE_ | D | 67 | -0.06576 | west | Y | 0.0083677 | -0.16923 | 0.0012088 | -0.089221 | 0.0012088 | west | N | 0.0012088 | 0
1006 | PBCTEGE_ | E | 67 | -0.06576 | west | Y | 0.0083677 | -0.16923 | 0.0012088 | -0.089221 | 0.0012088 | west | N | 0.0012088 | 0
1007 | PB5GEN_6 | MB | 114 | -0.06576 | west | Y | 0.0083677 | -0.16923 | 0.0012088 | -0.089221 | 0.0012088 | west | N | 0.0012088 | 0
1008 | PB6GEN_7 | MB | 515 | -0.06576 | west | Y | 0.0083677 | -0.16923 | 0.0012088 | -0.089221 | 0.0012088 | west | N | 0.0012088 | 0
1039 | MRGNAG_1 | A | 66 | -0.068204 | west | Y | 0.0059237 | -0.17168 | -0.0012352 | -0.091665 | 0.0012352 | west | N | 0.0012352 | 0
1040 | MRGNBG_2 | B | 69 | -0.068204 | west | Y | 0.0059237 | -0.17168 | -0.0012352 | -0.091665 | 0.0012352 | west | N | 0.0012352 | 0
1041 | MRGNCG_3 | C | 69 | -0.068204 | west | Y | 0.0059237 | -0.17168 | -0.0012352 | -0.091665 | 0.0012352 | west | N | 0.0012352 | 0
1042 | MRGNDG_4 | D | 67 | -0.068204 | west | Y | 0.0059237 | -0.17168 | -0.0012352 | -0.091665 | 0.0012352 | west | N | 0.0012352 | 0
1043 | MRGNEG_5 | E | 67 | -0.068204 | west | Y | 0.0059237 | -0.17168 | -0.0012352 | -0.091665 | 0.0012352 | west | N | 0.0012352 | 0
1044 | MRGNFG_6 | F | 65 | -0.068204 | west | Y | 0.0059237 | -0.17168 | -0.0012352 | -0.091665 | 0.0012352 | west | N | 0.0012352 | 0
1045 | CALENG1G | 1 | 70 | -0.067852 | west | N | 0.0062757 | -0.17132 | -0.00088316 | -0.091313 | 0.00088316 | west | N | 0.00088316 | 0
1046 | CALENG2G | 2 | 73.4 | -0.067852 | west | N | 0.0062757 | -0.17132 | -0.00088316 | -0.091313 | 0.00088316 | west | N | 0.00088316 | 0
1047 | CALENG3G | 3 | 70.4 | -0.067852 | west | N | 0.0062757 | -0.17132 | -0.00088316 | -0.091313 | 0.00088316 | west | N | 0.00088316 | 0
1058 | LONGSHOR | 1 | 150 | -0.068049 | west | Y | 0.0060787 | -0.17152 | -0.0010802 | -0.09151 | 0.0010802 | west | N | 0.0010802 | 0
1058 | LONGSHOR | 2 | 220 | -0.068049 | west | Y | 0.0060787 | -0.17152 | -0.0010802 | -0.09151 | 0.0010802 | west | N | 0.0010802 | 0
1061 | CIELOGEN | 1 | 99 | -0.068346 | west | Y | 0.0057817 | -0.17182 | -0.0013772 | -0.091807 | 0.0013772 | west | N | 0.0013772 | 0
1062 | CIELOGEN | 1 | 61 | -0.068346 | west | Y | 0.0057817 | -0.17182 | -0.0013772 | -0.091807 | 0.0013772 | west | N | 0.0013772 | 0
1068 | SCURRYCW | 1 | 141 | -0.068326 | west | Y | 0.0058017 | -0.1718 | -0.0013572 | -0.091787 | 0.0013572 | west | N | 0.0013572 | 0
1069 | KINDERMG | 1 | 25 | -0.068346 | west | N | 0.0057817 | -0.17182 | -0.0013772 | -0.091807 | 0.0013772 | west | N | 0.0013772 | 0
1070 | KINDERMG | 1 | 45.7 | -0.068346 | west | N | 0.0057817 | -0.17182 | -0.0013772 | -0.091807 | 0.0013772 | west | N | 0.0013772 | 0
1071 | KINDERMG | 1 | 45.7 | -0.068346 | west | N | 0.0057817 | -0.17182 | -0.0013772 | -0.091807 | 0.0013772 | west | N | 0.0013772 | 0
1073 | SCURRYCW | 2 | 120 | -0.068326 | west | Y | 0.0058017 | -0.1718 | -0.0013572 | -0.091787 | 0.0013572 | west | N | 0.0013572 | 0
1320 | BSP 1 | 1 | 25.8 | -0.067203 | west | N | 0.0069247 | -0.17067 | -0.00023416 | -0.090664 | 0.00023416 | west | N | 0.00023416 | 0
1326 | STANTONW | 1 | 100.5 | -0.067031 | west | Y | 0.0070967 | -0.1705 | -6.2165e-05 | -0.090492 | 6.2165e-05 | west | N | 6.2165e-05 | 0
1327 | WILDHRSE | 1 | 120 | -0.067626 | west | Y | 0.0065017 | -0.1711 | -0.00065716 | -0.091087 | 0.00065716 | west | N | 0.00065716 | 0
1328 | OCOTILLO | 1 | 58 | -0.067019 | west | Y | 0.0071087 | -0.17049 | -5.0165e-05 | -0.09048 | 5.0165e-05 | west | N | 5.0165e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.067185 | west | Y | 0.0069427 | -0.17066 | -0.00021616 | -0.090646 | 0.00021616 | west | N | 0.00021616 | 0
1343 | TRENTIPP | 1 | 150 | -0.068616 | west | Y | 0.0055117 | -0.17209 | -0.0016472 | -0.092077 | 0.0016472 | west | N | 0.0016472 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.066217 | west | Y | 0.0079107 | -0.16969 | 0.00075184 | -0.089678 | 0.00075184 | west | N | 0.00075184 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.066217 | west | Y | 0.0079107 | -0.16969 | 0.00075184 | -0.089678 | 0.00075184 | west | N | 0.00075184 | 0
1354 | AEPWIND_ | 1 | 101 | -0.068616 | west | Y | 0.0055117 | -0.17209 | -0.0016472 | -0.092077 | 0.0016472 | west | N | 0.0016472 | 0
1360 | GUNSIGHT | 1 | 120 | -0.067655 | west | Y | 0.0064727 | -0.17113 | -0.00068616 | -0.091116 | 0.00068616 | west | N | 0.00068616 | 0
1432 | GRHAMSES | 2 | 366 | -0.075068 | north | Y | -0.00094027 | -0.17854 | -0.0080992 | -0.098529 | 0.00094027 | North | N | 0.00094027 | 0
1433 | GRHAMSES | 1 | 242 | -0.074826 | north | Y | -0.00069827 | -0.1783 | -0.0078572 | -0.098287 | 0.00069827 | North | N | 0.00069827 | 0
1437 | MESQUITW | 1 | 400 | -0.071609 | west | Y | 0.0025187 | -0.17508 | -0.0046402 | -0.09507 | 0.0025187 | North | Y | 0.0046402 | 0.84857
1438 | MESQUITW | 1 | 236 | -0.071613 | west | Y | 0.0025147 | -0.17508 | -0.0046442 | -0.095074 | 0.0025147 | North | Y | 0.0046442 | 0.50255
1442 | COKFIELD | 1 | 165 | -0.072442 | west | Y | 0.0016857 | -0.17591 | -0.0054732 | -0.095903 | 0.0016857 | North | Y | 0.0054732 | 0.62493
1453 | WCPWRCO_ | 1 | 204 | -0.077019 | north | Y | -0.0028913 | -0.18049 | -0.01005 | -0.10048 | 0.0028913 | North | N | 0.0028913 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.077019 | north | Y | -0.0028913 | -0.18049 | -0.01005 | -0.10048 | 0.0028913 | North | N | 0.0028913 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.077019 | north | Y | -0.0028913 | -0.18049 | -0.01005 | -0.10048 | 0.0028913 | North | N | 0.0028913 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.075149 | west | Y | -0.0010213 | -0.17862 | -0.0081802 | -0.09861 | 0.0010213 | North | Y | 0.0081802 | 0.14318
1479 | WFCOGEN_ | 2 | 20 | -0.075149 | west | Y | -0.0010213 | -0.17862 | -0.0081802 | -0.09861 | 0.0010213 | North | Y | 0.0081802 | 0.14318
1482 | WFCOGEN_ | 1 | 20 | -0.075149 | west | Y | -0.0010213 | -0.17862 | -0.0081802 | -0.09861 | 0.0010213 | North | Y | 0.0081802 | 0.14318
1482 | WFCOGEN_ | 2 | 17 | -0.075149 | west | Y | -0.0010213 | -0.17862 | -0.0081802 | -0.09861 | 0.0010213 | North | Y | 0.0081802 | 0.1217
1600 | BARTNWND | 1 | 120 | -0.076464 | north | Y | -0.0023363 | -0.17994 | -0.0094952 | -0.099925 | 0.0023363 | North | N | 0.0023363 | 0
1643 | SLSTR1PP | 1 | 60 | -0.074975 | north | Y | -0.00084727 | -0.17845 | -0.0080062 | -0.098436 | 0.00084727 | North | N | 0.00084727 | 0
1675 | PEC_1G | 1 | 75 | -0.077047 | north | N | -0.0029193 | -0.18052 | -0.010078 | -0.10051 | 0.0029193 | North | N | 0.0029193 | 0
1676 | PEC_2G | 2 | 79.6 | -0.077047 | north | N | -0.0029193 | -0.18052 | -0.010078 | -0.10051 | 0.0029193 | North | N | 0.0029193 | 0
1677 | PEC_3G | 3 | 88.4 | -0.077047 | north | N | -0.0029193 | -0.18052 | -0.010078 | -0.10051 | 0.0029193 | North | N | 0.0029193 | 0
1678 | LAMARPWR | 1 | 160 | -0.077101 | north | Y | -0.0029733 | -0.18057 | -0.010132 | -0.10056 | 0.0029733 | North | N | 0.0029733 | 0
1679 | LAMARPWR | 2 | 156 | -0.077101 | north | Y | -0.0029733 | -0.18057 | -0.010132 | -0.10056 | 0.0029733 | North | N | 0.0029733 | 0
1680 | LAMARPWR | 3 | 196 | -0.077101 | north | Y | -0.0029733 | -0.18057 | -0.010132 | -0.10056 | 0.0029733 | North | N | 0.0029733 | 0
1681 | LAMARPWR | 4 | 156 | -0.077101 | north | Y | -0.0029733 | -0.18057 | -0.010132 | -0.10056 | 0.0029733 | North | N | 0.0029733 | 0
1682 | LAMARPWR | 5 | 157 | -0.077101 | north | Y | -0.0029733 | -0.18057 | -0.010132 | -0.10056 | 0.0029733 | North | N | 0.0029733 | 0
1683 | LAMARPWR | 6 | 198 | -0.077101 | north | Y | -0.0029733 | -0.18057 | -0.010132 | -0.10056 | 0.0029733 | North | N | 0.0029733 | 0
1687 | VALLEY_1 | 1 | 170 | -0.077228 | north | Y | -0.0031003 | -0.1807 | -0.010259 | -0.10069 | 0.0031003 | North | N | 0.0031003 | 0
1688 | VALLEY_2 | 2 | 520 | -0.077228 | north | Y | -0.0031003 | -0.1807 | -0.010259 | -0.10069 | 0.0031003 | North | N | 0.0031003 | 0
1689 | VALLEY_3 | 3 | 370 | -0.077156 | north | Y | -0.0030283 | -0.18063 | -0.010187 | -0.10062 | 0.0030283 | North | N | 0.0030283 | 0
1701 | MOSES_1G | 1 | 558 | -0.077016 | north | Y | -0.0028883 | -0.18049 | -0.010047 | -0.10048 | 0.0028883 | North | N | 0.0028883 | 0
1702 | MOSES_2G | 2 | 579 | -0.077016 | north | Y | -0.0028883 | -0.18049 | -0.010047 | -0.10048 | 0.0028883 | North | N | 0.0028883 | 0
1703 | MOSES_3G | 3 | 808 | -0.077016 | north | Y | -0.0028883 | -0.18049 | -0.010047 | -0.10048 | 0.0028883 | North | N | 0.0028883 | 0
1861 | EAGLEMNT | MB | 112 | -0.078947 | north | Y | -0.0048193 | -0.18242 | -0.011978 | -0.10241 | 0.0048193 | North | N | 0.0048193 | 0
1862 | EAGLEMNT | MB | 100 | -0.078947 | north | Y | -0.0048193 | -0.18242 | -0.011978 | -0.10241 | 0.0048193 | North | N | 0.0048193 | 0
1863 | EAGLEMNT | MB | 378 | -0.078947 | north | Y | -0.0048193 | -0.18242 | -0.011978 | -0.10241 | 0.0048193 | North | N | 0.0048193 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.079447 | north | Y | -0.0053193 | -0.18292 | -0.012478 | -0.10291 | 0.0053193 | North | N | 0.0053193 | 0
1878 | WLFHOLW_ | 2 | 205 | -0.079447 | north | Y | -0.0053193 | -0.18292 | -0.012478 | -0.10291 | 0.0053193 | North | N | 0.0053193 | 0
1879 | WLFHOLW_ | 3 | 272.4 | -0.079447 | north | Y | -0.0053193 | -0.18292 | -0.012478 | -0.10291 | 0.0053193 | North | N | 0.0053193 | 0
1889 | DECRDOVA | MB | 770 | -0.079733 | north | Y | -0.0056053 | -0.1832 | -0.012764 | -0.10319 | 0.0056053 | North | N | 0.0056053 | 0
1892 | DECRDOVA | A | 70 | -0.080231 | north | Y | -0.0061033 | -0.1837 | -0.013262 | -0.10369 | 0.0061033 | North | N | 0.0061033 | 0
1893 | DECRDOVA | B | 69 | -0.080231 | north | Y | -0.0061033 | -0.1837 | -0.013262 | -0.10369 | 0.0061033 | North | N | 0.0061033 | 0
1894 | DECRDOVA | C | 69 | -0.080231 | north | Y | -0.0061033 | -0.1837 | -0.013262 | -0.10369 | 0.0061033 | North | N | 0.0061033 | 0
1895 | DECRDOVA | D | 68 | -0.080231 | north | Y | -0.0061033 | -0.1837 | -0.013262 | -0.10369 | 0.0061033 | North | N | 0.0061033 | 0
1898 | COMCHEPK | 1 | 1157 | -0.079151 | north | N | -0.0050233 | -0.18262 | -0.012182 | -0.10261 | 0.0050233 | North | N | 0.0050233 | 0
1899 | COMCHEPK | 2 | 1158 | -0.079151 | north | N | -0.0050233 | -0.18262 | -0.012182 | -0.10261 | 0.0050233 | North | N | 0.0050233 | 0
1937 | MDLTHELP | 5 | 224 | -0.084084 | north | Y | -0.0099563 | -0.18756 | -0.017115 | -0.10754 | 0.0099563 | North | N | 0.0099563 | 0
1938 | MDLTHELP | 6 | 226 | -0.084084 | north | Y | -0.0099563 | -0.18756 | -0.017115 | -0.10754 | 0.0099563 | North | N | 0.0099563 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.084027 | north | Y | -0.0098993 | -0.1875 | -0.017058 | -0.10749 | 0.0098993 | North | N | 0.0098993 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.084027 | north | Y | -0.0098993 | -0.1875 | -0.017058 | -0.10749 | 0.0098993 | North | N | 0.0098993 | 0
1943 | MDLTHELP | 3 | 212 | -0.084084 | north | Y | -0.0099563 | -0.18756 | -0.017115 | -0.10754 | 0.0099563 | North | N | 0.0099563 | 0
1944 | MDLTHELP | 4 | 211 | -0.084084 | north | Y | -0.0099563 | -0.18756 | -0.017115 | -0.10754 | 0.0099563 | North | N | 0.0099563 | 0
1947 | HANDLEY_ | 3 | 395 | -0.080517 | north | Y | -0.0063893 | -0.18399 | -0.013548 | -0.10398 | 0.0063893 | North | N | 0.0063893 | 0
1948 | HANDLEY_ | 4 | 435 | -0.080371 | north | Y | -0.0062433 | -0.18384 | -0.013402 | -0.10383 | 0.0062433 | North | N | 0.0062433 | 0
1949 | HANDLEY_ | 5 | 435 | -0.080517 | north | Y | -0.0063893 | -0.18399 | -0.013548 | -0.10398 | 0.0063893 | North | N | 0.0063893 | 0
2371 | COLLIN_1 | MB | 138 | -0.077666 | north | Y | -0.0035383 | -0.18114 | -0.010697 | -0.10113 | 0.0035383 | North | N | 0.0035383 | 0
2413 | MTCK6_G | 6 | 118 | -0.078454 | north | Y | -0.0043263 | -0.18193 | -0.011485 | -0.10191 | 0.0043263 | North | N | 0.0043263 | 0
2414 | MTCK7_G | 7 | 115 | -0.078454 | north | Y | -0.0043263 | -0.18193 | -0.011485 | -0.10191 | 0.0043263 | North | N | 0.0043263 | 0
2417 | MTCK8_G | 8 | 556 | -0.078454 | north | Y | -0.0043263 | -0.18193 | -0.011485 | -0.10191 | 0.0043263 | North | N | 0.0043263 | 0
2451 | LKHB1_G | 1 | 388 | -0.077025 | north | Y | -0.0028973 | -0.1805 | -0.010056 | -0.10049 | 0.0028973 | North | N | 0.0028973 | 0
2452 | LKHB2_G | 2 | 515 | -0.077025 | north | Y | -0.0028973 | -0.1805 | -0.010056 | -0.10049 | 0.0028973 | North | N | 0.0028973 | 0
3097 | MARTLAKE | 1 | 785 | -0.073665 | north | Y | 0.00046273 | -0.17714 | -0.0066962 | -0.097126 | 0.00046273 | North | N | 0.00046273 | 0
3098 | MARTLAKE | 2 | 795 | -0.073665 | north | Y | 0.00046273 | -0.17714 | -0.0066962 | -0.097126 | 0.00046273 | North | N | 0.00046273 | 0
3099 | MARTLAKE | 3 | 780 | -0.073665 | north | Y | 0.00046273 | -0.17714 | -0.0066962 | -0.097126 | 0.00046273 | North | N | 0.00046273 | 0
3107 | STRYKER_ | 1 | 182 | -0.072564 | north | Y | 0.0015637 | -0.17604 | -0.0055952 | -0.096025 | 0.0015637 | North | N | 0.0015637 | 0
3108 | STRYKER_ | 2 | 484 | -0.072564 | north | Y | 0.0015637 | -0.17604 | -0.0055952 | -0.096025 | 0.0015637 | North | N | 0.0015637 | 0
3126 | TRINIDAD | 1 | 224 | -0.076654 | north | Y | -0.0025263 | -0.18013 | -0.0096852 | -0.10011 | 0.0025263 | North | N | 0.0025263 | 0
3309 | ASPN_G | 1 | 50 | -0.072848 | north | Y | 0.0012797 | -0.17632 | -0.0058792 | -0.096309 | 0.0012797 | North | N | 0.0012797 | 0
3348 | CHAMPION | MB | 42 | -0.07288 | north | N | 0.0012477 | -0.17635 | -0.0059112 | -0.096341 | 0.0012477 | North | N | 0.0012477 | 0
3381 | BBRN_1G | 1 | 615 | -0.068167 | north | Y | 0.0059607 | -0.17164 | -0.0011982 | -0.091628 | 0.0011982 | west | Y | 0.0059607 | 2.929
3382 | BBRN_2G | 2 | 587 | -0.068167 | north | Y | 0.0059607 | -0.17164 | -0.0011982 | -0.091628 | 0.0011982 | west | Y | 0.0059607 | 2.7956
3403 | THOUSE_1 | MB | 537 | -0.12749 | north | Y | -0.053362 | -0.23096 | -0.060521 | -0.15095 | 0.053362 | North | N | 0.053362 | 0
3404 | THOUSE_2 | 2 | 787 | -0.12749 | north | Y | -0.053362 | -0.23096 | -0.060521 | -0.15095 | 0.053362 | North | N | 0.053362 | 0
3416 | LAKE_CRK | MB | 75 | -0.13417 | north | Y | -0.060044 | -0.23764 | -0.067203 | -0.15763 | 0.060044 | North | N | 0.060044 | 0
3417 | LAKE_CRK | MB | 222 | -0.13417 | north | Y | -0.060044 | -0.23764 | -0.067203 | -0.15763 | 0.060044 | North | N | 0.060044 | 0
3432 | SANDOW_4 | 4 | 569 | 0.16206 | south | Y | 0.23619 | 0.058588 | 0.22903 | 0.1386 | 0.058588 | south | N | 0.058588 | 0
5026 | BRAUNIG_ | 1 | 209 | 0.098085 | south | Y | 0.17221 | -0.0053862 | 0.16505 | 0.074624 | 0.0053862 | south | N | 0.0053862 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.098085 | south | Y | 0.17221 | -0.0053862 | 0.16505 | 0.074624 | 0.0053862 | south | N | 0.0053862 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.098024 | south | Y | 0.17215 | -0.0054472 | 0.16499 | 0.074563 | 0.0054472 | south | N | 0.0054472 | 0
5031 | BRA_VHBC | 1 | 46 | 0.098085 | south | Y | 0.17221 | -0.0053862 | 0.16505 | 0.074624 | 0.0053862 | south | N | 0.0053862 | 0
5032 | BRA_VHBC | 2 | 47 | 0.098085 | south | Y | 0.17221 | -0.0053862 | 0.16505 | 0.074624 | 0.0053862 | south | N | 0.0053862 | 0
5033 | BRA_VHBC | 3 | 46 | 0.098085 | south | Y | 0.17221 | -0.0053862 | 0.16505 | 0.074624 | 0.0053862 | south | N | 0.0053862 | 0
5034 | BRA_VHBC | 4 | 46 | 0.098085 | south | Y | 0.17221 | -0.0053862 | 0.16505 | 0.074624 | 0.0053862 | south | N | 0.0053862 | 0
5111 | CALAVER_ | 1 | 424 | 0.098252 | south | Y | 0.17238 | -0.0052192 | 0.16522 | 0.074791 | 0.0052192 | south | N | 0.0052192 | 0
5112 | CALAVER_ | 2 | 425 | 0.098252 | south | Y | 0.17238 | -0.0052192 | 0.16522 | 0.074791 | 0.0052192 | south | N | 0.0052192 | 0
5264 | LEON_LCP | 3 | 58 | 0.097481 | south | Y | 0.17161 | -0.0059902 | 0.16445 | 0.07402 | 0.0059902 | south | N | 0.0059902 | 0
5265 | LEON_LCP | 4 | 89 | 0.097481 | south | Y | 0.17161 | -0.0059902 | 0.16445 | 0.07402 | 0.0059902 | south | N | 0.0059902 | 0
5266 | LEON_LCP | 1 | 44 | 0.097481 | south | Y | 0.17161 | -0.0059902 | 0.16445 | 0.07402 | 0.0059902 | south | N | 0.0059902 | 0
5267 | LEON_LCP | 2 | 44 | 0.097481 | south | Y | 0.17161 | -0.0059902 | 0.16445 | 0.07402 | 0.0059902 | south | N | 0.0059902 | 0
5268 | LEON_LCP | 3 | 43 | 0.097481 | south | Y | 0.17161 | -0.0059902 | 0.16445 | 0.07402 | 0.0059902 | south | N | 0.0059902 | 0
5269 | LEON_LCP | 4 | 45 | 0.097481 | south | Y | 0.17161 | -0.0059902 | 0.16445 | 0.07402 | 0.0059902 | south | N | 0.0059902 | 0
5396 | CALAVER_ | 1 | 412 | 0.09819 | south | Y | 0.17232 | -0.0052812 | 0.16516 | 0.074729 | 0.0052812 | south | N | 0.0052812 | 0
5397 | CALAVER_ | 2 | 400 | 0.09819 | south | Y | 0.17232 | -0.0052812 | 0.16516 | 0.074729 | 0.0052812 | south | N | 0.0052812 | 0
5401 | CALAVER_ | 1 | 546 | 0.097356 | south | Y | 0.17148 | -0.0061152 | 0.16432 | 0.073895 | 0.0061152 | south | N | 0.0061152 | 0
5402 | CALAVER_ | 2 | 750 | 0.097356 | south | Y | 0.17148 | -0.0061152 | 0.16432 | 0.073895 | 0.0061152 | south | N | 0.0061152 | 0
5436 | TUTTL_WB | MB | 61 | 0.09854 | south | Y | 0.17267 | -0.0049312 | 0.16551 | 0.075079 | 0.0049312 | south | N | 0.0049312 | 0
5438 | TUTTL_WB | MB | 95 | 0.09854 | south | Y | 0.17267 | -0.0049312 | 0.16551 | 0.075079 | 0.0049312 | south | N | 0.0049312 | 0
5439 | TUTTL_WB | MB | 151 | 0.09854 | south | Y | 0.17267 | -0.0049312 | 0.16551 | 0.075079 | 0.0049312 | south | N | 0.0049312 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.097835 | south | Y | 0.17196 | -0.0056362 | 0.1648 | 0.074374 | 0.0056362 | south | N | 0.0056362 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.097835 | south | Y | 0.17196 | -0.0056362 | 0.1648 | 0.074374 | 0.0056362 | south | N | 0.0056362 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.097835 | south | Y | 0.17196 | -0.0056362 | 0.1648 | 0.074374 | 0.0056362 | south | N | 0.0056362 | 0
5503 | RAYBURNG | 1 | 22 | 0.079072 | south | Y | 0.1532 | -0.024399 | 0.14604 | 0.055611 | 0.024399 | south | N | 0.024399 | 0
5505 | RAYBURNG | 1 | 11 | 0.079072 | south | Y | 0.1532 | -0.024399 | 0.14604 | 0.055611 | 0.024399 | south | N | 0.024399 | 0
5506 | RAYBURNG | 1 | 11 | 0.079072 | south | Y | 0.1532 | -0.024399 | 0.14604 | 0.055611 | 0.024399 | south | N | 0.024399 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.079797 | south | Y | 0.15392 | -0.023674 | 0.14677 | 0.056336 | 0.023674 | south | N | 0.023674 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.079797 | south | Y | 0.15392 | -0.023674 | 0.14677 | 0.056336 | 0.023674 | south | N | 0.023674 | 0
5511 | RAYBURNC | 1 | 46 | 0.079797 | south | Y | 0.15392 | -0.023674 | 0.14677 | 0.056336 | 0.023674 | south | N | 0.023674 | 0
5512 | RAYBURNC | 1 | 48 | 0.079797 | south | Y | 0.15392 | -0.023674 | 0.14677 | 0.056336 | 0.023674 | south | N | 0.023674 | 0
5728 | FALCONHY | 2 | 12 | 0.083269 | south | N | 0.1574 | -0.020202 | 0.15024 | 0.059808 | 0.020202 | south | N | 0.020202 | 0
5729 | FALCONHY | 3 | 11 | 0.083269 | south | N | 0.1574 | -0.020202 | 0.15024 | 0.059808 | 0.020202 | south | N | 0.020202 | 0
5890 | PEARSALL | 1 | 24 | 0.086878 | south | Y | 0.16101 | -0.016593 | 0.15385 | 0.063417 | 0.016593 | south | N | 0.016593 | 0
5891 | PEARSALL | 1 | 24 | 0.086878 | south | Y | 0.16101 | -0.016593 | 0.15385 | 0.063417 | 0.016593 | south | N | 0.016593 | 0
5892 | PEARSALL | 1 | 23 | 0.086878 | south | Y | 0.16101 | -0.016593 | 0.15385 | 0.063417 | 0.016593 | south | N | 0.016593 | 0
5903 | SANMIGUE | 1 | 396 | 0.092154 | south | Y | 0.16628 | -0.011317 | 0.15912 | 0.068693 | 0.011317 | south | N | 0.011317 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.05126 | houston | N | 0.12539 | -0.052211 | 0.11823 | 0.027799 | 0.027799 | houston | N | 0.027799 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.05126 | houston | N | 0.12539 | -0.052211 | 0.11823 | 0.027799 | 0.027799 | houston | N | 0.027799 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.074128 | 0
5932 | SI_RAY9 | 9 | 38 | 0.081993 | south | Y | 0.15612 | -0.021478 | 0.14896 | 0.058532 | 0.021478 | south | N | 0.021478 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.081993 | south | Y | 0.15612 | -0.021478 | 0.14896 | 0.058532 | 0.021478 | south | N | 0.021478 | 0
5934 | SI_RAY5 | 5 | 15 | 0.081993 | south | Y | 0.15612 | -0.021478 | 0.14896 | 0.058532 | 0.021478 | south | N | 0.021478 | 0
5935 | SI_RAY10 | 10 | 47 | 0.081993 | south | Y | 0.15612 | -0.021478 | 0.14896 | 0.058532 | 0.021478 | south | N | 0.021478 | 0
6016 | SWMESA | 1 | 75 | -0.058968 | west | Y | 0.01516 | -0.16244 | 0.0080008 | -0.082429 | 0.0080008 | west | N | 0.0080008 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.066969 | 0
6144 | MCADOO1A | 1 | 150 | -0.069312 | west | Y | 0.0048157 | -0.17278 | -0.0023432 | -0.092773 | 0.0023432 | west | N | 0.0023432 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.065509 | west | Y | 0.0086187 | -0.16898 | 0.0014598 | -0.08897 | 0.0014598 | west | N | 0.0014598 | 0
6476 | LANGFORD | 1 | 150 | -0.029953 | west | Y | 0.044175 | -0.13342 | 0.037016 | -0.053414 | 0.037016 | west | N | 0.037016 | 0
6637 | SNYDERW1 | 1 | 63 | -0.068268 | west | Y | 0.0058597 | -0.17174 | -0.0012992 | -0.091729 | 0.0012992 | west | N | 0.0012992 | 0
6752 | OKLA0A | 1 | 649.7 | -0.073078 | west | Y | 0.0010497 | -0.17655 | -0.0061092 | -0.096539 | 0.0010497 | North | Y | 0.0061092 | 3.2871
6948 | DENISNDM | 1 | 40 | -0.077295 | north | N | -0.0031673 | -0.18077 | -0.010326 | -0.10076 | 0.0031673 | North | N | 0.0031673 | 0
6948 | DENISNDM | 2 | 40 | -0.077295 | north | N | -0.0031673 | -0.18077 | -0.010326 | -0.10076 | 0.0031673 | North | N | 0.0031673 | 0
7000 | L_FERGUS | 1 | 422 | 0.10701 | south | Y | 0.18113 | 0.0035338 | 0.17397 | 0.083544 | 0.0035338 | south | N | 0.0035338 | 0
7004 | L_SIMGID | 1 | 132 | 0.12475 | south | Y | 0.19888 | 0.02128 | 0.19172 | 0.10129 | 0.02128 | south | N | 0.02128 | 0
7005 | L_SIMGID | 2 | 134 | 0.12475 | south | Y | 0.19888 | 0.02128 | 0.19172 | 0.10129 | 0.02128 | south | N | 0.02128 | 0
7006 | L_SIMGID | 3 | 323 | 0.12475 | south | Y | 0.19888 | 0.02128 | 0.19172 | 0.10129 | 0.02128 | south | N | 0.02128 | 0
7007 | L_LOSTPI | 1 | 158 | 0.12372 | south | Y | 0.19784 | 0.020246 | 0.19069 | 0.10026 | 0.020246 | south | N | 0.020246 | 0
7008 | L_LOSTPI | 2 | 160 | 0.12372 | south | Y | 0.19784 | 0.020246 | 0.19069 | 0.10026 | 0.020246 | south | N | 0.020246 | 0
7009 | L_LOSTPI | 3 | 175 | 0.12372 | south | Y | 0.19784 | 0.020246 | 0.19069 | 0.10026 | 0.020246 | south | N | 0.020246 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.11061 | south | Y | 0.18474 | 0.0071378 | 0.17758 | 0.087148 | 0.0071378 | south | N | 0.0071378 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.11061 | south | Y | 0.18474 | 0.0071378 | 0.17758 | 0.087148 | 0.0071378 | south | N | 0.0071378 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.1105 | south | Y | 0.18463 | 0.0070308 | 0.17747 | 0.087041 | 0.0070308 | south | N | 0.0070308 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.1082 | south | Y | 0.18233 | 0.0047328 | 0.17517 | 0.084743 | 0.0047328 | south | N | 0.0047328 | 0
7015 | L_HAYSEN | 2 | 225 | 0.1082 | south | Y | 0.18233 | 0.0047328 | 0.17517 | 0.084743 | 0.0047328 | south | N | 0.0047328 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.1082 | south | Y | 0.18233 | 0.0047328 | 0.17517 | 0.084743 | 0.0047328 | south | N | 0.0047328 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.1082 | south | Y | 0.18233 | 0.0047328 | 0.17517 | 0.084743 | 0.0047328 | south | N | 0.0047328 | 0
7020 | L_AUSTPL | 1 | 8 | 0.13092 | south | N | 0.20505 | 0.027452 | 0.19789 | 0.10746 | 0.027452 | south | N | 0.027452 | 0
7020 | L_AUSTPL | 2 | 8 | 0.13092 | south | N | 0.20505 | 0.027452 | 0.19789 | 0.10746 | 0.027452 | south | N | 0.027452 | 0
7022 | L_BUCHAN | 1 | 18 | 0.10263 | south | N | 0.17676 | -0.00083823 | 0.1696 | 0.079172 | 0.00083823 | south | N | 0.00083823 | 0
7023 | L_BUCHAN | 2 | 18 | 0.10263 | south | N | 0.17676 | -0.00083823 | 0.1696 | 0.079172 | 0.00083823 | south | N | 0.00083823 | 0
7024 | L_BUCHAN | 3 | 15 | 0.10263 | south | N | 0.17676 | -0.00083823 | 0.1696 | 0.079172 | 0.00083823 | south | N | 0.00083823 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.10359 | south | N | 0.17771 | 0.00011477 | 0.17055 | 0.080125 | 0.00011477 | south | N | 0.00011477 | 0
7028 | L_MARBFA | 1 | 18 | 0.11284 | south | N | 0.18697 | 0.0093678 | 0.17981 | 0.089378 | 0.0093678 | south | N | 0.0093678 | 0
7029 | L_MARBFA | 2 | 18 | 0.11284 | south | N | 0.18697 | 0.0093678 | 0.17981 | 0.089378 | 0.0093678 | south | N | 0.0093678 | 0
7031 | L_MARSFO | 1 | 35 | 0.12607 | south | N | 0.20019 | 0.022596 | 0.19304 | 0.10261 | 0.022596 | south | N | 0.022596 | 0
7032 | L_MARSFO | 2 | 34 | 0.12607 | south | N | 0.20019 | 0.022596 | 0.19304 | 0.10261 | 0.022596 | south | N | 0.022596 | 0
7033 | L_MARSFO | 3 | 35 | 0.12607 | south | N | 0.20019 | 0.022596 | 0.19304 | 0.10261 | 0.022596 | south | N | 0.022596 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.10778 | south | N | 0.18191 | 0.0043078 | 0.17475 | 0.084318 | 0.0043078 | south | N | 0.0043078 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.10778 | south | N | 0.18191 | 0.0043078 | 0.17475 | 0.084318 | 0.0043078 | south | N | 0.0043078 | 0
7038 | L_DELAWA | 1 | 35 | -0.065821 | west | Y | 0.0083067 | -0.16929 | 0.0011478 | -0.089282 | 0.0011478 | west | N | 0.0011478 | 0
7038 | L_DELAWA | 2 | 30 | -0.065821 | west | Y | 0.0083067 | -0.16929 | 0.0011478 | -0.089282 | 0.0011478 | west | N | 0.0011478 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.11284 | south | Y | 0.18696 | 0.0093658 | 0.17981 | 0.089376 | 0.0093658 | south | N | 0.0093658 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.11284 | south | Y | 0.18696 | 0.0093658 | 0.17981 | 0.089376 | 0.0093658 | south | N | 0.0093658 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.11284 | south | Y | 0.18696 | 0.0093658 | 0.17981 | 0.089376 | 0.0093658 | south | N | 0.0093658 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.11284 | south | Y | 0.18696 | 0.0093658 | 0.17981 | 0.089376 | 0.0093658 | south | N | 0.0093658 | 0
7487 | L_CANYHY | 1 | 6 | 0.11137 | south | N | 0.18549 | 0.0078958 | 0.17834 | 0.087906 | 0.0078958 | south | N | 0.0078958 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.10502 | south | N | 0.17915 | 0.0015478 | 0.17199 | 0.081558 | 0.0015478 | south | N | 0.0015478 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.10502 | south | N | 0.17915 | 0.0015478 | 0.17199 | 0.081558 | 0.0015478 | south | N | 0.0015478 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.10502 | south | N | 0.17915 | 0.0015478 | 0.17199 | 0.081558 | 0.0015478 | south | N | 0.0015478 | 0
7609 | L_SCHUMA | 1 | 4 | 0.10339 | south | N | 0.17752 | -8.2227e-05 | 0.17036 | 0.079928 | 8.2227e-05 | south | N | 8.2227e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.10378 | south | N | 0.17791 | 0.00030977 | 0.17075 | 0.08032 | 0.00030977 | south | N | 0.00030977 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.10378 | south | N | 0.17791 | 0.00030977 | 0.17075 | 0.08032 | 0.00030977 | south | N | 0.00030977 | 0
7800 | L_GUADGE | 1 | 147 | 0.10072 | south | Y | 0.17485 | -0.0027532 | 0.16769 | 0.077257 | 0.0027532 | south | N | 0.0027532 | 0
7801 | L_GUADGE | 2 | 138 | 0.10072 | south | Y | 0.17485 | -0.0027532 | 0.16769 | 0.077257 | 0.0027532 | south | N | 0.0027532 | 0
7802 | L_GUADGE | 3 | 140 | 0.10072 | south | Y | 0.17485 | -0.0027532 | 0.16769 | 0.077257 | 0.0027532 | south | N | 0.0027532 | 0
7803 | L_GUADGE | 4 | 147 | 0.10072 | south | Y | 0.17485 | -0.0027532 | 0.16769 | 0.077257 | 0.0027532 | south | N | 0.0027532 | 0
7804 | L_GUADGE | 5 | 182 | 0.10072 | south | Y | 0.17485 | -0.0027532 | 0.16769 | 0.077257 | 0.0027532 | south | N | 0.0027532 | 0
7805 | L_GUADGE | 6 | 198 | 0.10072 | south | Y | 0.17485 | -0.0027532 | 0.16769 | 0.077257 | 0.0027532 | south | N | 0.0027532 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.12491 | south | Y | 0.19904 | 0.021444 | 0.19188 | 0.10145 | 0.021444 | south | N | 0.021444 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.12491 | south | Y | 0.19904 | 0.021444 | 0.19188 | 0.10145 | 0.021444 | south | N | 0.021444 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.12491 | south | Y | 0.19904 | 0.021444 | 0.19188 | 0.10145 | 0.021444 | south | N | 0.021444 | 0
7810 | L_RIONOG | 1 | 142 | 0.10437 | south | Y | 0.1785 | 0.00090177 | 0.17134 | 0.080912 | 0.00090177 | south | N | 0.00090177 | 0
7811 | L_RIONOG | 2 | 145 | 0.10437 | south | Y | 0.1785 | 0.00090177 | 0.17134 | 0.080912 | 0.00090177 | south | N | 0.00090177 | 0
7812 | L_RIONOG | 3 | 151 | 0.10437 | south | Y | 0.1785 | 0.00090177 | 0.17134 | 0.080912 | 0.00090177 | south | N | 0.00090177 | 0
7813 | L_RIONOG | 4 | 290 | 0.10437 | south | Y | 0.1785 | 0.00090177 | 0.17134 | 0.080912 | 0.00090177 | south | N | 0.00090177 | 0
8032 | AMISTADH | 1 | 33 | 0.047114 | south | N | 0.12124 | -0.056357 | 0.11408 | 0.023653 | 0.023653 | houston | Y | 0.056357 | 0
8033 | AMISTADH | 2 | 25 | 0.047114 | south | N | 0.12124 | -0.056357 | 0.11408 | 0.023653 | 0.023653 | houston | Y | 0.056357 | 0
8048 | FALCONHY | 1 | 12 | 0.083269 | south | N | 0.1574 | -0.020202 | 0.15024 | 0.059808 | 0.020202 | south | N | 0.020202 | 0
8066 | DUP1V#1 | 1 | 73 | 0.079981 | south | N | 0.15411 | -0.02349 | 0.14695 | 0.05652 | 0.02349 | south | N | 0.02349 | 0
8134 | FOR69CG0 | 1 | 79 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
8138 | FOR69CG0 | 2 | 81 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.10347 | 0
8147 | UCAR #2 | 10 | 28 | 0.077528 | south | N | 0.15166 | -0.025943 | 0.1445 | 0.054067 | 0.025943 | south | N | 0.025943 | 0
8148 | UCAR #1 | 2 | 7 | 0.077528 | south | N | 0.15166 | -0.025943 | 0.1445 | 0.054067 | 0.025943 | south | N | 0.025943 | 0
8153 | FOR69CG0 | 3 | 79 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
8154 | FOR69CG0 | 4 | 80 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
8156 | FOR69CG0 | 6 | 25 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
8157 | FOR69CG0 | 7 | 46 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
8161 | COLETOU1 | 1 | 629 | 0.084633 | south | Y | 0.15876 | -0.018838 | 0.1516 | 0.061172 | 0.018838 | south | N | 0.018838 | 0
8173 | VICEC51A | 5 | 144 | 0.080874 | south | Y | 0.155 | -0.022597 | 0.14784 | 0.057413 | 0.022597 | south | N | 0.022597 | 0
8174 | VICEC61A | 6 | 188 | 0.080874 | south | Y | 0.155 | -0.022597 | 0.14784 | 0.057413 | 0.022597 | south | N | 0.022597 | 0
8189 | CUERO 2 | 1 | 12 | 0.097502 | south | N | 0.17163 | -0.0059692 | 0.16447 | 0.074041 | 0.0059692 | south | N | 0.0059692 | 0
8262 | ELPS | 1 | 6 | 0.059484 | south | N | 0.13361 | -0.043987 | 0.12645 | 0.036023 | 0.036023 | houston | Y | 0.043987 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.10347 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.10347 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.10347 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.10347 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.10347 | 0
8442 | NBEC71A | 1 | 336 | 0.081135 | south | Y | 0.15526 | -0.022336 | 0.1481 | 0.057674 | 0.022336 | south | N | 0.022336 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.10347 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | 0.074128 | -0.10347 | 0.066969 | -0.023461 | 0.023461 | houston | Y | 0.10347 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.081319 | south | Y | 0.15545 | -0.022152 | 0.14829 | 0.057858 | 0.022152 | south | N | 0.022152 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.081319 | south | Y | 0.15545 | -0.022152 | 0.14829 | 0.057858 | 0.022152 | south | N | 0.022152 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.081434 | south | N | 0.15556 | -0.022037 | 0.1484 | 0.057973 | 0.022037 | south | N | 0.022037 | 0
8506 | VAL #1 | 1 | 25 | 0.081349 | south | N | 0.15548 | -0.022122 | 0.14832 | 0.057888 | 0.022122 | south | N | 0.022122 | 0
8507 | VAL #2 | 2 | 25 | 0.081349 | south | N | 0.15548 | -0.022122 | 0.14832 | 0.057888 | 0.022122 | south | N | 0.022122 | 0
8511 | OXY_CC0A | 1 | 38 | 0.081428 | south | N | 0.15556 | -0.022043 | 0.1484 | 0.057967 | 0.022043 | south | N | 0.022043 | 0
8517 | CELANEBI | 1 | 29 | 0.081814 | south | N | 0.15594 | -0.021657 | 0.14878 | 0.058353 | 0.021657 | south | N | 0.021657 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.081145 | south | N | 0.15527 | -0.022326 | 0.14811 | 0.057684 | 0.022326 | south | N | 0.022326 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.081145 | south | N | 0.15527 | -0.022326 | 0.14811 | 0.057684 | 0.022326 | south | N | 0.022326 | 0
8562 | CNOPST1 | 3 | 153 | 0.081145 | south | N | 0.15527 | -0.022326 | 0.14811 | 0.057684 | 0.022326 | south | N | 0.022326 | 0
8926 | LGE_GT10 | 1 | 158 | 0.080309 | south | N | 0.15444 | -0.023162 | 0.14728 | 0.056848 | 0.023162 | south | N | 0.023162 | 0
8927 | LGE_GT20 | 2 | 153 | 0.080309 | south | N | 0.15444 | -0.023162 | 0.14728 | 0.056848 | 0.023162 | south | N | 0.023162 | 0
8928 | LGE_STG0 | 3 | 100 | 0.080309 | south | N | 0.15444 | -0.023162 | 0.14728 | 0.056848 | 0.023162 | south | N | 0.023162 | 0
8930 | ICPGN10A | 1 | 145 | 0.080309 | south | N | 0.15444 | -0.023162 | 0.14728 | 0.056848 | 0.023162 | south | N | 0.023162 | 0
8931 | ICPGN20A | 2 | 147 | 0.080309 | south | N | 0.15444 | -0.023162 | 0.14728 | 0.056848 | 0.023162 | south | N | 0.023162 | 0
8932 | ICPGN30A | 3 | 127 | 0.080309 | south | N | 0.15444 | -0.023162 | 0.14728 | 0.056848 | 0.023162 | south | N | 0.023162 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.082303 | south | Y | 0.15643 | -0.021168 | 0.14927 | 0.058842 | 0.021168 | south | N | 0.021168 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.082303 | south | Y | 0.15643 | -0.021168 | 0.14927 | 0.058842 | 0.021168 | south | N | 0.021168 | 0
8935 | FGNTS201 | 3 | 173 | 0.082303 | south | Y | 0.15643 | -0.021168 | 0.14927 | 0.058842 | 0.021168 | south | N | 0.021168 | 0
8936 | MVGN#1 | 1 | 207 | 0.082148 | south | Y | 0.15628 | -0.021323 | 0.14912 | 0.058687 | 0.021323 | south | N | 0.021323 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.082148 | south | Y | 0.15628 | -0.021323 | 0.14912 | 0.058687 | 0.021323 | south | N | 0.021323 | 0
8938 | MVGN#3 | 3 | 242 | 0.082148 | south | Y | 0.15628 | -0.021323 | 0.14912 | 0.058687 | 0.021323 | south | N | 0.021323 | 0
8981 | HECN1 | 1 | 144 | 0.082145 | south | Y | 0.15627 | -0.021326 | 0.14911 | 0.058684 | 0.021326 | south | N | 0.021326 | 0
8982 | HECN2 | 2 | 144 | 0.082145 | south | Y | 0.15627 | -0.021326 | 0.14911 | 0.058684 | 0.021326 | south | N | 0.021326 | 0
8983 | HECN3 | 3 | 171 | 0.082145 | south | Y | 0.15627 | -0.021326 | 0.14911 | 0.058684 | 0.021326 | south | N | 0.021326 | 0
9000 | DECKR_G1 | 1 | 310 | 0.1312 | south | Y | 0.20533 | 0.027733 | 0.19817 | 0.10774 | 0.027733 | south | N | 0.027733 | 0
9001 | DECKR_G2 | 2 | 413 | 0.1312 | south | Y | 0.20533 | 0.027733 | 0.19817 | 0.10774 | 0.027733 | south | N | 0.027733 | 0
9002 | DECKR_G3 | 3 | 42 | 0.13252 | south | Y | 0.20665 | 0.029052 | 0.19949 | 0.10906 | 0.029052 | south | N | 0.029052 | 0
9003 | DECKR_G4 | 4 | 44 | 0.13252 | south | Y | 0.20665 | 0.029052 | 0.19949 | 0.10906 | 0.029052 | south | N | 0.029052 | 0
9004 | DECKR_G5 | 5 | 44 | 0.13252 | south | Y | 0.20665 | 0.029052 | 0.19949 | 0.10906 | 0.029052 | south | N | 0.029052 | 0
9005 | DECKR_G6 | 6 | 47 | 0.13252 | south | Y | 0.20665 | 0.029052 | 0.19949 | 0.10906 | 0.029052 | south | N | 0.029052 | 0
9016 | SANDH_G1 | 1 | 49 | 0.12936 | south | Y | 0.20349 | 0.025889 | 0.19633 | 0.1059 | 0.025889 | south | N | 0.025889 | 0
9017 | SANDH_G2 | 2 | 46 | 0.12936 | south | Y | 0.20349 | 0.025889 | 0.19633 | 0.1059 | 0.025889 | south | N | 0.025889 | 0
9018 | SANDH_G3 | 3 | 46 | 0.12936 | south | Y | 0.20349 | 0.025889 | 0.19633 | 0.1059 | 0.025889 | south | N | 0.025889 | 0
9019 | SANDH_G4 | 4 | 47 | 0.12936 | south | Y | 0.20349 | 0.025889 | 0.19633 | 0.1059 | 0.025889 | south | N | 0.025889 | 0
9020 | SANDHG5A | 5A | 154 | 0.12936 | south | Y | 0.20349 | 0.025889 | 0.19633 | 0.1059 | 0.025889 | south | N | 0.025889 | 0
9021 | SANDHG5C | 5C | 148 | 0.12936 | south | Y | 0.20349 | 0.025889 | 0.19633 | 0.1059 | 0.025889 | south | N | 0.025889 | 0
9022 | SANDH_G6 | 6 | 48 | 0.12936 | south | Y | 0.20349 | 0.025889 | 0.19633 | 0.1059 | 0.025889 | south | N | 0.025889 | 0
9023 | SANDH_G7 | 7 | 48 | 0.12936 | south | Y | 0.20349 | 0.025889 | 0.19633 | 0.1059 | 0.025889 | south | N | 0.025889 | 0
11001 | NAV1CT | 1 | 70 | -0.066984 | west | Y | 0.0071437 | -0.17046 | -1.5165e-05 | -0.090445 | 1.5165e-05 | west | N | 1.5165e-05 | 0
11009 | NAV2CT | 1 | 70 | -0.066984 | west | Y | 0.0071437 | -0.17046 | -1.5165e-05 | -0.090445 | 1.5165e-05 | west | N | 1.5165e-05 | 0
11011 | NAV3ST | 1 | 92.8 | -0.066984 | west | Y | 0.0071437 | -0.17046 | -1.5165e-05 | -0.090445 | 1.5165e-05 | west | N | 1.5165e-05 | 0
11012 | NAV4CT | 1 | 80 | -0.066984 | west | Y | 0.0071437 | -0.17046 | -1.5165e-05 | -0.090445 | 1.5165e-05 | west | N | 1.5165e-05 | 0
11013 | NAV5CT | 1 | 80 | -0.066984 | west | Y | 0.0071437 | -0.17046 | -1.5165e-05 | -0.090445 | 1.5165e-05 | west | N | 1.5165e-05 | 0
11014 | NAV6ST | 1 | 115 | -0.066984 | west | Y | 0.0071437 | -0.17046 | -1.5165e-05 | -0.090445 | 1.5165e-05 | west | N | 1.5165e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.066972 | west | Y | 0.0071557 | -0.17044 | -3.1649e-06 | -0.090433 | 3.1649e-06 | west | N | 3.1649e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.066972 | west | Y | 0.0071557 | -0.17044 | -3.1649e-06 | -0.090433 | 3.1649e-06 | west | N | 3.1649e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.066972 | west | Y | 0.0071557 | -0.17044 | -3.1649e-06 | -0.090433 | 3.1649e-06 | west | N | 3.1649e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.066972 | west | Y | 0.0071557 | -0.17044 | -3.1649e-06 | -0.090433 | 3.1649e-06 | west | N | 3.1649e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.066972 | west | Y | 0.0071557 | -0.17044 | -3.1649e-06 | -0.090433 | 3.1649e-06 | west | N | 3.1649e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.066972 | west | Y | 0.0071557 | -0.17044 | -3.1649e-06 | -0.090433 | 3.1649e-06 | west | N | 3.1649e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.069211 | west | Y | 0.0049167 | -0.17268 | -0.0022422 | -0.092672 | 0.0022422 | west | N | 0.0022422 | 0
11057 | CHAMPION | 1 | 126.5 | -0.069211 | west | Y | 0.0049167 | -0.17268 | -0.0022422 | -0.092672 | 0.0022422 | west | N | 0.0022422 | 0
11058 | PYRON_1G | 1 | 249 | -0.069211 | west | Y | 0.0049167 | -0.17268 | -0.0022422 | -0.092672 | 0.0022422 | west | N | 0.0022422 | 0
11059 | INADALE_ | 1 | 197 | -0.069211 | west | Y | 0.0049167 | -0.17268 | -0.0022422 | -0.092672 | 0.0022422 | west | N | 0.0022422 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.068049 | west | Y | 0.0060787 | -0.17152 | -0.0010802 | -0.09151 | 0.0010802 | west | N | 0.0010802 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.068049 | west | Y | 0.0060787 | -0.17152 | -0.0010802 | -0.09151 | 0.0010802 | west | N | 0.0010802 | 0
11147 | NOTREES_ | 1 | 149 | -0.066029 | west | Y | 0.0080987 | -0.1695 | 0.00093984 | -0.08949 | 0.00093984 | west | N | 0.00093984 | 0
11309 | BULLCREK | 1 | 180 | -0.067861 | west | Y | 0.0062667 | -0.17133 | -0.00089216 | -0.091322 | 0.00089216 | west | N | 0.00089216 | 0
11310 | BULLCREK | 1 | 180 | -0.067861 | west | Y | 0.0062667 | -0.17133 | -0.00089216 | -0.091322 | 0.00089216 | west | N | 0.00089216 | 0
11320 | COYOTE_1 | 1 | 225 | -0.067797 | west | Y | 0.0063307 | -0.17127 | -0.00082816 | -0.091258 | 0.00082816 | west | N | 0.00082816 | 0
11415 | LORAINE_ | 1 | 125 | -0.068719 | west | Y | 0.0054087 | -0.17219 | -0.0017502 | -0.09218 | 0.0017502 | west | N | 0.0017502 | 0
11416 | LORAINE_ | 1 | 125 | -0.068719 | west | Y | 0.0054087 | -0.17219 | -0.0017502 | -0.09218 | 0.0017502 | west | N | 0.0017502 | 0
11691 | KMICHICT | 1 | 140 | -0.077156 | north | N | -0.0030283 | -0.18063 | -0.010187 | -0.10062 | 0.0030283 | North | N | 0.0030283 | 0
11692 | KMICHICT | 2 | 141 | -0.077156 | north | N | -0.0030283 | -0.18063 | -0.010187 | -0.10062 | 0.0030283 | North | N | 0.0030283 | 0
11693 | KMICHIST | 3 | 309 | -0.077156 | north | N | -0.0030283 | -0.18063 | -0.010187 | -0.10062 | 0.0030283 | North | N | 0.0030283 | 0
11694 | KMICHICT | 4 | 143 | -0.077156 | north | N | -0.0030283 | -0.18063 | -0.010187 | -0.10062 | 0.0030283 | North | N | 0.0030283 | 0
11695 | KMICHICT | 5 | 144 | -0.077156 | north | N | -0.0030283 | -0.18063 | -0.010187 | -0.10062 | 0.0030283 | North | N | 0.0030283 | 0
11696 | KMICHIST | 6 | 310 | -0.077156 | north | N | -0.0030283 | -0.18063 | -0.010187 | -0.10062 | 0.0030283 | North | N | 0.0030283 | 0
12322 | ENNSTRAC | 1 | 196 | -0.079414 | north | Y | -0.0052863 | -0.18289 | -0.012445 | -0.10287 | 0.0052863 | North | N | 0.0052863 | 0
12323 | ENNSTRAC | 2 | 111 | -0.079414 | north | Y | -0.0052863 | -0.18289 | -0.012445 | -0.10287 | 0.0052863 | North | N | 0.0052863 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.077697 | north | N | -0.0035693 | -0.18117 | -0.010728 | -0.10116 | 0.0035693 | North | N | 0.0035693 | 0
12411 | FPLEFR1A | 1 | 161 | -0.076362 | north | Y | -0.0022343 | -0.17983 | -0.0093932 | -0.099823 | 0.0022343 | North | N | 0.0022343 | 0
12412 | FPLEFR1B | 2 | 164 | -0.076362 | north | Y | -0.0022343 | -0.17983 | -0.0093932 | -0.099823 | 0.0022343 | North | N | 0.0022343 | 0
12413 | FPLEFR1C | 3 | 164 | -0.076362 | north | Y | -0.0022343 | -0.17983 | -0.0093932 | -0.099823 | 0.0022343 | North | N | 0.0022343 | 0
12414 | FPLEFR1S | 4 | 414 | -0.076362 | north | Y | -0.0022343 | -0.17983 | -0.0093932 | -0.099823 | 0.0022343 | North | N | 0.0022343 | 0
12421 | FPLEFR2A | 1 | 162 | -0.076362 | north | Y | -0.0022343 | -0.17983 | -0.0093932 | -0.099823 | 0.0022343 | North | N | 0.0022343 | 0
12422 | FPLEFR2B | 2 | 161 | -0.076362 | north | Y | -0.0022343 | -0.17983 | -0.0093932 | -0.099823 | 0.0022343 | North | N | 0.0022343 | 0
12423 | FPLEFR2C | 3 | 163 | -0.076362 | north | Y | -0.0022343 | -0.17983 | -0.0093932 | -0.099823 | 0.0022343 | North | N | 0.0022343 | 0
12424 | FPLEFR2S | 4 | 409 | -0.076362 | north | Y | -0.0022343 | -0.17983 | -0.0093932 | -0.099823 | 0.0022343 | North | N | 0.0022343 | 0
12440 | PARKD_1S | 1 | 0 | -0.077316 | north | N | -0.0031883 | -0.18079 | -0.010347 | -0.10078 | 0.0031883 | North | N | 0.0031883 | 0
12449 | PARKD_2S | 1 | 0 | -0.077316 | north | N | -0.0031883 | -0.18079 | -0.010347 | -0.10078 | 0.0031883 | North | N | 0.0031883 | 0
13116 | TGATEWAY | 1 | 148 | -0.073309 | north | N | 0.00081873 | -0.17678 | -0.0063402 | -0.09677 | 0.00081873 | North | N | 0.00081873 | 0
13117 | TGATEWAY | 2 | 130 | -0.073309 | north | N | 0.00081873 | -0.17678 | -0.0063402 | -0.09677 | 0.00081873 | North | N | 0.00081873 | 0
13118 | TGATEWAY | 3 | 145 | -0.073309 | north | N | 0.00081873 | -0.17678 | -0.0063402 | -0.09677 | 0.00081873 | North | N | 0.00081873 | 0
13119 | TGATEWAY | 4 | 399 | -0.073309 | north | N | 0.00081873 | -0.17678 | -0.0063402 | -0.09677 | 0.00081873 | North | N | 0.00081873 | 0
13131 | CALFREST | 1 | 150.7 | -0.069081 | north | Y | 0.0050467 | -0.17255 | -0.0021122 | -0.092542 | 0.0021122 | west | Y | 0.0050467 | 0.44224
13132 | CALFREST | 2 | 151 | -0.069081 | north | Y | 0.0050467 | -0.17255 | -0.0021122 | -0.092542 | 0.0021122 | west | Y | 0.0050467 | 0.44312
13133 | CALFREST | 3 | 177.4 | -0.069081 | north | Y | 0.0050467 | -0.17255 | -0.0021122 | -0.092542 | 0.0021122 | west | Y | 0.0050467 | 0.52059
13134 | CALFREST | 4 | 151.5 | -0.069241 | north | Y | 0.0048867 | -0.17271 | -0.0022722 | -0.092702 | 0.0022722 | west | Y | 0.0048867 | 0.39611
13135 | CALFREST | 5 | 152.3 | -0.069241 | north | Y | 0.0048867 | -0.17271 | -0.0022722 | -0.092702 | 0.0022722 | west | Y | 0.0048867 | 0.3982
13136 | CALFREST | 6 | 177.5 | -0.069241 | north | Y | 0.0048867 | -0.17271 | -0.0022722 | -0.092702 | 0.0022722 | west | Y | 0.0048867 | 0.46409
13432 | SANDOW_5 | 5 | 581 | 0.16206 | south | Y | 0.23619 | 0.058588 | 0.22903 | 0.1386 | 0.058588 | south | N | 0.058588 | 0
13691 | OAKGROVE | 1 | 855 | -0.046906 | north | Y | 0.027222 | -0.15038 | 0.020063 | -0.070367 | 0.020063 | west | Y | 0.027222 | 6.1209
13692 | OAKGROVE | 2 | 855 | -0.046906 | north | Y | 0.027222 | -0.15038 | 0.020063 | -0.070367 | 0.020063 | west | Y | 0.027222 | 6.1209
32798 | BRYN_TAM | 1 | 32 | -0.020344 | north | N | 0.053784 | -0.12382 | 0.046625 | -0.043805 | 0.043805 | houston | Y | 0.053784 | 0
32883 | BRYN_DNS | 1 | 48 | -0.017807 | north | Y | 0.056321 | -0.12128 | 0.049162 | -0.041268 | 0.041268 | houston | Y | 0.056321 | 0.72254
32884 | BRYN_DNS | 1 | 46 | -0.017807 | north | Y | 0.056321 | -0.12128 | 0.049162 | -0.041268 | 0.041268 | houston | Y | 0.056321 | 0.69243
32886 | BRYN_ATK | MB | 12 | -0.020373 | north | Y | 0.053755 | -0.12384 | 0.046596 | -0.043834 | 0.043834 | houston | Y | 0.053755 | 0
32887 | BRYN_ATK | MB | 51 | -0.020373 | north | Y | 0.053755 | -0.12384 | 0.046596 | -0.043834 | 0.043834 | houston | Y | 0.053755 | 0
32888 | BRYN_ATK | 1 | 17 | -0.020373 | north | Y | 0.053755 | -0.12384 | 0.046596 | -0.043834 | 0.043834 | houston | Y | 0.053755 | 0.16866
32890 | BRYN_ATK | MB | 22 | -0.020373 | north | Y | 0.053755 | -0.12384 | 0.046596 | -0.043834 | 0.043834 | houston | Y | 0.053755 | 0
32891 | BRYN_ATK | MB | 25 | -0.020373 | north | Y | 0.053755 | -0.12384 | 0.046596 | -0.043834 | 0.043834 | houston | Y | 0.053755 | 0
32892 | BRYN_DNS | 1 | 105 | -0.017807 | north | Y | 0.056321 | -0.12128 | 0.049162 | -0.041268 | 0.041268 | houston | Y | 0.056321 | 1.5806
36998 | RDCNYNG1 | 1 | 84 | -0.068525 | west | Y | 0.0056027 | -0.172 | -0.0015562 | -0.091986 | 0.0015562 | west | N | 0.0015562 | 0
38332 | WDWRDU2 | 1 | 80 | -0.058846 | west | Y | 0.015282 | -0.16232 | 0.0081228 | -0.082307 | 0.0081228 | west | N | 0.0081228 | 0
38437 | TNSRBNMS | 1 | 150 | -0.058783 | west | Y | 0.015345 | -0.16225 | 0.0081858 | -0.082244 | 0.0081858 | west | N | 0.0081858 | 0
38438 | TNSRBNMS | 1 | 150 | -0.058783 | west | Y | 0.015345 | -0.16225 | 0.0081858 | -0.082244 | 0.0081858 | west | N | 0.0081858 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.024599 | houston | N | 0.098727 | -0.078872 | 0.091568 | 0.0011382 | 0.0011382 | houston | N | 0.0011382 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.024599 | houston | N | 0.098727 | -0.078872 | 0.091568 | 0.0011382 | 0.0011382 | houston | N | 0.0011382 | 0
38600 | TNBP_CGN | 5 | 53 | 0.024599 | houston | N | 0.098727 | -0.078872 | 0.091568 | 0.0011382 | 0.0011382 | houston | N | 0.0011382 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.024599 | houston | N | 0.098727 | -0.078872 | 0.091568 | 0.0011382 | 0.0011382 | houston | N | 0.0011382 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.024599 | houston | N | 0.098727 | -0.078872 | 0.091568 | 0.0011382 | 0.0011382 | houston | N | 0.0011382 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.024599 | houston | N | 0.098727 | -0.078872 | 0.091568 | 0.0011382 | 0.0011382 | houston | N | 0.0011382 | 0
38614 | TNBPAMCG | 4 | 96 | 0.024599 | houston | N | 0.098727 | -0.078872 | 0.091568 | 0.0011382 | 0.0011382 | houston | N | 0.0011382 | 0
38615 | TNBPAMCG | 1 | 244 | 0.024599 | houston | N | 0.098727 | -0.078872 | 0.091568 | 0.0011382 | 0.0011382 | houston | N | 0.0011382 | 0
38690 | TNBP_CGN | 3 | 40 | 0.024599 | houston | N | 0.098727 | -0.078872 | 0.091568 | 0.0011382 | 0.0011382 | houston | N | 0.0011382 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.024617 | houston | N | 0.098745 | -0.078854 | 0.091586 | 0.0011562 | 0.0011562 | houston | N | 0.0011562 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.024617 | houston | N | 0.098745 | -0.078854 | 0.091586 | 0.0011562 | 0.0011562 | houston | N | 0.0011562 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.024617 | houston | N | 0.098745 | -0.078854 | 0.091586 | 0.0011562 | 0.0011562 | houston | N | 0.0011562 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.024617 | houston | N | 0.098745 | -0.078854 | 0.091586 | 0.0011562 | 0.0011562 | houston | N | 0.0011562 | 0
39470 | TNDOWCGN | 1 | 32 | 0.024616 | houston | N | 0.098744 | -0.078855 | 0.091585 | 0.0011552 | 0.0011552 | houston | N | 0.0011552 | 0
39480 | TNDOWCGN | 1 | 30 | 0.024616 | houston | N | 0.098744 | -0.078855 | 0.091585 | 0.0011552 | 0.0011552 | houston | N | 0.0011552 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.035287 | houston | N | 0.10941 | -0.068184 | 0.10226 | 0.011826 | 0.011826 | houston | N | 0.011826 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.035287 | houston | N | 0.10941 | -0.068184 | 0.10226 | 0.011826 | 0.011826 | houston | N | 0.011826 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.035287 | houston | N | 0.10941 | -0.068184 | 0.10226 | 0.011826 | 0.011826 | houston | N | 0.011826 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.035287 | houston | N | 0.10941 | -0.068184 | 0.10226 | 0.011826 | 0.011826 | houston | N | 0.011826 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.046906 | north | Y | 0.027222 | -0.15038 | 0.020063 | -0.070367 | 0.020063 | west | Y | 0.027222 | 1.0903
39970 | TNTNPONE | 1 | 153 | -0.046906 | north | Y | 0.027222 | -0.15038 | 0.020063 | -0.070367 | 0.020063 | west | Y | 0.027222 | 1.0953
48500 | APD_GT1_ | 1 | 136 | 0.018101 | houston | N | 0.092229 | -0.08537 | 0.08507 | -0.0053598 | 0.0053598 | houston | N | 0.0053598 | 0
48510 | AK_GT1__ | 1 | 33 | 0.028159 | houston | N | 0.10229 | -0.075312 | 0.095128 | 0.0046982 | 0.0046982 | houston | N | 0.0046982 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.018063 | houston | Y | 0.092191 | -0.085408 | 0.085032 | -0.0053978 | 0.0053978 | houston | N | 0.0053978 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.018063 | houston | Y | 0.092191 | -0.085408 | 0.085032 | -0.0053978 | 0.0053978 | houston | N | 0.0053978 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.018063 | houston | Y | 0.092191 | -0.085408 | 0.085032 | -0.0053978 | 0.0053978 | houston | N | 0.0053978 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.018063 | houston | Y | 0.092191 | -0.085408 | 0.085032 | -0.0053978 | 0.0053978 | houston | N | 0.0053978 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.036994 | houston | N | 0.11112 | -0.066477 | 0.10396 | 0.013533 | 0.013533 | houston | N | 0.013533 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.036994 | houston | N | 0.11112 | -0.066477 | 0.10396 | 0.013533 | 0.013533 | houston | N | 0.013533 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.028806 | houston | N | 0.10293 | -0.074665 | 0.095775 | 0.0053452 | 0.0053452 | houston | N | 0.0053452 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.028806 | houston | N | 0.10293 | -0.074665 | 0.095775 | 0.0053452 | 0.0053452 | houston | N | 0.0053452 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.028806 | houston | N | 0.10293 | -0.074665 | 0.095775 | 0.0053452 | 0.0053452 | houston | N | 0.0053452 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.020527 | houston | N | 0.094655 | -0.082944 | 0.087496 | -0.0029338 | 0.0029338 | houston | N | 0.0029338 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.020527 | houston | N | 0.094655 | -0.082944 | 0.087496 | -0.0029338 | 0.0029338 | houston | N | 0.0029338 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.020527 | houston | N | 0.094655 | -0.082944 | 0.087496 | -0.0029338 | 0.0029338 | houston | N | 0.0029338 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.020527 | houston | N | 0.094655 | -0.082944 | 0.087496 | -0.0029338 | 0.0029338 | houston | N | 0.0029338 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.018945 | houston | N | 0.093073 | -0.084526 | 0.085914 | -0.0045158 | 0.0045158 | houston | N | 0.0045158 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.018945 | houston | N | 0.093073 | -0.084526 | 0.085914 | -0.0045158 | 0.0045158 | houston | N | 0.0045158 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.021004 | houston | N | 0.095132 | -0.082467 | 0.087973 | -0.0024568 | 0.0024568 | houston | N | 0.0024568 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.021004 | houston | N | 0.095132 | -0.082467 | 0.087973 | -0.0024568 | 0.0024568 | houston | N | 0.0024568 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.021004 | houston | N | 0.095132 | -0.082467 | 0.087973 | -0.0024568 | 0.0024568 | houston | N | 0.0024568 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.021004 | houston | N | 0.095132 | -0.082467 | 0.087973 | -0.0024568 | 0.0024568 | houston | N | 0.0024568 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.021004 | houston | N | 0.095132 | -0.082467 | 0.087973 | -0.0024568 | 0.0024568 | houston | N | 0.0024568 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.016076 | houston | Y | 0.090204 | -0.087395 | 0.083045 | -0.0073848 | 0.0073848 | houston | N | 0.0073848 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.016882 | houston | Y | 0.09101 | -0.086589 | 0.083851 | -0.0065788 | 0.0065788 | houston | N | 0.0065788 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.015833 | houston | Y | 0.089961 | -0.087638 | 0.082802 | -0.0076278 | 0.0076278 | houston | N | 0.0076278 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.015833 | houston | Y | 0.089961 | -0.087638 | 0.082802 | -0.0076278 | 0.0076278 | houston | N | 0.0076278 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.015833 | houston | Y | 0.089961 | -0.087638 | 0.082802 | -0.0076278 | 0.0076278 | houston | N | 0.0076278 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.011361 | houston | N | 0.085489 | -0.09211 | 0.07833 | -0.0121 | 0.0121 | houston | N | 0.0121 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.017941 | houston | N | 0.092069 | -0.08553 | 0.08491 | -0.0055198 | 0.0055198 | houston | N | 0.0055198 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.017941 | houston | N | 0.092069 | -0.08553 | 0.08491 | -0.0055198 | 0.0055198 | houston | N | 0.0055198 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.015264 | houston | N | 0.089392 | -0.088207 | 0.082233 | -0.0081968 | 0.0081968 | houston | N | 0.0081968 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.015264 | houston | N | 0.089392 | -0.088207 | 0.082233 | -0.0081968 | 0.0081968 | houston | N | 0.0081968 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.015264 | houston | N | 0.089392 | -0.088207 | 0.082233 | -0.0081968 | 0.0081968 | houston | N | 0.0081968 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.015264 | houston | N | 0.089392 | -0.088207 | 0.082233 | -0.0081968 | 0.0081968 | houston | N | 0.0081968 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.018892 | houston | N | 0.09302 | -0.084579 | 0.085861 | -0.0045688 | 0.0045688 | houston | N | 0.0045688 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.018892 | houston | N | 0.09302 | -0.084579 | 0.085861 | -0.0045688 | 0.0045688 | houston | N | 0.0045688 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.018892 | houston | N | 0.09302 | -0.084579 | 0.085861 | -0.0045688 | 0.0045688 | houston | N | 0.0045688 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.018892 | houston | N | 0.09302 | -0.084579 | 0.085861 | -0.0045688 | 0.0045688 | houston | N | 0.0045688 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.019397 | houston | N | 0.093525 | -0.084074 | 0.086366 | -0.0040638 | 0.0040638 | houston | N | 0.0040638 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.019397 | houston | N | 0.093525 | -0.084074 | 0.086366 | -0.0040638 | 0.0040638 | houston | N | 0.0040638 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.019397 | houston | N | 0.093525 | -0.084074 | 0.086366 | -0.0040638 | 0.0040638 | houston | N | 0.0040638 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.019397 | houston | N | 0.093525 | -0.084074 | 0.086366 | -0.0040638 | 0.0040638 | houston | N | 0.0040638 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.019397 | houston | N | 0.093525 | -0.084074 | 0.086366 | -0.0040638 | 0.0040638 | houston | N | 0.0040638 | 0
48651 | EP_1_2 | 1 | 5 | 0.016119 | houston | N | 0.090247 | -0.087352 | 0.083088 | -0.0073418 | 0.0073418 | houston | N | 0.0073418 | 0
48651 | EP_1_2 | 2 | 21 | 0.016119 | houston | N | 0.090247 | -0.087352 | 0.083088 | -0.0073418 | 0.0073418 | houston | N | 0.0073418 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.020175 | north | N | 0.053953 | -0.12365 | 0.046794 | -0.043636 | 0.043636 | houston | Y | 0.053953 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.020175 | north | N | 0.053953 | -0.12365 | 0.046794 | -0.043636 | 0.043636 | houston | Y | 0.053953 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.020175 | north | N | 0.053953 | -0.12365 | 0.046794 | -0.043636 | 0.043636 | houston | Y | 0.053953 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.020175 | north | N | 0.053953 | -0.12365 | 0.046794 | -0.043636 | 0.043636 | houston | Y | 0.053953 | 0
48690 | GBY_GN5_ | 5 | 398 | 0.015067 | houston | Y | 0.089195 | -0.088404 | 0.082036 | -0.0083938 | 0.0083938 | houston | N | 0.0083938 | 0
48691 | GBY_7374 | A | 46 | 0.019819 | houston | Y | 0.093947 | -0.083652 | 0.086788 | -0.0036418 | 0.0036418 | houston | N | 0.0036418 | 0
48691 | GBY_7374 | B | 46 | 0.019819 | houston | Y | 0.093947 | -0.083652 | 0.086788 | -0.0036418 | 0.0036418 | houston | N | 0.0036418 | 0
48692 | GBY_8182 | C | 46 | 0.019819 | houston | Y | 0.093947 | -0.083652 | 0.086788 | -0.0036418 | 0.0036418 | houston | N | 0.0036418 | 0
48692 | GBY_8182 | D | 55 | 0.019819 | houston | Y | 0.093947 | -0.083652 | 0.086788 | -0.0036418 | 0.0036418 | houston | N | 0.0036418 | 0
48693 | GBY_8384 | E | 55 | 0.019819 | houston | Y | 0.093947 | -0.083652 | 0.086788 | -0.0036418 | 0.0036418 | houston | N | 0.0036418 | 0
48693 | GBY_8384 | F | 54 | 0.019819 | houston | Y | 0.093947 | -0.083652 | 0.086788 | -0.0036418 | 0.0036418 | houston | N | 0.0036418 | 0
48721 | LEG_1___ | 1 | 827 | -0.055778 | north | Y | 0.01835 | -0.15925 | 0.011191 | -0.079239 | 0.011191 | west | Y | 0.01835 | 5.9204
48722 | LEG_2___ | 2 | 819 | -0.055778 | north | Y | 0.01835 | -0.15925 | 0.011191 | -0.079239 | 0.011191 | west | Y | 0.01835 | 5.8631
48730 | MNS_GT | 1 | 46.1 | 0.029085 | houston | N | 0.10321 | -0.074386 | 0.096054 | 0.0056242 | 0.0056242 | houston | N | 0.0056242 | 0
48731 | CBE_GT1 | 1 | 76 | 0.050974 | houston | Y | 0.1251 | -0.052497 | 0.11794 | 0.027513 | 0.027513 | houston | N | 0.027513 | 0
48732 | CBE_GT2 | 1 | 76 | 0.050974 | houston | Y | 0.1251 | -0.052497 | 0.11794 | 0.027513 | 0.027513 | houston | N | 0.027513 | 0
48733 | CBE_ST12 | 1 | 105 | 0.050974 | houston | Y | 0.1251 | -0.052497 | 0.11794 | 0.027513 | 0.027513 | houston | N | 0.027513 | 0
48734 | CBE_GT3 | 1 | 74 | 0.050974 | houston | Y | 0.1251 | -0.052497 | 0.11794 | 0.027513 | 0.027513 | houston | N | 0.027513 | 0
48735 | CBE_GT4 | 1 | 74 | 0.050974 | houston | Y | 0.1251 | -0.052497 | 0.11794 | 0.027513 | 0.027513 | houston | N | 0.027513 | 0
48736 | CBE_ST34 | 1 | 102 | 0.050974 | houston | Y | 0.1251 | -0.052497 | 0.11794 | 0.027513 | 0.027513 | houston | N | 0.027513 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.018877 | houston | N | 0.093005 | -0.084594 | 0.085846 | -0.0045838 | 0.0045838 | houston | N | 0.0045838 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.018877 | houston | N | 0.093005 | -0.084594 | 0.085846 | -0.0045838 | 0.0045838 | houston | N | 0.0045838 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.018877 | houston | N | 0.093005 | -0.084594 | 0.085846 | -0.0045838 | 0.0045838 | houston | N | 0.0045838 | 0
48761 | PR_GT1__ | 1 | 35 | 0.019199 | houston | N | 0.093327 | -0.084272 | 0.086168 | -0.0042618 | 0.0042618 | houston | N | 0.0042618 | 0
48772 | PHR_GN2_ | MB | 459 | 0.02222 | houston | Y | 0.096348 | -0.081251 | 0.089189 | -0.0012408 | 0.0012408 | houston | N | 0.0012408 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.016114 | houston | N | 0.090242 | -0.087357 | 0.083083 | -0.0073468 | 0.0073468 | houston | N | 0.0073468 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.016114 | houston | N | 0.090242 | -0.087357 | 0.083083 | -0.0073468 | 0.0073468 | houston | N | 0.0073468 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.016114 | houston | N | 0.090242 | -0.087357 | 0.083083 | -0.0073468 | 0.0073468 | houston | N | 0.0073468 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.016114 | houston | N | 0.090242 | -0.087357 | 0.083083 | -0.0073468 | 0.0073468 | houston | N | 0.0073468 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.016114 | houston | N | 0.090242 | -0.087357 | 0.083083 | -0.0073468 | 0.0073468 | houston | N | 0.0073468 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.016114 | houston | N | 0.090242 | -0.087357 | 0.083083 | -0.0073468 | 0.0073468 | houston | N | 0.0073468 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.016114 | houston | N | 0.090242 | -0.087357 | 0.083083 | -0.0073468 | 0.0073468 | houston | N | 0.0073468 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.011361 | houston | N | 0.085489 | -0.09211 | 0.07833 | -0.0121 | 0.0121 | houston | N | 0.0121 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.011361 | houston | N | 0.085489 | -0.09211 | 0.07833 | -0.0121 | 0.0121 | houston | N | 0.0121 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.011361 | houston | N | 0.085489 | -0.09211 | 0.07833 | -0.0121 | 0.0121 | houston | N | 0.0121 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.011361 | houston | N | 0.085489 | -0.09211 | 0.07833 | -0.0121 | 0.0121 | houston | N | 0.0121 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.01593 | houston | N | 0.090058 | -0.087541 | 0.082899 | -0.0075308 | 0.0075308 | houston | N | 0.0075308 | 0
48820 | SHELLG1_ | 1 | 71 | 0.018577 | houston | N | 0.092705 | -0.084894 | 0.085546 | -0.0048838 | 0.0048838 | houston | N | 0.0048838 | 0
48821 | SHELLG2 | 2 | 72 | 0.018577 | houston | N | 0.092705 | -0.084894 | 0.085546 | -0.0048838 | 0.0048838 | houston | N | 0.0048838 | 0
48822 | SHELLG3_ | 1 | 39 | 0.018577 | houston | N | 0.092705 | -0.084894 | 0.085546 | -0.0048838 | 0.0048838 | houston | N | 0.0048838 | 0
48822 | SHELLG3_ | 2 | 30 | 0.018577 | houston | N | 0.092705 | -0.084894 | 0.085546 | -0.0048838 | 0.0048838 | houston | N | 0.0048838 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.019641 | houston | N | 0.093769 | -0.08383 | 0.08661 | -0.0038198 | 0.0038198 | houston | N | 0.0038198 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.019641 | houston | N | 0.093769 | -0.08383 | 0.08661 | -0.0038198 | 0.0038198 | houston | N | 0.0038198 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.018896 | houston | N | 0.093024 | -0.084575 | 0.085865 | -0.0045648 | 0.0045648 | houston | N | 0.0045648 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.018957 | houston | Y | 0.093085 | -0.084514 | 0.085926 | -0.0045038 | 0.0045038 | houston | N | 0.0045038 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.018974 | houston | Y | 0.093102 | -0.084497 | 0.085943 | -0.0044868 | 0.0044868 | houston | N | 0.0044868 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.018901 | houston | Y | 0.093029 | -0.08457 | 0.08587 | -0.0045598 | 0.0045598 | houston | N | 0.0045598 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.018884 | houston | Y | 0.093012 | -0.084587 | 0.085853 | -0.0045768 | 0.0045768 | houston | N | 0.0045768 | 0
48855 | SRB_GT21 | B2 | 12 | 0.018986 | houston | Y | 0.093114 | -0.084485 | 0.085955 | -0.0044748 | 0.0044748 | houston | N | 0.0044748 | 0
48855 | SRB_GT21 | MB | 18 | 0.018986 | houston | Y | 0.093114 | -0.084485 | 0.085955 | -0.0044748 | 0.0044748 | houston | N | 0.0044748 | 0
48865 | TECO_GT1 | 1 | 50 | 0.023264 | houston | Y | 0.097392 | -0.080207 | 0.090233 | -0.0001968 | 0.0001968 | houston | N | 0.0001968 | 0
48873 | THW_ST3_ | 3 | 104 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48874 | THW_ST4_ | 4 | 104 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48875 | THW_3132 | A | 54 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48875 | THW_3132 | B | 53 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48877 | THW_3334 | C | 54 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48877 | THW_3334 | D | 57 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48879 | THW_4142 | E | 54 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48879 | THW_4142 | F | 54 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48881 | THW_4344 | G | 58 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48881 | THW_4344 | H | 58 | 0.017177 | houston | Y | 0.091305 | -0.086294 | 0.084146 | -0.0062838 | 0.0062838 | houston | N | 0.0062838 | 0
48883 | THW_GT1_ | B2 | 12 | 0.016437 | houston | Y | 0.090565 | -0.087034 | 0.083406 | -0.0070238 | 0.0070238 | houston | N | 0.0070238 | 0
48885 | THW_5152 | A | 56 | 0.014719 | houston | Y | 0.088847 | -0.088752 | 0.081688 | -0.0087418 | 0.0087418 | houston | N | 0.0087418 | 0
48885 | THW_5152 | B | 59 | 0.014719 | houston | Y | 0.088847 | -0.088752 | 0.081688 | -0.0087418 | 0.0087418 | houston | N | 0.0087418 | 0
48886 | THW_5354 | C | 56 | 0.014719 | houston | Y | 0.088847 | -0.088752 | 0.081688 | -0.0087418 | 0.0087418 | houston | N | 0.0087418 | 0
48886 | THW_5354 | D | 56 | 0.014719 | houston | Y | 0.088847 | -0.088752 | 0.081688 | -0.0087418 | 0.0087418 | houston | N | 0.0087418 | 0
48887 | THW_5556 | E | 59 | 0.014719 | houston | Y | 0.088847 | -0.088752 | 0.081688 | -0.0087418 | 0.0087418 | houston | N | 0.0087418 | 0
48887 | THW_5556 | F | 56 | 0.014719 | houston | Y | 0.088847 | -0.088752 | 0.081688 | -0.0087418 | 0.0087418 | houston | N | 0.0087418 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.048127 | houston | Y | 0.12225 | -0.055344 | 0.1151 | 0.024666 | 0.024666 | houston | N | 0.024666 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.027884 | houston | Y | 0.10201 | -0.075587 | 0.094853 | 0.0044232 | 0.0044232 | houston | N | 0.0044232 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.027884 | houston | Y | 0.10201 | -0.075587 | 0.094853 | 0.0044232 | 0.0044232 | houston | N | 0.0044232 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.027884 | houston | Y | 0.10201 | -0.075587 | 0.094853 | 0.0044232 | 0.0044232 | houston | N | 0.0044232 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.027884 | houston | Y | 0.10201 | -0.075587 | 0.094853 | 0.0044232 | 0.0044232 | houston | N | 0.0044232 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.027884 | houston | N | 0.10201 | -0.075587 | 0.094853 | 0.0044232 | 0.0044232 | houston | N | 0.0044232 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.028858 | houston | Y | 0.10299 | -0.074613 | 0.095827 | 0.0053972 | 0.0053972 | houston | N | 0.0053972 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.028858 | houston | Y | 0.10299 | -0.074613 | 0.095827 | 0.0053972 | 0.0053972 | houston | N | 0.0053972 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.028858 | houston | Y | 0.10299 | -0.074613 | 0.095827 | 0.0053972 | 0.0053972 | houston | N | 0.0053972 | 0
48929 | WAPGT21_ | B1 | 13 | 0.027884 | houston | Y | 0.10201 | -0.075587 | 0.094853 | 0.0044232 | 0.0044232 | houston | N | 0.0044232 | 0
48940 | WARVUE_G | G1 | 12 | 0.016099 | houston | Y | 0.090227 | -0.087372 | 0.083068 | -0.0073618 | 0.0073618 | houston | N | 0.0073618 | 0
49803 | EXN_15GT | 1 | 34 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49826 | EXN938GT | 5 | 45.9 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49828 | EXN941GT | 10 | 17.7 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49829 | EXN942GT | 11 | 20.4 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49830 | EXN943GT | 12 | 19.9 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49831 | EXN944GT | 13 | 35 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49832 | EXN945GT | 9 | 18 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49837 | EXN_GT | 4 | 85.4 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49838 | EXN_14GT | 14 | 148 | 0.016687 | houston | N | 0.090815 | -0.086784 | 0.083656 | -0.0067738 | 0.0067738 | houston | N | 0.0067738 | 0
49851 | DOW17000 | 37 | 62 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49858 | DOW38100 | 31 | 71.4 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49859 | DOW38200 | 33 | 45 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49860 | DOW38300 | 32 | 101 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49862 | DOW39100 | 36 | 86 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49863 | DOW39200 | 35 | 88 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49865 | DOW41000 | 41 | 50 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49866 | DOW42000 | 42 | 18 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49869 | DOW49000 | 45 | 94 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49870 | DOW61000 | 61 | 70 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49871 | DOW62000 | 62 | 63 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49872 | DOW63000 | 63 | 72 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49873 | DOW64000 | 64 | 64.8 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49876 | DOW65000 | 65 | 101 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49877 | DOW66000 | 66 | 97 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49878 | DOW67000 | 67 | 103 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49882 | DOW81000 | 81 | 76 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49884 | DOW82000 | 82 | 80 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49885 | DOW83000 | 83 | 80 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
49886 | DOW84000 | 84 | 171 | 0.039155 | houston | N | 0.11328 | -0.064316 | 0.10612 | 0.015694 | 0.015694 | houston | N | 0.015694 | 0
58909 | PEARSALL | 1 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58909 | PEARSALL | 2 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58909 | PEARSALL | 3 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58909 | PEARSALL | 4 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58909 | PEARSALL | 5 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58909 | PEARSALL | 6 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58919 | PEARSALL | 1 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58919 | PEARSALL | 2 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58919 | PEARSALL | 3 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58919 | PEARSALL | 4 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58919 | PEARSALL | 5 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58919 | PEARSALL | 6 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58929 | PEARSALL | 1 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58929 | PEARSALL | 2 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58929 | PEARSALL | 3 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58929 | PEARSALL | 4 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58929 | PEARSALL | 5 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58929 | PEARSALL | 6 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58949 | PEARSALL | 1 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58949 | PEARSALL | 2 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58949 | PEARSALL | 3 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58949 | PEARSALL | 4 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58949 | PEARSALL | 5 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
58949 | PEARSALL | 6 | 8.4 | 0.085885 | south | Y | 0.16001 | -0.017586 | 0.15285 | 0.062424 | 0.017586 | south | N | 0.017586 | 0
60000 | DSKY2 | 1 | 76.5 | -0.055879 | west | Y | 0.018249 | -0.15935 | 0.01109 | -0.07934 | 0.01109 | west | N | 0.01109 | 0
60003 | KING_NE1 | 1 | 80 | -0.058968 | west | Y | 0.01516 | -0.16244 | 0.0080008 | -0.082429 | 0.0080008 | west | N | 0.0080008 | 0
60005 | KING_SE1 | 1 | 40 | -0.058968 | west | Y | 0.01516 | -0.16244 | 0.0080008 | -0.082429 | 0.0080008 | west | N | 0.0080008 | 0
60007 | KING_SW1 | 1 | 80 | -0.059463 | west | Y | 0.014665 | -0.16293 | 0.0075058 | -0.082924 | 0.0075058 | west | N | 0.0075058 | 0
60016 | WOODWRD1 | 1 | 80 | -0.05886 | west | Y | 0.015268 | -0.16233 | 0.0081088 | -0.082321 | 0.0081088 | west | N | 0.0081088 | 0
60017 | ORNNWP1 | 1 | 80 | -0.056308 | west | Y | 0.01782 | -0.15978 | 0.010661 | -0.079769 | 0.010661 | west | N | 0.010661 | 0
60018 | DSKY1 | 1 | 84 | -0.055473 | west | Y | 0.018655 | -0.15894 | 0.011496 | -0.078934 | 0.011496 | west | N | 0.011496 | 0
60019 | KING_NW1 | 1 | 80 | -0.059463 | west | Y | 0.014665 | -0.16293 | 0.0075058 | -0.082924 | 0.0075058 | west | N | 0.0075058 | 0
60057 | CALLAHAN | 1 | 114 | 0.10256 | south | Y | 0.17669 | -0.00091223 | 0.16953 | 0.079098 | 0.00091223 | south | N | 0.00091223 | 0
60058 | BUFF_GAP | 1 | 120 | -0.067599 | west | Y | 0.0065287 | -0.17107 | -0.00063016 | -0.09106 | 0.00063016 | west | N | 0.00063016 | 0
60060 | CIRELLO | 1 | 233 | -0.067599 | west | Y | 0.0065287 | -0.17107 | -0.00063016 | -0.09106 | 0.00063016 | west | N | 0.00063016 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.067599 | west | Y | 0.0065287 | -0.17107 | -0.00063016 | -0.09106 | 0.00063016 | west | N | 0.00063016 | 0
60066 | H_HOLLOW | 1 | 222 | 0.10256 | south | Y | 0.17669 | -0.00091223 | 0.16953 | 0.079098 | 0.00091223 | south | N | 0.00091223 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.10256 | south | Y | 0.17669 | -0.00091223 | 0.16953 | 0.079098 | 0.00091223 | south | N | 0.00091223 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.10256 | south | Y | 0.17669 | -0.00091223 | 0.16953 | 0.079098 | 0.00091223 | south | N | 0.00091223 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.10256 | south | Y | 0.17669 | -0.00091223 | 0.16953 | 0.079098 | 0.00091223 | south | N | 0.00091223 | 0
60074 | HORSH5 | 1 | 100 | 0.10256 | south | Y | 0.17669 | -0.00091223 | 0.16953 | 0.079098 | 0.00091223 | south | N | 0.00091223 | 0
60081 | WHRLWIND | 1 | 60 | -0.070297 | west | Y | 0.0038307 | -0.17377 | -0.0033282 | -0.093758 | 0.0033282 | west | N | 0.0033282 | 0
60201 | RIO DRCS | F | 0 | 0.052992 | south | N | 0.12712 | -0.050479 | 0.11996 | 0.029531 | 0.029531 | houston | Y | 0.050479 | 0
60202 | FRIEND_R | F | 0 | -0.042162 | west | N | 0.031966 | -0.14563 | 0.024807 | -0.065623 | 0.024807 | west | N | 0.024807 | 0
60203 | PRES0A | BT | 4.8 | -0.061307 | west | N | 0.012821 | -0.16478 | 0.0056618 | -0.084768 | 0.0056618 | west | N | 0.0056618 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.069075 | west | Y | 0.0050527 | -0.17255 | -0.0021062 | -0.092536 | 0.0021062 | west | N | 0.0021062 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.069075 | west | Y | 0.0050527 | -0.17255 | -0.0021062 | -0.092536 | 0.0021062 | west | N | 0.0021062 | 0
71057 | L_SWEETW | W1 | 135 | -0.069075 | west | Y | 0.0050527 | -0.17255 | -0.0021062 | -0.092536 | 0.0021062 | west | N | 0.0021062 | 0
71059 | L_SWEETW | W1 | 119 | -0.069075 | west | Y | 0.0050527 | -0.17255 | -0.0021062 | -0.092536 | 0.0021062 | west | N | 0.0021062 | 0
71060 | L_SWEETW | W1 | 105 | -0.069075 | west | Y | 0.0050527 | -0.17255 | -0.0021062 | -0.092536 | 0.0021062 | west | N | 0.0021062 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.069075 | west | Y | 0.0050527 | -0.17255 | -0.0021062 | -0.092536 | 0.0021062 | west | N | 0.0021062 | 0
76031 | L_GASCCR | W1 | 150 | -0.066829 | west | Y | 0.0072987 | -0.1703 | 0.00013984 | -0.09029 | 0.00013984 | west | N | 0.00013984 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.066536 | west | Y | 0.0075917 | -0.17001 | 0.00043284 | -0.089997 | 0.00043284 | west | N | 0.00043284 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.066536 | west | Y | 0.0075917 | -0.17001 | 0.00043284 | -0.089997 | 0.00043284 | west | N | 0.00043284 | 0
76096 | L_CAPRSI | W1 | 186 | -0.066536 | west | Y | 0.0075917 | -0.17001 | 0.00043284 | -0.089997 | 0.00043284 | west | N | 0.00043284 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.066536 | west | Y | 0.0075917 | -0.17001 | 0.00043284 | -0.089997 | 0.00043284 | west | N | 0.00043284 | 0
80003 | MILHWYS | F | 0 | 0.081993 | south | N | 0.15612 | -0.021478 | 0.14896 | 0.058532 | 0.021478 | south | N | 0.021478 | 0
80010 | EPLVT1 | F | 0 | 0.062361 | south | N | 0.13649 | -0.04111 | 0.12933 | 0.0389 | 0.0389 | houston | Y | 0.04111 | 0
80012 | LAR | F | 0 | 0.086311 | south | N | 0.16044 | -0.01716 | 0.15328 | 0.06285 | 0.01716 | south | N | 0.01716 | 0
80051 | FORPVCM0 | 8 | 28 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
80053 | FOR69CG0 | 10 | 74 | 0.074773 | south | N | 0.1489 | -0.028698 | 0.14174 | 0.051312 | 0.028698 | south | N | 0.028698 | 0
80080 | GWINDT11 | 1 | 94 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80080 | GWINDT11 | 2 | 41 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80080 | GWINDT11 | 3 | 38 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80080 | GWINDT11 | 4 | 19 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80081 | GWINDT21 | 1 | 94 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80081 | GWINDT21 | 2 | 36 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80081 | GWINDT21 | 3 | 43 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80081 | GWINDT21 | 4 | 22 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80137 | CSDR89 | 8 | 39 | 0.077528 | south | N | 0.15166 | -0.025943 | 0.1445 | 0.054067 | 0.025943 | south | N | 0.025943 | 0
80137 | CSDR89 | 9 | 15 | 0.077528 | south | N | 0.15166 | -0.025943 | 0.1445 | 0.054067 | 0.025943 | south | N | 0.025943 | 0
80138 | CSDR7 | 7 | 7 | 0.077528 | south | N | 0.15166 | -0.025943 | 0.1445 | 0.054067 | 0.025943 | south | N | 0.025943 | 0
80139 | CSDR56 | 5 | 15 | 0.077528 | south | N | 0.15166 | -0.025943 | 0.1445 | 0.054067 | 0.025943 | south | N | 0.025943 | 0
80139 | CSDR56 | 6 | 39 | 0.077528 | south | N | 0.15166 | -0.025943 | 0.1445 | 0.054067 | 0.025943 | south | N | 0.025943 | 0
80140 | CSDR11 | 11 | 39 | 0.077528 | south | N | 0.15166 | -0.025943 | 0.1445 | 0.054067 | 0.025943 | south | N | 0.025943 | 0
80180 | PNSCALT1 | 1 | 148 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80180 | PNSCALT1 | 2 | 50 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80181 | PNSCALT2 | 1 | 55 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80181 | PNSCALT2 | 2 | 50 | 0.081939 | south | Y | 0.15607 | -0.021532 | 0.14891 | 0.058478 | 0.021532 | south | N | 0.021532 | 0
80223 | REYSHR G | 1 | 12 | 0.080309 | south | N | 0.15444 | -0.023162 | 0.14728 | 0.056848 | 0.023162 | south | N | 0.023162 | 0
80224 | VISTRONG | 1 | 15 | 0.078415 | south | N | 0.15254 | -0.025056 | 0.14538 | 0.054954 | 0.025056 | south | N | 0.025056 | 0
80225 | VISTRONG | 2 | 23 | 0.078415 | south | N | 0.15254 | -0.025056 | 0.14538 | 0.054954 | 0.025056 | south | N | 0.025056 | 0
80226 | ALCOA G | 1 | 48 | 0.075423 | south | N | 0.14955 | -0.028048 | 0.14239 | 0.051962 | 0.028048 | south | N | 0.028048 | 0
80227 | AIRCO G | 1 | 8 | 0.077839 | south | N | 0.15197 | -0.025632 | 0.14481 | 0.054378 | 0.025632 | south | N | 0.025632 | 0
80261 | NBEC81A | 1 | 180 | 0.081161 | south | Y | 0.15529 | -0.02231 | 0.14813 | 0.0577 | 0.02231 | south | N | 0.02231 | 0
80262 | NBEC91A | 1 | 180 | 0.081135 | south | Y | 0.15526 | -0.022336 | 0.1481 | 0.057674 | 0.022336 | south | N | 0.022336 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.081319 | south | Y | 0.15545 | -0.022152 | 0.14829 | 0.057858 | 0.022152 | south | N | 0.022152 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.081319 | south | Y | 0.15545 | -0.022152 | 0.14829 | 0.057858 | 0.022152 | south | N | 0.022152 | 0
80265 | LARECU40 | 4 | 100 | 0.086318 | south | Y | 0.16045 | -0.017153 | 0.15329 | 0.062857 | 0.017153 | south | N | 0.017153 | 0
80266 | LARECU50 | 5 | 100 | 0.086318 | south | Y | 0.16045 | -0.017153 | 0.15329 | 0.062857 | 0.017153 | south | N | 0.017153 | 0
80291 | PAPALOTE | 1 | 25 | 0.080634 | south | Y | 0.15476 | -0.022837 | 0.1476 | 0.057173 | 0.022837 | south | N | 0.022837 | 0
80291 | PAPALOTE | 2 | 25 | 0.080634 | south | Y | 0.15476 | -0.022837 | 0.1476 | 0.057173 | 0.022837 | south | N | 0.022837 | 0
80291 | PAPALOTE | 3 | 25 | 0.080634 | south | Y | 0.15476 | -0.022837 | 0.1476 | 0.057173 | 0.022837 | south | N | 0.022837 | 0
80291 | PAPALOTE | 4 | 16 | 0.080634 | south | Y | 0.15476 | -0.022837 | 0.1476 | 0.057173 | 0.022837 | south | N | 0.022837 | 0
80294 | PAPALOTE | 5 | 25 | 0.080634 | south | Y | 0.15476 | -0.022837 | 0.1476 | 0.057173 | 0.022837 | south | N | 0.022837 | 0
80294 | PAPALOTE | 6 | 25 | 0.080634 | south | Y | 0.15476 | -0.022837 | 0.1476 | 0.057173 | 0.022837 | south | N | 0.022837 | 0
80294 | PAPALOTE | 7 | 25 | 0.080634 | south | Y | 0.15476 | -0.022837 | 0.1476 | 0.057173 | 0.022837 | south | N | 0.022837 | 0
80294 | PAPALOTE | 8 | 15 | 0.080634 | south | Y | 0.15476 | -0.022837 | 0.1476 | 0.057173 | 0.022837 | south | N | 0.022837 | 0
86104 | CID-138 | EQ | 0 | 0.086318 | south | N | 0.16045 | -0.017153 | 0.15329 | 0.062857 | 0.017153 | south | N | 0.017153 | 0
86105 | CID-230 | EQ | 500 | 0.086318 | south | N | 0.16045 | -0.017153 | 0.15329 | 0.062857 | 0.017153 | south | N | 0.017153 | 0
86106 | CUF-230 | EQ | 500 | 0.086318 | south | N | 0.16045 | -0.017153 | 0.15329 | 0.062857 | 0.017153 | south | N | 0.017153 | 0
86107 | CUF-138 | EQ | 0 | 0.086318 | south | N | 0.16045 | -0.017153 | 0.15329 | 0.062857 | 0.017153 | south | N | 0.017153 | 0
88198 | BEEVILLE | F | 0 | 0.085737 | south | N | 0.15986 | -0.017734 | 0.15271 | 0.062276 | 0.017734 | south | N | 0.017734 | 0
88253 | HAMILTON | F | 0 | 0.047114 | south | N | 0.12124 | -0.056357 | 0.11408 | 0.023653 | 0.023653 | houston | Y | 0.056357 | 0
88299 | ZAPATA | F | 0 | 0.084193 | south | N | 0.15832 | -0.019278 | 0.15116 | 0.060732 | 0.019278 | south | N | 0.019278 | 0
88508 | FALFURRI | F | 0 | 0.083306 | south | N | 0.15743 | -0.020165 | 0.15027 | 0.059845 | 0.020165 | south | N | 0.020165 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3415 TEMP_SS - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.16206 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 92.2116 | 569 | 0.23619 | 134.3902 | 569 | 134.3902
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.16206 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 94.1563 | 581 | 0.23619 | 137.2245
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.566 | 42 | 0.20665 | 8.6793
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.831 | 44 | 0.20665 | 9.0926 |  |  | Weighted Shift Factors
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.831 | 44 | 0.20665 | 9.0926 |  |  | North | -0.074128
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.2286 | 47 | 0.20665 | 9.7126 |  |  | South | 0.10121
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.1312 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 40.6732 | 310 | 0.20533 | 63.6528 |  |  |  | -0.17534
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.1312 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 54.1873 | 413 | 0.20533 | 84.802
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.13092 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0474 | 0 | 0.20505 | 0 |  |  | Line Rating | 532.85
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.13092 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0474 | 0 | 0.20505 | 0 |  |  | Conc Gen | 569
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.3386 | 49 | 0.20349 | 9.9709 |  |  | Weighted Imp. | 134.3902
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.9506 | 46 | 0.20349 | 9.3604 |  |  | PTDF | 0.23619
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.9506 | 46 | 0.20349 | 9.3604
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.0799 | 47 | 0.20349 | 9.5639 |  |  | Concentration | -1.347
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.12936 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.9214 | 154 | 0.20349 | 31.3371
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.12936 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.1453 | 148 | 0.20349 | 30.1162
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.2093 | 48 | 0.20349 | 9.7674
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.2093 | 48 | 0.20349 | 9.7674
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.12607 | south | 5 | N | N | Nsouth | Nsouth | -1 | 4.4123 | 0 | 0.20019 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.12607 | south | 5 | N | N | Nsouth | Nsouth | -1 | 4.2863 | 0 | 0.20019 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.12607 | south | 5 | N | N | Nsouth | Nsouth | -1 | 4.4123 | 0 | 0.20019 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.12491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.0495 | 152.5 | 0.19904 | 30.354
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.12491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.6748 | 149.5 | 0.19904 | 29.7569
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.12491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 29.0552 | 232.6 | 0.19904 | 46.2973
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.12475 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 16.4671 | 132 | 0.19888 | 26.252
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.12475 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 16.7166 | 134 | 0.19888 | 26.6497
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.12475 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 40.2946 | 323 | 0.19888 | 64.2378
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.12372 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.5473 | 158 | 0.19784 | 31.2595
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.12372 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.7947 | 160 | 0.19784 | 31.6552
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.12372 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.6505 | 175 | 0.19784 | 34.6228
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.11284 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.0311 | 0 | 0.18697 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.11284 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.0311 | 0 | 0.18697 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.6418 | 50 | 0.18696 | 9.3482
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.6418 | 50 | 0.18696 | 9.3482
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.6418 | 50 | 0.18696 | 9.3482
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.6418 | 50 | 0.18696 | 9.3482
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.11137 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.6682 | 0 | 0.18549 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.11061 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 64.5957 | 584 | 0.18474 | 107.8862
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.11061 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 65.8124 | 595 | 0.18474 | 109.9184
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.1105 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 47.8474 | 433 | 0.18463 | 79.9447
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.2269 | 223.9 | 0.18233 | 40.8241
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.3459 | 225 | 0.18233 | 41.0246
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.3026 | 224.6 | 0.18233 | 40.9517
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.5298 | 226.7 | 0.18233 | 41.3346
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.10778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.0178 | 0 | 0.18191 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.10778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.1256 | 0 | 0.18191 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.10701 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 45.1561 | 422 | 0.18113 | 76.438
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.10502 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25205 | 0 | 0.17915 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.10502 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25205 | 0 | 0.17915 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.10502 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.29405 | 0 | 0.17915 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.821 | 142 | 0.1785 | 25.3471
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.1341 | 145 | 0.1785 | 25.8826
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.7603 | 151 | 0.1785 | 26.9536
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 30.2682 | 290 | 0.1785 | 51.7652
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.10378 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.24907 | 0 | 0.17791 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.10378 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.24907 | 0 | 0.17791 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.10359 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4191 | 0 | 0.17771 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.10339 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41356 | 0 | 0.17752 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.10263 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8474 | 0 | 0.17676 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.10263 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8474 | 0 | 0.17676 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.10263 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.5395 | 0 | 0.17676 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.6917 | 114 | 0.17669 | 20.1423
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 22.7681 | 222 | 0.17669 | 39.2245
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 18.8709 | 184 | 0.17669 | 32.5104
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 22.9732 | 224 | 0.17669 | 39.5778
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.7943 | 115 | 0.17669 | 20.319
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.8055 | 147 | 0.17485 | 25.7023
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.8991 | 138 | 0.17485 | 24.1287
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.1005 | 140 | 0.17485 | 24.4784
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.8055 | 147 | 0.17485 | 25.7023
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.3307 | 182 | 0.17485 | 31.8219
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.9422 | 198 | 0.17485 | 34.6195
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.09854 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.17267 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.09854 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.17267 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.09854 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.17267 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.098252 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 41.6588 | 424 | 0.17238 | 73.089
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.098252 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 41.7571 | 425 | 0.17238 | 73.2614
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.09819 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 40.4543 | 412 | 0.17232 | 70.9949
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.09819 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 39.276 | 400 | 0.17232 | 68.9271
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.098085 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 20.4998 | 209 | 0.17221 | 35.9925
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.098085 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 21.1864 | 216 | 0.17221 | 37.1979
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5119 | 46 | 0.17221 | 7.9218
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.61 | 47 | 0.17221 | 8.094
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5119 | 46 | 0.17221 | 7.9218
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5119 | 46 | 0.17221 | 7.9218
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.098024 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 39.8958 | 407 | 0.17215 | 70.0658
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.097835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.1644 | 155 | 0.17196 | 26.6542
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.097835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 16.6319 | 170 | 0.17196 | 29.2337
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.097835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.1644 | 155 | 0.17196 | 26.6542
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.097502 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.17 | 0 | 0.17163 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.097481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.6539 | 58 | 0.17161 | 9.9533
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.097481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.6758 | 89 | 0.17161 | 15.2732
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2892 | 44 | 0.17161 | 7.5508
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2892 | 44 | 0.17161 | 7.5508
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.1917 | 43 | 0.17161 | 7.3792
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3866 | 45 | 0.17161 | 7.7224
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.097356 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 53.1564 | 546 | 0.17148 | 93.6301
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.097356 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 73.017 | 750 | 0.17148 | 128.6128
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.092154 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 36.493 | 396 | 0.16628 | 65.8476
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.086878 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.0851 | 24 | 0.16101 | 3.8641
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.086878 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 2.0851 | 24 | 0.16101 | 3.8641
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.086878 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.9982 | 23 | 0.16101 | 3.7031
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.086318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.6318 | 100 | 0.16045 | 16.0446
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.086318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.6318 | 100 | 0.16045 | 16.0446
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.086318 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16045 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.086318 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16045 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.086318 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16045 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.086318 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16045 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.086311 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16044 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.085737 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15986 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.084633 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 53.2342 | 629 | 0.15876 | 99.8605
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.084193 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15832 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.083306 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15743 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.083269 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.99923 | 0 | 0.1574 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.083269 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.91596 | 0 | 0.1574 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.083269 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.99923 | 0 | 0.1574 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.082303 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 12.0574 | 146.5 | 0.15643 | 22.9171
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.082303 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 12.1726 | 147.9 | 0.15643 | 23.1361
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.082303 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.2384 | 173 | 0.15643 | 27.0625
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.082148 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 17.0046 | 207 | 0.15628 | 32.3491
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.082148 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 17.8015 | 216.7 | 0.15628 | 33.865
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.082148 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.8798 | 242 | 0.15628 | 37.8187
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.082145 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.8289 | 144 | 0.15627 | 22.5033
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.082145 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.8289 | 144 | 0.15627 | 22.5033
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.082145 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.0468 | 171 | 0.15627 | 26.7226
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.081993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15612 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.081993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.1157 | 38 | 0.15612 | 5.9326
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.081993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5825 | 19.3 | 0.15612 | 3.0131
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.081993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2299 | 15 | 0.15612 | 2.3418
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.081993 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 3.8537 | 47 | 0.15612 | 7.3377
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.7023 | 94 | 0.15607 | 14.6703
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3595 | 41 | 0.15607 | 6.3987
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1137 | 38 | 0.15607 | 5.9305
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.5568 | 19 | 0.15607 | 2.9653
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.7023 | 94 | 0.15607 | 14.6703
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.9498 | 36 | 0.15607 | 5.6184
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.5234 | 43 | 0.15607 | 6.7109
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.8027 | 22 | 0.15607 | 3.4335
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 12.127 | 148 | 0.15607 | 23.0979
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.0969 | 50 | 0.15607 | 7.8033
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.5066 | 55 | 0.15607 | 8.5837
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.0969 | 50 | 0.15607 | 7.8033
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.081814 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.3726 | 0 | 0.15594 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.081434 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0945 | 0 | 0.15556 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.081428 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0943 | 0 | 0.15556 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.081349 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0337 | 0 | 0.15548 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.081349 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0337 | 0 | 0.15548 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.081319 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 27.1605 | 334 | 0.15545 | 51.9192
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.081319 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 27.6485 | 340 | 0.15545 | 52.8519
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.081319 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6374 | 180 | 0.15545 | 27.9804
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.081319 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6374 | 180 | 0.15545 | 27.9804
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.081161 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.609 | 180 | 0.15529 | 27.952
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.081145 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.0338 | 0 | 0.15527 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.081145 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.0581 | 0 | 0.15527 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.081145 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.4152 | 0 | 0.15527 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.081135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 27.2614 | 336 | 0.15526 | 52.1683
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.081135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6043 | 180 | 0.15526 | 27.9473
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.080874 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.6459 | 144 | 0.155 | 22.3202
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.080874 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.2043 | 188 | 0.155 | 29.1403
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 25 | 0.15476 | 3.869
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 25 | 0.15476 | 3.869
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 25 | 0.15476 | 3.869
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2901 | 16 | 0.15476 | 2.4762
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 25 | 0.15476 | 3.869
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 25 | 0.15476 | 3.869
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 25 | 0.15476 | 3.869
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2095 | 15 | 0.15476 | 2.3214
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.6888 | 0 | 0.15444 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.2873 | 0 | 0.15444 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 8.0309 | 0 | 0.15444 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.6448 | 0 | 0.15444 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.8054 | 0 | 0.15444 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 10.1992 | 0 | 0.15444 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.080309 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.96371 | 0 | 0.15444 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.079981 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.8386 | 0 | 0.15411 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8063 | 47.7 | 0.15392 | 7.3422
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.9764 | 37.3 | 0.15392 | 5.7414
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6707 | 46 | 0.15392 | 7.0805
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8303 | 48 | 0.15392 | 7.3884
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.079072 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7396 | 22 | 0.1532 | 3.3704
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.079072 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.86979 | 11 | 0.1532 | 1.6852
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.079072 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.86979 | 11 | 0.1532 | 1.6852
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.078415 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1762 | 0 | 0.15254 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.078415 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8035 | 0 | 0.15254 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.077839 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.62271 | 0 | 0.15197 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.1708 | 0 | 0.15166 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5427 | 0 | 0.15166 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0236 | 0 | 0.15166 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1629 | 0 | 0.15166 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5427 | 0 | 0.15166 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1629 | 0 | 0.15166 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0236 | 0 | 0.15166 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0236 | 0 | 0.15166 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.075423 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.6203 | 0 | 0.14955 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.9071 | 0 | 0.1489 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 6.0566 | 0 | 0.1489 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.9071 | 0 | 0.1489 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.9818 | 0 | 0.1489 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.8622 | 0 | 0.1489 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8693 | 0 | 0.1489 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.4396 | 0 | 0.1489 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0936 | 0 | 0.1489 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.2601 | 0 | 0.1489 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.5332 | 0 | 0.1489 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.062361 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.13649 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.059484 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3569 | 0 | 0.13361 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.05126 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 68.3296 | 0 | 0.12539 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.05126 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 68.0733 | 0 | 0.12539 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.874 | 76 | 0.1251 | 9.5077
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.874 | 76 | 0.1251 | 9.5077
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 5.3523 | 105 | 0.1251 | 13.1357
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.7721 | 74 | 0.1251 | 9.2575
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.7721 | 74 | 0.1251 | 9.2575
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 5.1993 | 102 | 0.1251 | 12.7604
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.048127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.1764 | 66 | 0.12225 | 8.0688
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.047114 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.5548 | 0 | 0.12124 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.047114 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.1779 | 0 | 0.12124 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.047114 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.12124 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4276 | 0 | 0.11328 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.7957 | 0 | 0.11328 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.762 | 0 | 0.11328 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.9547 | 0 | 0.11328 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.3673 | 0 | 0.11328 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.4456 | 0 | 0.11328 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9578 | 0 | 0.11328 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.70479 | 0 | 0.11328 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.6806 | 0 | 0.11328 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.7409 | 0 | 0.11328 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4668 | 0 | 0.11328 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.8192 | 0 | 0.11328 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.5372 | 0 | 0.11328 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.9547 | 0 | 0.11328 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.798 | 0 | 0.11328 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.033 | 0 | 0.11328 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.9758 | 0 | 0.11328 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1324 | 0 | 0.11328 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1324 | 0 | 0.11328 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.6955 | 0 | 0.11328 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.036994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6266 | 0 | 0.11112 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.036994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36994 | 0 | 0.11112 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.9169 | 0 | 0.10941 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.9169 | 0 | 0.10941 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.1992 | 0 | 0.10941 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.8639 | 0 | 0.10941 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.029085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3408 | 0 | 0.10321 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.028858 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 18.7866 | 651 | 0.10299 | 67.0437
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.028858 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 16.2759 | 564 | 0.10299 | 58.084
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.028858 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 17.3148 | 600 | 0.10299 | 61.7914
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.028806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.6954 | 0 | 0.10293 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.028806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.6954 | 0 | 0.10293 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.028806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 7.0575 | 0 | 0.10293 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.028159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.92925 | 0 | 0.10229 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.027884 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.4893 | 161 | 0.10201 | 16.4239
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.027884 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.6287 | 166 | 0.10201 | 16.9339
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.027884 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 6.9152 | 248 | 0.10201 | 25.2989
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.027884 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 15.2247 | 546 | 0.10201 | 55.6984
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.027884 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 17.9294 | 0 | 0.10201 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.027884 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.36249 | 13 | 0.10201 | 1.3262
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4691 | 0 | 0.098745 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2869 | 0 | 0.098745 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.5282 | 0 | 0.098745 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.5109 | 0 | 0.098745 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.024616 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.78771 | 0 | 0.098744 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.024616 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73848 | 0 | 0.098744 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7416 | 0 | 0.098727 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6408 | 0 | 0.098727 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3037 | 0 | 0.098727 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7686 | 0 | 0.098727 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7759 | 0 | 0.098727 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7464 | 0 | 0.098727 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.3615 | 0 | 0.098727 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.0022 | 0 | 0.098727 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98396 | 0 | 0.098727 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.023264 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1632 | 50 | 0.097392 | 4.8696
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.02222 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.096348 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9114 | 0 | 0.095132 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.84 | 0 | 0.095132 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8273 | 0 | 0.095132 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1447 | 0 | 0.095132 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25625 | 0 | 0.095132 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3343 | 0 | 0.094655 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2316 | 0 | 0.094655 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3343 | 0 | 0.094655 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3343 | 0 | 0.094655 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.91167 | 46 | 0.093947 | 4.3215
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.91167 | 46 | 0.093947 | 4.3215
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.91167 | 46 | 0.093947 | 4.3215
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.09 | 55 | 0.093947 | 5.1671
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.09 | 55 | 0.093947 | 5.1671
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.0702 | 54 | 0.093947 | 5.0731
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.019641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.532 | 0 | 0.093769 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.019641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5713 | 0 | 0.093769 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.1656 | 0 | 0.093525 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.0473 | 0 | 0.093525 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.055 | 0 | 0.093525 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.0453 | 0 | 0.093525 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.2178 | 0 | 0.093525 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.019199 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67197 | 0 | 0.093327 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.018986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.22783 | 12 | 0.093114 | 1.1174
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.018986 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.093114 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.018974 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.2066 | 169 | 0.093102 | 15.7342
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.018957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.1279 | 165 | 0.093085 | 15.359
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.018945 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.8228 | 0 | 0.093073 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.018945 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2333 | 0 | 0.093073 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.018901 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.0259 | 213 | 0.093029 | 19.8151
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.018896 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30612 | 0 | 0.093024 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2091 | 0 | 0.09302 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.194 | 0 | 0.09302 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5605 | 0 | 0.09302 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3905 | 0 | 0.09302 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.018884 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.3056 | 228 | 0.093012 | 21.2067
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.018877 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.3979 | 0 | 0.093005 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.018877 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.9939 | 0 | 0.093005 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.018877 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.9637 | 0 | 0.093005 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.319 | 0 | 0.092705 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3375 | 0 | 0.092705 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7245 | 0 | 0.092705 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55731 | 0 | 0.092705 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.018101 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4617 | 0 | 0.092229 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.75865 | 42 | 0.092191 | 3.872
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.75865 | 42 | 0.092191 | 3.872
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.68639 | 38 | 0.092191 | 3.5032
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.68639 | 38 | 0.092191 | 3.5032
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.017941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1038 | 0 | 0.092069 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.017941 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.422 | 0 | 0.092069 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.7864 | 104 | 0.091305 | 9.4957
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.7864 | 104 | 0.091305 | 9.4957
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.92756 | 54 | 0.091305 | 4.9305
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.91038 | 53 | 0.091305 | 4.8392
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.92756 | 54 | 0.091305 | 4.9305
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.97909 | 57 | 0.091305 | 5.2044
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.92756 | 54 | 0.091305 | 4.9305
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.92756 | 54 | 0.091305 | 4.9305
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.99627 | 58 | 0.091305 | 5.2957
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.99627 | 58 | 0.091305 | 5.2957
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.016882 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 12.4083 | 735 | 0.09101 | 66.8922
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56736 | 0 | 0.090815 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57904 | 0 | 0.090815 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.54566 | 0 | 0.090815 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76593 | 0 | 0.090815 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29536 | 0 | 0.090815 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34041 | 0 | 0.090815 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33207 | 0 | 0.090815 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58405 | 0 | 0.090815 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30037 | 0 | 0.090815 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4251 | 0 | 0.090815 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4697 | 0 | 0.090815 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.016437 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19724 | 12 | 0.090565 | 1.0868
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.016119 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.080595 | 0 | 0.090247 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.016119 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3385 | 0 | 0.090247 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0474 | 0 | 0.090242 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0635 | 0 | 0.090242 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.128 | 0 | 0.090242 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0152 | 0 | 0.090242 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.99907 | 0 | 0.090242 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6759 | 0 | 0.090242 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95073 | 0 | 0.090242 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.016099 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.19319 | 12 | 0.090227 | 1.0827
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.016076 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 11.9445 | 743 | 0.090204 | 67.0214
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.01593 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.501 | 0 | 0.090058 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.015833 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.7233 | 172 | 0.089961 | 15.4732
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.015833 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.7233 | 172 | 0.089961 | 15.4732
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.015833 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.7233 | 172 | 0.089961 | 15.4732
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.485 | 0 | 0.089392 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4636 | 0 | 0.089392 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4254 | 0 | 0.089392 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.1091 | 0 | 0.089392 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.015067 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 5.9967 | 398 | 0.089195 | 35.4995
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.82426 | 56 | 0.088847 | 4.9754
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.86842 | 59 | 0.088847 | 5.242
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.82426 | 56 | 0.088847 | 4.9754
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.82426 | 56 | 0.088847 | 4.9754
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.86842 | 59 | 0.088847 | 5.242
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.82426 | 56 | 0.088847 | 4.9754
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.9655 | 0 | 0.085489 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7723 | 0 | 0.085489 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7496 | 0 | 0.085489 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7496 | 0 | 0.085489 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.011361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8405 | 0 | 0.085489 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.074128 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.074128 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 10.2559 | 100 | 0.0013467 | 0.13467
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.052992 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.04822 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.10121 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.10121 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.017807 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.85474 | 48 | -0.11902 | -5.7129
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.017807 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.81912 | 46 | -0.11902 | -5.4749
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.017807 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.8697 | 105 | -0.11902 | -12.497
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.111 | 0 | -0.12139 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.1473 | 0 | -0.12139 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.1473 | 0 | -0.12139 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.6665 | 0 | -0.12139 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.020344 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.65101 | 0 | -0.12156 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.12159 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.12159 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.020373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.34634 | 17 | -0.12159 | -2.067
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.12159 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.12159 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.02606 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.0658 | 463 | -0.12727 | -58.9271
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.029953 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.493 | 150 | -0.13117 | -19.6748
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.042162 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.14337 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -40.1046 | 855 | -0.14812 | -126.6411
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -40.1046 | 855 | -0.14812 | -126.6411
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -7.1438 | 152.3 | -0.14812 | -22.5584
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -7.1766 | 153 | -0.14812 | -22.6621
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.055473 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.6597 | 84 | -0.15669 | -13.1616
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055778 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -46.1284 | 827 | -0.15699 | -129.831
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055778 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -45.6822 | 819 | -0.15699 | -128.5751
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.055879 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2747 | 76.5 | -0.15709 | -12.0175
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.056308 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5046 | 80 | -0.15752 | -12.6016
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.058783 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8174 | 150 | -0.16 | -23.9993
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.058783 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8174 | 150 | -0.16 | -23.9993
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.058846 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7077 | 80 | -0.16006 | -12.8047
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.05886 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7088 | 80 | -0.16007 | -12.8058
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.058968 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4226 | 75 | -0.16018 | -12.0135
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.058968 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7174 | 80 | -0.16018 | -12.8144
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.058968 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3587 | 40 | -0.16018 | -6.4072
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.059463 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.757 | 80 | -0.16068 | -12.854
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.059463 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.757 | 80 | -0.16068 | -12.854
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.061307 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.29427 | 0 | -0.16252 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.065509 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1038 | 169.5 | -0.16672 | -28.2593
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.3402 | 66 | -0.16697 | -11.0202
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.2744 | 65 | -0.16697 | -10.8532
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.4059 | 67 | -0.16697 | -11.1871
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.4059 | 67 | -0.16697 | -11.1871
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.4059 | 67 | -0.16697 | -11.1871
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.06576 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.16697 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.06576 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.16697 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.065821 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3037 | 35 | -0.16703 | -5.8462
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.065821 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9746 | 30 | -0.16703 | -5.011
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.066029 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.8383 | 149 | -0.16724 | -24.919
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.066217 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.43703 | 6.6 | -0.16743 | -1.105
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.066217 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2712 | 34.3 | -0.16743 | -5.7428
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4853 | 112.5 | -0.16775 | -18.8717
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.9471 | 149.5 | -0.16775 | -25.0784
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.3757 | 186 | -0.16775 | -31.2012
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.272 | 214.5 | -0.16775 | -35.982
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.066829 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.0244 | 150 | -0.16804 | -25.2062
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -13.9436 | 208.2 | -0.16818 | -35.016
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.5167 | 142.1 | -0.16818 | -23.899
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -8.8671 | 132.4 | -0.16818 | -22.2676
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.1082 | 136 | -0.16818 | -22.8731
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.8449 | 147 | -0.16818 | -24.7231
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -14.0641 | 210 | -0.16818 | -35.3187
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6889 | 70 | -0.1682 | -11.7737
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6889 | 70 | -0.1682 | -11.7737
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -6.2161 | 92.8 | -0.1682 | -15.6086
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.3587 | 80 | -0.1682 | -13.4557
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.3587 | 80 | -0.1682 | -13.4557
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.7032 | 115 | -0.1682 | -19.3426
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.067019 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8871 | 58 | -0.16823 | -9.7574
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.067031 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.7366 | 100.5 | -0.16824 | -16.9085
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.067185 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.391 | 214.2 | -0.1684 | -36.0707
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.067203 | west | 8 | N | N | Nwest | Nwest | 1 | -1.7338 | 0 | -0.16842 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.067599 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1119 | 120 | -0.16881 | -20.2574
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.067599 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.7506 | 233 | -0.16881 | -39.333
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.067599 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.5053 | 170.2 | -0.16881 | -28.7317
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.067626 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1151 | 120 | -0.16884 | -20.2606
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.067655 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1186 | 120 | -0.16887 | -20.2641
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.067797 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.2543 | 225 | -0.16901 | -38.0271
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.067852 | west | 8 | N | N | Nwest | Nwest | 1 | -4.7496 | 0 | -0.16906 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.067852 | west | 8 | N | N | Nwest | Nwest | 1 | -4.9803 | 0 | -0.16906 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.067852 | west | 8 | N | N | Nwest | Nwest | 1 | -4.7768 | 0 | -0.16906 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.067861 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.215 | 180 | -0.16907 | -30.4332
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.067861 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.215 | 180 | -0.16907 | -30.4332
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.2073 | 150 | -0.16926 | -25.3892
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.9708 | 220 | -0.16926 | -37.2375
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.6098 | 200 | -0.16926 | -33.8523
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2952 | 121.9 | -0.16926 | -20.633
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.068167 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -41.9227 | 615 | -0.16938 | -104.1683
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.068167 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -40.014 | 587 | -0.16938 | -99.4256
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.5015 | 66 | -0.16942 | -11.1815
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.7061 | 69 | -0.16942 | -11.6897
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.7061 | 69 | -0.16942 | -11.6897
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.5697 | 67 | -0.16942 | -11.3509
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.5697 | 67 | -0.16942 | -11.3509
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.4333 | 65 | -0.16942 | -11.0121
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.068268 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.3009 | 63 | -0.16948 | -10.6773
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.068326 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.634 | 141 | -0.16954 | -23.9049
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.068326 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1991 | 120 | -0.16954 | -20.3446
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.068346 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.7663 | 99 | -0.16956 | -16.7863
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.068346 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1691 | 61 | -0.16956 | -10.3431
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.068346 | west | 7 | N | N | Nwest | Nwest | 1 | -1.7087 | 0 | -0.16956 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.068346 | west | 7 | N | N | Nwest | Nwest | 1 | -3.1234 | 0 | -0.16956 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.068346 | west | 7 | N | N | Nwest | Nwest | 1 | -3.1234 | 0 | -0.16956 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.068525 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.7561 | 84 | -0.16974 | -14.2579
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.068616 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.2924 | 150 | -0.16983 | -25.4742
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.068616 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9302 | 101 | -0.16983 | -17.1527
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.068719 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.5899 | 125 | -0.16993 | -21.2414
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.068719 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.5899 | 125 | -0.16993 | -21.2414
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5903 | 37.5 | -0.17029 | -6.3858
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4256 | 107.5 | -0.17029 | -18.3059
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.3251 | 135 | -0.17029 | -22.9888
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2199 | 119 | -0.17029 | -20.2642
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2529 | 105 | -0.17029 | -17.8802
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5605 | 80.5 | -0.17029 | -13.7081
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.069081 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -10.4105 | 150.7 | -0.17029 | -25.6632
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.069081 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -10.4312 | 151 | -0.17029 | -25.7143
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.069081 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.255 | 177.4 | -0.17029 | -30.21
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.4651 | 209 | -0.17042 | -35.6185
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.7552 | 126.5 | -0.17042 | -21.5585
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.2335 | 249 | -0.17042 | -42.4354
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.6346 | 197 | -0.17042 | -33.5734
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.069241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -10.49 | 151.5 | -0.17045 | -25.8237
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.069241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -10.5454 | 152.3 | -0.17045 | -25.96
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.069241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.2903 | 177.5 | -0.17045 | -30.2555
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.069312 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.3968 | 150 | -0.17052 | -25.5786
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.070297 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2178 | 60 | -0.17151 | -10.2906
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.071609 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.6436 | 400 | -0.17282 | -69.1285
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.071613 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.9007 | 236 | -0.17283 | -40.7868
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.072442 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.9529 | 165 | -0.17365 | -28.653
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.072564 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -13.2066 | 182 | -0.17378 | -31.6273
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.072564 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -35.121 | 484 | -0.17378 | -84.1077
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.072848 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -3.6424 | 50 | -0.17406 | -8.703
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.07288 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.17409 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.073078 | west | 4 | Y | N | Ywest | Nwest | 1 | -47.4788 | 649.7 | -0.17429 | -113.2364
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | 1 | -10.8497 | 0 | -0.17452 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | 1 | -9.5302 | 0 | -0.17452 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | 1 | -10.6298 | 0 | -0.17452 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | 1 | -29.2503 | 0 | -0.17452 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.073665 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -57.827 | 785 | -0.17488 | -137.2787
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.073665 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -58.5637 | 795 | -0.17488 | -139.0275
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.073665 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -57.4587 | 780 | -0.17488 | -136.4043
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.074826 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -18.1079 | 242 | -0.17604 | -42.6013
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.074975 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -4.4985 | 60 | -0.17619 | -10.5712
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.075068 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -27.4749 | 366 | -0.17628 | -64.5186
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.503 | 20 | -0.17636 | -3.5272
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.503 | 20 | -0.17636 | -3.5272
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.503 | 20 | -0.17636 | -3.5272
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.2775 | 17 | -0.17636 | -2.9981
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.2943 | 161 | -0.17757 | -28.5895
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.5234 | 164 | -0.17757 | -29.1222
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.5234 | 164 | -0.17757 | -29.1222
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -31.6139 | 414 | -0.17757 | -73.5158
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.3706 | 162 | -0.17757 | -28.767
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.2943 | 161 | -0.17757 | -28.5895
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.447 | 163 | -0.17757 | -28.9446
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -31.2321 | 409 | -0.17757 | -72.6279
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.076464 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -9.1757 | 120 | -0.17768 | -21.3212
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.076534 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91841 | 0 | -0.17775 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.076534 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91841 | 0 | -0.17775 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.076654 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -17.1705 | 224 | -0.17787 | -39.8421
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.07694 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5388 | 20 | -0.17815 | -3.563
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.07694 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.9235 | 25 | -0.17815 | -4.4538
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.07694 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.1545 | 41 | -0.17815 | -7.3042
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.077016 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -42.9749 | 558 | -0.17823 | -99.4514
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.077016 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -44.5923 | 579 | -0.17823 | -103.1942
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.077016 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -62.2289 | 808 | -0.17823 | -144.0085
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.077019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.7119 | 204 | -0.17823 | -36.3592
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.077019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.4808 | 201 | -0.17823 | -35.8245
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.077019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.6386 | 242 | -0.17823 | -43.132
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.077025 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -29.8857 | 388 | -0.17824 | -69.1561
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.077025 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -39.6679 | 515 | -0.17824 | -91.7922
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.077038 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -6.086 | 79 | -0.17825 | -14.0818
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.077038 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -8.166 | 106 | -0.17825 | -18.8945
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.077038 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -11.2475 | 146 | -0.17825 | -26.0245
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.077038 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.8549 | 76 | -0.17825 | -13.547
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.077047 | north | 8 | N | N | Nnorth | Nnorth | 1 | -5.7785 | 0 | -0.17826 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.077047 | north | 8 | N | N | Nnorth | Nnorth | 1 | -6.1329 | 0 | -0.17826 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.077047 | north | 8 | N | N | Nnorth | Nnorth | 1 | -6.811 | 0 | -0.17826 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.077054 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.0822 | 40 | -0.17827 | -7.1307
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.3362 | 160 | -0.17831 | -28.5301
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.0278 | 156 | -0.17831 | -27.8169
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.1118 | 196 | -0.17831 | -34.9494
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.0278 | 156 | -0.17831 | -27.8169
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.1049 | 157 | -0.17831 | -27.9952
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.266 | 198 | -0.17831 | -35.306
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.077156 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -28.5477 | 370 | -0.17837 | -65.9963
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -10.8018 | 0 | -0.17837 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -10.879 | 0 | -0.17837 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -23.8412 | 0 | -0.17837 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -11.0333 | 0 | -0.17837 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -11.1105 | 0 | -0.17837 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -23.9184 | 0 | -0.17837 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.077228 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -13.1288 | 170 | -0.17844 | -30.3349
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.077228 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -40.1586 | 520 | -0.17844 | -92.789
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.077295 | north | 5 | N | N | Nnorth | Nnorth | 1 | -3.0918 | 0 | -0.17851 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.077295 | north | 5 | N | N | Nnorth | Nnorth | 1 | -3.0918 | 0 | -0.17851 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.077316 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.17853 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.077316 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.17853 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.077666 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.17888 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.077671 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -8.738 | 112.5 | -0.17888 | -20.1244
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.077697 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.17891 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.07783 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -5.6816 | 73 | -0.17904 | -13.0701
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.07783 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.2618 | 119 | -0.17904 | -21.306
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.07783 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -15.9551 | 205 | -0.17904 | -36.7037
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.07783 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -7.9387 | 102 | -0.17904 | -18.2623
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.07783 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -7.4717 | 96 | -0.17904 | -17.1881
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.077968 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.6781 | 60 | -0.17918 | -10.7508
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.077968 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.912 | 63 | -0.17918 | -11.2884
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.078033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4735 | 288 | -0.17925 | -51.6226
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.078033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.4709 | 147 | -0.17925 | -26.3491
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.078033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.4709 | 147 | -0.17925 | -26.3491
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.078248 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.4085 | 18 | -0.17946 | -3.2303
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.078248 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.4085 | 18 | -0.17946 | -3.2303
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.078248 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.9734 | 38 | -0.17946 | -6.8195
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.078454 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.2576 | 118 | -0.17967 | -21.2006
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.078454 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -9.0222 | 115 | -0.17967 | -20.6616
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.078454 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -43.6204 | 556 | -0.17967 | -99.8945
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.078947 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.18016 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.078947 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.18016 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.078947 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.18016 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.079151 | north | 3 | N | N | Nnorth | Nnorth | 1 | -91.5777 | 0 | -0.18036 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.079151 | north | 3 | N | N | Nnorth | Nnorth | 1 | -91.6569 | 0 | -0.18036 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.079414 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.5651 | 196 | -0.18063 | -35.4028
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.079414 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.815 | 111 | -0.18063 | -20.0495
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.079447 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -17.2638 | 217.3 | -0.18066 | -39.2573
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.079447 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -16.2866 | 205 | -0.18066 | -37.0352
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.079447 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.6414 | 272.4 | -0.18066 | -49.2116
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.079733 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.18095 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.6162 | 70 | -0.18144 | -12.701
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.5359 | 69 | -0.18144 | -12.5196
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.5359 | 69 | -0.18144 | -12.5196
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.4557 | 68 | -0.18144 | -12.3381
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.080371 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -34.9614 | 435 | -0.18158 | -78.9887
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.080517 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -31.8042 | 395 | -0.18173 | -71.7831
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.080517 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -35.0249 | 435 | -0.18173 | -79.0522
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.082839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -13.917 | 168 | -0.18405 | -30.9206
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.082839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.4555 | 90 | -0.18405 | -16.5646
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.084027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.1834 | 216.4 | -0.18524 | -40.0858
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.084027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.1582 | 216.1 | -0.18524 | -40.0302
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.8348 | 224 | -0.1853 | -41.5064
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -19.003 | 226 | -0.1853 | -41.877
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -17.8258 | 212 | -0.1853 | -39.2828
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -17.7417 | 211 | -0.1853 | -39.0975
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.098341 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.4751 | 0 | -0.19955 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.098341 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.4751 | 0 | -0.19955 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.10289 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.4338 | 150 | -0.2041 | -30.6156
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.10289 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.2314 | 80 | -0.2041 | -16.3283
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.11412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.1011 | 255 | -0.21533 | -54.9102
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.11412 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -17.0042 | 149 | -0.21533 | -32.0848
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.11412 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -17.4607 | 153 | -0.21533 | -32.9461
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.12749 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.2287 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.12749 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -100.3346 | 787 | -0.2287 | -179.9887
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.13417 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.23538 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.13417 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.23538 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3415 TEMP_SS - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.13417 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.23538 | 0 | 0 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.13417 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.23538 | 0 | 0 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.12749 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.2287 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.12749 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -100.3346 | 787 | -0.2287 | -179.9887 | 787 | 179.9887 | Weighted Shift Factors
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.11412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.1011 | 255 | -0.21533 | -54.9102 | 1042 | 234.899 | North | -0.074128
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.11412 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -17.0042 | 149 | -0.21533 | -32.0848 |  |  | South | 0.10121
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.11412 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -17.4607 | 153 | -0.21533 | -32.9461 |  |  |  | -0.17534
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.10289 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.4338 | 150 | -0.2041 | -30.6156
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.10289 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.2314 | 80 | -0.2041 | -16.3283 |  |  | Line Rating | 532.85
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.098341 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.4751 | 0 | -0.19955 | 0 |  |  | Conc Gen | 1042
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.098341 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.4751 | 0 | -0.19955 | 0 |  |  | Weighted Imp. | 234.899
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.8348 | 224 | -0.1853 | -41.5064 |  |  | PTDF | 0.22543
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -19.003 | 226 | -0.1853 | -41.877
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -17.8258 | 212 | -0.1853 | -39.2828 |  |  | Concentration | -1.2857
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.084084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -17.7417 | 211 | -0.1853 | -39.0975
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.084027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.1834 | 216.4 | -0.18524 | -40.0858
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.084027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.1582 | 216.1 | -0.18524 | -40.0302
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.082839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -13.917 | 168 | -0.18405 | -30.9206
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.082839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.4555 | 90 | -0.18405 | -16.5646
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.080517 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -31.8042 | 395 | -0.18173 | -71.7831
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.080517 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -35.0249 | 435 | -0.18173 | -79.0522
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.080371 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -34.9614 | 435 | -0.18158 | -78.9887
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.6162 | 70 | -0.18144 | -12.701
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.5359 | 69 | -0.18144 | -12.5196
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.5359 | 69 | -0.18144 | -12.5196
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.080231 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.4557 | 68 | -0.18144 | -12.3381
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.079733 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.18095 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.079447 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -17.2638 | 217.3 | -0.18066 | -39.2573
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.079447 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -16.2866 | 205 | -0.18066 | -37.0352
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.079447 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.6414 | 272.4 | -0.18066 | -49.2116
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.079414 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.5651 | 196 | -0.18063 | -35.4028
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.079414 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.815 | 111 | -0.18063 | -20.0495
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.079151 | north | 3 | N | N | Nnorth | Nnorth | 1 | -91.5777 | 0 | -0.18036 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.079151 | north | 3 | N | N | Nnorth | Nnorth | 1 | -91.6569 | 0 | -0.18036 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.078947 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.18016 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.078947 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.18016 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.078947 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.18016 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.078454 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.2576 | 118 | -0.17967 | -21.2006
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.078454 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -9.0222 | 115 | -0.17967 | -20.6616
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.078454 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -43.6204 | 556 | -0.17967 | -99.8945
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.078248 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.4085 | 18 | -0.17946 | -3.2303
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.078248 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.4085 | 18 | -0.17946 | -3.2303
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.078248 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.9734 | 38 | -0.17946 | -6.8195
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.078033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4735 | 288 | -0.17925 | -51.6226
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.078033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.4709 | 147 | -0.17925 | -26.3491
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.078033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.4709 | 147 | -0.17925 | -26.3491
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.077968 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.6781 | 60 | -0.17918 | -10.7508
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.077968 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.912 | 63 | -0.17918 | -11.2884
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.07783 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -5.6816 | 73 | -0.17904 | -13.0701
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.07783 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.2618 | 119 | -0.17904 | -21.306
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.07783 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -15.9551 | 205 | -0.17904 | -36.7037
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.07783 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -7.9387 | 102 | -0.17904 | -18.2623
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.07783 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -7.4717 | 96 | -0.17904 | -17.1881
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.077697 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.17891 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.077671 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -8.738 | 0 | -0.17888 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.077666 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.17888 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.077316 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.17853 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.077316 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.17853 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.077295 | north | 5 | N | N | Nnorth | Nnorth | 1 | -3.0918 | 0 | -0.17851 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.077295 | north | 5 | N | N | Nnorth | Nnorth | 1 | -3.0918 | 0 | -0.17851 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.077228 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -13.1288 | 170 | -0.17844 | -30.3349
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.077228 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -40.1586 | 520 | -0.17844 | -92.789
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.077156 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -28.5477 | 370 | -0.17837 | -65.9963
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -10.8018 | 0 | -0.17837 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -10.879 | 0 | -0.17837 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -23.8412 | 0 | -0.17837 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -11.0333 | 0 | -0.17837 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -11.1105 | 0 | -0.17837 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.077156 | north | 1 | N | N | Nnorth | Nnorth | 1 | -23.9184 | 0 | -0.17837 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.3362 | 160 | -0.17831 | -28.5301
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.0278 | 156 | -0.17831 | -27.8169
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.1118 | 196 | -0.17831 | -34.9494
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.0278 | 156 | -0.17831 | -27.8169
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.1049 | 157 | -0.17831 | -27.9952
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.077101 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.266 | 198 | -0.17831 | -35.306
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.077054 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.0822 | 40 | -0.17827 | -7.1307
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.077047 | north | 8 | N | N | Nnorth | Nnorth | 1 | -5.7785 | 0 | -0.17826 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.077047 | north | 8 | N | N | Nnorth | Nnorth | 1 | -6.1329 | 0 | -0.17826 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.077047 | north | 8 | N | N | Nnorth | Nnorth | 1 | -6.811 | 0 | -0.17826 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.077038 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -6.086 | 79 | -0.17825 | -14.0818
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.077038 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -8.166 | 106 | -0.17825 | -18.8945
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.077038 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -11.2475 | 146 | -0.17825 | -26.0245
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.077038 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.8549 | 76 | -0.17825 | -13.547
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.077025 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -29.8857 | 388 | -0.17824 | -69.1561
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.077025 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -39.6679 | 515 | -0.17824 | -91.7922
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.077019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.7119 | 204 | -0.17823 | -36.3592
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.077019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.4808 | 201 | -0.17823 | -35.8245
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.077019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.6386 | 242 | -0.17823 | -43.132
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.077016 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -42.9749 | 0 | -0.17823 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.077016 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -44.5923 | 0 | -0.17823 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.077016 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -62.2289 | 0 | -0.17823 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.07694 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5388 | 20 | -0.17815 | -3.563
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.07694 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.9235 | 25 | -0.17815 | -4.4538
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.07694 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.1545 | 41 | -0.17815 | -7.3042
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.076654 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -17.1705 | 224 | -0.17787 | -39.8421
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.076534 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91841 | 0 | -0.17775 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.076534 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91841 | 0 | -0.17775 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.076464 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -9.1757 | 0 | -0.17768 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.2943 | 161 | -0.17757 | -28.5895
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.5234 | 164 | -0.17757 | -29.1222
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.5234 | 164 | -0.17757 | -29.1222
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -31.6139 | 414 | -0.17757 | -73.5158
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.3706 | 162 | -0.17757 | -28.767
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.2943 | 161 | -0.17757 | -28.5895
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.447 | 163 | -0.17757 | -28.9446
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.076362 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -31.2321 | 409 | -0.17757 | -72.6279
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.503 | 20 | -0.17636 | -3.5272
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.503 | 20 | -0.17636 | -3.5272
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.503 | 20 | -0.17636 | -3.5272
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.075149 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.2775 | 17 | -0.17636 | -2.9981
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.075068 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -27.4749 | 366 | -0.17628 | -64.5186
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.074975 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -4.4985 | 0 | -0.17619 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.074826 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -18.1079 | 242 | -0.17604 | -42.6013
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.073665 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -57.827 | 0 | -0.17488 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.073665 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -58.5637 | 0 | -0.17488 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.073665 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -57.4587 | 0 | -0.17488 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | 1 | -10.8497 | 0 | -0.17452 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | 1 | -9.5302 | 0 | -0.17452 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | 1 | -10.6298 | 0 | -0.17452 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.073309 | north | 1 | N | N | Nnorth | Nnorth | 1 | -29.2503 | 0 | -0.17452 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.073078 | west | 4 | Y | N | Ywest | Nwest | 1 | -47.4788 | 0 | -0.17429 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.07288 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.17409 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.072848 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -3.6424 | 0 | -0.17406 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.072564 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -13.2066 | 182 | -0.17378 | -31.6273
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.072564 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -35.121 | 484 | -0.17378 | -84.1077
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.072442 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.9529 | 0 | -0.17365 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.071613 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.9007 | 0 | -0.17283 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.071609 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.6436 | 0 | -0.17282 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.070297 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2178 | 0 | -0.17151 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.069312 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.3968 | 0 | -0.17052 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.069241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -10.49 | 151.5 | -0.17045 | -25.8237
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.069241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -10.5454 | 152.3 | -0.17045 | -25.96
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.069241 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.2903 | 177.5 | -0.17045 | -30.2555
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.4651 | 0 | -0.17042 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.7552 | 0 | -0.17042 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.2335 | 0 | -0.17042 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.069211 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.6346 | 0 | -0.17042 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.069081 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -10.4105 | 150.7 | -0.17029 | -25.6632
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.069081 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -10.4312 | 151 | -0.17029 | -25.7143
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.069081 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.255 | 177.4 | -0.17029 | -30.21
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5903 | 0 | -0.17029 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4256 | 0 | -0.17029 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.3251 | 0 | -0.17029 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2199 | 0 | -0.17029 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2529 | 0 | -0.17029 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.069075 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5605 | 0 | -0.17029 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.068719 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.5899 | 0 | -0.16993 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.068719 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.5899 | 0 | -0.16993 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.068616 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.2924 | 0 | -0.16983 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.068616 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9302 | 0 | -0.16983 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.068525 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.7561 | 0 | -0.16974 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.068346 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.7663 | 0 | -0.16956 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.068346 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1691 | 0 | -0.16956 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.068346 | west | 7 | N | N | Nwest | Nwest | 1 | -1.7087 | 0 | -0.16956 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.068346 | west | 7 | N | N | Nwest | Nwest | 1 | -3.1234 | 0 | -0.16956 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.068346 | west | 7 | N | N | Nwest | Nwest | 1 | -3.1234 | 0 | -0.16956 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.068326 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.634 | 0 | -0.16954 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.068326 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1991 | 0 | -0.16954 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.068268 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.3009 | 0 | -0.16948 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.5015 | 66 | -0.16942 | -11.1815
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.7061 | 69 | -0.16942 | -11.6897
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.7061 | 69 | -0.16942 | -11.6897
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.5697 | 67 | -0.16942 | -11.3509
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.5697 | 67 | -0.16942 | -11.3509
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.068204 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.4333 | 65 | -0.16942 | -11.0121
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.068167 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -41.9227 | 0 | -0.16938 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.068167 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -40.014 | 0 | -0.16938 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.2073 | 0 | -0.16926 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.9708 | 0 | -0.16926 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.6098 | 0 | -0.16926 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.068049 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2952 | 0 | -0.16926 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.067861 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.215 | 0 | -0.16907 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.067861 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.215 | 0 | -0.16907 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.067852 | west | 8 | N | N | Nwest | Nwest | 1 | -4.7496 | 0 | -0.16906 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.067852 | west | 8 | N | N | Nwest | Nwest | 1 | -4.9803 | 0 | -0.16906 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.067852 | west | 8 | N | N | Nwest | Nwest | 1 | -4.7768 | 0 | -0.16906 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.067797 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.2543 | 0 | -0.16901 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.067655 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1186 | 0 | -0.16887 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.067626 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1151 | 0 | -0.16884 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.067599 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1119 | 0 | -0.16881 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.067599 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.7506 | 0 | -0.16881 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.067599 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.5053 | 0 | -0.16881 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.067203 | west | 8 | N | N | Nwest | Nwest | 1 | -1.7338 | 0 | -0.16842 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.067185 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.391 | 0 | -0.1684 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.067031 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.7366 | 0 | -0.16824 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.067019 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8871 | 0 | -0.16823 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6889 | 70 | -0.1682 | -11.7737
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6889 | 70 | -0.1682 | -11.7737
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -6.2161 | 92.8 | -0.1682 | -15.6086
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.3587 | 80 | -0.1682 | -13.4557
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.3587 | 80 | -0.1682 | -13.4557
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.066984 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.7032 | 115 | -0.1682 | -19.3426
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -13.9436 | 208.2 | -0.16818 | -35.016
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.5167 | 142.1 | -0.16818 | -23.899
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -8.8671 | 132.4 | -0.16818 | -22.2676
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.1082 | 136 | -0.16818 | -22.8731
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.8449 | 147 | -0.16818 | -24.7231
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.066972 | west | 9 | Y | Y | Ywest | Ywest | 1 | -14.0641 | 210 | -0.16818 | -35.3187
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.066829 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.0244 | 0 | -0.16804 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4853 | 0 | -0.16775 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.9471 | 0 | -0.16775 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.3757 | 0 | -0.16775 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.066536 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.272 | 0 | -0.16775 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.066217 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.43703 | 0 | -0.16743 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.066217 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2712 | 0 | -0.16743 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.066029 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.8383 | 0 | -0.16724 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.065821 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3037 | 0 | -0.16703 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.065821 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9746 | 0 | -0.16703 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.3402 | 66 | -0.16697 | -11.0202
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.2744 | 65 | -0.16697 | -10.8532
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.4059 | 67 | -0.16697 | -11.1871
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.4059 | 67 | -0.16697 | -11.1871
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.06576 | west | 13 | Y | Y | Ywest | Ywest | 1 | -4.4059 | 67 | -0.16697 | -11.1871
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.06576 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.16697 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.06576 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.16697 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.065509 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1038 | 0 | -0.16672 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.061307 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.29427 | 0 | -0.16252 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.059463 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.757 | 0 | -0.16068 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.059463 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.757 | 0 | -0.16068 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.058968 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4226 | 0 | -0.16018 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.058968 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7174 | 0 | -0.16018 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.058968 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3587 | 0 | -0.16018 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.05886 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7088 | 0 | -0.16007 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.058846 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7077 | 0 | -0.16006 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.058783 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8174 | 0 | -0.16 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.058783 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8174 | 0 | -0.16 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.056308 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5046 | 0 | -0.15752 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.055879 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2747 | 0 | -0.15709 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055778 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -46.1284 | 0 | -0.15699 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055778 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -45.6822 | 0 | -0.15699 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.055473 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.6597 | 0 | -0.15669 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -40.1046 | 0 | -0.14812 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -40.1046 | 0 | -0.14812 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -7.1438 | 0 | -0.14812 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.046906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -7.1766 | 0 | -0.14812 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.042162 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.14337 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.029953 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.493 | 0 | -0.13117 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.02606 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.0658 | 0 | -0.12727 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.12159 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.12159 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.020373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.34634 | 17 | -0.12159 | -2.067
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.12159 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.020373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.12159 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.020344 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.65101 | 0 | -0.12156 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.111 | 0 | -0.12139 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.1473 | 0 | -0.12139 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.1473 | 0 | -0.12139 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.020175 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.6665 | 0 | -0.12139 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.017807 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.85474 | 48 | -0.11902 | -5.7129
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.017807 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.81912 | 46 | -0.11902 | -5.4749
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.017807 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.8697 | 105 | -0.11902 | -12.497
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.10121 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.10121 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.052992 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.04822 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 10.2559 | 0 | 0.0013467 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.074128 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.074128 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.074128 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.9655 | 0 | 0.085489 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7723 | 0 | 0.085489 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7496 | 0 | 0.085489 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011361 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7496 | 0 | 0.085489 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.011361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8405 | 0 | 0.085489 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.82426 | 56 | 0.088847 | 4.9754
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.86842 | 59 | 0.088847 | 5.242
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.82426 | 56 | 0.088847 | 4.9754
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.82426 | 56 | 0.088847 | 4.9754
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.86842 | 59 | 0.088847 | 5.242
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.014719 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.82426 | 56 | 0.088847 | 4.9754
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.015067 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 5.9967 | 398 | 0.089195 | 35.4995
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.485 | 0 | 0.089392 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4636 | 0 | 0.089392 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4254 | 0 | 0.089392 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.015264 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.1091 | 0 | 0.089392 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.015833 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.7233 | 172 | 0.089961 | 15.4732
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.015833 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.7233 | 172 | 0.089961 | 15.4732
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.015833 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.7233 | 172 | 0.089961 | 15.4732
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.01593 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.501 | 0 | 0.090058 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.016076 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 11.9445 | 743 | 0.090204 | 67.0214
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.016099 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.19319 | 0 | 0.090227 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0474 | 0 | 0.090242 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0635 | 0 | 0.090242 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.128 | 0 | 0.090242 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0152 | 0 | 0.090242 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.99907 | 0 | 0.090242 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6759 | 0 | 0.090242 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.016114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95073 | 0 | 0.090242 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.016119 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.080595 | 0 | 0.090247 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.016119 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3385 | 0 | 0.090247 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.016437 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19724 | 12 | 0.090565 | 1.0868
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56736 | 0 | 0.090815 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57904 | 0 | 0.090815 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.54566 | 0 | 0.090815 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76593 | 0 | 0.090815 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29536 | 0 | 0.090815 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34041 | 0 | 0.090815 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33207 | 0 | 0.090815 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58405 | 0 | 0.090815 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30037 | 0 | 0.090815 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4251 | 0 | 0.090815 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.016687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4697 | 0 | 0.090815 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.016882 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 12.4083 | 735 | 0.09101 | 66.8922
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.7864 | 104 | 0.091305 | 9.4957
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.7864 | 104 | 0.091305 | 9.4957
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.92756 | 54 | 0.091305 | 4.9305
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.91038 | 53 | 0.091305 | 4.8392
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.92756 | 54 | 0.091305 | 4.9305
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.97909 | 57 | 0.091305 | 5.2044
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.92756 | 54 | 0.091305 | 4.9305
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.92756 | 54 | 0.091305 | 4.9305
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.99627 | 58 | 0.091305 | 5.2957
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.017177 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.99627 | 58 | 0.091305 | 5.2957
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.017941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1038 | 0 | 0.092069 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.017941 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.422 | 0 | 0.092069 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.75865 | 42 | 0.092191 | 3.872
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.75865 | 42 | 0.092191 | 3.872
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.68639 | 38 | 0.092191 | 3.5032
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.018063 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.68639 | 38 | 0.092191 | 3.5032
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.018101 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4617 | 0 | 0.092229 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.319 | 0 | 0.092705 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3375 | 0 | 0.092705 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7245 | 0 | 0.092705 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.018577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55731 | 0 | 0.092705 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.018877 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.3979 | 0 | 0.093005 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.018877 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.9939 | 0 | 0.093005 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.018877 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.9637 | 0 | 0.093005 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.018884 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.3056 | 228 | 0.093012 | 21.2067
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2091 | 0 | 0.09302 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.194 | 0 | 0.09302 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5605 | 0 | 0.09302 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.018892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3905 | 0 | 0.09302 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.018896 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30612 | 0 | 0.093024 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.018901 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.0259 | 213 | 0.093029 | 19.8151
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.018945 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.8228 | 0 | 0.093073 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.018945 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2333 | 0 | 0.093073 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.018957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.1279 | 165 | 0.093085 | 15.359
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.018974 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.2066 | 169 | 0.093102 | 15.7342
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.018986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.22783 | 12 | 0.093114 | 1.1174
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.018986 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.093114 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.019199 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67197 | 0 | 0.093327 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.1656 | 0 | 0.093525 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.0473 | 0 | 0.093525 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.055 | 0 | 0.093525 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.0453 | 0 | 0.093525 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.019397 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.2178 | 0 | 0.093525 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.019641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.532 | 0 | 0.093769 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.019641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5713 | 0 | 0.093769 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.91167 | 46 | 0.093947 | 4.3215
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.91167 | 46 | 0.093947 | 4.3215
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.91167 | 46 | 0.093947 | 4.3215
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.09 | 55 | 0.093947 | 5.1671
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.09 | 55 | 0.093947 | 5.1671
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.019819 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.0702 | 54 | 0.093947 | 5.0731
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3343 | 0 | 0.094655 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2316 | 0 | 0.094655 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3343 | 0 | 0.094655 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.020527 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3343 | 0 | 0.094655 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9114 | 0 | 0.095132 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.84 | 0 | 0.095132 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8273 | 0 | 0.095132 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1447 | 0 | 0.095132 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.021004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25625 | 0 | 0.095132 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.02222 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.096348 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.023264 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1632 | 50 | 0.097392 | 4.8696
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7416 | 0 | 0.098727 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6408 | 0 | 0.098727 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3037 | 0 | 0.098727 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7686 | 0 | 0.098727 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7759 | 0 | 0.098727 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.7464 | 0 | 0.098727 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.3615 | 0 | 0.098727 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.024599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.0022 | 0 | 0.098727 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.024599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98396 | 0 | 0.098727 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.024616 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.78771 | 0 | 0.098744 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.024616 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73848 | 0 | 0.098744 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4691 | 0 | 0.098745 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2869 | 0 | 0.098745 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.5282 | 0 | 0.098745 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.024617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.5109 | 0 | 0.098745 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.027884 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.4893 | 161 | 0.10201 | 16.4239
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.027884 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.6287 | 166 | 0.10201 | 16.9339
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.027884 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 6.9152 | 248 | 0.10201 | 25.2989
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.027884 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 15.2247 | 546 | 0.10201 | 55.6984
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.027884 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 17.9294 | 0 | 0.10201 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.027884 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.36249 | 13 | 0.10201 | 1.3262
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.028159 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.92925 | 0 | 0.10229 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.028806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.6954 | 0 | 0.10293 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.028806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.6954 | 0 | 0.10293 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.028806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 7.0575 | 0 | 0.10293 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.028858 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 18.7866 | 0 | 0.10299 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.028858 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 16.2759 | 0 | 0.10299 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.028858 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 17.3148 | 0 | 0.10299 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.029085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3408 | 0 | 0.10321 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.9169 | 0 | 0.10941 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.9169 | 0 | 0.10941 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.1992 | 0 | 0.10941 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.035287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.8639 | 0 | 0.10941 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.036994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6266 | 0 | 0.11112 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.036994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36994 | 0 | 0.11112 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4276 | 0 | 0.11328 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.7957 | 0 | 0.11328 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.762 | 0 | 0.11328 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.9547 | 0 | 0.11328 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.3673 | 0 | 0.11328 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.4456 | 0 | 0.11328 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9578 | 0 | 0.11328 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.70479 | 0 | 0.11328 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.6806 | 0 | 0.11328 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.7409 | 0 | 0.11328 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4668 | 0 | 0.11328 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.8192 | 0 | 0.11328 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.5372 | 0 | 0.11328 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.9547 | 0 | 0.11328 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.798 | 0 | 0.11328 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.033 | 0 | 0.11328 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.9758 | 0 | 0.11328 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1324 | 0 | 0.11328 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1324 | 0 | 0.11328 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.039155 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.6955 | 0 | 0.11328 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.047114 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.5548 | 0 | 0.12124 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.047114 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.1779 | 0 | 0.12124 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.047114 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.12124 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.048127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.1764 | 66 | 0.12225 | 8.0688
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.874 | 76 | 0.1251 | 9.5077
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.874 | 76 | 0.1251 | 9.5077
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 5.3523 | 105 | 0.1251 | 13.1357
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.7721 | 74 | 0.1251 | 9.2575
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.7721 | 74 | 0.1251 | 9.2575
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.050974 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 5.1993 | 102 | 0.1251 | 12.7604
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.05126 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 68.3296 | 0 | 0.12539 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.05126 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 68.0733 | 0 | 0.12539 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.059484 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3569 | 0 | 0.13361 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.062361 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.13649 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.9071 | 0 | 0.1489 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 6.0566 | 0 | 0.1489 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.9071 | 0 | 0.1489 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.9818 | 0 | 0.1489 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.8622 | 0 | 0.1489 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8693 | 0 | 0.1489 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.4396 | 0 | 0.1489 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0936 | 0 | 0.1489 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.2601 | 0 | 0.1489 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.074773 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.5332 | 0 | 0.1489 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.075423 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.6203 | 0 | 0.14955 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.1708 | 0 | 0.15166 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5427 | 0 | 0.15166 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0236 | 0 | 0.15166 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1629 | 0 | 0.15166 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5427 | 0 | 0.15166 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1629 | 0 | 0.15166 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0236 | 0 | 0.15166 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.077528 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0236 | 0 | 0.15166 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.077839 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.62271 | 0 | 0.15197 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.078415 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1762 | 0 | 0.15254 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.078415 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8035 | 0 | 0.15254 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.079072 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7396 | 22 | 0.1532 | 3.3704
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.079072 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.86979 | 11 | 0.1532 | 1.6852
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.079072 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.86979 | 11 | 0.1532 | 1.6852
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8063 | 47.7 | 0.15392 | 7.3422
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.9764 | 37.3 | 0.15392 | 5.7414
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6707 | 46 | 0.15392 | 7.0805
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.079797 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8303 | 48 | 0.15392 | 7.3884
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.079981 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.8386 | 0 | 0.15411 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.6888 | 0 | 0.15444 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.2873 | 0 | 0.15444 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 8.0309 | 0 | 0.15444 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.6448 | 0 | 0.15444 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.8054 | 0 | 0.15444 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.080309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 10.1992 | 0 | 0.15444 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.080309 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.96371 | 0 | 0.15444 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 0 | 0.15476 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 0 | 0.15476 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 0 | 0.15476 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2901 | 0 | 0.15476 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 0 | 0.15476 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 0 | 0.15476 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0158 | 0 | 0.15476 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.080634 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2095 | 0 | 0.15476 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.080874 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.6459 | 144 | 0.155 | 22.3202
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.080874 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.2043 | 188 | 0.155 | 29.1403
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.081135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 27.2614 | 336 | 0.15526 | 52.1683
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.081135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6043 | 180 | 0.15526 | 27.9473
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.081145 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.0338 | 0 | 0.15527 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.081145 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.0581 | 0 | 0.15527 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.081145 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.4152 | 0 | 0.15527 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.081161 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.609 | 180 | 0.15529 | 27.952
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.081319 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 27.1605 | 334 | 0.15545 | 51.9192
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.081319 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 27.6485 | 340 | 0.15545 | 52.8519
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.081319 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6374 | 180 | 0.15545 | 27.9804
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.081319 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6374 | 180 | 0.15545 | 27.9804
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.081349 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0337 | 0 | 0.15548 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.081349 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0337 | 0 | 0.15548 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.081428 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0943 | 0 | 0.15556 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.081434 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0945 | 0 | 0.15556 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.081814 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.3726 | 0 | 0.15594 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.7023 | 0 | 0.15607 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3595 | 0 | 0.15607 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1137 | 0 | 0.15607 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.5568 | 0 | 0.15607 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.7023 | 0 | 0.15607 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.9498 | 0 | 0.15607 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.5234 | 0 | 0.15607 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.8027 | 0 | 0.15607 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 12.127 | 0 | 0.15607 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.0969 | 0 | 0.15607 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.5066 | 0 | 0.15607 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.081939 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.0969 | 0 | 0.15607 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.081993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.1157 | 38 | 0.15612 | 5.9326
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.081993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5825 | 19.3 | 0.15612 | 3.0131
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.081993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2299 | 15 | 0.15612 | 2.3418
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.081993 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 3.8537 | 47 | 0.15612 | 7.3377
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.081993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15612 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.082145 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.8289 | 144 | 0.15627 | 22.5033
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.082145 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.8289 | 144 | 0.15627 | 22.5033
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.082145 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.0468 | 171 | 0.15627 | 26.7226
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.082148 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 17.0046 | 207 | 0.15628 | 32.3491
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.082148 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 17.8015 | 216.7 | 0.15628 | 33.865
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.082148 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.8798 | 242 | 0.15628 | 37.8187
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.082303 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 12.0574 | 146.5 | 0.15643 | 22.9171
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.082303 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 12.1726 | 147.9 | 0.15643 | 23.1361
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.082303 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.2384 | 173 | 0.15643 | 27.0625
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.083269 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.99923 | 0 | 0.1574 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.083269 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.91596 | 0 | 0.1574 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.083269 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.99923 | 0 | 0.1574 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.083306 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15743 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.084193 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15832 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.084633 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 53.2342 | 0 | 0.15876 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.085737 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15986 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.085885 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.72143 | 8.4 | 0.16001 | 1.3441
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.086311 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16044 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.086318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.6318 | 100 | 0.16045 | 16.0446
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.086318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.6318 | 100 | 0.16045 | 16.0446
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.086318 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16045 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.086318 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16045 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.086318 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16045 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.086318 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16045 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.086878 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.0851 | 24 | 0.16101 | 3.8641
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.086878 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 2.0851 | 24 | 0.16101 | 3.8641
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.086878 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.9982 | 23 | 0.16101 | 3.7031
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.092154 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 36.493 | 0 | 0.16628 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.097356 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 53.1564 | 0 | 0.17148 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.097356 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 73.017 | 0 | 0.17148 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.097481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.6539 | 58 | 0.17161 | 9.9533
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.097481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.6758 | 89 | 0.17161 | 15.2732
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2892 | 44 | 0.17161 | 7.5508
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2892 | 44 | 0.17161 | 7.5508
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.1917 | 43 | 0.17161 | 7.3792
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.097481 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3866 | 45 | 0.17161 | 7.7224
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.097502 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.17 | 0 | 0.17163 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.097835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.1644 | 155 | 0.17196 | 26.6542
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.097835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 16.6319 | 170 | 0.17196 | 29.2337
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.097835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.1644 | 155 | 0.17196 | 26.6542
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.098024 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 39.8958 | 407 | 0.17215 | 70.0658
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.098085 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 20.4998 | 209 | 0.17221 | 35.9925
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.098085 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 21.1864 | 216 | 0.17221 | 37.1979
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5119 | 46 | 0.17221 | 7.9218
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.61 | 47 | 0.17221 | 8.094
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5119 | 46 | 0.17221 | 7.9218
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.098085 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5119 | 46 | 0.17221 | 7.9218
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.09819 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 40.4543 | 412 | 0.17232 | 70.9949
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.09819 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 39.276 | 400 | 0.17232 | 68.9271
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.098252 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 41.6588 | 0 | 0.17238 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.098252 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 41.7571 | 0 | 0.17238 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.09854 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.17267 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.09854 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.17267 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.09854 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.17267 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.8055 | 147 | 0.17485 | 25.7023
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.8991 | 138 | 0.17485 | 24.1287
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.1005 | 140 | 0.17485 | 24.4784
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.8055 | 147 | 0.17485 | 25.7023
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.3307 | 182 | 0.17485 | 31.8219
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.10072 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.9422 | 198 | 0.17485 | 34.6195
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.6917 | 0 | 0.17669 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 22.7681 | 0 | 0.17669 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 18.8709 | 0 | 0.17669 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 22.9732 | 0 | 0.17669 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.10256 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.7943 | 0 | 0.17669 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.10263 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8474 | 0 | 0.17676 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.10263 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8474 | 0 | 0.17676 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.10263 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.5395 | 0 | 0.17676 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.10339 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41356 | 0 | 0.17752 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.10359 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4191 | 0 | 0.17771 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.10378 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.24907 | 0 | 0.17791 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.10378 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.24907 | 0 | 0.17791 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.821 | 142 | 0.1785 | 25.3471
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.1341 | 145 | 0.1785 | 25.8826
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.7603 | 151 | 0.1785 | 26.9536
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.10437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 30.2682 | 290 | 0.1785 | 51.7652
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.10502 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25205 | 0 | 0.17915 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.10502 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25205 | 0 | 0.17915 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.10502 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.29405 | 0 | 0.17915 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.10701 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 45.1561 | 422 | 0.18113 | 76.438
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.10778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.0178 | 0 | 0.18191 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.10778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.1256 | 0 | 0.18191 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.2269 | 223.9 | 0.18233 | 40.8241
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.3459 | 225 | 0.18233 | 41.0246
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.3026 | 224.6 | 0.18233 | 40.9517
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.1082 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.5298 | 226.7 | 0.18233 | 41.3346
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.1105 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 47.8474 | 0 | 0.18463 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.11061 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 64.5957 | 0 | 0.18474 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.11061 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 65.8124 | 0 | 0.18474 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.11137 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.6682 | 0 | 0.18549 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.6418 | 50 | 0.18696 | 9.3482
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.6418 | 50 | 0.18696 | 9.3482
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.6418 | 50 | 0.18696 | 9.3482
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.11284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.6418 | 50 | 0.18696 | 9.3482
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.11284 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.0311 | 0 | 0.18697 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.11284 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.0311 | 0 | 0.18697 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.12372 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.5473 | 158 | 0.19784 | 31.2595
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.12372 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.7947 | 160 | 0.19784 | 31.6552
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.12372 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.6505 | 175 | 0.19784 | 34.6228
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.12475 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 16.4671 | 132 | 0.19888 | 26.252
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.12475 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 16.7166 | 134 | 0.19888 | 26.6497
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.12475 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 40.2946 | 323 | 0.19888 | 64.2378
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.12491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.0495 | 152.5 | 0.19904 | 30.354
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.12491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.6748 | 149.5 | 0.19904 | 29.7569
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.12491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 29.0552 | 232.6 | 0.19904 | 46.2973
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.12607 | south | 5 | N | N | Nsouth | Nsouth | -1 | 4.4123 | 0 | 0.20019 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.12607 | south | 5 | N | N | Nsouth | Nsouth | -1 | 4.2863 | 0 | 0.20019 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.12607 | south | 5 | N | N | Nsouth | Nsouth | -1 | 4.4123 | 0 | 0.20019 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.3386 | 49 | 0.20349 | 9.9709
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.9506 | 46 | 0.20349 | 9.3604
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.9506 | 46 | 0.20349 | 9.3604
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.0799 | 47 | 0.20349 | 9.5639
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.12936 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.9214 | 154 | 0.20349 | 31.3371
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.12936 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.1453 | 148 | 0.20349 | 30.1162
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.2093 | 48 | 0.20349 | 9.7674
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.12936 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.2093 | 48 | 0.20349 | 9.7674
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.13092 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0474 | 0 | 0.20505 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.13092 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0474 | 0 | 0.20505 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.1312 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 40.6732 | 310 | 0.20533 | 63.6528
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.1312 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 54.1873 | 413 | 0.20533 | 84.802
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.566 | 42 | 0.20665 | 8.6793
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.831 | 44 | 0.20665 | 9.0926
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.831 | 44 | 0.20665 | 9.0926
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.13252 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.2286 | 47 | 0.20665 | 9.7126
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.16206 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 92.2116 | 0 | 0.23619 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.16206 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 94.1563 | 0 | 0.23619 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 581
| 25 | 577
| 30 | 572
| 35 | 567
| 40 | 562
| 45 | 557
| 50 | 552
| 55 | 547
| 60 | 542
| 65 | 537
| 70 | 531
| 75 | 526
| 80 | 521
| 85 | 515
| 90 | 510
| 95 | 504
| 100 | 498
| 105 | 492
| 110 | 486
| 115 | 480
| Max | 581
| Min | 480
| Avg | 532.85