## test results
CRE test for: |  | 3407 ELM_MOTT - 3575 WACONCST | [5 empty] | FAIL
Line Rating: |  | 378.15
Direction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3407 ELM_MOTT - 3575 WACONCST
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.018003
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.016163
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.017837
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.0038218
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3407 ELM_MOTT - 3575 WACONCST
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.021219
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.015854
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.017898
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0035869
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3407 ELM_MOTT - 3575 WACONCST
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.033857
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.00010501
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.02159
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.034061
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.012342
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.021424
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.033857 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.033857 | 0.033857
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.090436
[6 empty] | Concentration |  | 2.6711 | FAIL
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.038584
[6 empty] | Concentration |  | 1.1396 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 9.0323
| Percent of line rating => | [6 empty] | 2.389% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 11.8714
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | 0.015367 | 0.016614 | 0.0012466 | 0.015367
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.03715 | 0.21915 | 0.2563 | -0.03715
[7 empty] | B4 (S-W) | 0.014772 | -0.38958 | -0.40436 | 0.014772
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.040533 | -0.18705 | -0.14651 | -0.040533
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.052541 | 0.20179 | 0.25433 | -0.052541
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | 3.823%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -9.243%
[7 empty] | B4 | 3.675%
[7 empty] | B5 | -10.08%
[7 empty] | B6 | -13.07%
[7 empty] | Max Abs Error | 13.07% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3407 ELM_MOTT - 3575 WACONCST C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3407 ELM_MOTT - 3575 WACONCST C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.071274 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 18.1749
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.071274 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 10.6198
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.067214 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.0082
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.067214 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.0082
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.071274 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 10.9049
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.080393 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 12.0589
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.080393 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 6.4314
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.024361 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 1.7784
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.024361 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 2.899
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.024361 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 4.994
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.024361 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 2.4848
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.024361 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 2.3387
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.021175 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.2541
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.021175 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.2541
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.026254 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 4.4107
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.026254 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 2.3629
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.022002 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.39604
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.022002 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.39604
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.022002 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.83608
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.020515 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 5.9083
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.020515 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.0157
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.020515 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.0157
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.019245 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 2.1651
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.017684 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.70736
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017676 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 1.3964
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017676 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 1.8737
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017676 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 2.5807
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017676 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 1.3434
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.018612 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.1167
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.018612 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.1726
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.017636 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.35272
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.017636 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.4409
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.017636 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.72308
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.003836 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 1.7761
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 1.1618
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 1.1442
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.1794
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.1794
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.1794
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.017603 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 2.0067
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.017603 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 9.0655
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 1.1949
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 1.2492
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 1.2492
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 1.213
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 1.213
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 1.1768
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.018008 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 1.2606
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.018008 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 1.3218
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.018008 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 1.2678
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 2.7067
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 3.9699
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.018163 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 1.7981
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.018163 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 1.1079
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.018158 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 2.5603
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.018163 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.45408
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.018163 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.83005
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.018163 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.83005
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.018158 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 2.179
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.017926 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.46249
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.017866 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 1.7955
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.018001 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 2.1601
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.017864 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 1.0361
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.017898 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 3.8338
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.01839 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 2.7585
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.017759 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.11721
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.017759 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 0.60913
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.01839 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 1.8574
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.018009 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 2.1611
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.01904 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 6.9686
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.019866 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 4.8076
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.018599 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 7.4396
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.018599 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 4.3894
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.018705 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 3.0863
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.01913 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 3.9025
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.01913 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 3.8451
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.01913 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 4.6295
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.38458
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.38458
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.38458
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.32689
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.021242 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 2.549
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.026661 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 1.5997
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.017718 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 1.3289
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.017718 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 1.4104
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.017718 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 1.5663
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 2.8381
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.7671
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 3.4766
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.7671
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 2.7849
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 3.5121
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.017848 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 3.0342
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.017848 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 9.281
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017768 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 6.5742
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.017682 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 9.8666
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.017682 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 10.2379
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.017682 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 14.2871
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.019293 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 2.1608
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.019293 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 1.9293
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.019293 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 7.2928
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.019927 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 4.3301
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.019927 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 4.085
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.019927 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 5.4281
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.020168 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 15.5294
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 1.6361
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.6127
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.6127
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 1.5894
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.020035 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 23.1805
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.020035 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 23.2005
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 4.3788
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 4.4178
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.018649 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 4.0356
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.018649 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 4.03
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 4.1442
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 4.1246
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.019253 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 7.6049
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.019261 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 8.3785
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.019253 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 8.3751
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.018058 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 2.492
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.018137 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 2.1402
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.018137 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 2.0858
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.018137 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 10.0842
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.017598 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 6.828
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.017598 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 9.063
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.015955 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 12.5247
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.015955 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 12.6842
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.015955 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 12.4449
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.015332 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 2.7904
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.015332 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 7.4207
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.019122 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 4.2833
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.015523 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.77615
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.015539 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.65264
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.013267 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 8.1592
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.013267 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 7.7877
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.023155 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 12.4342
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.023155 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 18.223
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.055032 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -4.1274
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.055032 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -12.2171
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.024592 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -13.9928
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.01533 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -3.204
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.01533 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -3.3113
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.015318 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -6.2344
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.70518
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -0.72051
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.70518
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.70518
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.01536 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -6.5126
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.01536 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -6.528
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.01522 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -0.88276
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.01522 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -1.3546
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.66968
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.66968
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.65446
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -0.6849
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.015347 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -6.323
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.015347 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -6.1388
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.015232 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -8.3167
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.015232 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -11.424
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.015412 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -0.94013
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.015412 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -1.4641
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.015412 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -2.3272
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.015306 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -2.3724
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.015306 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -2.602
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.015306 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -2.3724
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.012382 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.2724
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.012382 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.1362
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.012382 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.1362
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.5963
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.46629
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.57505
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.60005
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.012946 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.15535
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.012946 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.14241
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.013293 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.31903
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.013293 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.31903
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.013293 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.30574
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.014386 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -5.6969
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.008123 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -10.828
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.008123 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -10.7873
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.012817 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.48705
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.012817 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.24737
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.012817 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.19226
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.012817 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.6024
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.016263 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 1.2197
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.018438 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 2.7657
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.0177 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 3.0002
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.010529 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 1.5794
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.018145 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 1.1431
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.018843 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 12.2423
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.017909 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.71636
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.017909 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.71636
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.017388 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -7.3377
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.019631 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -2.5913
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.019631 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -2.6306
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.019631 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -6.3408
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.019426 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -3.0693
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.019426 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -3.1082
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.019426 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -3.3996
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.017378 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -10.1488
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.017378 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -10.3399
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.017361 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -7.5173
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -3.7967
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -3.8153
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -3.8085
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -3.8442
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.020454 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.16363
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.020454 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.16363
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.017366 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.31259
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.017366 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.31259
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.017366 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.26049
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.017019 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.23316
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.018124 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.32623
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.018124 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.32623
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.019795 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.69283
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.019795 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.67303
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.019795 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.69283
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.017546 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.49129
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.017546 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.50883
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.017616 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 0.61656
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.017616 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 0.52848
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.8874
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.8874
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.8874
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.8874
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.017456 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.10474
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.016454 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.03949
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.016454 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.03949
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.016454 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.046071
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.01619 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.06476
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.016266 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.039038
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.016266 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.039038
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -2.3185
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -2.1765
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -2.2081
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -2.3185
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -2.8705
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -3.1229
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.0196 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -2.989
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.0196 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -2.9302
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.0196 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -4.559
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -2.3218
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -2.3709
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -2.469
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -4.7418
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.005202 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.17167
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.005202 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.13005
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.012946 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.15535
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.012535 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -0.91505
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.92699
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -0.95045
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.34034
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.085085
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.92699
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -0.93872
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -0.91995
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.29335
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.53976
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.013243 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -8.3298
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.012673 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -1.8249
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.012673 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -2.3825
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.015279 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.18335
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.007731 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.046386
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.012691 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -4.2642
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.012719 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -4.2481
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.012719 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -4.3245
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.012736 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.48397
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.012723 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.31807
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.012723 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.31807
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.012736 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.48397
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.012793 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.371
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.012693 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -1.8824
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.012693 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -1.8862
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.012693 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -1.942
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -1.9856
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -1.9228
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -1.2567
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -1.8222
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -1.8473
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -1.596
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.01285 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -1.8825
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.01285 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -1.9005
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.01285 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -2.2231
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -2.6568
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -2.7813
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -3.1061
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -1.8482
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -1.8482
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -2.1948
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.020503 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -6.3559
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.020503 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -8.4677
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.87016
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.91159
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.91159
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.97375
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.99122
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.93053
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.93053
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.95076
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.020229 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -3.1153
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.020229 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -2.9939
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.97099
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.97099
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 1.2488
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 1.2488
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 1.6556
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 1.4272
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 1.4272
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 2.0516
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 3.7139
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 2.5348
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 2.3618
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 2.426
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 2.6222
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 3.746
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 3.8086
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 2.3052
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 4.5375
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 3.5899
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 3.609
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 2.1997
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.01766 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 2.6313
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.018054 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 3.2497
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.018054 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 3.2497
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.01804 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 4.059
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.018159 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 2.2699
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.018159 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 2.2699
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 2.4875
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 2.5053
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 5.4903
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 2.5408
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 2.5586
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 5.5081
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.020679 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 4.0531
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.020679 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 2.2954
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.017987 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.7872
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.8392
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.8392
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 7.1672
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 2.8045
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.7872
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 2.8219
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 7.0806
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017687 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017687 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 2.3368
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 2.0526
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 2.2894
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 6.2998
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.013702 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 2.0649
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.013702 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 2.069
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.013702 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 2.4307
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.013817 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 2.0933
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.013817 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 2.1043
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.013817 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 2.4525
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.024592 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -14.288
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 6.3185
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 6.3185
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.002372 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.075904
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001814 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.087072
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001814 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.083444
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.028464
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.12097
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002372 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.040324
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.052184
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.0593
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001814 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.19047
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.018214 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 1.53
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.016238 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 1.299
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.016226 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 2.4339
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.016226 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 2.4339
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.28306
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.26667
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.21189
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -0.61249
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -0.61369
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -0.6089
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.38381
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -0.97551
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.15992
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.4012
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.3716
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.4108
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.408
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.004 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.128
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.004 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.12
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.62737
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.62737
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -0.67259
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -0.61889
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 1.1255
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 1.1307
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.002992 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.40691
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.004549 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.15012
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.12541
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.12541
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.11347
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.11347
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.005916 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.42004
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.005916 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.05916
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.00465 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.75795
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.00465 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.75795
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.00465 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -1.1393
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.21885
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.20202
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.21885
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.21885
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.003122 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.46518
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.003122 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.20324
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.31313
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.30143
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.29937
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.18753
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.04198
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.002678 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -1.9898
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.002803 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -2.0602
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.00264 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.45408
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.00264 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.45408
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.00264 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.45408
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.337
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.002967 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -0.51329
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.002967 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.40054
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.41547
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.41189
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.40551
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -0.687
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.1993
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.1968
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.25722
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.22919
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -0.52093
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -0.50146
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -0.50274
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -0.50114
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -0.85865
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.002685 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.013425
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.002685 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.056385
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 0.45304
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.45833
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.45833
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 1.1164
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.002522 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -1.0038
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.14987
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.14987
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.14987
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.17919
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.17919
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.17593
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.008997 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 7.4405
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.008997 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 7.3685
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.004692 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.2163
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.61423
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.61423
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.84861
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.59807
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.59807
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.82436
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.003112 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -0.56016
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.003112 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -0.49356
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.003112 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -0.48858
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.003162 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.11067
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.003629 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -1.6657
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.17446
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.17714
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.18788
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.16909
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.16641
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.27914
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.15836
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.30389
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.29999
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.29999
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.001948 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.31558
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.002655 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.41684
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.21762
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.22068
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.11954
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.09195
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.00323 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.25194
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.00323 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.2584
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.003115 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.050463
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.003124 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -0.51546
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.003127 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -0.52846
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.003115 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -0.66349
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.003113 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -0.70976
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.003129 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.037548
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.003129 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.056322
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.003791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.18955
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.2963
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.2963
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.15385
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.151
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.15385
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.16239
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.15385
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.15385
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.16524
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.16524
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.002734 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.032808
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.13821
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.14561
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.13821
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.13821
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.14561
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.13821
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.007638 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.50411
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.004507 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -0.72563
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.004507 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -0.74816
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.004507 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -1.1177
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.004507 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -2.4608
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.004507 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -2.898
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.004658 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -3.0324
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.004658 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -2.6271
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.004658 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -2.7948
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.004507 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.058591
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.002681 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.032172
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.094248
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.096188
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.090644
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.12723
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.049064
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.056549
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.055163
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.09702
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.049896
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.23673
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.41026
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.3875
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.44625
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.28125
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.63125
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.5375
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.55
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.3125
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.1125
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.5875
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.4375
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.39375
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.45
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.405
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.63125
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.60625
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.64375
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.475
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.5
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.5
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -1.0688
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.10988
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.015654 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 1.1975
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.016263 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 1.301
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.016263 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 0.65052
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.016361 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 1.3089
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.016241 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 1.2993
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.015735 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 1.2588
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.01557 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 1.3079
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.016361 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 1.3089
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -1.8302
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.018093 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 2.1712
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.018093 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 4.2157
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.018093 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 3.0794
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -3.564
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -2.9539
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -3.5961
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -1.8462
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -1.6054
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.018644 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 1.1186
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.00628 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.012929 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.016724 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.080275
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 0.68419
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 1.9613
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 2.4631
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 2.1712
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 1.9157
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 1.4687
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.017882 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 2.6823
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 2.007
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 2.6671
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 3.3182
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 3.8267
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.012817 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.008319 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.013309 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.32855
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.5116
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -0.86832
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -1.2041
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.52521
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.48678
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.24339
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -1.2041
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.46116
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.55083
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.28182
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.47404
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.18232
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.085085
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.18232
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.47404
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.47404
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -1.8959
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.6405
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -0.70455
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.6405
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.012567 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.1508
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.012292 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.18438
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.012292 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.28272
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.011834 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.56803
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.012202 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.097616
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.012695 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -2.2851
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.012691 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -2.2844
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.012719 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -2.2894
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.012719 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -2.2894
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.01331 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -1.331
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.01331 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -1.331
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.3154
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.3154
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.3154
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.20186
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.3154
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.3154
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.3154
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.18924
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.01331 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.01331 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -6.655
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.01331 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -6.655
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.01331 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.013384 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.005202 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.013038 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.012996 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:3407 ELM_MOTT - 3575 WACONCST C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | [7 empty] | 9.0323
Number of Bus | Name of Bus | ID | Max MW | L:3407 ELM_MOTT - 3575 WACONCST C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.071274 | north | Y | 0.053271 | 0.087437 | 0.053437 | 0.075096 | 0.053271 | North | N | 0.053271 | 0
239 | BOSQUESW | 1 | 149 | 0.071274 | north | Y | 0.053271 | 0.087437 | 0.053437 | 0.075096 | 0.053271 | North | N | 0.053271 | 0
244 | WHITNYDM | 1 | 15 | 0.067214 | north | N | 0.049211 | 0.083377 | 0.049377 | 0.071036 | 0.049211 | North | N | 0.049211 | 0
245 | WHITNYDM | 2 | 15 | 0.067214 | north | N | 0.049211 | 0.083377 | 0.049377 | 0.071036 | 0.049211 | North | N | 0.049211 | 0
247 | BOSQUESW | 2 | 153 | 0.071274 | north | Y | 0.053271 | 0.087437 | 0.053437 | 0.075096 | 0.053271 | North | N | 0.053271 | 0
251 | BOSQUESW | 2 | 150 | 0.080393 | north | Y | 0.06239 | 0.096556 | 0.062556 | 0.084215 | 0.06239 | North | N | 0.06239 | 0
253 | BOSQUESW | 2 | 80 | 0.080393 | north | Y | 0.06239 | 0.096556 | 0.062556 | 0.084215 | 0.06239 | North | N | 0.06239 | 0
332 | RWMILLER | 1 | 73 | 0.024361 | north | Y | 0.006358 | 0.040524 | 0.0065237 | 0.028183 | 0.006358 | North | N | 0.006358 | 0
333 | RWMILLER | 2 | 119 | 0.024361 | north | Y | 0.006358 | 0.040524 | 0.0065237 | 0.028183 | 0.006358 | North | N | 0.006358 | 0
334 | RWMILLER | 3 | 205 | 0.024361 | north | Y | 0.006358 | 0.040524 | 0.0065237 | 0.028183 | 0.006358 | North | N | 0.006358 | 0
335 | RWMILLER | 4 | 102 | 0.024361 | north | Y | 0.006358 | 0.040524 | 0.0065237 | 0.028183 | 0.006358 | North | N | 0.006358 | 0
336 | RWMILLER | 5 | 96 | 0.024361 | north | Y | 0.006358 | 0.040524 | 0.0065237 | 0.028183 | 0.006358 | North | N | 0.006358 | 0
344 | MRSSHPRD | 1 | 12 | 0.021175 | north | N | 0.003172 | 0.037338 | 0.0033377 | 0.024997 | 0.003172 | North | N | 0.003172 | 0
345 | MRSSHPRD | 2 | 12 | 0.021175 | north | N | 0.003172 | 0.037338 | 0.0033377 | 0.024997 | 0.003172 | North | N | 0.003172 | 0
366 | JNSNCNTY | 1 | 168 | 0.026254 | north | Y | 0.008251 | 0.042417 | 0.0084167 | 0.030076 | 0.008251 | North | N | 0.008251 | 0
367 | JNSNCNTY | 2 | 90 | 0.026254 | north | Y | 0.008251 | 0.042417 | 0.0084167 | 0.030076 | 0.008251 | North | N | 0.008251 | 0
503 | NTHTEXAS | 1 | 18 | 0.022002 | north | Y | 0.003999 | 0.038165 | 0.0041647 | 0.025824 | 0.003999 | North | N | 0.003999 | 0
504 | NTHTEXAS | 2 | 18 | 0.022002 | north | Y | 0.003999 | 0.038165 | 0.0041647 | 0.025824 | 0.003999 | North | N | 0.003999 | 0
505 | NTHTEXAS | 3 | 38 | 0.022002 | north | Y | 0.003999 | 0.038165 | 0.0041647 | 0.025824 | 0.003999 | North | N | 0.003999 | 0
580 | JCKCNTY8 | 1 | 288 | 0.020515 | north | Y | 0.002512 | 0.036678 | 0.0026777 | 0.024337 | 0.002512 | North | N | 0.002512 | 0
581 | JCKCNTY8 | 2 | 147 | 0.020515 | north | Y | 0.002512 | 0.036678 | 0.0026777 | 0.024337 | 0.002512 | North | N | 0.002512 | 0
582 | JCKCNTY8 | 3 | 147 | 0.020515 | north | Y | 0.002512 | 0.036678 | 0.0026777 | 0.024337 | 0.002512 | North | N | 0.002512 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.019245 | north | Y | 0.001242 | 0.035408 | 0.0014077 | 0.023067 | 0.001242 | North | N | 0.001242 | 0
837 | NEWMAN_G | 1 | 40 | 0.017684 | north | Y | -0.000319 | 0.033847 | -0.00015334 | 0.021506 | 0.00015334 | west | Y | 0.000319 | 0.0066263
842 | OLINGER_ | 1 | 79 | 0.017676 | north | Y | -0.000327 | 0.033839 | -0.00016134 | 0.021498 | 0.00016134 | west | Y | 0.000327 | 0.013087
843 | OLINGER_ | 1 | 106 | 0.017676 | north | Y | -0.000327 | 0.033839 | -0.00016134 | 0.021498 | 0.00016134 | west | Y | 0.000327 | 0.01756
844 | OLINGER_ | 1 | 146 | 0.017676 | north | Y | -0.000327 | 0.033839 | -0.00016134 | 0.021498 | 0.00016134 | west | Y | 0.000327 | 0.024186
845 | OLINGER_ | 1 | 76 | 0.017676 | north | Y | -0.000327 | 0.033839 | -0.00016134 | 0.021498 | 0.00016134 | west | Y | 0.000327 | 0.01259
923 | SPENCER_ | 1 | 60 | 0.018612 | north | Y | 0.000609 | 0.034775 | 0.00077466 | 0.022434 | 0.000609 | North | N | 0.000609 | 0
924 | SPENCER_ | 1 | 63 | 0.018612 | north | Y | 0.000609 | 0.034775 | 0.00077466 | 0.022434 | 0.000609 | North | N | 0.000609 | 0
948 | STEAM1 | 1 | 20 | 0.017636 | north | Y | -0.000367 | 0.033799 | -0.00020134 | 0.021458 | 0.00020134 | west | Y | 0.000367 | 0.0033132
949 | STEAM2 | 1 | 25 | 0.017636 | north | Y | -0.000367 | 0.033799 | -0.00020134 | 0.021458 | 0.00020134 | west | Y | 0.000367 | 0.0041414
950 | STEAM3 | 1 | 41 | 0.017636 | north | Y | -0.000367 | 0.033799 | -0.00020134 | 0.021458 | 0.00020134 | west | Y | 0.000367 | 0.006792
990 | GIBN_CRE | 1 | 463 | 0.003836 | north | Y | -0.014167 | 0.019999 | -0.014001 | 0.0076578 | 0.0076578 | houston | Y | 0.014167 | 3.0138
1002 | PBCTAGE_ | A | 66 | 0.017603 | west | Y | -0.0004 | 0.033766 | -0.00023434 | 0.021425 | 0.00023434 | west | N | 0.00023434 | 0
1003 | PBCTBGE_ | B | 65 | 0.017603 | west | Y | -0.0004 | 0.033766 | -0.00023434 | 0.021425 | 0.00023434 | west | N | 0.00023434 | 0
1004 | PBCTCGE_ | C | 67 | 0.017603 | west | Y | -0.0004 | 0.033766 | -0.00023434 | 0.021425 | 0.00023434 | west | N | 0.00023434 | 0
1005 | PBCTDGE_ | D | 67 | 0.017603 | west | Y | -0.0004 | 0.033766 | -0.00023434 | 0.021425 | 0.00023434 | west | N | 0.00023434 | 0
1006 | PBCTEGE_ | E | 67 | 0.017603 | west | Y | -0.0004 | 0.033766 | -0.00023434 | 0.021425 | 0.00023434 | west | N | 0.00023434 | 0
1007 | PB5GEN_6 | MB | 114 | 0.017603 | west | Y | -0.0004 | 0.033766 | -0.00023434 | 0.021425 | 0.00023434 | west | N | 0.00023434 | 0
1008 | PB6GEN_7 | MB | 515 | 0.017603 | west | Y | -0.0004 | 0.033766 | -0.00023434 | 0.021425 | 0.00023434 | west | N | 0.00023434 | 0
1039 | MRGNAG_1 | A | 66 | 0.018105 | west | Y | 0.000102 | 0.034268 | 0.00026766 | 0.021927 | 0.000102 | North | Y | 0.00026766 | 0.010933
1040 | MRGNBG_2 | B | 69 | 0.018105 | west | Y | 0.000102 | 0.034268 | 0.00026766 | 0.021927 | 0.000102 | North | Y | 0.00026766 | 0.01143
1041 | MRGNCG_3 | C | 69 | 0.018105 | west | Y | 0.000102 | 0.034268 | 0.00026766 | 0.021927 | 0.000102 | North | Y | 0.00026766 | 0.01143
1042 | MRGNDG_4 | D | 67 | 0.018105 | west | Y | 0.000102 | 0.034268 | 0.00026766 | 0.021927 | 0.000102 | North | Y | 0.00026766 | 0.011099
1043 | MRGNEG_5 | E | 67 | 0.018105 | west | Y | 0.000102 | 0.034268 | 0.00026766 | 0.021927 | 0.000102 | North | Y | 0.00026766 | 0.011099
1044 | MRGNFG_6 | F | 65 | 0.018105 | west | Y | 0.000102 | 0.034268 | 0.00026766 | 0.021927 | 0.000102 | North | Y | 0.00026766 | 0.010768
1045 | CALENG1G | 1 | 70 | 0.018008 | west | N | 5.0046e-06 | 0.034171 | 0.00017066 | 0.02183 | 5.0046e-06 | North | Y | 0.00017066 | 0
1046 | CALENG2G | 2 | 73.4 | 0.018008 | west | N | 5.0046e-06 | 0.034171 | 0.00017066 | 0.02183 | 5.0046e-06 | North | Y | 0.00017066 | 0
1047 | CALENG3G | 3 | 70.4 | 0.018008 | west | N | 5.0046e-06 | 0.034171 | 0.00017066 | 0.02183 | 5.0046e-06 | North | Y | 0.00017066 | 0
1058 | LONGSHOR | 1 | 150 | 0.018045 | west | Y | 4.2005e-05 | 0.034208 | 0.00020766 | 0.021867 | 4.2005e-05 | North | Y | 0.00020766 | 0.024849
1058 | LONGSHOR | 2 | 220 | 0.018045 | west | Y | 4.2005e-05 | 0.034208 | 0.00020766 | 0.021867 | 4.2005e-05 | North | Y | 0.00020766 | 0.036445
1061 | CIELOGEN | 1 | 99 | 0.018163 | west | Y | 0.00016 | 0.034326 | 0.00032566 | 0.021985 | 0.00016 | North | Y | 0.00032566 | 0.0164
1062 | CIELOGEN | 1 | 61 | 0.018163 | west | Y | 0.00016 | 0.034326 | 0.00032566 | 0.021985 | 0.00016 | North | Y | 0.00032566 | 0.010105
1068 | SCURRYCW | 1 | 141 | 0.018158 | west | Y | 0.000155 | 0.034321 | 0.00032066 | 0.02198 | 0.000155 | North | Y | 0.00032066 | 0.023358
1069 | KINDERMG | 1 | 25 | 0.018163 | west | N | 0.00016 | 0.034326 | 0.00032566 | 0.021985 | 0.00016 | North | Y | 0.00032566 | 0
1070 | KINDERMG | 1 | 45.7 | 0.018163 | west | N | 0.00016 | 0.034326 | 0.00032566 | 0.021985 | 0.00016 | North | Y | 0.00032566 | 0
1071 | KINDERMG | 1 | 45.7 | 0.018163 | west | N | 0.00016 | 0.034326 | 0.00032566 | 0.021985 | 0.00016 | North | Y | 0.00032566 | 0
1073 | SCURRYCW | 2 | 120 | 0.018158 | west | Y | 0.000155 | 0.034321 | 0.00032066 | 0.02198 | 0.000155 | North | Y | 0.00032066 | 0.019879
1320 | BSP 1 | 1 | 25.8 | 0.017926 | west | N | -7.6995e-05 | 0.034089 | 8.8662e-05 | 0.021748 | 7.6995e-05 | North | Y | 8.8662e-05 | 0
1326 | STANTONW | 1 | 100.5 | 0.017866 | west | Y | -0.000137 | 0.034029 | 2.8662e-05 | 0.021688 | 2.8662e-05 | west | N | 2.8662e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.018001 | west | Y | -1.9954e-06 | 0.034164 | 0.00016366 | 0.021823 | 1.9954e-06 | North | Y | 0.00016366 | 0.0194
1328 | OCOTILLO | 1 | 58 | 0.017864 | west | Y | -0.000139 | 0.034027 | 2.6662e-05 | 0.021686 | 2.6662e-05 | west | N | 2.6662e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.017898 | west | Y | -0.000105 | 0.034061 | 6.0662e-05 | 0.02172 | 6.0662e-05 | west | N | 6.0662e-05 | 0
1343 | TRENTIPP | 1 | 150 | 0.01839 | west | Y | 0.000387 | 0.034553 | 0.00055266 | 0.022212 | 0.000387 | North | Y | 0.00055266 | 0.024849
1349 | WESTXWIN | 1 | 6.6 | 0.017759 | west | Y | -0.000244 | 0.033922 | -7.8338e-05 | 0.021581 | 7.8338e-05 | west | N | 7.8338e-05 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.017759 | west | Y | -0.000244 | 0.033922 | -7.8338e-05 | 0.021581 | 7.8338e-05 | west | N | 7.8338e-05 | 0
1354 | AEPWIND_ | 1 | 101 | 0.01839 | west | Y | 0.000387 | 0.034553 | 0.00055266 | 0.022212 | 0.000387 | North | Y | 0.00055266 | 0.016731
1360 | GUNSIGHT | 1 | 120 | 0.018009 | west | Y | 6.0046e-06 | 0.034172 | 0.00017166 | 0.021831 | 6.0046e-06 | North | Y | 0.00017166 | 0.019879
1432 | GRHAMSES | 2 | 366 | 0.01904 | north | Y | 0.001037 | 0.035203 | 0.0012027 | 0.022862 | 0.001037 | North | N | 0.001037 | 0
1433 | GRHAMSES | 1 | 242 | 0.019866 | north | Y | 0.001863 | 0.036029 | 0.0020287 | 0.023688 | 0.001863 | North | N | 0.001863 | 0
1437 | MESQUITW | 1 | 400 | 0.018599 | west | Y | 0.000596 | 0.034762 | 0.00076166 | 0.022421 | 0.000596 | North | Y | 0.00076166 | 0.066263
1438 | MESQUITW | 1 | 236 | 0.018599 | west | Y | 0.000596 | 0.034762 | 0.00076166 | 0.022421 | 0.000596 | North | Y | 0.00076166 | 0.039095
1442 | COKFIELD | 1 | 165 | 0.018705 | west | Y | 0.000702 | 0.034868 | 0.00086766 | 0.022527 | 0.000702 | North | Y | 0.00086766 | 0.027334
1453 | WCPWRCO_ | 1 | 204 | 0.01913 | north | Y | 0.001127 | 0.035293 | 0.0012927 | 0.022952 | 0.001127 | North | N | 0.001127 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.01913 | north | Y | 0.001127 | 0.035293 | 0.0012927 | 0.022952 | 0.001127 | North | N | 0.001127 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.01913 | north | Y | 0.001127 | 0.035293 | 0.0012927 | 0.022952 | 0.001127 | North | N | 0.001127 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.019229 | west | Y | 0.001226 | 0.035392 | 0.0013917 | 0.023051 | 0.001226 | North | Y | 0.0013917 | 0.0033132
1479 | WFCOGEN_ | 2 | 20 | 0.019229 | west | Y | 0.001226 | 0.035392 | 0.0013917 | 0.023051 | 0.001226 | North | Y | 0.0013917 | 0.0033132
1482 | WFCOGEN_ | 1 | 20 | 0.019229 | west | Y | 0.001226 | 0.035392 | 0.0013917 | 0.023051 | 0.001226 | North | Y | 0.0013917 | 0.0033132
1482 | WFCOGEN_ | 2 | 17 | 0.019229 | west | Y | 0.001226 | 0.035392 | 0.0013917 | 0.023051 | 0.001226 | North | Y | 0.0013917 | 0.0028162
1600 | BARTNWND | 1 | 120 | 0.021242 | north | Y | 0.003239 | 0.037405 | 0.0034047 | 0.025064 | 0.003239 | North | N | 0.003239 | 0
1643 | SLSTR1PP | 1 | 60 | 0.026661 | north | Y | 0.008658 | 0.042824 | 0.0088237 | 0.030483 | 0.008658 | North | N | 0.008658 | 0
1675 | PEC_1G | 1 | 75 | 0.017718 | north | N | -0.000285 | 0.033881 | -0.00011934 | 0.02154 | 0.00011934 | west | Y | 0.000285 | 0
1676 | PEC_2G | 2 | 79.6 | 0.017718 | north | N | -0.000285 | 0.033881 | -0.00011934 | 0.02154 | 0.00011934 | west | Y | 0.000285 | 0
1677 | PEC_3G | 3 | 88.4 | 0.017718 | north | N | -0.000285 | 0.033881 | -0.00011934 | 0.02154 | 0.00011934 | west | Y | 0.000285 | 0
1678 | LAMARPWR | 1 | 160 | 0.017738 | north | Y | -0.000265 | 0.033901 | -9.9338e-05 | 0.02156 | 9.9338e-05 | west | Y | 0.000265 | 0.026505
1679 | LAMARPWR | 2 | 156 | 0.017738 | north | Y | -0.000265 | 0.033901 | -9.9338e-05 | 0.02156 | 9.9338e-05 | west | Y | 0.000265 | 0.025843
1680 | LAMARPWR | 3 | 196 | 0.017738 | north | Y | -0.000265 | 0.033901 | -9.9338e-05 | 0.02156 | 9.9338e-05 | west | Y | 0.000265 | 0.032469
1681 | LAMARPWR | 4 | 156 | 0.017738 | north | Y | -0.000265 | 0.033901 | -9.9338e-05 | 0.02156 | 9.9338e-05 | west | Y | 0.000265 | 0.025843
1682 | LAMARPWR | 5 | 157 | 0.017738 | north | Y | -0.000265 | 0.033901 | -9.9338e-05 | 0.02156 | 9.9338e-05 | west | Y | 0.000265 | 0.026008
1683 | LAMARPWR | 6 | 198 | 0.017738 | north | Y | -0.000265 | 0.033901 | -9.9338e-05 | 0.02156 | 9.9338e-05 | west | Y | 0.000265 | 0.0328
1687 | VALLEY_1 | 1 | 170 | 0.017848 | north | Y | -0.000155 | 0.034011 | 1.0662e-05 | 0.02167 | 1.0662e-05 | west | Y | 0.000155 | 0.024537
1688 | VALLEY_2 | 2 | 520 | 0.017848 | north | Y | -0.000155 | 0.034011 | 1.0662e-05 | 0.02167 | 1.0662e-05 | west | Y | 0.000155 | 0.075053
1689 | VALLEY_3 | 3 | 370 | 0.017768 | north | Y | -0.000235 | 0.033931 | -6.9338e-05 | 0.02159 | 6.9338e-05 | west | Y | 0.000235 | 0.061293
1701 | MOSES_1G | 1 | 558 | 0.017682 | north | Y | -0.000321 | 0.033845 | -0.00015534 | 0.021504 | 0.00015534 | west | Y | 0.000321 | 0.092437
1702 | MOSES_2G | 2 | 579 | 0.017682 | north | Y | -0.000321 | 0.033845 | -0.00015534 | 0.021504 | 0.00015534 | west | Y | 0.000321 | 0.095916
1703 | MOSES_3G | 3 | 808 | 0.017682 | north | Y | -0.000321 | 0.033845 | -0.00015534 | 0.021504 | 0.00015534 | west | Y | 0.000321 | 0.13385
1861 | EAGLEMNT | MB | 112 | 0.019293 | north | Y | 0.00129 | 0.035456 | 0.0014557 | 0.023115 | 0.00129 | North | N | 0.00129 | 0
1862 | EAGLEMNT | MB | 100 | 0.019293 | north | Y | 0.00129 | 0.035456 | 0.0014557 | 0.023115 | 0.00129 | North | N | 0.00129 | 0
1863 | EAGLEMNT | MB | 378 | 0.019293 | north | Y | 0.00129 | 0.035456 | 0.0014557 | 0.023115 | 0.00129 | North | N | 0.00129 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.019927 | north | Y | 0.001924 | 0.03609 | 0.0020897 | 0.023749 | 0.001924 | North | N | 0.001924 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.019927 | north | Y | 0.001924 | 0.03609 | 0.0020897 | 0.023749 | 0.001924 | North | N | 0.001924 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.019927 | north | Y | 0.001924 | 0.03609 | 0.0020897 | 0.023749 | 0.001924 | North | N | 0.001924 | 0
1889 | DECRDOVA | MB | 770 | 0.020168 | north | Y | 0.002165 | 0.036331 | 0.0023307 | 0.02399 | 0.002165 | North | N | 0.002165 | 0
1892 | DECRDOVA | A | 70 | 0.023373 | north | Y | 0.00537 | 0.039536 | 0.0055357 | 0.027195 | 0.00537 | North | N | 0.00537 | 0
1893 | DECRDOVA | B | 69 | 0.023373 | north | Y | 0.00537 | 0.039536 | 0.0055357 | 0.027195 | 0.00537 | North | N | 0.00537 | 0
1894 | DECRDOVA | C | 69 | 0.023373 | north | Y | 0.00537 | 0.039536 | 0.0055357 | 0.027195 | 0.00537 | North | N | 0.00537 | 0
1895 | DECRDOVA | D | 68 | 0.023373 | north | Y | 0.00537 | 0.039536 | 0.0055357 | 0.027195 | 0.00537 | North | N | 0.00537 | 0
1898 | COMCHEPK | 1 | 1157 | 0.020035 | north | N | 0.002032 | 0.036198 | 0.0021977 | 0.023857 | 0.002032 | North | N | 0.002032 | 0
1899 | COMCHEPK | 2 | 1158 | 0.020035 | north | N | 0.002032 | 0.036198 | 0.0021977 | 0.023857 | 0.002032 | North | N | 0.002032 | 0
1937 | MDLTHELP | 5 | 224 | 0.019548 | north | Y | 0.001545 | 0.035711 | 0.0017107 | 0.02337 | 0.001545 | North | N | 0.001545 | 0
1938 | MDLTHELP | 6 | 226 | 0.019548 | north | Y | 0.001545 | 0.035711 | 0.0017107 | 0.02337 | 0.001545 | North | N | 0.001545 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.018649 | north | Y | 0.000646 | 0.034812 | 0.00081166 | 0.022471 | 0.000646 | North | N | 0.000646 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.018649 | north | Y | 0.000646 | 0.034812 | 0.00081166 | 0.022471 | 0.000646 | North | N | 0.000646 | 0
1943 | MDLTHELP | 3 | 212 | 0.019548 | north | Y | 0.001545 | 0.035711 | 0.0017107 | 0.02337 | 0.001545 | North | N | 0.001545 | 0
1944 | MDLTHELP | 4 | 211 | 0.019548 | north | Y | 0.001545 | 0.035711 | 0.0017107 | 0.02337 | 0.001545 | North | N | 0.001545 | 0
1947 | HANDLEY_ | 3 | 395 | 0.019253 | north | Y | 0.00125 | 0.035416 | 0.0014157 | 0.023075 | 0.00125 | North | N | 0.00125 | 0
1948 | HANDLEY_ | 4 | 435 | 0.019261 | north | Y | 0.001258 | 0.035424 | 0.0014237 | 0.023083 | 0.001258 | North | N | 0.001258 | 0
1949 | HANDLEY_ | 5 | 435 | 0.019253 | north | Y | 0.00125 | 0.035416 | 0.0014157 | 0.023075 | 0.00125 | North | N | 0.00125 | 0
2371 | COLLIN_1 | MB | 138 | 0.018058 | north | Y | 5.5005e-05 | 0.034221 | 0.00022066 | 0.02188 | 5.5005e-05 | North | N | 5.5005e-05 | 0
2413 | MTCK6_G | 6 | 118 | 0.018137 | north | Y | 0.000134 | 0.0343 | 0.00029966 | 0.021959 | 0.000134 | North | N | 0.000134 | 0
2414 | MTCK7_G | 7 | 115 | 0.018137 | north | Y | 0.000134 | 0.0343 | 0.00029966 | 0.021959 | 0.000134 | North | N | 0.000134 | 0
2417 | MTCK8_G | 8 | 556 | 0.018137 | north | Y | 0.000134 | 0.0343 | 0.00029966 | 0.021959 | 0.000134 | North | N | 0.000134 | 0
2451 | LKHB1_G | 1 | 388 | 0.017598 | north | Y | -0.000405 | 0.033761 | -0.00023934 | 0.02142 | 0.00023934 | west | Y | 0.000405 | 0.064275
2452 | LKHB2_G | 2 | 515 | 0.017598 | north | Y | -0.000405 | 0.033761 | -0.00023934 | 0.02142 | 0.00023934 | west | Y | 0.000405 | 0.085314
3097 | MARTLAKE | 1 | 785 | 0.015955 | north | Y | -0.002048 | 0.032118 | -0.0018823 | 0.019777 | 0.0018823 | west | Y | 0.002048 | 0.13004
3098 | MARTLAKE | 2 | 795 | 0.015955 | north | Y | -0.002048 | 0.032118 | -0.0018823 | 0.019777 | 0.0018823 | west | Y | 0.002048 | 0.1317
3099 | MARTLAKE | 3 | 780 | 0.015955 | north | Y | -0.002048 | 0.032118 | -0.0018823 | 0.019777 | 0.0018823 | west | Y | 0.002048 | 0.12921
3107 | STRYKER_ | 1 | 182 | 0.015332 | north | Y | -0.002671 | 0.031495 | -0.0025053 | 0.019154 | 0.0025053 | west | Y | 0.002671 | 0.03015
3108 | STRYKER_ | 2 | 484 | 0.015332 | north | Y | -0.002671 | 0.031495 | -0.0025053 | 0.019154 | 0.0025053 | west | Y | 0.002671 | 0.080178
3126 | TRINIDAD | 1 | 224 | 0.019122 | north | Y | 0.001119 | 0.035285 | 0.0012847 | 0.022944 | 0.001119 | North | N | 0.001119 | 0
3309 | ASPN_G | 1 | 50 | 0.015523 | north | Y | -0.00248 | 0.031686 | -0.0023143 | 0.019345 | 0.0023143 | west | Y | 0.00248 | 0.0082829
3348 | CHAMPION | MB | 42 | 0.015539 | north | N | -0.002464 | 0.031702 | -0.0022983 | 0.019361 | 0.0022983 | west | Y | 0.002464 | 0
3381 | BBRN_1G | 1 | 615 | 0.013267 | north | Y | -0.004736 | 0.02943 | -0.0045703 | 0.017089 | 0.0045703 | west | Y | 0.004736 | 0.10188
3382 | BBRN_2G | 2 | 587 | 0.013267 | north | Y | -0.004736 | 0.02943 | -0.0045703 | 0.017089 | 0.0045703 | west | Y | 0.004736 | 0.097241
3403 | THOUSE_1 | MB | 537 | 0.023155 | north | Y | 0.005152 | 0.039318 | 0.0053177 | 0.026977 | 0.005152 | North | N | 0.005152 | 0
3404 | THOUSE_2 | 2 | 787 | 0.023155 | north | Y | 0.005152 | 0.039318 | 0.0053177 | 0.026977 | 0.005152 | North | N | 0.005152 | 0
3416 | LAKE_CRK | MB | 75 | -0.055032 | north | Y | -0.073035 | -0.038869 | -0.072869 | -0.05121 | 0.038869 | south | Y | 0.073035 | 0
3417 | LAKE_CRK | MB | 222 | -0.055032 | north | Y | -0.073035 | -0.038869 | -0.072869 | -0.05121 | 0.038869 | south | Y | 0.073035 | 0
3432 | SANDOW_4 | 4 | 569 | -0.024592 | south | Y | -0.042595 | -0.0084285 | -0.042429 | -0.02077 | 0.0084285 | south | N | 0.0084285 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.01533 | south | Y | -0.033333 | 0.00083348 | -0.033167 | -0.011508 | 0.00083348 | south | N | 0.00083348 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.01533 | south | Y | -0.033333 | 0.00083348 | -0.033167 | -0.011508 | 0.00083348 | south | N | 0.00083348 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.015318 | south | Y | -0.033321 | 0.00084548 | -0.033155 | -0.011496 | 0.00084548 | south | N | 0.00084548 | 0
5031 | BRA_VHBC | 1 | 46 | -0.01533 | south | Y | -0.033333 | 0.00083348 | -0.033167 | -0.011508 | 0.00083348 | south | N | 0.00083348 | 0
5032 | BRA_VHBC | 2 | 47 | -0.01533 | south | Y | -0.033333 | 0.00083348 | -0.033167 | -0.011508 | 0.00083348 | south | N | 0.00083348 | 0
5033 | BRA_VHBC | 3 | 46 | -0.01533 | south | Y | -0.033333 | 0.00083348 | -0.033167 | -0.011508 | 0.00083348 | south | N | 0.00083348 | 0
5034 | BRA_VHBC | 4 | 46 | -0.01533 | south | Y | -0.033333 | 0.00083348 | -0.033167 | -0.011508 | 0.00083348 | south | N | 0.00083348 | 0
5111 | CALAVER_ | 1 | 424 | -0.01536 | south | Y | -0.033363 | 0.00080348 | -0.033197 | -0.011538 | 0.00080348 | south | N | 0.00080348 | 0
5112 | CALAVER_ | 2 | 425 | -0.01536 | south | Y | -0.033363 | 0.00080348 | -0.033197 | -0.011538 | 0.00080348 | south | N | 0.00080348 | 0
5264 | LEON_LCP | 3 | 58 | -0.01522 | south | Y | -0.033223 | 0.00094348 | -0.033057 | -0.011398 | 0.00094348 | south | N | 0.00094348 | 0
5265 | LEON_LCP | 4 | 89 | -0.01522 | south | Y | -0.033223 | 0.00094348 | -0.033057 | -0.011398 | 0.00094348 | south | N | 0.00094348 | 0
5266 | LEON_LCP | 1 | 44 | -0.01522 | south | Y | -0.033223 | 0.00094348 | -0.033057 | -0.011398 | 0.00094348 | south | N | 0.00094348 | 0
5267 | LEON_LCP | 2 | 44 | -0.01522 | south | Y | -0.033223 | 0.00094348 | -0.033057 | -0.011398 | 0.00094348 | south | N | 0.00094348 | 0
5268 | LEON_LCP | 3 | 43 | -0.01522 | south | Y | -0.033223 | 0.00094348 | -0.033057 | -0.011398 | 0.00094348 | south | N | 0.00094348 | 0
5269 | LEON_LCP | 4 | 45 | -0.01522 | south | Y | -0.033223 | 0.00094348 | -0.033057 | -0.011398 | 0.00094348 | south | N | 0.00094348 | 0
5396 | CALAVER_ | 1 | 412 | -0.015347 | south | Y | -0.03335 | 0.00081648 | -0.033184 | -0.011525 | 0.00081648 | south | N | 0.00081648 | 0
5397 | CALAVER_ | 2 | 400 | -0.015347 | south | Y | -0.03335 | 0.00081648 | -0.033184 | -0.011525 | 0.00081648 | south | N | 0.00081648 | 0
5401 | CALAVER_ | 1 | 546 | -0.015232 | south | Y | -0.033235 | 0.00093148 | -0.033069 | -0.01141 | 0.00093148 | south | N | 0.00093148 | 0
5402 | CALAVER_ | 2 | 750 | -0.015232 | south | Y | -0.033235 | 0.00093148 | -0.033069 | -0.01141 | 0.00093148 | south | N | 0.00093148 | 0
5436 | TUTTL_WB | MB | 61 | -0.015412 | south | Y | -0.033415 | 0.00075148 | -0.033249 | -0.01159 | 0.00075148 | south | N | 0.00075148 | 0
5438 | TUTTL_WB | MB | 95 | -0.015412 | south | Y | -0.033415 | 0.00075148 | -0.033249 | -0.01159 | 0.00075148 | south | N | 0.00075148 | 0
5439 | TUTTL_WB | MB | 151 | -0.015412 | south | Y | -0.033415 | 0.00075148 | -0.033249 | -0.01159 | 0.00075148 | south | N | 0.00075148 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.015306 | south | Y | -0.033309 | 0.00085748 | -0.033143 | -0.011484 | 0.00085748 | south | N | 0.00085748 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.015306 | south | Y | -0.033309 | 0.00085748 | -0.033143 | -0.011484 | 0.00085748 | south | N | 0.00085748 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.015306 | south | Y | -0.033309 | 0.00085748 | -0.033143 | -0.011484 | 0.00085748 | south | N | 0.00085748 | 0
5503 | RAYBURNG | 1 | 22 | -0.012382 | south | Y | -0.030385 | 0.0037815 | -0.030219 | -0.0085602 | 0.0037815 | south | N | 0.0037815 | 0
5505 | RAYBURNG | 1 | 11 | -0.012382 | south | Y | -0.030385 | 0.0037815 | -0.030219 | -0.0085602 | 0.0037815 | south | N | 0.0037815 | 0
5506 | RAYBURNG | 1 | 11 | -0.012382 | south | Y | -0.030385 | 0.0037815 | -0.030219 | -0.0085602 | 0.0037815 | south | N | 0.0037815 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.012501 | south | Y | -0.030504 | 0.0036625 | -0.030338 | -0.0086792 | 0.0036625 | south | N | 0.0036625 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.012501 | south | Y | -0.030504 | 0.0036625 | -0.030338 | -0.0086792 | 0.0036625 | south | N | 0.0036625 | 0
5511 | RAYBURNC | 1 | 46 | -0.012501 | south | Y | -0.030504 | 0.0036625 | -0.030338 | -0.0086792 | 0.0036625 | south | N | 0.0036625 | 0
5512 | RAYBURNC | 1 | 48 | -0.012501 | south | Y | -0.030504 | 0.0036625 | -0.030338 | -0.0086792 | 0.0036625 | south | N | 0.0036625 | 0
5728 | FALCONHY | 2 | 12 | -0.012946 | south | N | -0.030949 | 0.0032175 | -0.030783 | -0.0091242 | 0.0032175 | south | N | 0.0032175 | 0
5729 | FALCONHY | 3 | 11 | -0.012946 | south | N | -0.030949 | 0.0032175 | -0.030783 | -0.0091242 | 0.0032175 | south | N | 0.0032175 | 0
5890 | PEARSALL | 1 | 24 | -0.013293 | south | Y | -0.031296 | 0.0028705 | -0.03113 | -0.0094712 | 0.0028705 | south | N | 0.0028705 | 0
5891 | PEARSALL | 1 | 24 | -0.013293 | south | Y | -0.031296 | 0.0028705 | -0.03113 | -0.0094712 | 0.0028705 | south | N | 0.0028705 | 0
5892 | PEARSALL | 1 | 23 | -0.013293 | south | Y | -0.031296 | 0.0028705 | -0.03113 | -0.0094712 | 0.0028705 | south | N | 0.0028705 | 0
5903 | SANMIGUE | 1 | 396 | -0.014386 | south | Y | -0.032389 | 0.0017775 | -0.032223 | -0.010564 | 0.0017775 | south | N | 0.0017775 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.008123 | houston | N | -0.026126 | 0.0080405 | -0.02596 | -0.0043012 | 0.0043012 | houston | N | 0.0043012 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.008123 | houston | N | -0.026126 | 0.0080405 | -0.02596 | -0.0043012 | 0.0043012 | houston | N | 0.0043012 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.018003 | 0
5932 | SI_RAY9 | 9 | 38 | -0.012817 | south | Y | -0.03082 | 0.0033465 | -0.030654 | -0.0089952 | 0.0033465 | south | N | 0.0033465 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.012817 | south | Y | -0.03082 | 0.0033465 | -0.030654 | -0.0089952 | 0.0033465 | south | N | 0.0033465 | 0
5934 | SI_RAY5 | 5 | 15 | -0.012817 | south | Y | -0.03082 | 0.0033465 | -0.030654 | -0.0089952 | 0.0033465 | south | N | 0.0033465 | 0
5935 | SI_RAY10 | 10 | 47 | -0.012817 | south | Y | -0.03082 | 0.0033465 | -0.030654 | -0.0089952 | 0.0033465 | south | N | 0.0033465 | 0
6016 | SWMESA | 1 | 75 | 0.016263 | west | Y | -0.00174 | 0.032426 | -0.0015743 | 0.020085 | 0.0015743 | west | N | 0.0015743 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.017837 | 0
6144 | MCADOO1A | 1 | 150 | 0.018438 | west | Y | 0.000435 | 0.034601 | 0.00060066 | 0.02226 | 0.000435 | North | Y | 0.00060066 | 0.024849
6407 | TURKTRAK | 1 | 169.5 | 0.0177 | west | Y | -0.000303 | 0.033863 | -0.00013734 | 0.021522 | 0.00013734 | west | N | 0.00013734 | 0
6476 | LANGFORD | 1 | 150 | 0.010529 | west | Y | -0.007474 | 0.026692 | -0.0073083 | 0.014351 | 0.0073083 | west | N | 0.0073083 | 0
6637 | SNYDERW1 | 1 | 63 | 0.018145 | west | Y | 0.000142 | 0.034308 | 0.00030766 | 0.021967 | 0.000142 | North | Y | 0.00030766 | 0.010436
6752 | OKLA0A | 1 | 649.7 | 0.018843 | west | Y | 0.00084 | 0.035006 | 0.0010057 | 0.022665 | 0.00084 | North | Y | 0.0010057 | 0.10763
6948 | DENISNDM | 1 | 40 | 0.017909 | north | N | -9.3995e-05 | 0.034072 | 7.1662e-05 | 0.021731 | 7.1662e-05 | west | Y | 9.3995e-05 | 0
6948 | DENISNDM | 2 | 40 | 0.017909 | north | N | -9.3995e-05 | 0.034072 | 7.1662e-05 | 0.021731 | 7.1662e-05 | west | Y | 9.3995e-05 | 0
7000 | L_FERGUS | 1 | 422 | -0.017388 | south | Y | -0.035391 | -0.0012245 | -0.035225 | -0.013566 | 0.0012245 | south | N | 0.0012245 | 0
7004 | L_SIMGID | 1 | 132 | -0.019631 | south | Y | -0.037634 | -0.0034675 | -0.037468 | -0.015809 | 0.0034675 | south | N | 0.0034675 | 0
7005 | L_SIMGID | 2 | 134 | -0.019631 | south | Y | -0.037634 | -0.0034675 | -0.037468 | -0.015809 | 0.0034675 | south | N | 0.0034675 | 0
7006 | L_SIMGID | 3 | 323 | -0.019631 | south | Y | -0.037634 | -0.0034675 | -0.037468 | -0.015809 | 0.0034675 | south | N | 0.0034675 | 0
7007 | L_LOSTPI | 1 | 158 | -0.019426 | south | Y | -0.037429 | -0.0032625 | -0.037263 | -0.015604 | 0.0032625 | south | N | 0.0032625 | 0
7008 | L_LOSTPI | 2 | 160 | -0.019426 | south | Y | -0.037429 | -0.0032625 | -0.037263 | -0.015604 | 0.0032625 | south | N | 0.0032625 | 0
7009 | L_LOSTPI | 3 | 175 | -0.019426 | south | Y | -0.037429 | -0.0032625 | -0.037263 | -0.015604 | 0.0032625 | south | N | 0.0032625 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.017378 | south | Y | -0.035381 | -0.0012145 | -0.035215 | -0.013556 | 0.0012145 | south | N | 0.0012145 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.017378 | south | Y | -0.035381 | -0.0012145 | -0.035215 | -0.013556 | 0.0012145 | south | N | 0.0012145 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.017361 | south | Y | -0.035364 | -0.0011975 | -0.035198 | -0.013539 | 0.0011975 | south | N | 0.0011975 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.016957 | south | Y | -0.03496 | -0.00079352 | -0.034794 | -0.013135 | 0.00079352 | south | N | 0.00079352 | 0
7015 | L_HAYSEN | 2 | 225 | -0.016957 | south | Y | -0.03496 | -0.00079352 | -0.034794 | -0.013135 | 0.00079352 | south | N | 0.00079352 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.016957 | south | Y | -0.03496 | -0.00079352 | -0.034794 | -0.013135 | 0.00079352 | south | N | 0.00079352 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.016957 | south | Y | -0.03496 | -0.00079352 | -0.034794 | -0.013135 | 0.00079352 | south | N | 0.00079352 | 0
7020 | L_AUSTPL | 1 | 8 | -0.020454 | south | N | -0.038457 | -0.0042905 | -0.038291 | -0.016632 | 0.0042905 | south | N | 0.0042905 | 0
7020 | L_AUSTPL | 2 | 8 | -0.020454 | south | N | -0.038457 | -0.0042905 | -0.038291 | -0.016632 | 0.0042905 | south | N | 0.0042905 | 0
7022 | L_BUCHAN | 1 | 18 | -0.017366 | south | N | -0.035369 | -0.0012025 | -0.035203 | -0.013544 | 0.0012025 | south | N | 0.0012025 | 0
7023 | L_BUCHAN | 2 | 18 | -0.017366 | south | N | -0.035369 | -0.0012025 | -0.035203 | -0.013544 | 0.0012025 | south | N | 0.0012025 | 0
7024 | L_BUCHAN | 3 | 15 | -0.017366 | south | N | -0.035369 | -0.0012025 | -0.035203 | -0.013544 | 0.0012025 | south | N | 0.0012025 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.017019 | south | N | -0.035022 | -0.00085552 | -0.034856 | -0.013197 | 0.00085552 | south | N | 0.00085552 | 0
7028 | L_MARBFA | 1 | 18 | -0.018124 | south | N | -0.036127 | -0.0019605 | -0.035961 | -0.014302 | 0.0019605 | south | N | 0.0019605 | 0
7029 | L_MARBFA | 2 | 18 | -0.018124 | south | N | -0.036127 | -0.0019605 | -0.035961 | -0.014302 | 0.0019605 | south | N | 0.0019605 | 0
7031 | L_MARSFO | 1 | 35 | -0.019795 | south | N | -0.037798 | -0.0036315 | -0.037632 | -0.015973 | 0.0036315 | south | N | 0.0036315 | 0
7032 | L_MARSFO | 2 | 34 | -0.019795 | south | N | -0.037798 | -0.0036315 | -0.037632 | -0.015973 | 0.0036315 | south | N | 0.0036315 | 0
7033 | L_MARSFO | 3 | 35 | -0.019795 | south | N | -0.037798 | -0.0036315 | -0.037632 | -0.015973 | 0.0036315 | south | N | 0.0036315 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.017546 | south | N | -0.035549 | -0.0013825 | -0.035383 | -0.013724 | 0.0013825 | south | N | 0.0013825 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.017546 | south | N | -0.035549 | -0.0013825 | -0.035383 | -0.013724 | 0.0013825 | south | N | 0.0013825 | 0
7038 | L_DELAWA | 1 | 35 | 0.017616 | west | Y | -0.000387 | 0.033779 | -0.00022134 | 0.021438 | 0.00022134 | west | N | 0.00022134 | 0
7038 | L_DELAWA | 2 | 30 | 0.017616 | west | Y | -0.000387 | 0.033779 | -0.00022134 | 0.021438 | 0.00022134 | west | N | 0.00022134 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.017748 | south | Y | -0.035751 | -0.0015845 | -0.035585 | -0.013926 | 0.0015845 | south | N | 0.0015845 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.017748 | south | Y | -0.035751 | -0.0015845 | -0.035585 | -0.013926 | 0.0015845 | south | N | 0.0015845 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.017748 | south | Y | -0.035751 | -0.0015845 | -0.035585 | -0.013926 | 0.0015845 | south | N | 0.0015845 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.017748 | south | Y | -0.035751 | -0.0015845 | -0.035585 | -0.013926 | 0.0015845 | south | N | 0.0015845 | 0
7487 | L_CANYHY | 1 | 6 | -0.017456 | south | N | -0.035459 | -0.0012925 | -0.035293 | -0.013634 | 0.0012925 | south | N | 0.0012925 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.016454 | south | N | -0.034457 | -0.00029052 | -0.034291 | -0.012632 | 0.00029052 | south | N | 0.00029052 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.016454 | south | N | -0.034457 | -0.00029052 | -0.034291 | -0.012632 | 0.00029052 | south | N | 0.00029052 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.016454 | south | N | -0.034457 | -0.00029052 | -0.034291 | -0.012632 | 0.00029052 | south | N | 0.00029052 | 0
7609 | L_SCHUMA | 1 | 4 | -0.01619 | south | N | -0.034193 | -2.6519e-05 | -0.034027 | -0.012368 | 2.6519e-05 | south | N | 2.6519e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.016266 | south | N | -0.034269 | -0.00010252 | -0.034103 | -0.012444 | 0.00010252 | south | N | 0.00010252 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.016266 | south | N | -0.034269 | -0.00010252 | -0.034103 | -0.012444 | 0.00010252 | south | N | 0.00010252 | 0
7800 | L_GUADGE | 1 | 147 | -0.015772 | south | Y | -0.033775 | 0.00039148 | -0.033609 | -0.01195 | 0.00039148 | south | N | 0.00039148 | 0
7801 | L_GUADGE | 2 | 138 | -0.015772 | south | Y | -0.033775 | 0.00039148 | -0.033609 | -0.01195 | 0.00039148 | south | N | 0.00039148 | 0
7802 | L_GUADGE | 3 | 140 | -0.015772 | south | Y | -0.033775 | 0.00039148 | -0.033609 | -0.01195 | 0.00039148 | south | N | 0.00039148 | 0
7803 | L_GUADGE | 4 | 147 | -0.015772 | south | Y | -0.033775 | 0.00039148 | -0.033609 | -0.01195 | 0.00039148 | south | N | 0.00039148 | 0
7804 | L_GUADGE | 5 | 182 | -0.015772 | south | Y | -0.033775 | 0.00039148 | -0.033609 | -0.01195 | 0.00039148 | south | N | 0.00039148 | 0
7805 | L_GUADGE | 6 | 198 | -0.015772 | south | Y | -0.033775 | 0.00039148 | -0.033609 | -0.01195 | 0.00039148 | south | N | 0.00039148 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.0196 | south | Y | -0.037603 | -0.0034365 | -0.037437 | -0.015778 | 0.0034365 | south | N | 0.0034365 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.0196 | south | Y | -0.037603 | -0.0034365 | -0.037437 | -0.015778 | 0.0034365 | south | N | 0.0034365 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.0196 | south | Y | -0.037603 | -0.0034365 | -0.037437 | -0.015778 | 0.0034365 | south | N | 0.0034365 | 0
7810 | L_RIONOG | 1 | 142 | -0.016351 | south | Y | -0.034354 | -0.00018752 | -0.034188 | -0.012529 | 0.00018752 | south | N | 0.00018752 | 0
7811 | L_RIONOG | 2 | 145 | -0.016351 | south | Y | -0.034354 | -0.00018752 | -0.034188 | -0.012529 | 0.00018752 | south | N | 0.00018752 | 0
7812 | L_RIONOG | 3 | 151 | -0.016351 | south | Y | -0.034354 | -0.00018752 | -0.034188 | -0.012529 | 0.00018752 | south | N | 0.00018752 | 0
7813 | L_RIONOG | 4 | 290 | -0.016351 | south | Y | -0.034354 | -0.00018752 | -0.034188 | -0.012529 | 0.00018752 | south | N | 0.00018752 | 0
8032 | AMISTADH | 1 | 33 | -0.005202 | south | N | -0.023205 | 0.010961 | -0.023039 | -0.0013802 | 0.0013802 | houston | Y | 0.010961 | 0
8033 | AMISTADH | 2 | 25 | -0.005202 | south | N | -0.023205 | 0.010961 | -0.023039 | -0.0013802 | 0.0013802 | houston | Y | 0.010961 | 0
8048 | FALCONHY | 1 | 12 | -0.012946 | south | N | -0.030949 | 0.0032175 | -0.030783 | -0.0091242 | 0.0032175 | south | N | 0.0032175 | 0
8066 | DUP1V#1 | 1 | 73 | -0.012535 | south | N | -0.030538 | 0.0036285 | -0.030372 | -0.0087132 | 0.0036285 | south | N | 0.0036285 | 0
8134 | FOR69CG0 | 1 | 79 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
8138 | FOR69CG0 | 2 | 81 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.016163 | 0
8147 | UCAR #2 | 10 | 28 | -0.012155 | south | N | -0.030158 | 0.0040085 | -0.029992 | -0.0083332 | 0.0040085 | south | N | 0.0040085 | 0
8148 | UCAR #1 | 2 | 7 | -0.012155 | south | N | -0.030158 | 0.0040085 | -0.029992 | -0.0083332 | 0.0040085 | south | N | 0.0040085 | 0
8153 | FOR69CG0 | 3 | 79 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
8154 | FOR69CG0 | 4 | 80 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
8156 | FOR69CG0 | 6 | 25 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
8157 | FOR69CG0 | 7 | 46 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
8161 | COLETOU1 | 1 | 629 | -0.013243 | south | Y | -0.031246 | 0.0029205 | -0.03108 | -0.0094212 | 0.0029205 | south | N | 0.0029205 | 0
8173 | VICEC51A | 5 | 144 | -0.012673 | south | Y | -0.030676 | 0.0034905 | -0.03051 | -0.0088512 | 0.0034905 | south | N | 0.0034905 | 0
8174 | VICEC61A | 6 | 188 | -0.012673 | south | Y | -0.030676 | 0.0034905 | -0.03051 | -0.0088512 | 0.0034905 | south | N | 0.0034905 | 0
8189 | CUERO 2 | 1 | 12 | -0.015279 | south | N | -0.033282 | 0.00088448 | -0.033116 | -0.011457 | 0.00088448 | south | N | 0.00088448 | 0
8262 | ELPS | 1 | 6 | -0.007731 | south | N | -0.025734 | 0.0084325 | -0.025568 | -0.0039092 | 0.0039092 | houston | Y | 0.0084325 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.016163 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.016163 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.016163 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.016163 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.016163 | 0
8442 | NBEC71A | 1 | 336 | -0.012691 | south | Y | -0.030694 | 0.0034725 | -0.030528 | -0.0088692 | 0.0034725 | south | N | 0.0034725 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.016163 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.018003 | 0.016163 | -0.017837 | 0.0038218 | 0.0038218 | houston | Y | 0.016163 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.012719 | south | Y | -0.030722 | 0.0034445 | -0.030556 | -0.0088972 | 0.0034445 | south | N | 0.0034445 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.012719 | south | Y | -0.030722 | 0.0034445 | -0.030556 | -0.0088972 | 0.0034445 | south | N | 0.0034445 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.012736 | south | N | -0.030739 | 0.0034275 | -0.030573 | -0.0089142 | 0.0034275 | south | N | 0.0034275 | 0
8506 | VAL #1 | 1 | 25 | -0.012723 | south | N | -0.030726 | 0.0034405 | -0.03056 | -0.0089012 | 0.0034405 | south | N | 0.0034405 | 0
8507 | VAL #2 | 2 | 25 | -0.012723 | south | N | -0.030726 | 0.0034405 | -0.03056 | -0.0089012 | 0.0034405 | south | N | 0.0034405 | 0
8511 | OXY_CC0A | 1 | 38 | -0.012736 | south | N | -0.030739 | 0.0034275 | -0.030573 | -0.0089142 | 0.0034275 | south | N | 0.0034275 | 0
8517 | CELANEBI | 1 | 29 | -0.012793 | south | N | -0.030796 | 0.0033705 | -0.03063 | -0.0089712 | 0.0033705 | south | N | 0.0033705 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.012693 | south | N | -0.030696 | 0.0034705 | -0.03053 | -0.0088712 | 0.0034705 | south | N | 0.0034705 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.012693 | south | N | -0.030696 | 0.0034705 | -0.03053 | -0.0088712 | 0.0034705 | south | N | 0.0034705 | 0
8562 | CNOPST1 | 3 | 153 | -0.012693 | south | N | -0.030696 | 0.0034705 | -0.03053 | -0.0088712 | 0.0034705 | south | N | 0.0034705 | 0
8926 | LGE_GT10 | 1 | 158 | -0.012567 | south | N | -0.03057 | 0.0035965 | -0.030404 | -0.0087452 | 0.0035965 | south | N | 0.0035965 | 0
8927 | LGE_GT20 | 2 | 153 | -0.012567 | south | N | -0.03057 | 0.0035965 | -0.030404 | -0.0087452 | 0.0035965 | south | N | 0.0035965 | 0
8928 | LGE_STG0 | 3 | 100 | -0.012567 | south | N | -0.03057 | 0.0035965 | -0.030404 | -0.0087452 | 0.0035965 | south | N | 0.0035965 | 0
8930 | ICPGN10A | 1 | 145 | -0.012567 | south | N | -0.03057 | 0.0035965 | -0.030404 | -0.0087452 | 0.0035965 | south | N | 0.0035965 | 0
8931 | ICPGN20A | 2 | 147 | -0.012567 | south | N | -0.03057 | 0.0035965 | -0.030404 | -0.0087452 | 0.0035965 | south | N | 0.0035965 | 0
8932 | ICPGN30A | 3 | 127 | -0.012567 | south | N | -0.03057 | 0.0035965 | -0.030404 | -0.0087452 | 0.0035965 | south | N | 0.0035965 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.01285 | south | Y | -0.030853 | 0.0033135 | -0.030687 | -0.0090282 | 0.0033135 | south | N | 0.0033135 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.01285 | south | Y | -0.030853 | 0.0033135 | -0.030687 | -0.0090282 | 0.0033135 | south | N | 0.0033135 | 0
8935 | FGNTS201 | 3 | 173 | -0.01285 | south | Y | -0.030853 | 0.0033135 | -0.030687 | -0.0090282 | 0.0033135 | south | N | 0.0033135 | 0
8936 | MVGN#1 | 1 | 207 | -0.012835 | south | Y | -0.030838 | 0.0033285 | -0.030672 | -0.0090132 | 0.0033285 | south | N | 0.0033285 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.012835 | south | Y | -0.030838 | 0.0033285 | -0.030672 | -0.0090132 | 0.0033285 | south | N | 0.0033285 | 0
8938 | MVGN#3 | 3 | 242 | -0.012835 | south | Y | -0.030838 | 0.0033285 | -0.030672 | -0.0090132 | 0.0033285 | south | N | 0.0033285 | 0
8981 | HECN1 | 1 | 144 | -0.012835 | south | Y | -0.030838 | 0.0033285 | -0.030672 | -0.0090132 | 0.0033285 | south | N | 0.0033285 | 0
8982 | HECN2 | 2 | 144 | -0.012835 | south | Y | -0.030838 | 0.0033285 | -0.030672 | -0.0090132 | 0.0033285 | south | N | 0.0033285 | 0
8983 | HECN3 | 3 | 171 | -0.012835 | south | Y | -0.030838 | 0.0033285 | -0.030672 | -0.0090132 | 0.0033285 | south | N | 0.0033285 | 0
9000 | DECKR_G1 | 1 | 310 | -0.020503 | south | Y | -0.038506 | -0.0043395 | -0.03834 | -0.016681 | 0.0043395 | south | N | 0.0043395 | 0
9001 | DECKR_G2 | 2 | 413 | -0.020503 | south | Y | -0.038506 | -0.0043395 | -0.03834 | -0.016681 | 0.0043395 | south | N | 0.0043395 | 0
9002 | DECKR_G3 | 3 | 42 | -0.020718 | south | Y | -0.038721 | -0.0045545 | -0.038555 | -0.016896 | 0.0045545 | south | N | 0.0045545 | 0
9003 | DECKR_G4 | 4 | 44 | -0.020718 | south | Y | -0.038721 | -0.0045545 | -0.038555 | -0.016896 | 0.0045545 | south | N | 0.0045545 | 0
9004 | DECKR_G5 | 5 | 44 | -0.020718 | south | Y | -0.038721 | -0.0045545 | -0.038555 | -0.016896 | 0.0045545 | south | N | 0.0045545 | 0
9005 | DECKR_G6 | 6 | 47 | -0.020718 | south | Y | -0.038721 | -0.0045545 | -0.038555 | -0.016896 | 0.0045545 | south | N | 0.0045545 | 0
9016 | SANDH_G1 | 1 | 49 | -0.020229 | south | Y | -0.038232 | -0.0040655 | -0.038066 | -0.016407 | 0.0040655 | south | N | 0.0040655 | 0
9017 | SANDH_G2 | 2 | 46 | -0.020229 | south | Y | -0.038232 | -0.0040655 | -0.038066 | -0.016407 | 0.0040655 | south | N | 0.0040655 | 0
9018 | SANDH_G3 | 3 | 46 | -0.020229 | south | Y | -0.038232 | -0.0040655 | -0.038066 | -0.016407 | 0.0040655 | south | N | 0.0040655 | 0
9019 | SANDH_G4 | 4 | 47 | -0.020229 | south | Y | -0.038232 | -0.0040655 | -0.038066 | -0.016407 | 0.0040655 | south | N | 0.0040655 | 0
9020 | SANDHG5A | 5A | 154 | -0.020229 | south | Y | -0.038232 | -0.0040655 | -0.038066 | -0.016407 | 0.0040655 | south | N | 0.0040655 | 0
9021 | SANDHG5C | 5C | 148 | -0.020229 | south | Y | -0.038232 | -0.0040655 | -0.038066 | -0.016407 | 0.0040655 | south | N | 0.0040655 | 0
9022 | SANDH_G6 | 6 | 48 | -0.020229 | south | Y | -0.038232 | -0.0040655 | -0.038066 | -0.016407 | 0.0040655 | south | N | 0.0040655 | 0
9023 | SANDH_G7 | 7 | 48 | -0.020229 | south | Y | -0.038232 | -0.0040655 | -0.038066 | -0.016407 | 0.0040655 | south | N | 0.0040655 | 0
11001 | NAV1CT | 1 | 70 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
11009 | NAV2CT | 1 | 70 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
11011 | NAV3ST | 1 | 92.8 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
11012 | NAV4CT | 1 | 80 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
11013 | NAV5CT | 1 | 80 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
11014 | NAV6ST | 1 | 115 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.017838 | west | Y | -0.000165 | 0.034001 | 6.6241e-07 | 0.02166 | 6.6241e-07 | west | N | 6.6241e-07 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.017838 | west | Y | -0.000165 | 0.034001 | 6.6241e-07 | 0.02166 | 6.6241e-07 | west | N | 6.6241e-07 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.017838 | west | Y | -0.000165 | 0.034001 | 6.6241e-07 | 0.02166 | 6.6241e-07 | west | N | 6.6241e-07 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.017838 | west | Y | -0.000165 | 0.034001 | 6.6241e-07 | 0.02166 | 6.6241e-07 | west | N | 6.6241e-07 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.017838 | west | Y | -0.000165 | 0.034001 | 6.6241e-07 | 0.02166 | 6.6241e-07 | west | N | 6.6241e-07 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.017838 | west | Y | -0.000165 | 0.034001 | 6.6241e-07 | 0.02166 | 6.6241e-07 | west | N | 6.6241e-07 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.018223 | west | Y | 0.00022 | 0.034386 | 0.00038566 | 0.022045 | 0.00022 | North | Y | 0.00038566 | 0.034622
11057 | CHAMPION | 1 | 126.5 | 0.018223 | west | Y | 0.00022 | 0.034386 | 0.00038566 | 0.022045 | 0.00022 | North | Y | 0.00038566 | 0.020956
11058 | PYRON_1G | 1 | 249 | 0.018223 | west | Y | 0.00022 | 0.034386 | 0.00038566 | 0.022045 | 0.00022 | North | Y | 0.00038566 | 0.041249
11059 | INADALE_ | 1 | 197 | 0.018223 | west | Y | 0.00022 | 0.034386 | 0.00038566 | 0.022045 | 0.00022 | North | Y | 0.00038566 | 0.032635
11061 | PNTHRCK1 | 1 | 200 | 0.018045 | west | Y | 4.2005e-05 | 0.034208 | 0.00020766 | 0.021867 | 4.2005e-05 | North | Y | 0.00020766 | 0.033132
11065 | ELBOWCK_ | 1 | 121.9 | 0.018045 | west | Y | 4.2005e-05 | 0.034208 | 0.00020766 | 0.021867 | 4.2005e-05 | North | Y | 0.00020766 | 0.020194
11147 | NOTREES_ | 1 | 149 | 0.01766 | west | Y | -0.000343 | 0.033823 | -0.00017734 | 0.021482 | 0.00017734 | west | N | 0.00017734 | 0
11309 | BULLCREK | 1 | 180 | 0.018054 | west | Y | 5.1005e-05 | 0.034217 | 0.00021666 | 0.021876 | 5.1005e-05 | North | Y | 0.00021666 | 0.029818
11310 | BULLCREK | 1 | 180 | 0.018054 | west | Y | 5.1005e-05 | 0.034217 | 0.00021666 | 0.021876 | 5.1005e-05 | North | Y | 0.00021666 | 0.029818
11320 | COYOTE_1 | 1 | 225 | 0.01804 | west | Y | 3.7005e-05 | 0.034203 | 0.00020266 | 0.021862 | 3.7005e-05 | North | Y | 0.00020266 | 0.037273
11415 | LORAINE_ | 1 | 125 | 0.018159 | west | Y | 0.000156 | 0.034322 | 0.00032166 | 0.021981 | 0.000156 | North | Y | 0.00032166 | 0.020707
11416 | LORAINE_ | 1 | 125 | 0.018159 | west | Y | 0.000156 | 0.034322 | 0.00032166 | 0.021981 | 0.000156 | North | Y | 0.00032166 | 0.020707
11691 | KMICHICT | 1 | 140 | 0.017768 | north | N | -0.000235 | 0.033931 | -6.9338e-05 | 0.02159 | 6.9338e-05 | west | Y | 0.000235 | 0
11692 | KMICHICT | 2 | 141 | 0.017768 | north | N | -0.000235 | 0.033931 | -6.9338e-05 | 0.02159 | 6.9338e-05 | west | Y | 0.000235 | 0
11693 | KMICHIST | 3 | 309 | 0.017768 | north | N | -0.000235 | 0.033931 | -6.9338e-05 | 0.02159 | 6.9338e-05 | west | Y | 0.000235 | 0
11694 | KMICHICT | 4 | 143 | 0.017768 | north | N | -0.000235 | 0.033931 | -6.9338e-05 | 0.02159 | 6.9338e-05 | west | Y | 0.000235 | 0
11695 | KMICHICT | 5 | 144 | 0.017768 | north | N | -0.000235 | 0.033931 | -6.9338e-05 | 0.02159 | 6.9338e-05 | west | Y | 0.000235 | 0
11696 | KMICHIST | 6 | 310 | 0.017768 | north | N | -0.000235 | 0.033931 | -6.9338e-05 | 0.02159 | 6.9338e-05 | west | Y | 0.000235 | 0
12322 | ENNSTRAC | 1 | 196 | 0.020679 | north | Y | 0.002676 | 0.036842 | 0.0028417 | 0.024501 | 0.002676 | North | N | 0.002676 | 0
12323 | ENNSTRAC | 2 | 111 | 0.020679 | north | Y | 0.002676 | 0.036842 | 0.0028417 | 0.024501 | 0.002676 | North | N | 0.002676 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.017987 | north | N | -1.5995e-05 | 0.03415 | 0.00014966 | 0.021809 | 1.5995e-05 | North | N | 1.5995e-05 | 0
12411 | FPLEFR1A | 1 | 161 | 0.017312 | north | Y | -0.000691 | 0.033475 | -0.00052534 | 0.021134 | 0.00052534 | west | Y | 0.000691 | 0.026671
12412 | FPLEFR1B | 2 | 164 | 0.017312 | north | Y | -0.000691 | 0.033475 | -0.00052534 | 0.021134 | 0.00052534 | west | Y | 0.000691 | 0.027168
12413 | FPLEFR1C | 3 | 164 | 0.017312 | north | Y | -0.000691 | 0.033475 | -0.00052534 | 0.021134 | 0.00052534 | west | Y | 0.000691 | 0.027168
12414 | FPLEFR1S | 4 | 414 | 0.017312 | north | Y | -0.000691 | 0.033475 | -0.00052534 | 0.021134 | 0.00052534 | west | Y | 0.000691 | 0.068582
12421 | FPLEFR2A | 1 | 162 | 0.017312 | north | Y | -0.000691 | 0.033475 | -0.00052534 | 0.021134 | 0.00052534 | west | Y | 0.000691 | 0.026837
12422 | FPLEFR2B | 2 | 161 | 0.017312 | north | Y | -0.000691 | 0.033475 | -0.00052534 | 0.021134 | 0.00052534 | west | Y | 0.000691 | 0.026671
12423 | FPLEFR2C | 3 | 163 | 0.017312 | north | Y | -0.000691 | 0.033475 | -0.00052534 | 0.021134 | 0.00052534 | west | Y | 0.000691 | 0.027002
12424 | FPLEFR2S | 4 | 409 | 0.017312 | north | Y | -0.000691 | 0.033475 | -0.00052534 | 0.021134 | 0.00052534 | west | Y | 0.000691 | 0.067754
12440 | PARKD_1S | 1 | 0 | 0.017687 | north | N | -0.000316 | 0.03385 | -0.00015034 | 0.021509 | 0.00015034 | west | Y | 0.000316 | 0
12449 | PARKD_2S | 1 | 0 | 0.017687 | north | N | -0.000316 | 0.03385 | -0.00015034 | 0.021509 | 0.00015034 | west | Y | 0.000316 | 0
13116 | TGATEWAY | 1 | 148 | 0.015789 | north | N | -0.002214 | 0.031952 | -0.0020483 | 0.019611 | 0.0020483 | west | Y | 0.002214 | 0
13117 | TGATEWAY | 2 | 130 | 0.015789 | north | N | -0.002214 | 0.031952 | -0.0020483 | 0.019611 | 0.0020483 | west | Y | 0.002214 | 0
13118 | TGATEWAY | 3 | 145 | 0.015789 | north | N | -0.002214 | 0.031952 | -0.0020483 | 0.019611 | 0.0020483 | west | Y | 0.002214 | 0
13119 | TGATEWAY | 4 | 399 | 0.015789 | north | N | -0.002214 | 0.031952 | -0.0020483 | 0.019611 | 0.0020483 | west | Y | 0.002214 | 0
13131 | CALFREST | 1 | 150.7 | 0.013702 | north | Y | -0.004301 | 0.029865 | -0.0041353 | 0.017524 | 0.0041353 | west | Y | 0.004301 | 0.024965
13132 | CALFREST | 2 | 151 | 0.013702 | north | Y | -0.004301 | 0.029865 | -0.0041353 | 0.017524 | 0.0041353 | west | Y | 0.004301 | 0.025014
13133 | CALFREST | 3 | 177.4 | 0.013702 | north | Y | -0.004301 | 0.029865 | -0.0041353 | 0.017524 | 0.0041353 | west | Y | 0.004301 | 0.029388
13134 | CALFREST | 4 | 151.5 | 0.013817 | north | Y | -0.004186 | 0.02998 | -0.0040203 | 0.017639 | 0.0040203 | west | Y | 0.004186 | 0.025097
13135 | CALFREST | 5 | 152.3 | 0.013817 | north | Y | -0.004186 | 0.02998 | -0.0040203 | 0.017639 | 0.0040203 | west | Y | 0.004186 | 0.02523
13136 | CALFREST | 6 | 177.5 | 0.013817 | north | Y | -0.004186 | 0.02998 | -0.0040203 | 0.017639 | 0.0040203 | west | Y | 0.004186 | 0.029404
13432 | SANDOW_5 | 5 | 581 | -0.024592 | south | Y | -0.042595 | -0.0084285 | -0.042429 | -0.02077 | 0.0084285 | south | N | 0.0084285 | 0
13691 | OAKGROVE | 1 | 855 | 0.00739 | north | Y | -0.010613 | 0.023553 | -0.010447 | 0.011212 | 0.010447 | west | Y | 0.010613 | 0.14164
13692 | OAKGROVE | 2 | 855 | 0.00739 | north | Y | -0.010613 | 0.023553 | -0.010447 | 0.011212 | 0.010447 | west | Y | 0.010613 | 0.14164
32798 | BRYN_TAM | 1 | 32 | 0.002372 | north | N | -0.015631 | 0.018535 | -0.015465 | 0.0061938 | 0.0061938 | houston | Y | 0.015631 | 0
32883 | BRYN_DNS | 1 | 48 | 0.001814 | north | Y | -0.016189 | 0.017977 | -0.016023 | 0.0056358 | 0.0056358 | houston | Y | 0.016189 | 0.50655
32884 | BRYN_DNS | 1 | 46 | 0.001814 | north | Y | -0.016189 | 0.017977 | -0.016023 | 0.0056358 | 0.0056358 | houston | Y | 0.016189 | 0.48545
32886 | BRYN_ATK | MB | 12 | 0.002372 | north | Y | -0.015631 | 0.018535 | -0.015465 | 0.0061938 | 0.0061938 | houston | Y | 0.015631 | 0
32887 | BRYN_ATK | MB | 51 | 0.002372 | north | Y | -0.015631 | 0.018535 | -0.015465 | 0.0061938 | 0.0061938 | houston | Y | 0.015631 | 0
32888 | BRYN_ATK | 1 | 17 | 0.002372 | north | Y | -0.015631 | 0.018535 | -0.015465 | 0.0061938 | 0.0061938 | houston | Y | 0.015631 | 0.16043
32890 | BRYN_ATK | MB | 22 | 0.002372 | north | Y | -0.015631 | 0.018535 | -0.015465 | 0.0061938 | 0.0061938 | houston | Y | 0.015631 | 0
32891 | BRYN_ATK | MB | 25 | 0.002372 | north | Y | -0.015631 | 0.018535 | -0.015465 | 0.0061938 | 0.0061938 | houston | Y | 0.015631 | 0
32892 | BRYN_DNS | 1 | 105 | 0.001814 | north | Y | -0.016189 | 0.017977 | -0.016023 | 0.0056358 | 0.0056358 | houston | Y | 0.016189 | 1.1081
36998 | RDCNYNG1 | 1 | 84 | 0.018214 | west | Y | 0.000211 | 0.034377 | 0.00037666 | 0.022036 | 0.000211 | North | Y | 0.00037666 | 0.013915
38332 | WDWRDU2 | 1 | 80 | 0.016238 | west | Y | -0.001765 | 0.032401 | -0.0015993 | 0.02006 | 0.0015993 | west | N | 0.0015993 | 0
38437 | TNSRBNMS | 1 | 150 | 0.016226 | west | Y | -0.001777 | 0.032389 | -0.0016113 | 0.020048 | 0.0016113 | west | N | 0.0016113 | 0
38438 | TNSRBNMS | 1 | 150 | 0.016226 | west | Y | -0.001777 | 0.032389 | -0.0016113 | 0.020048 | 0.0016113 | west | N | 0.0016113 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.003998 | houston | N | -0.022001 | 0.012165 | -0.021835 | -0.00017619 | 0.00017619 | houston | N | 0.00017619 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.003998 | houston | N | -0.022001 | 0.012165 | -0.021835 | -0.00017619 | 0.00017619 | houston | N | 0.00017619 | 0
38600 | TNBP_CGN | 5 | 53 | -0.003998 | houston | N | -0.022001 | 0.012165 | -0.021835 | -0.00017619 | 0.00017619 | houston | N | 0.00017619 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.003998 | houston | N | -0.022001 | 0.012165 | -0.021835 | -0.00017619 | 0.00017619 | houston | N | 0.00017619 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.003998 | houston | N | -0.022001 | 0.012165 | -0.021835 | -0.00017619 | 0.00017619 | houston | N | 0.00017619 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.003998 | houston | N | -0.022001 | 0.012165 | -0.021835 | -0.00017619 | 0.00017619 | houston | N | 0.00017619 | 0
38614 | TNBPAMCG | 4 | 96 | -0.003998 | houston | N | -0.022001 | 0.012165 | -0.021835 | -0.00017619 | 0.00017619 | houston | N | 0.00017619 | 0
38615 | TNBPAMCG | 1 | 244 | -0.003998 | houston | N | -0.022001 | 0.012165 | -0.021835 | -0.00017619 | 0.00017619 | houston | N | 0.00017619 | 0
38690 | TNBP_CGN | 3 | 40 | -0.003998 | houston | N | -0.022001 | 0.012165 | -0.021835 | -0.00017619 | 0.00017619 | houston | N | 0.00017619 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.004 | houston | N | -0.022003 | 0.012163 | -0.021837 | -0.00017819 | 0.00017819 | houston | N | 0.00017819 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.004 | houston | N | -0.022003 | 0.012163 | -0.021837 | -0.00017819 | 0.00017819 | houston | N | 0.00017819 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.004 | houston | N | -0.022003 | 0.012163 | -0.021837 | -0.00017819 | 0.00017819 | houston | N | 0.00017819 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.004 | houston | N | -0.022003 | 0.012163 | -0.021837 | -0.00017819 | 0.00017819 | houston | N | 0.00017819 | 0
39470 | TNDOWCGN | 1 | 32 | -0.004 | houston | N | -0.022003 | 0.012163 | -0.021837 | -0.00017819 | 0.00017819 | houston | N | 0.00017819 | 0
39480 | TNDOWCGN | 1 | 30 | -0.004 | houston | N | -0.022003 | 0.012163 | -0.021837 | -0.00017819 | 0.00017819 | houston | N | 0.00017819 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.005652 | houston | N | -0.023655 | 0.010511 | -0.023489 | -0.0018302 | 0.0018302 | houston | N | 0.0018302 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.005652 | houston | N | -0.023655 | 0.010511 | -0.023489 | -0.0018302 | 0.0018302 | houston | N | 0.0018302 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.005652 | houston | N | -0.023655 | 0.010511 | -0.023489 | -0.0018302 | 0.0018302 | houston | N | 0.0018302 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.005652 | houston | N | -0.023655 | 0.010511 | -0.023489 | -0.0018302 | 0.0018302 | houston | N | 0.0018302 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.00739 | north | Y | -0.010613 | 0.023553 | -0.010447 | 0.011212 | 0.010447 | west | Y | 0.010613 | 0.02523
39970 | TNTNPONE | 1 | 153 | 0.00739 | north | Y | -0.010613 | 0.023553 | -0.010447 | 0.011212 | 0.010447 | west | Y | 0.010613 | 0.025346
48500 | APD_GT1_ | 1 | 136 | -0.002992 | houston | N | -0.020995 | 0.013171 | -0.020829 | 0.00082981 | 0.00082981 | houston | N | 0.00082981 | 0
48510 | AK_GT1__ | 1 | 33 | -0.004549 | houston | N | -0.022552 | 0.011614 | -0.022386 | -0.00072719 | 0.00072719 | houston | N | 0.00072719 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.002986 | houston | Y | -0.020989 | 0.013177 | -0.020823 | 0.00083581 | 0.00083581 | houston | N | 0.00083581 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.002986 | houston | Y | -0.020989 | 0.013177 | -0.020823 | 0.00083581 | 0.00083581 | houston | N | 0.00083581 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.002986 | houston | Y | -0.020989 | 0.013177 | -0.020823 | 0.00083581 | 0.00083581 | houston | N | 0.00083581 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.002986 | houston | Y | -0.020989 | 0.013177 | -0.020823 | 0.00083581 | 0.00083581 | houston | N | 0.00083581 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.005916 | houston | N | -0.023919 | 0.010247 | -0.023753 | -0.0020942 | 0.0020942 | houston | N | 0.0020942 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.005916 | houston | N | -0.023919 | 0.010247 | -0.023753 | -0.0020942 | 0.0020942 | houston | N | 0.0020942 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.00465 | houston | N | -0.022653 | 0.011513 | -0.022487 | -0.00082819 | 0.00082819 | houston | N | 0.00082819 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.00465 | houston | N | -0.022653 | 0.011513 | -0.022487 | -0.00082819 | 0.00082819 | houston | N | 0.00082819 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.00465 | houston | N | -0.022653 | 0.011513 | -0.022487 | -0.00082819 | 0.00082819 | houston | N | 0.00082819 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.003367 | houston | N | -0.02137 | 0.012796 | -0.021204 | 0.00045481 | 0.00045481 | houston | N | 0.00045481 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.003367 | houston | N | -0.02137 | 0.012796 | -0.021204 | 0.00045481 | 0.00045481 | houston | N | 0.00045481 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.003367 | houston | N | -0.02137 | 0.012796 | -0.021204 | 0.00045481 | 0.00045481 | houston | N | 0.00045481 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.003367 | houston | N | -0.02137 | 0.012796 | -0.021204 | 0.00045481 | 0.00045481 | houston | N | 0.00045481 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.003122 | houston | N | -0.021125 | 0.013041 | -0.020959 | 0.00069981 | 0.00069981 | houston | N | 0.00069981 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.003122 | houston | N | -0.021125 | 0.013041 | -0.020959 | 0.00069981 | 0.00069981 | houston | N | 0.00069981 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.003441 | houston | N | -0.021444 | 0.012722 | -0.021278 | 0.00038081 | 0.00038081 | houston | N | 0.00038081 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.003441 | houston | N | -0.021444 | 0.012722 | -0.021278 | 0.00038081 | 0.00038081 | houston | N | 0.00038081 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.003441 | houston | N | -0.021444 | 0.012722 | -0.021278 | 0.00038081 | 0.00038081 | houston | N | 0.00038081 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.003441 | houston | N | -0.021444 | 0.012722 | -0.021278 | 0.00038081 | 0.00038081 | houston | N | 0.00038081 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.003441 | houston | N | -0.021444 | 0.012722 | -0.021278 | 0.00038081 | 0.00038081 | houston | N | 0.00038081 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.002678 | houston | Y | -0.020681 | 0.013485 | -0.020515 | 0.0011438 | 0.0011438 | houston | N | 0.0011438 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.002803 | houston | Y | -0.020806 | 0.01336 | -0.02064 | 0.0010188 | 0.0010188 | houston | N | 0.0010188 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.00264 | houston | Y | -0.020643 | 0.013523 | -0.020477 | 0.0011818 | 0.0011818 | houston | N | 0.0011818 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.00264 | houston | Y | -0.020643 | 0.013523 | -0.020477 | 0.0011818 | 0.0011818 | houston | N | 0.0011818 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.00264 | houston | Y | -0.020643 | 0.013523 | -0.020477 | 0.0011818 | 0.0011818 | houston | N | 0.0011818 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.001948 | houston | N | -0.019951 | 0.014215 | -0.019785 | 0.0018738 | 0.0018738 | houston | N | 0.0018738 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.002967 | houston | N | -0.02097 | 0.013196 | -0.020804 | 0.00085481 | 0.00085481 | houston | N | 0.00085481 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.002967 | houston | N | -0.02097 | 0.013196 | -0.020804 | 0.00085481 | 0.00085481 | houston | N | 0.00085481 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.002552 | houston | N | -0.020555 | 0.013611 | -0.020389 | 0.0012698 | 0.0012698 | houston | N | 0.0012698 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.002552 | houston | N | -0.020555 | 0.013611 | -0.020389 | 0.0012698 | 0.0012698 | houston | N | 0.0012698 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.002552 | houston | N | -0.020555 | 0.013611 | -0.020389 | 0.0012698 | 0.0012698 | houston | N | 0.0012698 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.002552 | houston | N | -0.020555 | 0.013611 | -0.020389 | 0.0012698 | 0.0012698 | houston | N | 0.0012698 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.003114 | houston | N | -0.021117 | 0.013049 | -0.020951 | 0.00070781 | 0.00070781 | houston | N | 0.00070781 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.003114 | houston | N | -0.021117 | 0.013049 | -0.020951 | 0.00070781 | 0.00070781 | houston | N | 0.00070781 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.003114 | houston | N | -0.021117 | 0.013049 | -0.020951 | 0.00070781 | 0.00070781 | houston | N | 0.00070781 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.003114 | houston | N | -0.021117 | 0.013049 | -0.020951 | 0.00070781 | 0.00070781 | houston | N | 0.00070781 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.003192 | houston | N | -0.021195 | 0.012971 | -0.021029 | 0.00062981 | 0.00062981 | houston | N | 0.00062981 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.003192 | houston | N | -0.021195 | 0.012971 | -0.021029 | 0.00062981 | 0.00062981 | houston | N | 0.00062981 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.003192 | houston | N | -0.021195 | 0.012971 | -0.021029 | 0.00062981 | 0.00062981 | houston | N | 0.00062981 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.003192 | houston | N | -0.021195 | 0.012971 | -0.021029 | 0.00062981 | 0.00062981 | houston | N | 0.00062981 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.003192 | houston | N | -0.021195 | 0.012971 | -0.021029 | 0.00062981 | 0.00062981 | houston | N | 0.00062981 | 0
48651 | EP_1_2 | 1 | 5 | -0.002685 | houston | N | -0.020688 | 0.013478 | -0.020522 | 0.0011368 | 0.0011368 | houston | N | 0.0011368 | 0
48651 | EP_1_2 | 2 | 21 | -0.002685 | houston | N | -0.020688 | 0.013478 | -0.020522 | 0.0011368 | 0.0011368 | houston | N | 0.0011368 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.002938 | north | N | -0.015065 | 0.019101 | -0.014899 | 0.0067598 | 0.0067598 | houston | Y | 0.015065 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.002938 | north | N | -0.015065 | 0.019101 | -0.014899 | 0.0067598 | 0.0067598 | houston | Y | 0.015065 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.002938 | north | N | -0.015065 | 0.019101 | -0.014899 | 0.0067598 | 0.0067598 | houston | Y | 0.015065 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.002938 | north | N | -0.015065 | 0.019101 | -0.014899 | 0.0067598 | 0.0067598 | houston | Y | 0.015065 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.002522 | houston | Y | -0.020525 | 0.013641 | -0.020359 | 0.0012998 | 0.0012998 | houston | N | 0.0012998 | 0
48691 | GBY_7374 | A | 46 | -0.003258 | houston | Y | -0.021261 | 0.012905 | -0.021095 | 0.00056381 | 0.00056381 | houston | N | 0.00056381 | 0
48691 | GBY_7374 | B | 46 | -0.003258 | houston | Y | -0.021261 | 0.012905 | -0.021095 | 0.00056381 | 0.00056381 | houston | N | 0.00056381 | 0
48692 | GBY_8182 | C | 46 | -0.003258 | houston | Y | -0.021261 | 0.012905 | -0.021095 | 0.00056381 | 0.00056381 | houston | N | 0.00056381 | 0
48692 | GBY_8182 | D | 55 | -0.003258 | houston | Y | -0.021261 | 0.012905 | -0.021095 | 0.00056381 | 0.00056381 | houston | N | 0.00056381 | 0
48693 | GBY_8384 | E | 55 | -0.003258 | houston | Y | -0.021261 | 0.012905 | -0.021095 | 0.00056381 | 0.00056381 | houston | N | 0.00056381 | 0
48693 | GBY_8384 | F | 54 | -0.003258 | houston | Y | -0.021261 | 0.012905 | -0.021095 | 0.00056381 | 0.00056381 | houston | N | 0.00056381 | 0
48721 | LEG_1___ | 1 | 827 | 0.008997 | north | Y | -0.009006 | 0.02516 | -0.0088403 | 0.012819 | 0.0088403 | west | Y | 0.009006 | 0.137
48722 | LEG_2___ | 2 | 819 | 0.008997 | north | Y | -0.009006 | 0.02516 | -0.0088403 | 0.012819 | 0.0088403 | west | Y | 0.009006 | 0.13567
48730 | MNS_GT | 1 | 46.1 | -0.004692 | houston | N | -0.022695 | 0.011471 | -0.022529 | -0.00087019 | 0.00087019 | houston | N | 0.00087019 | 0
48731 | CBE_GT1 | 1 | 76 | -0.008082 | houston | Y | -0.026085 | 0.0080815 | -0.025919 | -0.0042602 | 0.0042602 | houston | N | 0.0042602 | 0
48732 | CBE_GT2 | 1 | 76 | -0.008082 | houston | Y | -0.026085 | 0.0080815 | -0.025919 | -0.0042602 | 0.0042602 | houston | N | 0.0042602 | 0
48733 | CBE_ST12 | 1 | 105 | -0.008082 | houston | Y | -0.026085 | 0.0080815 | -0.025919 | -0.0042602 | 0.0042602 | houston | N | 0.0042602 | 0
48734 | CBE_GT3 | 1 | 74 | -0.008082 | houston | Y | -0.026085 | 0.0080815 | -0.025919 | -0.0042602 | 0.0042602 | houston | N | 0.0042602 | 0
48735 | CBE_GT4 | 1 | 74 | -0.008082 | houston | Y | -0.026085 | 0.0080815 | -0.025919 | -0.0042602 | 0.0042602 | houston | N | 0.0042602 | 0
48736 | CBE_ST34 | 1 | 102 | -0.008082 | houston | Y | -0.026085 | 0.0080815 | -0.025919 | -0.0042602 | 0.0042602 | houston | N | 0.0042602 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.003112 | houston | N | -0.021115 | 0.013051 | -0.020949 | 0.00070981 | 0.00070981 | houston | N | 0.00070981 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.003112 | houston | N | -0.021115 | 0.013051 | -0.020949 | 0.00070981 | 0.00070981 | houston | N | 0.00070981 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.003112 | houston | N | -0.021115 | 0.013051 | -0.020949 | 0.00070981 | 0.00070981 | houston | N | 0.00070981 | 0
48761 | PR_GT1__ | 1 | 35 | -0.003162 | houston | N | -0.021165 | 0.013001 | -0.020999 | 0.00065981 | 0.00065981 | houston | N | 0.00065981 | 0
48772 | PHR_GN2_ | MB | 459 | -0.003629 | houston | Y | -0.021632 | 0.012534 | -0.021466 | 0.00019281 | 0.00019281 | houston | N | 0.00019281 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.002684 | houston | N | -0.020687 | 0.013479 | -0.020521 | 0.0011378 | 0.0011378 | houston | N | 0.0011378 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.002684 | houston | N | -0.020687 | 0.013479 | -0.020521 | 0.0011378 | 0.0011378 | houston | N | 0.0011378 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.002684 | houston | N | -0.020687 | 0.013479 | -0.020521 | 0.0011378 | 0.0011378 | houston | N | 0.0011378 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.002684 | houston | N | -0.020687 | 0.013479 | -0.020521 | 0.0011378 | 0.0011378 | houston | N | 0.0011378 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.002684 | houston | N | -0.020687 | 0.013479 | -0.020521 | 0.0011378 | 0.0011378 | houston | N | 0.0011378 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.002684 | houston | N | -0.020687 | 0.013479 | -0.020521 | 0.0011378 | 0.0011378 | houston | N | 0.0011378 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.002684 | houston | N | -0.020687 | 0.013479 | -0.020521 | 0.0011378 | 0.0011378 | houston | N | 0.0011378 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.001948 | houston | N | -0.019951 | 0.014215 | -0.019785 | 0.0018738 | 0.0018738 | houston | N | 0.0018738 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.001948 | houston | N | -0.019951 | 0.014215 | -0.019785 | 0.0018738 | 0.0018738 | houston | N | 0.0018738 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.001948 | houston | N | -0.019951 | 0.014215 | -0.019785 | 0.0018738 | 0.0018738 | houston | N | 0.0018738 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.001948 | houston | N | -0.019951 | 0.014215 | -0.019785 | 0.0018738 | 0.0018738 | houston | N | 0.0018738 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.002655 | houston | N | -0.020658 | 0.013508 | -0.020492 | 0.0011668 | 0.0011668 | houston | N | 0.0011668 | 0
48820 | SHELLG1_ | 1 | 71 | -0.003065 | houston | N | -0.021068 | 0.013098 | -0.020902 | 0.00075681 | 0.00075681 | houston | N | 0.00075681 | 0
48821 | SHELLG2 | 2 | 72 | -0.003065 | houston | N | -0.021068 | 0.013098 | -0.020902 | 0.00075681 | 0.00075681 | houston | N | 0.00075681 | 0
48822 | SHELLG3_ | 1 | 39 | -0.003065 | houston | N | -0.021068 | 0.013098 | -0.020902 | 0.00075681 | 0.00075681 | houston | N | 0.00075681 | 0
48822 | SHELLG3_ | 2 | 30 | -0.003065 | houston | N | -0.021068 | 0.013098 | -0.020902 | 0.00075681 | 0.00075681 | houston | N | 0.00075681 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.00323 | houston | N | -0.021233 | 0.012933 | -0.021067 | 0.00059181 | 0.00059181 | houston | N | 0.00059181 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.00323 | houston | N | -0.021233 | 0.012933 | -0.021067 | 0.00059181 | 0.00059181 | houston | N | 0.00059181 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.003115 | houston | N | -0.021118 | 0.013048 | -0.020952 | 0.00070681 | 0.00070681 | houston | N | 0.00070681 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.003124 | houston | Y | -0.021127 | 0.013039 | -0.020961 | 0.00069781 | 0.00069781 | houston | N | 0.00069781 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.003127 | houston | Y | -0.02113 | 0.013036 | -0.020964 | 0.00069481 | 0.00069481 | houston | N | 0.00069481 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.003115 | houston | Y | -0.021118 | 0.013048 | -0.020952 | 0.00070681 | 0.00070681 | houston | N | 0.00070681 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.003113 | houston | Y | -0.021116 | 0.01305 | -0.02095 | 0.00070881 | 0.00070881 | houston | N | 0.00070881 | 0
48855 | SRB_GT21 | B2 | 12 | -0.003129 | houston | Y | -0.021132 | 0.013034 | -0.020966 | 0.00069281 | 0.00069281 | houston | N | 0.00069281 | 0
48855 | SRB_GT21 | MB | 18 | -0.003129 | houston | Y | -0.021132 | 0.013034 | -0.020966 | 0.00069281 | 0.00069281 | houston | N | 0.00069281 | 0
48865 | TECO_GT1 | 1 | 50 | -0.003791 | houston | Y | -0.021794 | 0.012372 | -0.021628 | 3.0812e-05 | 3.0812e-05 | houston | N | 3.0812e-05 | 0
48873 | THW_ST3_ | 3 | 104 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48874 | THW_ST4_ | 4 | 104 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48875 | THW_3132 | A | 54 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48875 | THW_3132 | B | 53 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48877 | THW_3334 | C | 54 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48877 | THW_3334 | D | 57 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48879 | THW_4142 | E | 54 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48879 | THW_4142 | F | 54 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48881 | THW_4344 | G | 58 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48881 | THW_4344 | H | 58 | -0.002849 | houston | Y | -0.020852 | 0.013314 | -0.020686 | 0.00097281 | 0.00097281 | houston | N | 0.00097281 | 0
48883 | THW_GT1_ | B2 | 12 | -0.002734 | houston | Y | -0.020737 | 0.013429 | -0.020571 | 0.0010878 | 0.0010878 | houston | N | 0.0010878 | 0
48885 | THW_5152 | A | 56 | -0.002468 | houston | Y | -0.020471 | 0.013695 | -0.020305 | 0.0013538 | 0.0013538 | houston | N | 0.0013538 | 0
48885 | THW_5152 | B | 59 | -0.002468 | houston | Y | -0.020471 | 0.013695 | -0.020305 | 0.0013538 | 0.0013538 | houston | N | 0.0013538 | 0
48886 | THW_5354 | C | 56 | -0.002468 | houston | Y | -0.020471 | 0.013695 | -0.020305 | 0.0013538 | 0.0013538 | houston | N | 0.0013538 | 0
48886 | THW_5354 | D | 56 | -0.002468 | houston | Y | -0.020471 | 0.013695 | -0.020305 | 0.0013538 | 0.0013538 | houston | N | 0.0013538 | 0
48887 | THW_5556 | E | 59 | -0.002468 | houston | Y | -0.020471 | 0.013695 | -0.020305 | 0.0013538 | 0.0013538 | houston | N | 0.0013538 | 0
48887 | THW_5556 | F | 56 | -0.002468 | houston | Y | -0.020471 | 0.013695 | -0.020305 | 0.0013538 | 0.0013538 | houston | N | 0.0013538 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.007638 | houston | Y | -0.025641 | 0.0085255 | -0.025475 | -0.0038162 | 0.0038162 | houston | N | 0.0038162 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.004507 | houston | Y | -0.02251 | 0.011656 | -0.022344 | -0.00068519 | 0.00068519 | houston | N | 0.00068519 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.004507 | houston | Y | -0.02251 | 0.011656 | -0.022344 | -0.00068519 | 0.00068519 | houston | N | 0.00068519 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.004507 | houston | Y | -0.02251 | 0.011656 | -0.022344 | -0.00068519 | 0.00068519 | houston | N | 0.00068519 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.004507 | houston | Y | -0.02251 | 0.011656 | -0.022344 | -0.00068519 | 0.00068519 | houston | N | 0.00068519 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.004507 | houston | N | -0.02251 | 0.011656 | -0.022344 | -0.00068519 | 0.00068519 | houston | N | 0.00068519 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.004658 | houston | Y | -0.022661 | 0.011505 | -0.022495 | -0.00083619 | 0.00083619 | houston | N | 0.00083619 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.004658 | houston | Y | -0.022661 | 0.011505 | -0.022495 | -0.00083619 | 0.00083619 | houston | N | 0.00083619 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.004658 | houston | Y | -0.022661 | 0.011505 | -0.022495 | -0.00083619 | 0.00083619 | houston | N | 0.00083619 | 0
48929 | WAPGT21_ | B1 | 13 | -0.004507 | houston | Y | -0.02251 | 0.011656 | -0.022344 | -0.00068519 | 0.00068519 | houston | N | 0.00068519 | 0
48940 | WARVUE_G | G1 | 12 | -0.002681 | houston | Y | -0.020684 | 0.013482 | -0.020518 | 0.0011408 | 0.0011408 | houston | N | 0.0011408 | 0
49803 | EXN_15GT | 1 | 34 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49826 | EXN938GT | 5 | 45.9 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49828 | EXN941GT | 10 | 17.7 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49829 | EXN942GT | 11 | 20.4 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49830 | EXN943GT | 12 | 19.9 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49831 | EXN944GT | 13 | 35 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49832 | EXN945GT | 9 | 18 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49837 | EXN_GT | 4 | 85.4 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49838 | EXN_14GT | 14 | 148 | -0.002772 | houston | N | -0.020775 | 0.013391 | -0.020609 | 0.0010498 | 0.0010498 | houston | N | 0.0010498 | 0
49851 | DOW17000 | 37 | 62 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49858 | DOW38100 | 31 | 71.4 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49859 | DOW38200 | 33 | 45 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49860 | DOW38300 | 32 | 101 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49862 | DOW39100 | 36 | 86 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49863 | DOW39200 | 35 | 88 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49865 | DOW41000 | 41 | 50 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49866 | DOW42000 | 42 | 18 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49869 | DOW49000 | 45 | 94 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49870 | DOW61000 | 61 | 70 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49871 | DOW62000 | 62 | 63 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49872 | DOW63000 | 63 | 72 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49873 | DOW64000 | 64 | 64.8 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49876 | DOW65000 | 65 | 101 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49877 | DOW66000 | 66 | 97 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49878 | DOW67000 | 67 | 103 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49882 | DOW81000 | 81 | 76 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49884 | DOW82000 | 82 | 80 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49885 | DOW83000 | 83 | 80 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
49886 | DOW84000 | 84 | 171 | -0.00625 | houston | N | -0.024253 | 0.0099135 | -0.024087 | -0.0024282 | 0.0024282 | houston | N | 0.0024282 | 0
58909 | PEARSALL | 1 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58909 | PEARSALL | 2 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58909 | PEARSALL | 3 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58909 | PEARSALL | 4 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58909 | PEARSALL | 5 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58909 | PEARSALL | 6 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58919 | PEARSALL | 1 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58919 | PEARSALL | 2 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58919 | PEARSALL | 3 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58919 | PEARSALL | 4 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58919 | PEARSALL | 5 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58919 | PEARSALL | 6 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58929 | PEARSALL | 1 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58929 | PEARSALL | 2 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58929 | PEARSALL | 3 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58929 | PEARSALL | 4 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58929 | PEARSALL | 5 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58929 | PEARSALL | 6 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58949 | PEARSALL | 1 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58949 | PEARSALL | 2 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58949 | PEARSALL | 3 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58949 | PEARSALL | 4 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58949 | PEARSALL | 5 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
58949 | PEARSALL | 6 | 8.4 | -0.013081 | south | Y | -0.031084 | 0.0030825 | -0.030918 | -0.0092592 | 0.0030825 | south | N | 0.0030825 | 0
60000 | DSKY2 | 1 | 76.5 | 0.015654 | west | Y | -0.002349 | 0.031817 | -0.0021833 | 0.019476 | 0.0021833 | west | N | 0.0021833 | 0
60003 | KING_NE1 | 1 | 80 | 0.016263 | west | Y | -0.00174 | 0.032426 | -0.0015743 | 0.020085 | 0.0015743 | west | N | 0.0015743 | 0
60005 | KING_SE1 | 1 | 40 | 0.016263 | west | Y | -0.00174 | 0.032426 | -0.0015743 | 0.020085 | 0.0015743 | west | N | 0.0015743 | 0
60007 | KING_SW1 | 1 | 80 | 0.016361 | west | Y | -0.001642 | 0.032524 | -0.0014763 | 0.020183 | 0.0014763 | west | N | 0.0014763 | 0
60016 | WOODWRD1 | 1 | 80 | 0.016241 | west | Y | -0.001762 | 0.032404 | -0.0015963 | 0.020063 | 0.0015963 | west | N | 0.0015963 | 0
60017 | ORNNWP1 | 1 | 80 | 0.015735 | west | Y | -0.002268 | 0.031898 | -0.0021023 | 0.019557 | 0.0021023 | west | N | 0.0021023 | 0
60018 | DSKY1 | 1 | 84 | 0.01557 | west | Y | -0.002433 | 0.031733 | -0.0022673 | 0.019392 | 0.0022673 | west | N | 0.0022673 | 0
60019 | KING_NW1 | 1 | 80 | 0.016361 | west | Y | -0.001642 | 0.032524 | -0.0014763 | 0.020183 | 0.0014763 | west | N | 0.0014763 | 0
60057 | CALLAHAN | 1 | 114 | -0.016054 | south | Y | -0.034057 | 0.00010948 | -0.033891 | -0.012232 | 0.00010948 | south | N | 0.00010948 | 0
60058 | BUFF_GAP | 1 | 120 | 0.018093 | west | Y | 9.0005e-05 | 0.034256 | 0.00025566 | 0.021915 | 9.0005e-05 | North | Y | 0.00025566 | 0.019879
60060 | CIRELLO | 1 | 233 | 0.018093 | west | Y | 9.0005e-05 | 0.034256 | 0.00025566 | 0.021915 | 9.0005e-05 | North | Y | 0.00025566 | 0.038598
60063 | BUFF_GAP | 1 | 170.2 | 0.018093 | west | Y | 9.0005e-05 | 0.034256 | 0.00025566 | 0.021915 | 9.0005e-05 | North | Y | 0.00025566 | 0.028195
60066 | H_HOLLOW | 1 | 222 | -0.016054 | south | Y | -0.034057 | 0.00010948 | -0.033891 | -0.012232 | 0.00010948 | south | N | 0.00010948 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.016054 | south | Y | -0.034057 | 0.00010948 | -0.033891 | -0.012232 | 0.00010948 | south | N | 0.00010948 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.016054 | south | Y | -0.034057 | 0.00010948 | -0.033891 | -0.012232 | 0.00010948 | south | N | 0.00010948 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.016054 | south | Y | -0.034057 | 0.00010948 | -0.033891 | -0.012232 | 0.00010948 | south | N | 0.00010948 | 0
60074 | HORSH5 | 1 | 100 | -0.016054 | south | Y | -0.034057 | 0.00010948 | -0.033891 | -0.012232 | 0.00010948 | south | N | 0.00010948 | 0
60081 | WHRLWIND | 1 | 60 | 0.018644 | west | Y | 0.000641 | 0.034807 | 0.00080666 | 0.022466 | 0.000641 | North | Y | 0.00080666 | 0.0099395
60201 | RIO DRCS | F | 0 | -0.00628 | south | N | -0.024283 | 0.0098835 | -0.024117 | -0.0024582 | 0.0024582 | houston | Y | 0.0098835 | 0
60202 | FRIEND_R | F | 0 | 0.012929 | west | N | -0.005074 | 0.029092 | -0.0049083 | 0.016751 | 0.0049083 | west | N | 0.0049083 | 0
60203 | PRES0A | BT | 4.8 | 0.016724 | west | N | -0.001279 | 0.032887 | -0.0011133 | 0.020546 | 0.0011133 | west | N | 0.0011133 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.018245 | west | Y | 0.000242 | 0.034408 | 0.00040766 | 0.022067 | 0.000242 | North | Y | 0.00040766 | 0.0062122
71054 | L_SWEETW | W1 | 107.5 | 0.018245 | west | Y | 0.000242 | 0.034408 | 0.00040766 | 0.022067 | 0.000242 | North | Y | 0.00040766 | 0.017808
71057 | L_SWEETW | W1 | 135 | 0.018245 | west | Y | 0.000242 | 0.034408 | 0.00040766 | 0.022067 | 0.000242 | North | Y | 0.00040766 | 0.022364
71059 | L_SWEETW | W1 | 119 | 0.018245 | west | Y | 0.000242 | 0.034408 | 0.00040766 | 0.022067 | 0.000242 | North | Y | 0.00040766 | 0.019713
71060 | L_SWEETW | W1 | 105 | 0.018245 | west | Y | 0.000242 | 0.034408 | 0.00040766 | 0.022067 | 0.000242 | North | Y | 0.00040766 | 0.017394
71061 | L_SWEETW | W1 | 80.5 | 0.018245 | west | Y | 0.000242 | 0.034408 | 0.00040766 | 0.022067 | 0.000242 | North | Y | 0.00040766 | 0.013335
76031 | L_GASCCR | W1 | 150 | 0.017882 | west | Y | -0.000121 | 0.034045 | 4.4662e-05 | 0.021704 | 4.4662e-05 | west | N | 4.4662e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
76096 | L_CAPRSI | W1 | 186 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.01784 | west | Y | -0.000163 | 0.034003 | 2.6624e-06 | 0.021662 | 2.6624e-06 | west | N | 2.6624e-06 | 0
80003 | MILHWYS | F | 0 | -0.012817 | south | N | -0.03082 | 0.0033465 | -0.030654 | -0.0089952 | 0.0033465 | south | N | 0.0033465 | 0
80010 | EPLVT1 | F | 0 | -0.008319 | south | N | -0.026322 | 0.0078445 | -0.026156 | -0.0044972 | 0.0044972 | houston | Y | 0.0078445 | 0
80012 | LAR | F | 0 | -0.013309 | south | N | -0.031312 | 0.0028545 | -0.031146 | -0.0094872 | 0.0028545 | south | N | 0.0028545 | 0
80051 | FORPVCM0 | 8 | 28 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
80053 | FOR69CG0 | 10 | 74 | -0.011734 | south | N | -0.029737 | 0.0044295 | -0.029571 | -0.0079122 | 0.0044295 | south | N | 0.0044295 | 0
80080 | GWINDT11 | 1 | 94 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80080 | GWINDT11 | 2 | 41 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80080 | GWINDT11 | 3 | 38 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80080 | GWINDT11 | 4 | 19 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80081 | GWINDT21 | 1 | 94 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80081 | GWINDT21 | 2 | 36 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80081 | GWINDT21 | 3 | 43 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80081 | GWINDT21 | 4 | 22 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80137 | CSDR89 | 8 | 39 | -0.012155 | south | N | -0.030158 | 0.0040085 | -0.029992 | -0.0083332 | 0.0040085 | south | N | 0.0040085 | 0
80137 | CSDR89 | 9 | 15 | -0.012155 | south | N | -0.030158 | 0.0040085 | -0.029992 | -0.0083332 | 0.0040085 | south | N | 0.0040085 | 0
80138 | CSDR7 | 7 | 7 | -0.012155 | south | N | -0.030158 | 0.0040085 | -0.029992 | -0.0083332 | 0.0040085 | south | N | 0.0040085 | 0
80139 | CSDR56 | 5 | 15 | -0.012155 | south | N | -0.030158 | 0.0040085 | -0.029992 | -0.0083332 | 0.0040085 | south | N | 0.0040085 | 0
80139 | CSDR56 | 6 | 39 | -0.012155 | south | N | -0.030158 | 0.0040085 | -0.029992 | -0.0083332 | 0.0040085 | south | N | 0.0040085 | 0
80140 | CSDR11 | 11 | 39 | -0.012155 | south | N | -0.030158 | 0.0040085 | -0.029992 | -0.0083332 | 0.0040085 | south | N | 0.0040085 | 0
80180 | PNSCALT1 | 1 | 148 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80180 | PNSCALT1 | 2 | 50 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80181 | PNSCALT2 | 1 | 55 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80181 | PNSCALT2 | 2 | 50 | -0.01281 | south | Y | -0.030813 | 0.0033535 | -0.030647 | -0.0089882 | 0.0033535 | south | N | 0.0033535 | 0
80223 | REYSHR G | 1 | 12 | -0.012567 | south | N | -0.03057 | 0.0035965 | -0.030404 | -0.0087452 | 0.0035965 | south | N | 0.0035965 | 0
80224 | VISTRONG | 1 | 15 | -0.012292 | south | N | -0.030295 | 0.0038715 | -0.030129 | -0.0084702 | 0.0038715 | south | N | 0.0038715 | 0
80225 | VISTRONG | 2 | 23 | -0.012292 | south | N | -0.030295 | 0.0038715 | -0.030129 | -0.0084702 | 0.0038715 | south | N | 0.0038715 | 0
80226 | ALCOA G | 1 | 48 | -0.011834 | south | N | -0.029837 | 0.0043295 | -0.029671 | -0.0080122 | 0.0043295 | south | N | 0.0043295 | 0
80227 | AIRCO G | 1 | 8 | -0.012202 | south | N | -0.030205 | 0.0039615 | -0.030039 | -0.0083802 | 0.0039615 | south | N | 0.0039615 | 0
80261 | NBEC81A | 1 | 180 | -0.012695 | south | Y | -0.030698 | 0.0034685 | -0.030532 | -0.0088732 | 0.0034685 | south | N | 0.0034685 | 0
80262 | NBEC91A | 1 | 180 | -0.012691 | south | Y | -0.030694 | 0.0034725 | -0.030528 | -0.0088692 | 0.0034725 | south | N | 0.0034725 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.012719 | south | Y | -0.030722 | 0.0034445 | -0.030556 | -0.0088972 | 0.0034445 | south | N | 0.0034445 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.012719 | south | Y | -0.030722 | 0.0034445 | -0.030556 | -0.0088972 | 0.0034445 | south | N | 0.0034445 | 0
80265 | LARECU40 | 4 | 100 | -0.01331 | south | Y | -0.031313 | 0.0028535 | -0.031147 | -0.0094882 | 0.0028535 | south | N | 0.0028535 | 0
80266 | LARECU50 | 5 | 100 | -0.01331 | south | Y | -0.031313 | 0.0028535 | -0.031147 | -0.0094882 | 0.0028535 | south | N | 0.0028535 | 0
80291 | PAPALOTE | 1 | 25 | -0.012616 | south | Y | -0.030619 | 0.0035475 | -0.030453 | -0.0087942 | 0.0035475 | south | N | 0.0035475 | 0
80291 | PAPALOTE | 2 | 25 | -0.012616 | south | Y | -0.030619 | 0.0035475 | -0.030453 | -0.0087942 | 0.0035475 | south | N | 0.0035475 | 0
80291 | PAPALOTE | 3 | 25 | -0.012616 | south | Y | -0.030619 | 0.0035475 | -0.030453 | -0.0087942 | 0.0035475 | south | N | 0.0035475 | 0
80291 | PAPALOTE | 4 | 16 | -0.012616 | south | Y | -0.030619 | 0.0035475 | -0.030453 | -0.0087942 | 0.0035475 | south | N | 0.0035475 | 0
80294 | PAPALOTE | 5 | 25 | -0.012616 | south | Y | -0.030619 | 0.0035475 | -0.030453 | -0.0087942 | 0.0035475 | south | N | 0.0035475 | 0
80294 | PAPALOTE | 6 | 25 | -0.012616 | south | Y | -0.030619 | 0.0035475 | -0.030453 | -0.0087942 | 0.0035475 | south | N | 0.0035475 | 0
80294 | PAPALOTE | 7 | 25 | -0.012616 | south | Y | -0.030619 | 0.0035475 | -0.030453 | -0.0087942 | 0.0035475 | south | N | 0.0035475 | 0
80294 | PAPALOTE | 8 | 15 | -0.012616 | south | Y | -0.030619 | 0.0035475 | -0.030453 | -0.0087942 | 0.0035475 | south | N | 0.0035475 | 0
86104 | CID-138 | EQ | 0 | -0.01331 | south | N | -0.031313 | 0.0028535 | -0.031147 | -0.0094882 | 0.0028535 | south | N | 0.0028535 | 0
86105 | CID-230 | EQ | 500 | -0.01331 | south | N | -0.031313 | 0.0028535 | -0.031147 | -0.0094882 | 0.0028535 | south | N | 0.0028535 | 0
86106 | CUF-230 | EQ | 500 | -0.01331 | south | N | -0.031313 | 0.0028535 | -0.031147 | -0.0094882 | 0.0028535 | south | N | 0.0028535 | 0
86107 | CUF-138 | EQ | 0 | -0.01331 | south | N | -0.031313 | 0.0028535 | -0.031147 | -0.0094882 | 0.0028535 | south | N | 0.0028535 | 0
88198 | BEEVILLE | F | 0 | -0.013384 | south | N | -0.031387 | 0.0027795 | -0.031221 | -0.0095622 | 0.0027795 | south | N | 0.0027795 | 0
88253 | HAMILTON | F | 0 | -0.005202 | south | N | -0.023205 | 0.010961 | -0.023039 | -0.0013802 | 0.0013802 | houston | Y | 0.010961 | 0
88299 | ZAPATA | F | 0 | -0.013038 | south | N | -0.031041 | 0.0031255 | -0.030875 | -0.0092162 | 0.0031255 | south | N | 0.0031255 | 0
88508 | FALFURRI | F | 0 | -0.012996 | south | N | -0.030999 | 0.0031675 | -0.030833 | -0.0091742 | 0.0031675 | south | N | 0.0031675 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3407 ELM_MOTT - 3575 WACONCST C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.080393 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0589 | 150 | 0.096247 | 14.437 | 150 | 14.437
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.080393 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4314 | 80 | 0.096247 | 7.6997 | 230 | 22.1368
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.071274 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.1749 | 255 | 0.087128 | 22.2176 | 485 | 44.3543
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.071274 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.6198 | 149 | 0.087128 | 12.982 | 634 | 57.3364 | Weighted Shift Factors
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.071274 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.9049 | 153 | 0.087128 | 13.3305 |  |  | North | 0.018003
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.067214 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0082 | 0 | 0.083068 | 0 |  |  | South | -0.015854
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.067214 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0082 | 0 | 0.083068 | 0 |  |  |  | 0.033857
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.026661 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.5997 | 60 | 0.042515 | 2.5509
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.026254 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4107 | 168 | 0.042108 | 7.0741 |  |  | Line Rating | 378.15
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.026254 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3629 | 90 | 0.042108 | 3.7897 |  |  | Conc Gen | 634
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.024361 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7784 | 73 | 0.040215 | 2.9357 |  |  | Weighted Imp. | 57.3364
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.024361 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.899 | 119 | 0.040215 | 4.7856 |  |  | PTDF | 0.090436
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.024361 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.994 | 205 | 0.040215 | 8.244
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.024361 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.4848 | 102 | 0.040215 | 4.1019 |  |  | Concentration | 2.6711
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.024361 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.3387 | 96 | 0.040215 | 3.8606
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6361 | 70 | 0.039227 | 2.7459
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6127 | 69 | 0.039227 | 2.7066
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6127 | 69 | 0.039227 | 2.7066
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5894 | 68 | 0.039227 | 2.6674
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.023155 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.039009 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.023155 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.223 | 787 | 0.039009 | 30.6999
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.022002 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.39604 | 18 | 0.037856 | 0.6814
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.022002 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.39604 | 18 | 0.037856 | 0.6814
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.022002 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.83608 | 38 | 0.037856 | 1.4385
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.021242 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.549 | 120 | 0.037096 | 4.4515
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.021175 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.2541 | 0 | 0.037029 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.021175 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.2541 | 0 | 0.037029 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.020679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0531 | 196 | 0.036533 | 7.1604
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.020679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2954 | 111 | 0.036533 | 4.0551
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.020515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.9083 | 288 | 0.036369 | 10.4742
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.020515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0157 | 147 | 0.036369 | 5.3462
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.020515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0157 | 147 | 0.036369 | 5.3462
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.020168 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.036022 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.020035 | north | 3 | N | N | Nnorth | Nnorth | 1 | 23.1805 | 0 | 0.035889 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.020035 | north | 3 | N | N | Nnorth | Nnorth | 1 | 23.2005 | 0 | 0.035889 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.019927 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3301 | 217.3 | 0.035781 | 7.7752
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.019927 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.085 | 205 | 0.035781 | 7.3351
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.019927 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.4281 | 272.4 | 0.035781 | 9.7467
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.019866 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.8076 | 242 | 0.03572 | 8.6442
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3788 | 224 | 0.035402 | 7.93
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4178 | 226 | 0.035402 | 8.0008
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1442 | 212 | 0.035402 | 7.5052
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1246 | 211 | 0.035402 | 7.4698
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.019293 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.035147 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.019293 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.035147 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.019293 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.035147 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.019261 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.3785 | 435 | 0.035115 | 15.2749
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.019253 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.6049 | 395 | 0.035107 | 13.8672
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.019253 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.3751 | 435 | 0.035107 | 15.2714
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.019245 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.1651 | 112.5 | 0.035099 | 3.9486
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.38458 | 20 | 0.035083 | 0.70166
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.38458 | 20 | 0.035083 | 0.70166
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.38458 | 20 | 0.035083 | 0.70166
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.32689 | 17 | 0.035083 | 0.59641
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.01913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9025 | 204 | 0.034984 | 7.1367
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.01913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8451 | 201 | 0.034984 | 7.0317
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.01913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6295 | 242 | 0.034984 | 8.4661
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.019122 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.2833 | 224 | 0.034976 | 7.8346
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.01904 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.9686 | 366 | 0.034894 | 12.7711
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.018843 | west | 4 | Y | N | Ywest | Nwest | 1 | 12.2423 | 649.7 | 0.034697 | 22.5425
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.018705 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0863 | 165 | 0.034559 | 5.7022
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.018649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0356 | 216.4 | 0.034503 | 7.4664
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.018649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.03 | 216.1 | 0.034503 | 7.456
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.018644 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1186 | 60 | 0.034498 | 2.0699
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.018612 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1167 | 60 | 0.034466 | 2.0679
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.018612 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1726 | 63 | 0.034466 | 2.1713
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.018599 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4396 | 400 | 0.034453 | 13.7811
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.018599 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3894 | 236 | 0.034453 | 8.1309
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.018438 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7657 | 150 | 0.034292 | 5.1438
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.01839 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7585 | 150 | 0.034244 | 5.1366
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.01839 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8574 | 101 | 0.034244 | 3.4586
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68419 | 37.5 | 0.034099 | 1.2787
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9613 | 107.5 | 0.034099 | 3.6656
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4631 | 135 | 0.034099 | 4.6033
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1712 | 119 | 0.034099 | 4.0578
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9157 | 105 | 0.034099 | 3.5804
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.4687 | 80.5 | 0.034099 | 2.745
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8086 | 209 | 0.034077 | 7.122
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3052 | 126.5 | 0.034077 | 4.3107
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5375 | 249 | 0.034077 | 8.4851
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5899 | 197 | 0.034077 | 6.7131
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.018214 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.53 | 84 | 0.034068 | 2.8617
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.018163 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7981 | 99 | 0.034017 | 3.3677
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.018163 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1079 | 61 | 0.034017 | 2.075
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.018163 | west | 7 | N | N | Nwest | Nwest | 1 | 0.45408 | 0 | 0.034017 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.018163 | west | 7 | N | N | Nwest | Nwest | 1 | 0.83005 | 0 | 0.034017 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.018163 | west | 7 | N | N | Nwest | Nwest | 1 | 0.83005 | 0 | 0.034017 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.018159 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2699 | 125 | 0.034013 | 4.2516
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.018159 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2699 | 125 | 0.034013 | 4.2516
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.018158 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5603 | 141 | 0.034012 | 4.7957
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.018158 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.179 | 120 | 0.034012 | 4.0814
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.018145 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1431 | 63 | 0.033999 | 2.1419
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.018137 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.1402 | 118 | 0.033991 | 4.0109
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.018137 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0858 | 115 | 0.033991 | 3.9089
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.018137 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.0842 | 556 | 0.033991 | 18.8989
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1949 | 66 | 0.033959 | 2.2413
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.2492 | 69 | 0.033959 | 2.3432
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.2492 | 69 | 0.033959 | 2.3432
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.213 | 67 | 0.033959 | 2.2752
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.213 | 67 | 0.033959 | 2.2752
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1768 | 65 | 0.033959 | 2.2073
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.018093 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1712 | 120 | 0.033947 | 4.0736
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.018093 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2157 | 233 | 0.033947 | 7.9096
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.018093 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0794 | 170.2 | 0.033947 | 5.7777
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.018058 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033912 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.018054 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2497 | 180 | 0.033908 | 6.1034
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.018054 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2497 | 180 | 0.033908 | 6.1034
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7067 | 150 | 0.033899 | 5.0848
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9699 | 220 | 0.033899 | 7.4577
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.609 | 200 | 0.033899 | 6.7798
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1997 | 121.9 | 0.033899 | 4.1323
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.01804 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.059 | 225 | 0.033894 | 7.6261
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.018009 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1611 | 120 | 0.033863 | 4.0635
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.018008 | west | 8 | N | N | Nwest | Nwest | 1 | 1.2606 | 0 | 0.033862 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.018008 | west | 8 | N | N | Nwest | Nwest | 1 | 1.3218 | 0 | 0.033862 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.018008 | west | 8 | N | N | Nwest | Nwest | 1 | 1.2678 | 0 | 0.033862 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.018001 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1601 | 120 | 0.033855 | 4.0626
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.017987 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.033841 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.017926 | west | 8 | N | N | Nwest | Nwest | 1 | 0.46249 | 0 | 0.03378 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.017909 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71636 | 0 | 0.033763 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.017909 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71636 | 0 | 0.033763 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.017898 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8338 | 214.2 | 0.033752 | 7.2296
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.017882 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6823 | 150 | 0.033736 | 5.0604
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.017866 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7955 | 100.5 | 0.03372 | 3.3888
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.017864 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0361 | 58 | 0.033718 | 1.9556
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.017848 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0342 | 170 | 0.033702 | 5.7293
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.017848 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.281 | 520 | 0.033702 | 17.5249
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2488 | 70 | 0.033694 | 2.3586
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2488 | 70 | 0.033694 | 2.3586
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.6556 | 92.8 | 0.033694 | 3.1268
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4272 | 80 | 0.033694 | 2.6955
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4272 | 80 | 0.033694 | 2.6955
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0516 | 115 | 0.033694 | 3.8748
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.007 | 112.5 | 0.033694 | 3.7905
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6671 | 149.5 | 0.033694 | 5.0372
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3182 | 186 | 0.033694 | 6.267
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8267 | 214.5 | 0.033694 | 7.2273
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7139 | 208.2 | 0.033692 | 7.0146
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5348 | 142.1 | 0.033692 | 4.7876
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3618 | 132.4 | 0.033692 | 4.4608
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.426 | 136 | 0.033692 | 4.5821
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6222 | 147 | 0.033692 | 4.9527
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.746 | 210 | 0.033692 | 7.0753
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.017768 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.5742 | 370 | 0.033622 | 12.4401
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4875 | 0 | 0.033622 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5053 | 0 | 0.033622 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.4903 | 0 | 0.033622 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5408 | 0 | 0.033622 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5586 | 0 | 0.033622 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.5081 | 0 | 0.033622 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.017759 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.11721 | 6.6 | 0.033613 | 0.22184
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.017759 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.60913 | 34.3 | 0.033613 | 1.1529
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8381 | 160 | 0.033592 | 5.3747
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7671 | 156 | 0.033592 | 5.2403
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4766 | 196 | 0.033592 | 6.584
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7671 | 156 | 0.033592 | 5.2403
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7849 | 157 | 0.033592 | 5.2739
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5121 | 198 | 0.033592 | 6.6512
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.017718 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.3289 | 0 | 0.033572 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.017718 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.4104 | 0 | 0.033572 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.017718 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5663 | 0 | 0.033572 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.0177 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0002 | 169.5 | 0.033554 | 5.6874
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017687 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.033541 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017687 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.033541 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.017684 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.70736 | 40 | 0.033538 | 1.3415
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.017682 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.8666 | 558 | 0.033536 | 18.713
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.017682 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.2379 | 579 | 0.033536 | 19.4172
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.017682 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.2871 | 808 | 0.033536 | 27.0969
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.017676 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3964 | 79 | 0.03353 | 2.6489
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.017676 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8737 | 106 | 0.03353 | 3.5542
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.017676 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5807 | 146 | 0.03353 | 4.8953
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.017676 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.3434 | 76 | 0.03353 | 2.5483
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.01766 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6313 | 149 | 0.033514 | 4.9936
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.017636 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.35272 | 20 | 0.03349 | 0.6698
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.017636 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.4409 | 25 | 0.03349 | 0.83724
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.017636 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.72308 | 41 | 0.03349 | 1.3731
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.017616 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.61656 | 35 | 0.03347 | 1.1714
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.017616 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.52848 | 30 | 0.03347 | 1.0041
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1618 | 66 | 0.033457 | 2.2081
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1442 | 65 | 0.033457 | 2.1747
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1794 | 67 | 0.033457 | 2.2416
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1794 | 67 | 0.033457 | 2.2416
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1794 | 67 | 0.033457 | 2.2416
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.017603 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033457 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.017603 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033457 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.017598 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.828 | 388 | 0.033452 | 12.9793
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.017598 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.063 | 515 | 0.033452 | 17.2277
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7872 | 161 | 0.033166 | 5.3397
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8392 | 164 | 0.033166 | 5.4392
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8392 | 164 | 0.033166 | 5.4392
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.1672 | 414 | 0.033166 | 13.7306
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8045 | 162 | 0.033166 | 5.3729
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7872 | 161 | 0.033166 | 5.3397
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8219 | 163 | 0.033166 | 5.406
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0806 | 409 | 0.033166 | 13.5648
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.016724 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.080275 | 0 | 0.032578 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.016361 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3089 | 80 | 0.032215 | 2.5772
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.016361 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3089 | 80 | 0.032215 | 2.5772
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.016263 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2197 | 75 | 0.032117 | 2.4088
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.016263 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.301 | 80 | 0.032117 | 2.5693
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.016263 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.65052 | 40 | 0.032117 | 1.2847
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.016241 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2993 | 80 | 0.032095 | 2.5676
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.016238 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.299 | 80 | 0.032092 | 2.5673
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.016226 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4339 | 150 | 0.03208 | 4.812
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.016226 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4339 | 150 | 0.03208 | 4.812
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.015955 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.5247 | 785 | 0.031809 | 24.9699
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.015955 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.6842 | 795 | 0.031809 | 25.288
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.015955 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.4449 | 780 | 0.031809 | 24.8108
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.3368 | 0 | 0.031643 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.0526 | 0 | 0.031643 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2894 | 0 | 0.031643 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.2998 | 0 | 0.031643 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.015735 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2588 | 80 | 0.031589 | 2.5271
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.015654 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1975 | 76.5 | 0.031508 | 2.4103
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.01557 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3079 | 84 | 0.031424 | 2.6396
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.015539 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.031393 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.015523 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.77615 | 50 | 0.031377 | 1.5688
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.015332 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7904 | 182 | 0.031186 | 5.6758
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.015332 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.4207 | 484 | 0.031186 | 15.0939
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.013817 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0933 | 151.5 | 0.029671 | 4.4951
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.013817 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.1043 | 152.3 | 0.029671 | 4.5189
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.013817 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4525 | 177.5 | 0.029671 | 5.2666
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.013702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0649 | 150.7 | 0.029556 | 4.4541
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.013702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.069 | 151 | 0.029556 | 4.4629
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.013702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4307 | 177.4 | 0.029556 | 5.2432
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.013267 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.1592 | 615 | 0.029121 | 17.9093
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.013267 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.7877 | 587 | 0.029121 | 17.0939
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.012929 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.028783 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.010529 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5794 | 150 | 0.026383 | 3.9574
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.008997 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.4405 | 827 | 0.024851 | 20.5516
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.008997 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.3685 | 819 | 0.024851 | 20.3528
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.3185 | 855 | 0.023244 | 19.8734
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.3185 | 855 | 0.023244 | 19.8734
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1255 | 152.3 | 0.023244 | 3.54
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1307 | 153 | 0.023244 | 3.5563
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.003836 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.7761 | 463 | 0.01969 | 9.1164
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.45304 | 0 | 0.018792 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.45833 | 0 | 0.018792 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.45833 | 0 | 0.018792 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.1164 | 0 | 0.018792 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.002372 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.075904 | 0 | 0.018226 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018226 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018226 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.002372 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.040324 | 17 | 0.018226 | 0.30984
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018226 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018226 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.001814 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.087072 | 48 | 0.017668 | 0.84805
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.001814 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.083444 | 46 | 0.017668 | 0.81272
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.001814 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.19047 | 105 | 0.017668 | 1.8551
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.015854 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.015854 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.00628 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.0095738 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -1.6054 | 100 | -0.00020024 | -0.020024
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018003 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018003 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.337 | 0 | -0.019951 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30389 | 0 | -0.019951 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.29999 | 0 | -0.019951 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.29999 | 0 | -0.019951 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.001948 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31558 | 0 | -0.019951 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13821 | 56 | -0.020471 | -1.1464
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14561 | 59 | -0.020471 | -1.2078
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13821 | 56 | -0.020471 | -1.1464
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13821 | 56 | -0.020471 | -1.1464
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14561 | 59 | -0.020471 | -1.2078
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13821 | 56 | -0.020471 | -1.1464
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.002522 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0038 | 398 | -0.020525 | -8.1689
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41547 | 0 | -0.020555 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41189 | 0 | -0.020555 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40551 | 0 | -0.020555 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.687 | 0 | -0.020555 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.00264 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45408 | 172 | -0.020643 | -3.5506
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.00264 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45408 | 172 | -0.020643 | -3.5506
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.00264 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45408 | 172 | -0.020643 | -3.5506
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.002655 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.41684 | 0 | -0.020658 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.002678 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.9898 | 743 | -0.020681 | -15.366
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.002681 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.032172 | 12 | -0.020684 | -0.24821
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17446 | 0 | -0.020687 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17714 | 0 | -0.020687 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18788 | 0 | -0.020687 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16909 | 0 | -0.020687 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16641 | 0 | -0.020687 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27914 | 0 | -0.020687 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15836 | 0 | -0.020687 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.002685 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.013425 | 0 | -0.020688 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.002685 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.056385 | 0 | -0.020688 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002734 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.032808 | 12 | -0.020737 | -0.24884
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.094248 | 0 | -0.020775 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.096188 | 0 | -0.020775 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.090644 | 0 | -0.020775 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12723 | 0 | -0.020775 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.049064 | 0 | -0.020775 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.056549 | 0 | -0.020775 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.055163 | 0 | -0.020775 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09702 | 0 | -0.020775 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.049896 | 0 | -0.020775 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23673 | 0 | -0.020775 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41026 | 0 | -0.020775 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.002803 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -2.0602 | 735 | -0.020806 | -15.2924
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.2963 | 104 | -0.020852 | -2.1686
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.2963 | 104 | -0.020852 | -2.1686
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15385 | 54 | -0.020852 | -1.126
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.151 | 53 | -0.020852 | -1.1052
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15385 | 54 | -0.020852 | -1.126
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16239 | 57 | -0.020852 | -1.1886
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15385 | 54 | -0.020852 | -1.126
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15385 | 54 | -0.020852 | -1.126
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16524 | 58 | -0.020852 | -1.2094
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16524 | 58 | -0.020852 | -1.2094
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.002967 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51329 | 0 | -0.02097 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.002967 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40054 | 0 | -0.02097 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12541 | 42 | -0.020989 | -0.88154
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12541 | 42 | -0.020989 | -0.88154
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11347 | 38 | -0.020989 | -0.79758
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11347 | 38 | -0.020989 | -0.79758
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.002992 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40691 | 0 | -0.020995 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21762 | 0 | -0.021068 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22068 | 0 | -0.021068 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11954 | 0 | -0.021068 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09195 | 0 | -0.021068 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.003112 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.56016 | 0 | -0.021115 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.003112 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49356 | 0 | -0.021115 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.003112 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.48858 | 0 | -0.021115 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.003113 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.70976 | 228 | -0.021116 | -4.8144
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1993 | 0 | -0.021117 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1968 | 0 | -0.021117 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25722 | 0 | -0.021117 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22919 | 0 | -0.021117 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.003115 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.050463 | 0 | -0.021118 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.003115 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.66349 | 213 | -0.021118 | -4.4981
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.003122 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.46518 | 0 | -0.021125 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.003122 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20324 | 0 | -0.021125 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.003124 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.51546 | 165 | -0.021127 | -3.486
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.003127 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.52846 | 169 | -0.02113 | -3.571
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.003129 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.037548 | 12 | -0.021132 | -0.25358
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.003129 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.021132 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.003162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11067 | 0 | -0.021165 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.52093 | 0 | -0.021195 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50146 | 0 | -0.021195 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50274 | 0 | -0.021195 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50114 | 0 | -0.021195 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85865 | 0 | -0.021195 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.00323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.25194 | 0 | -0.021233 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.00323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.2584 | 0 | -0.021233 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14987 | 46 | -0.021261 | -0.97801
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14987 | 46 | -0.021261 | -0.97801
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14987 | 46 | -0.021261 | -0.97801
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17919 | 55 | -0.021261 | -1.1694
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17919 | 55 | -0.021261 | -1.1694
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17593 | 54 | -0.021261 | -1.1481
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.21885 | 0 | -0.02137 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.20202 | 0 | -0.02137 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.21885 | 0 | -0.02137 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.21885 | 0 | -0.02137 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31313 | 0 | -0.021444 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30143 | 0 | -0.021444 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.29937 | 0 | -0.021444 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18753 | 0 | -0.021444 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04198 | 0 | -0.021444 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.003629 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.021632 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.003791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.18955 | 50 | -0.021794 | -1.0897
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28306 | 0 | -0.022001 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26667 | 0 | -0.022001 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21189 | 0 | -0.022001 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.61249 | 0 | -0.022001 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.61369 | 0 | -0.022001 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.6089 | 0 | -0.022001 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.38381 | 0 | -0.022001 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.97551 | 0 | -0.022001 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15992 | 0 | -0.022001 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.128 | 0 | -0.022003 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12 | 0 | -0.022003 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4012 | 0 | -0.022003 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.3716 | 0 | -0.022003 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4108 | 0 | -0.022003 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.408 | 0 | -0.022003 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.004507 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.72563 | 161 | -0.02251 | -3.6241
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.004507 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.74816 | 166 | -0.02251 | -3.7367
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.004507 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.1177 | 248 | -0.02251 | -5.5825
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.004507 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -2.4608 | 546 | -0.02251 | -12.2905
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.004507 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -2.898 | 0 | -0.02251 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.004507 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.058591 | 13 | -0.02251 | -0.29263
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.004549 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15012 | 0 | -0.022552 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.00465 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75795 | 0 | -0.022653 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.00465 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75795 | 0 | -0.022653 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.00465 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1393 | 0 | -0.022653 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.004658 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -3.0324 | 651 | -0.022661 | -14.7523
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.004658 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -2.6271 | 564 | -0.022661 | -12.7808
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.004658 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -2.7948 | 600 | -0.022661 | -13.5966
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.004692 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2163 | 0 | -0.022695 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.005202 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17167 | 0 | -0.023205 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.005202 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13005 | 0 | -0.023205 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.005202 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.023205 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.62737 | 0 | -0.023655 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.62737 | 0 | -0.023655 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67259 | 0 | -0.023655 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.61889 | 0 | -0.023655 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.005916 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42004 | 0 | -0.023919 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.005916 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.05916 | 0 | -0.023919 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3875 | 0 | -0.024253 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44625 | 0 | -0.024253 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28125 | 0 | -0.024253 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63125 | 0 | -0.024253 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5375 | 0 | -0.024253 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55 | 0 | -0.024253 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3125 | 0 | -0.024253 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1125 | 0 | -0.024253 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5875 | 0 | -0.024253 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4375 | 0 | -0.024253 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39375 | 0 | -0.024253 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45 | 0 | -0.024253 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.405 | 0 | -0.024253 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63125 | 0 | -0.024253 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.60625 | 0 | -0.024253 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64375 | 0 | -0.024253 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.475 | 0 | -0.024253 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5 | 0 | -0.024253 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5 | 0 | -0.024253 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0688 | 0 | -0.024253 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.007638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.50411 | 66 | -0.025641 | -1.6923
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.007731 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.046386 | 0 | -0.025734 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61423 | 76 | -0.026085 | -1.9825
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61423 | 76 | -0.026085 | -1.9825
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.84861 | 105 | -0.026085 | -2.7389
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.59807 | 74 | -0.026085 | -1.9303
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.59807 | 74 | -0.026085 | -1.9303
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.82436 | 102 | -0.026085 | -2.6607
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.008123 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -10.828 | 0 | -0.026126 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.008123 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -10.7873 | 0 | -0.026126 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.008319 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026322 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.92699 | 0 | -0.029737 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.95045 | 0 | -0.029737 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.92699 | 0 | -0.029737 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.93872 | 0 | -0.029737 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.91995 | 0 | -0.029737 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.29335 | 0 | -0.029737 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.53976 | 0 | -0.029737 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.32855 | 0 | -0.029737 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5116 | 0 | -0.029737 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.86832 | 0 | -0.029737 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.011834 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56803 | 0 | -0.029837 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.34034 | 0 | -0.030158 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.085085 | 0 | -0.030158 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47404 | 0 | -0.030158 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18232 | 0 | -0.030158 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.085085 | 0 | -0.030158 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18232 | 0 | -0.030158 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47404 | 0 | -0.030158 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47404 | 0 | -0.030158 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.012202 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.097616 | 0 | -0.030205 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.012292 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18438 | 0 | -0.030295 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.012292 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28272 | 0 | -0.030295 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.012382 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.2724 | 22 | -0.030385 | -0.66847
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.012382 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1362 | 11 | -0.030385 | -0.33423
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.012382 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1362 | 11 | -0.030385 | -0.33423
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5963 | 47.7 | -0.030504 | -1.455
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.46629 | 37.3 | -0.030504 | -1.1378
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57505 | 46 | -0.030504 | -1.4032
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60005 | 48 | -0.030504 | -1.4642
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.012535 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.91505 | 0 | -0.030538 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.9856 | 0 | -0.03057 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.9228 | 0 | -0.03057 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.2567 | 0 | -0.03057 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8222 | 0 | -0.03057 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8473 | 0 | -0.03057 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.596 | 0 | -0.03057 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.012567 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.1508 | 0 | -0.03057 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 25 | -0.030619 | -0.76547
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 25 | -0.030619 | -0.76547
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 25 | -0.030619 | -0.76547
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.20186 | 16 | -0.030619 | -0.4899
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 25 | -0.030619 | -0.76547
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 25 | -0.030619 | -0.76547
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 25 | -0.030619 | -0.76547
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.18924 | 15 | -0.030619 | -0.45928
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.012673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8249 | 144 | -0.030676 | -4.4173
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.012673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3825 | 188 | -0.030676 | -5.7671
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.012691 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.2642 | 336 | -0.030694 | -10.3132
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.012691 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2844 | 180 | -0.030694 | -5.5249
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.012693 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8824 | 0 | -0.030696 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.012693 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8862 | 0 | -0.030696 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.012693 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.942 | 0 | -0.030696 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.012695 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2851 | 180 | -0.030698 | -5.5256
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.012719 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.2481 | 334 | -0.030722 | -10.2611
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.012719 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.3245 | 340 | -0.030722 | -10.4455
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.012719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2894 | 180 | -0.030722 | -5.53
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.012719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2894 | 180 | -0.030722 | -5.53
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.012723 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.31807 | 0 | -0.030726 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.012723 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.31807 | 0 | -0.030726 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.012736 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48397 | 0 | -0.030739 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.012736 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48397 | 0 | -0.030739 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.012793 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.371 | 0 | -0.030796 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2041 | 94 | -0.030813 | -2.8964
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52521 | 41 | -0.030813 | -1.2633
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.48678 | 38 | -0.030813 | -1.1709
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.24339 | 19 | -0.030813 | -0.58545
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2041 | 94 | -0.030813 | -2.8964
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46116 | 36 | -0.030813 | -1.1093
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.55083 | 43 | -0.030813 | -1.325
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.28182 | 22 | -0.030813 | -0.67789
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8959 | 148 | -0.030813 | -4.5603
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.6405 | 50 | -0.030813 | -1.5406
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.70455 | 55 | -0.030813 | -1.6947
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.6405 | 50 | -0.030813 | -1.5406
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.012817 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.03082 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.012817 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.48705 | 38 | -0.03082 | -1.1712
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.012817 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.24737 | 19.3 | -0.03082 | -0.59483
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.012817 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.19226 | 15 | -0.03082 | -0.4623
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.012817 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.6024 | 47 | -0.03082 | -1.4485
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8482 | 144 | -0.030838 | -4.4407
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8482 | 144 | -0.030838 | -4.4407
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1948 | 171 | -0.030838 | -5.2733
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6568 | 207 | -0.030838 | -6.3835
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7813 | 216.7 | -0.030838 | -6.6826
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1061 | 242 | -0.030838 | -7.4628
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.01285 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8825 | 146.5 | -0.030853 | -4.52
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.01285 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9005 | 147.9 | -0.030853 | -4.5632
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.01285 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2231 | 173 | -0.030853 | -5.3376
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.012946 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15535 | 0 | -0.030949 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.012946 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14241 | 0 | -0.030949 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.012946 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15535 | 0 | -0.030949 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.012996 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.030999 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.013038 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031041 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.013243 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.3298 | 629 | -0.031246 | -19.6537
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.013293 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31903 | 24 | -0.031296 | -0.7511
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.013293 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.31903 | 24 | -0.031296 | -0.7511
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.013293 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.30574 | 23 | -0.031296 | -0.71981
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.013309 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031312 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.01331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.331 | 100 | -0.031313 | -3.1313
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.01331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.331 | 100 | -0.031313 | -3.1313
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.01331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031313 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.01331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031313 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.01331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031313 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.01331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031313 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.013384 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031387 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014386 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -5.6969 | 396 | -0.032389 | -12.826
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.01522 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.88276 | 58 | -0.033223 | -1.9269
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.01522 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3546 | 89 | -0.033223 | -2.9568
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.66968 | 44 | -0.033223 | -1.4618
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.66968 | 44 | -0.033223 | -1.4618
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.65446 | 43 | -0.033223 | -1.4286
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.6849 | 45 | -0.033223 | -1.495
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.015232 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.3167 | 546 | -0.033235 | -18.1463
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.015232 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -11.424 | 750 | -0.033235 | -24.9262
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.015279 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18335 | 0 | -0.033282 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.015306 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3724 | 155 | -0.033309 | -5.1629
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.015306 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.602 | 170 | -0.033309 | -5.6625
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.015306 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3724 | 155 | -0.033309 | -5.1629
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.015318 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.2344 | 407 | -0.033321 | -13.5616
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.01533 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.204 | 209 | -0.033333 | -6.9666
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.01533 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3113 | 216 | -0.033333 | -7.1999
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.70518 | 46 | -0.033333 | -1.5333
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.72051 | 47 | -0.033333 | -1.5667
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.70518 | 46 | -0.033333 | -1.5333
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.70518 | 46 | -0.033333 | -1.5333
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.015347 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.323 | 412 | -0.03335 | -13.7402
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.015347 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.1388 | 400 | -0.03335 | -13.34
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01536 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -6.5126 | 424 | -0.033363 | -14.1459
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01536 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -6.528 | 425 | -0.033363 | -14.1793
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015412 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.033415 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015412 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.033415 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015412 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.033415 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3185 | 147 | -0.033775 | -4.9649
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1765 | 138 | -0.033775 | -4.6609
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2081 | 140 | -0.033775 | -4.7285
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3185 | 147 | -0.033775 | -4.9649
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8705 | 182 | -0.033775 | -6.147
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1229 | 198 | -0.033775 | -6.6874
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8302 | 114 | -0.034057 | -3.8825
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.564 | 222 | -0.034057 | -7.5607
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9539 | 184 | -0.034057 | -6.2665
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5961 | 224 | -0.034057 | -7.6288
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8462 | 115 | -0.034057 | -3.9166
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.01619 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.06476 | 0 | -0.034193 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.016266 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.039038 | 0 | -0.034269 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.016266 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.039038 | 0 | -0.034269 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3218 | 142 | -0.034354 | -4.8783
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3709 | 145 | -0.034354 | -4.9813
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.469 | 151 | -0.034354 | -5.1875
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.7418 | 290 | -0.034354 | -9.9627
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.016454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03949 | 0 | -0.034457 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.016454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03949 | 0 | -0.034457 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.016454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.046071 | 0 | -0.034457 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7967 | 223.9 | -0.03496 | -7.8275
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8153 | 225 | -0.03496 | -7.866
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8085 | 224.6 | -0.03496 | -7.852
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8442 | 226.7 | -0.03496 | -7.9254
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.017019 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.23316 | 0 | -0.035022 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.017361 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -7.5173 | 433 | -0.035364 | -15.3126
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.017366 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.31259 | 0 | -0.035369 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.017366 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.31259 | 0 | -0.035369 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.017366 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.26049 | 0 | -0.035369 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.017378 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.1488 | 584 | -0.035381 | -20.6625
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.017378 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.3399 | 595 | -0.035381 | -21.0517
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.017388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.3377 | 422 | -0.035391 | -14.935
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.017456 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10474 | 0 | -0.035459 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.017546 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.49129 | 0 | -0.035549 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.017546 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.50883 | 0 | -0.035549 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.8874 | 50 | -0.035751 | -1.7875
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.8874 | 50 | -0.035751 | -1.7875
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.8874 | 50 | -0.035751 | -1.7875
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.8874 | 50 | -0.035751 | -1.7875
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.018124 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32623 | 0 | -0.036127 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.018124 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32623 | 0 | -0.036127 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.019426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0693 | 158 | -0.037429 | -5.9138
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.019426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1082 | 160 | -0.037429 | -5.9886
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.019426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3996 | 175 | -0.037429 | -6.5501
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.0196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.989 | 152.5 | -0.037603 | -5.7345
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.0196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9302 | 149.5 | -0.037603 | -5.6216
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.0196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.559 | 232.6 | -0.037603 | -8.7465
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.019631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.5913 | 132 | -0.037634 | -4.9677
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.019631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.6306 | 134 | -0.037634 | -5.043
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.019631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3408 | 323 | -0.037634 | -12.1558
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.019795 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69283 | 0 | -0.037798 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.019795 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.67303 | 0 | -0.037798 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.019795 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69283 | 0 | -0.037798 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.99122 | 49 | -0.038232 | -1.8734
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.93053 | 46 | -0.038232 | -1.7587
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.93053 | 46 | -0.038232 | -1.7587
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.95076 | 47 | -0.038232 | -1.7969
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.020229 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1153 | 154 | -0.038232 | -5.8877
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.020229 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9939 | 148 | -0.038232 | -5.6583
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.97099 | 48 | -0.038232 | -1.8351
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.97099 | 48 | -0.038232 | -1.8351
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.020454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16363 | 0 | -0.038457 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.020454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16363 | 0 | -0.038457 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.020503 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3559 | 310 | -0.038506 | -11.9369
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.020503 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.4677 | 413 | -0.038506 | -15.903
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.87016 | 42 | -0.038721 | -1.6263
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.91159 | 44 | -0.038721 | -1.7037
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.91159 | 44 | -0.038721 | -1.7037
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.97375 | 47 | -0.038721 | -1.8199
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.055032 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.039178 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.055032 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.039178 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.024592 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.9928 | 569 | -0.042595 | -24.2366
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.024592 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.288 | 581 | -0.042595 | -24.7477

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3407 ELM_MOTT - 3575 WACONCST C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.024592 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.9928 | 0 | -0.042595 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.024592 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.288 | 0 | -0.042595 | 0 | 0 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.055032 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.039178 | 0 | 0 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.055032 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.039178 | 0 | 0 | 0 | Weighted Shift Factors
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.87016 | 42 | -0.038721 | -1.6263 | 42 | 1.6263 | North | 0.018003
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.91159 | 44 | -0.038721 | -1.7037 | 86 | 3.33 | South | -0.015854
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.91159 | 44 | -0.038721 | -1.7037 | 130 | 5.0337 |  | 0.033857
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.020718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.97375 | 47 | -0.038721 | -1.8199 | 177 | 6.8536
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.020503 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3559 | 310 | -0.038506 | -11.9369 | 487 | 18.7905 | Line Rating | 378.15
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.020503 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.4677 | 413 | -0.038506 | -15.903 |  |  | Conc Gen | 487
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.020454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16363 | 0 | -0.038457 | 0 |  |  | Weighted Imp. | 18.7905
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.020454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16363 | 0 | -0.038457 | 0 |  |  | PTDF | 0.038584
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.99122 | 49 | -0.038232 | -1.8734
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.93053 | 46 | -0.038232 | -1.7587 |  |  | Concentration | 1.1396
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.93053 | 46 | -0.038232 | -1.7587
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.95076 | 47 | -0.038232 | -1.7969
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.020229 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1153 | 154 | -0.038232 | -5.8877
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.020229 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9939 | 148 | -0.038232 | -5.6583
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.97099 | 48 | -0.038232 | -1.8351
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.020229 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.97099 | 48 | -0.038232 | -1.8351
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.019795 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69283 | 0 | -0.037798 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.019795 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.67303 | 0 | -0.037798 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.019795 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69283 | 0 | -0.037798 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.019631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.5913 | 132 | -0.037634 | -4.9677
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.019631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.6306 | 134 | -0.037634 | -5.043
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.019631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3408 | 323 | -0.037634 | -12.1558
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.0196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.989 | 152.5 | -0.037603 | -5.7345
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.0196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9302 | 149.5 | -0.037603 | -5.6216
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.0196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.559 | 232.6 | -0.037603 | -8.7465
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.019426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0693 | 158 | -0.037429 | -5.9138
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.019426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1082 | 160 | -0.037429 | -5.9886
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.019426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3996 | 175 | -0.037429 | -6.5501
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.018124 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32623 | 0 | -0.036127 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.018124 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32623 | 0 | -0.036127 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.8874 | 50 | -0.035751 | -1.7875
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.8874 | 50 | -0.035751 | -1.7875
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.8874 | 50 | -0.035751 | -1.7875
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.017748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.8874 | 50 | -0.035751 | -1.7875
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.017546 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.49129 | 0 | -0.035549 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.017546 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.50883 | 0 | -0.035549 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.017456 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10474 | 0 | -0.035459 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.017388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.3377 | 422 | -0.035391 | -14.935
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.017378 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.1488 | 0 | -0.035381 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.017378 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.3399 | 0 | -0.035381 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.017366 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.31259 | 0 | -0.035369 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.017366 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.31259 | 0 | -0.035369 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.017366 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.26049 | 0 | -0.035369 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.017361 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -7.5173 | 0 | -0.035364 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.017019 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.23316 | 0 | -0.035022 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7967 | 223.9 | -0.03496 | -7.8275
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8153 | 225 | -0.03496 | -7.866
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8085 | 224.6 | -0.03496 | -7.852
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.016957 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8442 | 226.7 | -0.03496 | -7.9254
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.016454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03949 | 0 | -0.034457 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.016454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03949 | 0 | -0.034457 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.016454 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.046071 | 0 | -0.034457 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3218 | 142 | -0.034354 | -4.8783
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3709 | 145 | -0.034354 | -4.9813
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.469 | 151 | -0.034354 | -5.1875
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.016351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.7418 | 290 | -0.034354 | -9.9627
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.016266 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.039038 | 0 | -0.034269 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.016266 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.039038 | 0 | -0.034269 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.01619 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.06476 | 0 | -0.034193 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8302 | 0 | -0.034057 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.564 | 0 | -0.034057 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9539 | 0 | -0.034057 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5961 | 0 | -0.034057 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8462 | 0 | -0.034057 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3185 | 147 | -0.033775 | -4.9649
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1765 | 138 | -0.033775 | -4.6609
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2081 | 140 | -0.033775 | -4.7285
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3185 | 147 | -0.033775 | -4.9649
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8705 | 182 | -0.033775 | -6.147
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.015772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1229 | 198 | -0.033775 | -6.6874
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015412 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.033415 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015412 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.033415 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015412 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.033415 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01536 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -6.5126 | 0 | -0.033363 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01536 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -6.528 | 0 | -0.033363 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.015347 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.323 | 412 | -0.03335 | -13.7402
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.015347 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.1388 | 400 | -0.03335 | -13.34
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.01533 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.204 | 209 | -0.033333 | -6.9666
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.01533 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3113 | 216 | -0.033333 | -7.1999
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.70518 | 46 | -0.033333 | -1.5333
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.72051 | 47 | -0.033333 | -1.5667
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.70518 | 46 | -0.033333 | -1.5333
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.01533 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.70518 | 46 | -0.033333 | -1.5333
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.015318 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.2344 | 407 | -0.033321 | -13.5616
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.015306 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3724 | 155 | -0.033309 | -5.1629
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.015306 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.602 | 170 | -0.033309 | -5.6625
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.015306 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3724 | 155 | -0.033309 | -5.1629
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.015279 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18335 | 0 | -0.033282 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.015232 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.3167 | 0 | -0.033235 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.015232 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -11.424 | 0 | -0.033235 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.01522 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.88276 | 58 | -0.033223 | -1.9269
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.01522 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3546 | 89 | -0.033223 | -2.9568
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.66968 | 44 | -0.033223 | -1.4618
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.66968 | 44 | -0.033223 | -1.4618
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.65446 | 43 | -0.033223 | -1.4286
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.01522 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.6849 | 45 | -0.033223 | -1.495
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014386 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -5.6969 | 0 | -0.032389 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.013384 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031387 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.01331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.331 | 100 | -0.031313 | -3.1313
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.01331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.331 | 100 | -0.031313 | -3.1313
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.01331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031313 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.01331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031313 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.01331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031313 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.01331 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031313 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.013309 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031312 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.013293 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.31903 | 24 | -0.031296 | -0.7511
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.013293 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.31903 | 24 | -0.031296 | -0.7511
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.013293 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.30574 | 23 | -0.031296 | -0.71981
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.013243 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.3298 | 0 | -0.031246 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.013081 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.10988 | 8.4 | -0.031084 | -0.26111
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.013038 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031041 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.012996 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.030999 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.012946 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15535 | 0 | -0.030949 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.012946 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14241 | 0 | -0.030949 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.012946 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15535 | 0 | -0.030949 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.01285 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8825 | 146.5 | -0.030853 | -4.52
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.01285 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9005 | 147.9 | -0.030853 | -4.5632
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.01285 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2231 | 173 | -0.030853 | -5.3376
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6568 | 207 | -0.030838 | -6.3835
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7813 | 216.7 | -0.030838 | -6.6826
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1061 | 242 | -0.030838 | -7.4628
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8482 | 144 | -0.030838 | -4.4407
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8482 | 144 | -0.030838 | -4.4407
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.012835 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1948 | 171 | -0.030838 | -5.2733
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.012817 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.48705 | 38 | -0.03082 | -1.1712
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.012817 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.24737 | 19.3 | -0.03082 | -0.59483
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.012817 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.19226 | 15 | -0.03082 | -0.4623
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.012817 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.6024 | 47 | -0.03082 | -1.4485
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.012817 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.03082 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2041 | 0 | -0.030813 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52521 | 0 | -0.030813 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.48678 | 0 | -0.030813 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.24339 | 0 | -0.030813 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2041 | 0 | -0.030813 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46116 | 0 | -0.030813 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.55083 | 0 | -0.030813 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.28182 | 0 | -0.030813 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8959 | 0 | -0.030813 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.6405 | 0 | -0.030813 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.70455 | 0 | -0.030813 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.01281 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.6405 | 0 | -0.030813 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.012793 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.371 | 0 | -0.030796 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.012736 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48397 | 0 | -0.030739 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.012736 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48397 | 0 | -0.030739 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.012723 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.31807 | 0 | -0.030726 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.012723 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.31807 | 0 | -0.030726 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.012719 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.2481 | 334 | -0.030722 | -10.2611
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.012719 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.3245 | 340 | -0.030722 | -10.4455
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.012719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2894 | 180 | -0.030722 | -5.53
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.012719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2894 | 180 | -0.030722 | -5.53
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.012695 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2851 | 180 | -0.030698 | -5.5256
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.012693 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8824 | 0 | -0.030696 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.012693 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8862 | 0 | -0.030696 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.012693 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.942 | 0 | -0.030696 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.012691 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.2642 | 336 | -0.030694 | -10.3132
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.012691 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2844 | 180 | -0.030694 | -5.5249
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.012673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.8249 | 144 | -0.030676 | -4.4173
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.012673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3825 | 188 | -0.030676 | -5.7671
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 0 | -0.030619 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 0 | -0.030619 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 0 | -0.030619 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.20186 | 0 | -0.030619 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 0 | -0.030619 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 0 | -0.030619 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.3154 | 0 | -0.030619 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.012616 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.18924 | 0 | -0.030619 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.9856 | 0 | -0.03057 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.9228 | 0 | -0.03057 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.2567 | 0 | -0.03057 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8222 | 0 | -0.03057 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8473 | 0 | -0.03057 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.012567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.596 | 0 | -0.03057 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.012567 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.1508 | 0 | -0.03057 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.012535 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.91505 | 0 | -0.030538 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5963 | 47.7 | -0.030504 | -1.455
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.46629 | 37.3 | -0.030504 | -1.1378
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57505 | 46 | -0.030504 | -1.4032
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.012501 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60005 | 48 | -0.030504 | -1.4642
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.012382 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.2724 | 22 | -0.030385 | -0.66847
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.012382 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1362 | 11 | -0.030385 | -0.33423
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.012382 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1362 | 11 | -0.030385 | -0.33423
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.012292 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18438 | 0 | -0.030295 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.012292 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28272 | 0 | -0.030295 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.012202 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.097616 | 0 | -0.030205 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.34034 | 0 | -0.030158 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.085085 | 0 | -0.030158 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47404 | 0 | -0.030158 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18232 | 0 | -0.030158 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.085085 | 0 | -0.030158 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18232 | 0 | -0.030158 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47404 | 0 | -0.030158 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.012155 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47404 | 0 | -0.030158 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.011834 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56803 | 0 | -0.029837 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.92699 | 0 | -0.029737 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.95045 | 0 | -0.029737 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.92699 | 0 | -0.029737 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.93872 | 0 | -0.029737 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.91995 | 0 | -0.029737 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.29335 | 0 | -0.029737 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.53976 | 0 | -0.029737 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.32855 | 0 | -0.029737 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5116 | 0 | -0.029737 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.011734 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.86832 | 0 | -0.029737 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.008319 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026322 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.008123 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -10.828 | 0 | -0.026126 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.008123 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -10.7873 | 0 | -0.026126 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61423 | 76 | -0.026085 | -1.9825
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61423 | 76 | -0.026085 | -1.9825
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.84861 | 105 | -0.026085 | -2.7389
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.59807 | 74 | -0.026085 | -1.9303
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.59807 | 74 | -0.026085 | -1.9303
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.008082 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.82436 | 102 | -0.026085 | -2.6607
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.007731 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.046386 | 0 | -0.025734 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.007638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.50411 | 66 | -0.025641 | -1.6923
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3875 | 0 | -0.024253 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44625 | 0 | -0.024253 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28125 | 0 | -0.024253 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63125 | 0 | -0.024253 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5375 | 0 | -0.024253 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55 | 0 | -0.024253 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3125 | 0 | -0.024253 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1125 | 0 | -0.024253 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5875 | 0 | -0.024253 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4375 | 0 | -0.024253 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39375 | 0 | -0.024253 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45 | 0 | -0.024253 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.405 | 0 | -0.024253 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63125 | 0 | -0.024253 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.60625 | 0 | -0.024253 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64375 | 0 | -0.024253 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.475 | 0 | -0.024253 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5 | 0 | -0.024253 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5 | 0 | -0.024253 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.00625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0688 | 0 | -0.024253 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.005916 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42004 | 0 | -0.023919 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.005916 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.05916 | 0 | -0.023919 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.62737 | 0 | -0.023655 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.62737 | 0 | -0.023655 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.67259 | 0 | -0.023655 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.005652 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.61889 | 0 | -0.023655 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.005202 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17167 | 0 | -0.023205 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.005202 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13005 | 0 | -0.023205 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.005202 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.023205 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.004692 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2163 | 0 | -0.022695 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.004658 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -3.0324 | 0 | -0.022661 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.004658 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -2.6271 | 0 | -0.022661 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.004658 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -2.7948 | 0 | -0.022661 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.00465 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75795 | 0 | -0.022653 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.00465 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75795 | 0 | -0.022653 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.00465 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1393 | 0 | -0.022653 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.004549 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15012 | 0 | -0.022552 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.004507 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.72563 | 161 | -0.02251 | -3.6241
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.004507 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.74816 | 166 | -0.02251 | -3.7367
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.004507 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.1177 | 248 | -0.02251 | -5.5825
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.004507 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -2.4608 | 546 | -0.02251 | -12.2905
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.004507 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -2.898 | 0 | -0.02251 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.004507 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.058591 | 13 | -0.02251 | -0.29263
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4012 | 0 | -0.022003 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.3716 | 0 | -0.022003 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4108 | 0 | -0.022003 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.004 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.408 | 0 | -0.022003 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.128 | 0 | -0.022003 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12 | 0 | -0.022003 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28306 | 0 | -0.022001 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26667 | 0 | -0.022001 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21189 | 0 | -0.022001 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.61249 | 0 | -0.022001 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.61369 | 0 | -0.022001 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.6089 | 0 | -0.022001 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.38381 | 0 | -0.022001 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.003998 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.97551 | 0 | -0.022001 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.003998 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15992 | 0 | -0.022001 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.003791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.18955 | 50 | -0.021794 | -1.0897
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.003629 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.021632 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31313 | 0 | -0.021444 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30143 | 0 | -0.021444 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.29937 | 0 | -0.021444 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18753 | 0 | -0.021444 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.003441 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04198 | 0 | -0.021444 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.21885 | 0 | -0.02137 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.20202 | 0 | -0.02137 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.21885 | 0 | -0.02137 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.003367 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.21885 | 0 | -0.02137 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14987 | 46 | -0.021261 | -0.97801
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14987 | 46 | -0.021261 | -0.97801
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14987 | 46 | -0.021261 | -0.97801
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17919 | 55 | -0.021261 | -1.1694
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17919 | 55 | -0.021261 | -1.1694
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.003258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17593 | 54 | -0.021261 | -1.1481
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.00323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.25194 | 0 | -0.021233 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.00323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.2584 | 0 | -0.021233 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.52093 | 0 | -0.021195 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50146 | 0 | -0.021195 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50274 | 0 | -0.021195 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50114 | 0 | -0.021195 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.003192 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85865 | 0 | -0.021195 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.003162 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11067 | 0 | -0.021165 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.003129 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.037548 | 12 | -0.021132 | -0.25358
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.003129 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.021132 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.003127 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.52846 | 169 | -0.02113 | -3.571
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.003124 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.51546 | 165 | -0.021127 | -3.486
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.003122 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.46518 | 0 | -0.021125 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.003122 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20324 | 0 | -0.021125 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.003115 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.66349 | 213 | -0.021118 | -4.4981
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.003115 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.050463 | 0 | -0.021118 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1993 | 0 | -0.021117 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1968 | 0 | -0.021117 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25722 | 0 | -0.021117 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.003114 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22919 | 0 | -0.021117 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.003113 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.70976 | 228 | -0.021116 | -4.8144
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.003112 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.56016 | 0 | -0.021115 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.003112 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49356 | 0 | -0.021115 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.003112 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.48858 | 0 | -0.021115 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21762 | 0 | -0.021068 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22068 | 0 | -0.021068 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11954 | 0 | -0.021068 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09195 | 0 | -0.021068 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.002992 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40691 | 0 | -0.020995 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12541 | 42 | -0.020989 | -0.88154
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12541 | 42 | -0.020989 | -0.88154
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11347 | 38 | -0.020989 | -0.79758
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.002986 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11347 | 38 | -0.020989 | -0.79758
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.002967 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51329 | 0 | -0.02097 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.002967 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.40054 | 0 | -0.02097 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.2963 | 104 | -0.020852 | -2.1686
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.2963 | 104 | -0.020852 | -2.1686
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15385 | 54 | -0.020852 | -1.126
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.151 | 53 | -0.020852 | -1.1052
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15385 | 54 | -0.020852 | -1.126
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16239 | 57 | -0.020852 | -1.1886
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15385 | 54 | -0.020852 | -1.126
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15385 | 54 | -0.020852 | -1.126
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16524 | 58 | -0.020852 | -1.2094
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.002849 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16524 | 58 | -0.020852 | -1.2094
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.002803 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -2.0602 | 735 | -0.020806 | -15.2924
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.094248 | 0 | -0.020775 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.096188 | 0 | -0.020775 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.090644 | 0 | -0.020775 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12723 | 0 | -0.020775 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.049064 | 0 | -0.020775 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.056549 | 0 | -0.020775 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.055163 | 0 | -0.020775 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09702 | 0 | -0.020775 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.049896 | 0 | -0.020775 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23673 | 0 | -0.020775 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.002772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41026 | 0 | -0.020775 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002734 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.032808 | 12 | -0.020737 | -0.24884
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.002685 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.013425 | 0 | -0.020688 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.002685 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.056385 | 0 | -0.020688 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17446 | 0 | -0.020687 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17714 | 0 | -0.020687 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18788 | 0 | -0.020687 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16909 | 0 | -0.020687 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16641 | 0 | -0.020687 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27914 | 0 | -0.020687 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.002684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15836 | 0 | -0.020687 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.002681 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.032172 | 0 | -0.020684 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.002678 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.9898 | 743 | -0.020681 | -15.366
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.002655 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.41684 | 0 | -0.020658 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.00264 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45408 | 172 | -0.020643 | -3.5506
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.00264 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45408 | 172 | -0.020643 | -3.5506
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.00264 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45408 | 172 | -0.020643 | -3.5506
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41547 | 0 | -0.020555 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41189 | 0 | -0.020555 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40551 | 0 | -0.020555 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.002552 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.687 | 0 | -0.020555 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.002522 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0038 | 398 | -0.020525 | -8.1689
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13821 | 56 | -0.020471 | -1.1464
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14561 | 59 | -0.020471 | -1.2078
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13821 | 56 | -0.020471 | -1.1464
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13821 | 56 | -0.020471 | -1.1464
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14561 | 59 | -0.020471 | -1.2078
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.002468 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13821 | 56 | -0.020471 | -1.1464
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.337 | 0 | -0.019951 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30389 | 0 | -0.019951 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.29999 | 0 | -0.019951 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.001948 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.29999 | 0 | -0.019951 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.001948 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31558 | 0 | -0.019951 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.018003 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018003 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018003 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.016054 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -1.6054 | 0 | -0.00020024 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.00628 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.0095738 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.015854 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.015854 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.001814 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.087072 | 48 | 0.017668 | 0.84805
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.001814 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.083444 | 46 | 0.017668 | 0.81272
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.001814 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.19047 | 105 | 0.017668 | 1.8551
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018226 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018226 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.002372 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.040324 | 17 | 0.018226 | 0.30984
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018226 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.002372 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018226 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.002372 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.075904 | 0 | 0.018226 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.45304 | 0 | 0.018792 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.45833 | 0 | 0.018792 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.45833 | 0 | 0.018792 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.002938 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.1164 | 0 | 0.018792 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.003836 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.7761 | 0 | 0.01969 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.3185 | 0 | 0.023244 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.3185 | 0 | 0.023244 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1255 | 0 | 0.023244 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.00739 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1307 | 0 | 0.023244 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.008997 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.4405 | 0 | 0.024851 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.008997 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.3685 | 0 | 0.024851 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.010529 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5794 | 0 | 0.026383 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.012929 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.028783 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.013267 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.1592 | 0 | 0.029121 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.013267 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.7877 | 0 | 0.029121 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.013702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0649 | 150.7 | 0.029556 | 4.4541
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.013702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.069 | 151 | 0.029556 | 4.4629
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.013702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4307 | 177.4 | 0.029556 | 5.2432
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.013817 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0933 | 151.5 | 0.029671 | 4.4951
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.013817 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.1043 | 152.3 | 0.029671 | 4.5189
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.013817 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4525 | 177.5 | 0.029671 | 5.2666
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.015332 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7904 | 182 | 0.031186 | 5.6758
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.015332 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.4207 | 484 | 0.031186 | 15.0939
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.015523 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.77615 | 0 | 0.031377 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.015539 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.031393 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.01557 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3079 | 0 | 0.031424 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.015654 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1975 | 0 | 0.031508 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.015735 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2588 | 0 | 0.031589 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.3368 | 0 | 0.031643 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.0526 | 0 | 0.031643 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2894 | 0 | 0.031643 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.015789 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.2998 | 0 | 0.031643 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.015955 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.5247 | 0 | 0.031809 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.015955 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.6842 | 0 | 0.031809 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.015955 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.4449 | 0 | 0.031809 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.016226 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4339 | 0 | 0.03208 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.016226 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4339 | 0 | 0.03208 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.016238 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.299 | 0 | 0.032092 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.016241 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2993 | 0 | 0.032095 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.016263 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2197 | 0 | 0.032117 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.016263 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.301 | 0 | 0.032117 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.016263 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.65052 | 0 | 0.032117 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.016361 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3089 | 0 | 0.032215 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.016361 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3089 | 0 | 0.032215 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.016724 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.080275 | 0 | 0.032578 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7872 | 161 | 0.033166 | 5.3397
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8392 | 164 | 0.033166 | 5.4392
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8392 | 164 | 0.033166 | 5.4392
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.1672 | 414 | 0.033166 | 13.7306
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8045 | 162 | 0.033166 | 5.3729
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7872 | 161 | 0.033166 | 5.3397
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8219 | 163 | 0.033166 | 5.406
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.017312 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0806 | 409 | 0.033166 | 13.5648
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.017598 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.828 | 388 | 0.033452 | 12.9793
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.017598 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.063 | 515 | 0.033452 | 17.2277
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1618 | 66 | 0.033457 | 2.2081
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1442 | 65 | 0.033457 | 2.1747
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1794 | 67 | 0.033457 | 2.2416
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1794 | 67 | 0.033457 | 2.2416
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.017603 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1794 | 67 | 0.033457 | 2.2416
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.017603 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033457 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.017603 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033457 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.017616 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.61656 | 0 | 0.03347 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.017616 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.52848 | 0 | 0.03347 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.017636 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.35272 | 20 | 0.03349 | 0.6698
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.017636 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.4409 | 25 | 0.03349 | 0.83724
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.017636 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.72308 | 41 | 0.03349 | 1.3731
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.01766 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6313 | 0 | 0.033514 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.017676 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3964 | 79 | 0.03353 | 2.6489
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.017676 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8737 | 106 | 0.03353 | 3.5542
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.017676 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5807 | 146 | 0.03353 | 4.8953
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.017676 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.3434 | 76 | 0.03353 | 2.5483
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.017682 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.8666 | 0 | 0.033536 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.017682 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.2379 | 0 | 0.033536 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.017682 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.2871 | 0 | 0.033536 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.017684 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.70736 | 40 | 0.033538 | 1.3415
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017687 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.033541 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017687 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.033541 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.0177 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0002 | 0 | 0.033554 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.017718 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.3289 | 0 | 0.033572 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.017718 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.4104 | 0 | 0.033572 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.017718 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5663 | 0 | 0.033572 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8381 | 160 | 0.033592 | 5.3747
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7671 | 156 | 0.033592 | 5.2403
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4766 | 196 | 0.033592 | 6.584
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7671 | 156 | 0.033592 | 5.2403
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7849 | 157 | 0.033592 | 5.2739
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.017738 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5121 | 198 | 0.033592 | 6.6512
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.017759 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.11721 | 0 | 0.033613 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.017759 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.60913 | 0 | 0.033613 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.017768 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.5742 | 370 | 0.033622 | 12.4401
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4875 | 0 | 0.033622 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5053 | 0 | 0.033622 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.4903 | 0 | 0.033622 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5408 | 0 | 0.033622 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5586 | 0 | 0.033622 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.017768 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.5081 | 0 | 0.033622 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7139 | 208.2 | 0.033692 | 7.0146
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5348 | 142.1 | 0.033692 | 4.7876
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3618 | 132.4 | 0.033692 | 4.4608
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.426 | 136 | 0.033692 | 4.5821
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6222 | 147 | 0.033692 | 4.9527
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.017838 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.746 | 210 | 0.033692 | 7.0753
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.007 | 0 | 0.033694 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6671 | 0 | 0.033694 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3182 | 0 | 0.033694 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.01784 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8267 | 0 | 0.033694 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2488 | 70 | 0.033694 | 2.3586
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2488 | 70 | 0.033694 | 2.3586
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.6556 | 92.8 | 0.033694 | 3.1268
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4272 | 80 | 0.033694 | 2.6955
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4272 | 80 | 0.033694 | 2.6955
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.01784 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0516 | 115 | 0.033694 | 3.8748
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.017848 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0342 | 170 | 0.033702 | 5.7293
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.017848 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.281 | 520 | 0.033702 | 17.5249
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.017864 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0361 | 0 | 0.033718 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.017866 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7955 | 0 | 0.03372 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.017882 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6823 | 0 | 0.033736 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.017898 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8338 | 0 | 0.033752 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.017909 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71636 | 0 | 0.033763 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.017909 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71636 | 0 | 0.033763 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.017926 | west | 8 | N | N | Nwest | Nwest | 1 | 0.46249 | 0 | 0.03378 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.017987 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.033841 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.018001 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1601 | 0 | 0.033855 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.018008 | west | 8 | N | N | Nwest | Nwest | 1 | 1.2606 | 0 | 0.033862 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.018008 | west | 8 | N | N | Nwest | Nwest | 1 | 1.3218 | 0 | 0.033862 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.018008 | west | 8 | N | N | Nwest | Nwest | 1 | 1.2678 | 0 | 0.033862 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.018009 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1611 | 0 | 0.033863 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.01804 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.059 | 0 | 0.033894 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7067 | 0 | 0.033899 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9699 | 0 | 0.033899 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.609 | 0 | 0.033899 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.018045 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1997 | 0 | 0.033899 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.018054 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2497 | 0 | 0.033908 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.018054 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2497 | 0 | 0.033908 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.018058 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033912 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.018093 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1712 | 0 | 0.033947 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.018093 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2157 | 0 | 0.033947 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.018093 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0794 | 0 | 0.033947 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1949 | 66 | 0.033959 | 2.2413
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.2492 | 69 | 0.033959 | 2.3432
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.2492 | 69 | 0.033959 | 2.3432
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.213 | 67 | 0.033959 | 2.2752
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.213 | 67 | 0.033959 | 2.2752
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.018105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.1768 | 65 | 0.033959 | 2.2073
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.018137 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.1402 | 118 | 0.033991 | 4.0109
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.018137 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0858 | 115 | 0.033991 | 3.9089
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.018137 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.0842 | 556 | 0.033991 | 18.8989
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.018145 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1431 | 0 | 0.033999 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.018158 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5603 | 0 | 0.034012 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.018158 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.179 | 0 | 0.034012 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.018159 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2699 | 0 | 0.034013 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.018159 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2699 | 0 | 0.034013 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.018163 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7981 | 0 | 0.034017 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.018163 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1079 | 0 | 0.034017 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.018163 | west | 7 | N | N | Nwest | Nwest | 1 | 0.45408 | 0 | 0.034017 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.018163 | west | 7 | N | N | Nwest | Nwest | 1 | 0.83005 | 0 | 0.034017 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.018163 | west | 7 | N | N | Nwest | Nwest | 1 | 0.83005 | 0 | 0.034017 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.018214 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.53 | 0 | 0.034068 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8086 | 0 | 0.034077 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3052 | 0 | 0.034077 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5375 | 0 | 0.034077 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.018223 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5899 | 0 | 0.034077 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68419 | 0 | 0.034099 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9613 | 0 | 0.034099 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4631 | 0 | 0.034099 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1712 | 0 | 0.034099 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9157 | 0 | 0.034099 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.018245 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.4687 | 0 | 0.034099 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.01839 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7585 | 0 | 0.034244 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.01839 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8574 | 0 | 0.034244 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.018438 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7657 | 0 | 0.034292 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.018599 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3894 | 0 | 0.034453 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.018599 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4396 | 0 | 0.034453 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.018612 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1167 | 60 | 0.034466 | 2.0679
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.018612 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1726 | 63 | 0.034466 | 2.1713
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.018644 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1186 | 0 | 0.034498 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.018649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0356 | 216.4 | 0.034503 | 7.4664
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.018649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.03 | 216.1 | 0.034503 | 7.456
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.018705 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0863 | 0 | 0.034559 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.018843 | west | 4 | Y | N | Ywest | Nwest | 1 | 12.2423 | 0 | 0.034697 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.01904 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.9686 | 366 | 0.034894 | 12.7711
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.019122 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.2833 | 224 | 0.034976 | 7.8346
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.01913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9025 | 204 | 0.034984 | 7.1367
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.01913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8451 | 201 | 0.034984 | 7.0317
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.01913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6295 | 242 | 0.034984 | 8.4661
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.38458 | 20 | 0.035083 | 0.70166
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.38458 | 20 | 0.035083 | 0.70166
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.38458 | 20 | 0.035083 | 0.70166
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.019229 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.32689 | 17 | 0.035083 | 0.59641
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.019245 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.1651 | 0 | 0.035099 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.019253 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.6049 | 395 | 0.035107 | 13.8672
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.019253 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.3751 | 435 | 0.035107 | 15.2714
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.019261 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.3785 | 435 | 0.035115 | 15.2749
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.019293 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.035147 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.019293 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.035147 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.019293 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.035147 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3788 | 224 | 0.035402 | 7.93
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4178 | 226 | 0.035402 | 8.0008
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1442 | 212 | 0.035402 | 7.5052
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.019548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1246 | 211 | 0.035402 | 7.4698
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.019866 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.8076 | 242 | 0.03572 | 8.6442
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.019927 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3301 | 217.3 | 0.035781 | 7.7752
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.019927 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.085 | 205 | 0.035781 | 7.3351
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.019927 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.4281 | 272.4 | 0.035781 | 9.7467
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.020035 | north | 3 | N | N | Nnorth | Nnorth | 1 | 23.1805 | 0 | 0.035889 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.020035 | north | 3 | N | N | Nnorth | Nnorth | 1 | 23.2005 | 0 | 0.035889 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.020168 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.036022 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.020515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.9083 | 288 | 0.036369 | 10.4742
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.020515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0157 | 147 | 0.036369 | 5.3462
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.020515 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0157 | 147 | 0.036369 | 5.3462
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.020679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0531 | 196 | 0.036533 | 7.1604
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.020679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2954 | 111 | 0.036533 | 4.0551
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.021175 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.2541 | 0 | 0.037029 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.021175 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.2541 | 0 | 0.037029 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.021242 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.549 | 0 | 0.037096 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.022002 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.39604 | 18 | 0.037856 | 0.6814
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.022002 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.39604 | 18 | 0.037856 | 0.6814
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.022002 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.83608 | 38 | 0.037856 | 1.4385
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.023155 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.039009 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.023155 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.223 | 787 | 0.039009 | 30.6999
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6361 | 70 | 0.039227 | 2.7459
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6127 | 69 | 0.039227 | 2.7066
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6127 | 69 | 0.039227 | 2.7066
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.023373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5894 | 68 | 0.039227 | 2.6674
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.024361 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7784 | 73 | 0.040215 | 2.9357
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.024361 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.899 | 119 | 0.040215 | 4.7856
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.024361 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.994 | 205 | 0.040215 | 8.244
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.024361 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.4848 | 102 | 0.040215 | 4.1019
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.024361 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.3387 | 96 | 0.040215 | 3.8606
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.026254 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4107 | 168 | 0.042108 | 7.0741
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.026254 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3629 | 90 | 0.042108 | 3.7897
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.026661 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.5997 | 0 | 0.042515 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.067214 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0082 | 0 | 0.083068 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.067214 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0082 | 0 | 0.083068 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.071274 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.1749 | 255 | 0.087128 | 22.2176
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.071274 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.6198 | 149 | 0.087128 | 12.982
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.071274 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.9049 | 153 | 0.087128 | 13.3305
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.080393 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0589 | 150 | 0.096247 | 14.437
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.080393 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4314 | 80 | 0.096247 | 7.6997

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 408
| 25 | 408
| 30 | 408
| 35 | 408
| 40 | 408
| 45 | 408
| 50 | 408
| 55 | 408
| 60 | 407
| 65 | 399
| 70 | 391
| 75 | 382
| 80 | 373
| 85 | 364
| 90 | 354
| 95 | 354
| 100 | 335
| 105 | 324
| 110 | 314
| 115 | 302
| Max | 408
| Min | 302
| Avg | 378.15