## test results
CRE test for: |  | 3405 THOUSE__ - 3412 TEMP_PEC | [5 empty] | PASS
Line Rating: |  | 1239.6
Direction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3405 THOUSE__ - 3412 TEMP_PEC
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.13539
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.18096
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.12263
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.039542
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3405 THOUSE__ - 3412 TEMP_PEC
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.14749
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.17766
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.12321
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.036838
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3405 THOUSE__ - 3412 TEMP_PEC
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.31305
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.01218
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.17223
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.30417
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.14142
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.15947
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.31305 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.31305 | 0.31305
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.37131
[6 empty] | Concentration |  | 1.1861 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.35921
[6 empty] | Concentration |  | 1.1474 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 84.6083
| Percent of line rating => | [6 empty] | 6.825% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.2839
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | 0.00097566 | 0.016614 | 0.015638 | 0.00097566
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.0019707 | 0.21915 | 0.22112 | -0.0019707
[7 empty] | B4 (S-W) | 0.00094017 | -0.38958 | -0.39052 | 0.00094017
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.0054777 | -0.18705 | -0.18157 | -0.0054777
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0029446 | 0.20179 | 0.20474 | -0.0029446
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | 0.2427%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -0.4903%
[7 empty] | B4 | 0.2339%
[7 empty] | B5 | -1.363%
[7 empty] | B6 | -0.7326%
[7 empty] | Max Abs Error | 1.363% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK 3414 TEMP_SS_
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.19433 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 49.5536
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.19433 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 28.9549
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.15799 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.3699
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.15799 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.3699
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.19433 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 29.7322
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.16187 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 24.2807
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.16187 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 12.9497
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14073 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 10.2734
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14073 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 16.7471
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14073 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 28.8501
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14073 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 14.3547
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14073 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 13.5103
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.13945 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.6734
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.13945 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.6734
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.14912 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 25.0522
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.14912 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 13.4208
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.14236 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.5624
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.14236 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.5624
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.14236 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 5.4096
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14249 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 41.0357
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14249 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 20.9453
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14249 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 20.9453
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.14218 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 15.9949
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.141 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 5.6401
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14101 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 11.1396
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14101 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 14.9467
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14101 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 20.587
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14101 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 10.7165
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14294 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 8.5765
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14294 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 9.0053
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.1408 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.8159
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.1408 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.52
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.1408 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 5.7727
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.048744 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 22.5685
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 7.9496
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 7.8291
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.07
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.07
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.07
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12045 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 13.7311
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12045 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 62.0307
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 8.2392
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.6138
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.6138
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.3641
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.3641
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 8.1144
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12422 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 8.6952
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12422 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 9.1175
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12422 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 8.7449
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 18.6859
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 27.4061
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12508 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 12.3828
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12508 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 7.6298
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12504 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 17.6312
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12508 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 3.127
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12508 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.7161
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12508 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.7161
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12504 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 15.0053
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.123 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 3.1735
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.12272 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 12.3338
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.12378 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 14.8541
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.1227 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 7.1169
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.123 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 26.3472
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12547 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 18.82
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12118 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.79975
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12118 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 4.1563
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12547 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 12.6722
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.12384 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 14.8603
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.13753 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 50.3367
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.13674 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 33.0913
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.13111 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 52.4436
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.13112 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 30.9438
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.13266 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 21.8884
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14121 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 28.8066
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14121 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 28.383
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14121 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 34.1726
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.7518
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.7518
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.7518
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 2.339
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.13931 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 16.7167
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.13461 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 8.0768
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14108 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 10.5808
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14108 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 11.2298
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14108 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 12.4713
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 22.5917
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.0269
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 27.6748
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.0269
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 22.1681
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 27.9572
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14145 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 24.0462
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14145 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 73.553
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14131 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 52.2858
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14102 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 78.6914
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14102 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 81.6529
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14102 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 113.9474
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.1448 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 16.2172
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.1448 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 14.4796
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.1448 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 54.7329
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.14569 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 31.658
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.14569 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 29.866
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.14569 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 39.6854
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.14611 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 112.5032
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 10.1863
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 10.0407
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 10.0407
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 9.8952
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.14506 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 167.8309
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.14506 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 167.976
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 34.7791
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 35.0897
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.15559 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 33.6686
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.15559 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 33.6219
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 32.916
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 32.7607
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.14796 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 58.4446
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.14762 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 64.2138
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.14796 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 64.363
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.14235 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 19.6444
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14388 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 16.978
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14388 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 16.5463
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14388 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 79.9978
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14104 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 54.7231
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14104 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 72.6351
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13443 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 105.526
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13443 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 106.8703
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13443 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 104.8538
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13207 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 24.0364
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13207 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 63.9209
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.13603 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 30.4703
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.13284 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 6.642
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.13289 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 5.5813
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.12455 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 76.6007
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.12455 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 73.1132
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.24531 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 131.7336
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.24531 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 193.0621
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.14575 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 10.9314
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.14575 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 32.3569
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.26963 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -153.4172
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17257 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -36.0673
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17257 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -37.2753
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.17249 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -70.2038
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.9383
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -8.1108
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.9383
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.9383
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.17289 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -73.3066
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.17289 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -73.4795
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17152 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -9.9483
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17152 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -15.2655
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -7.547
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -7.547
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -7.3754
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -7.7185
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.17277 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -71.1796
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.17277 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -69.1064
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.17129 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -93.5265
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.17129 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -128.4705
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.17339 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -10.5769
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.17339 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -16.4722
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.17339 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -26.1822
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.17216 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -26.6853
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.17216 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -29.2677
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.17216 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -26.6853
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.13857 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -3.0486
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.13857 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.5243
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.13857 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.5243
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -6.6709
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -5.2165
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -6.4332
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -6.7129
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.14612 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.7534
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.14612 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -1.6073
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.15257 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.6618
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.15257 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.6618
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.15257 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -3.5092
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.16198 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -64.1453
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.089094 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -118.7623
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.089094 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -118.3168
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14384 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -5.4659
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14384 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -2.7761
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14384 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -2.1576
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14384 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -6.7605
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10823 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 8.1169
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.12679 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 19.0187
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.11984 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 20.3125
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.055862 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 8.3793
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.12494 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 7.8712
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.1338 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 86.9312
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14158 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.6633
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14158 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.6633
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.19388 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -81.8157
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.21693 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -28.6344
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.21693 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -29.0682
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.21693 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -70.0674
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21903 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -34.6064
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21903 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -35.0445
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21903 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -38.3299
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.19502 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -113.8893
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.19502 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -116.0345
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.19482 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -84.3579
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -42.6787
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -42.8884
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -42.8121
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -43.2124
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.22581 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.8064
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.22581 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.8064
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.19245 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.4641
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.19245 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.4641
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.19245 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -2.8868
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.18965 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -2.5983
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.20133 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.624
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.20133 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.624
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.21825 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -7.6387
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.21825 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -7.4205
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.21825 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -7.6387
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.19535 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -5.4697
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.19535 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -5.6651
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12056 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 4.2195
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12056 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.6167
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -9.8621
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -9.8621
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -9.8621
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -9.8621
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.19543 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -1.1726
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.18452 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.44286
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.18452 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.44286
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.18452 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.51667
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.18184 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.72736
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.18203 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.43686
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.18203 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.43686
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -26.0572
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -24.4619
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -24.8164
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -26.0572
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -32.2613
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -35.0975
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.22062 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -33.6441
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.22062 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -32.9822
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.22062 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -51.3155
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -26.0946
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -26.6459
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -27.7485
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -53.2918
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.081574 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -2.6919
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.081574 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -2.0394
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.14612 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.7534
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.14016 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -10.2315
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -10.3409
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -10.6027
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -3.8025
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.95064
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -10.3409
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -10.4718
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -10.2624
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -3.2725
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -6.0213
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.1485 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -93.4078
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.14174 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -20.4108
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.14174 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -26.6475
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.17093 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -2.0511
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.10366 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.62197
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.1423 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -47.8141
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14263 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -47.6391
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14263 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -48.4949
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.14283 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -5.4277
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.14268 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.5671
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.14268 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.5671
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.14283 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -5.4274
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.14352 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -4.162
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.14232 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -21.1062
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.14232 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -21.1489
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.14232 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -21.7751
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -22.2508
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -21.5467
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -14.0828
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -20.4201
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -20.7017
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -17.8852
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.14439 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -21.1536
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.14439 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -21.3557
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.14439 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -24.98
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.14412 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -29.8322
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.14412 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -31.2302
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.14412 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -34.8763
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.14411 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -20.7521
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.14411 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -20.7521
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.14411 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -24.6432
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.22672 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -70.282
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.22672 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -93.6337
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -9.6231
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -10.0813
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -10.0813
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -10.7687
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -10.9834
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.311
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.311
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -10.5351
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.22415 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -34.5194
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.22415 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -33.1745
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -10.7593
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -10.7593
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.5857
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.5857
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 11.3822
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.8122
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.8122
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 14.1051
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 25.532
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 17.426
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 16.2365
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 16.678
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 18.0269
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 25.7527
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 26.482
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 16.0286
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 31.5503
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 24.9615
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 24.9146
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 15.1854
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.12093 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 18.0186
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12421 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.358
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12421 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.358
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.12409 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 27.9214
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12579 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.7244
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12579 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.7244
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 19.7838
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 19.9251
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 43.6657
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 20.2078
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 20.3491
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 43.807
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14286 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 28.0011
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14286 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 15.8578
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.14241 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 22.4993
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 22.9185
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 22.9185
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 57.8553
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 22.639
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 22.4993
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 22.7788
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 57.1565
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14165 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14165 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 19.7966
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 17.3889
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 19.3953
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 53.3706
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12625 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 19.0256
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12625 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 19.0634
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12625 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 22.3964
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12646 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 19.1585
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12646 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 19.2597
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12646 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 22.4465
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.26963 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -156.6527
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 73.2367
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 73.2367
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.039834 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 1.2747
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.035852 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 1.7209
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.035852 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 1.6492
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.47894
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 2.0355
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.039912 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.6785
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.87806
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.9978
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.035852 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 3.7645
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.1254 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 10.5333
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.10801 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 8.6406
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.10789 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.1841
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.10789 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.1841
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -2.9437
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -2.7732
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -2.2036
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -6.3696
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -6.3821
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -6.3322
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -3.9914
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -10.1448
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.6631
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -4.1732
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -3.8653
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -4.273
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -4.2439
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.041606 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -1.3314
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.041606 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -1.2482
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -6.7275
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -6.7275
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -7.2124
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -6.6366
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 13.0456
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 13.1055
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.029996 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -4.0795
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.047916 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -1.5812
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.257
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.257
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.1373
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.1373
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.063658 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -4.5197
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.063658 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.63658
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.049073 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -7.9989
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.049073 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -7.9989
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.049073 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -12.0229
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.2308
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -2.0592
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.2308
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.2308
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.0315 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -4.6935
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.0315 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -2.0507
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -3.2005
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -3.0809
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -3.0598
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -1.9168
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.42907
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.026389 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -19.607
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.027825 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -20.4514
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.025956 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.4644
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.025956 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.4644
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.025956 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.4644
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -3.1119
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.029711 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -5.14
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.029711 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -4.011
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -4.0604
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -4.0255
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -3.9631
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -6.7141
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -2.0099
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -1.9848
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -2.5941
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -2.3114
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -5.2723
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -5.0753
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -5.0882
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -5.072
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -8.6903
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.026465 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.13232
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.026465 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.55576
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 5.8904
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 5.9592
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 5.9592
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 14.516
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.024589 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -9.7864
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.5206
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.5206
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.5206
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.8181
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.8181
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -1.7851
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.10149 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 83.9297
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.10149 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 83.1179
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.049565 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -2.2849
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.7268
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.7268
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -9.2937
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.5498
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.5498
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -9.0281
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.031379 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -5.6482
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.031379 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -4.9767
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.031379 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -4.9265
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.031953 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -1.1184
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.037337 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -17.1377
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -1.7196
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -1.7461
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -1.8519
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -1.6667
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -1.6403
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -2.7514
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -1.5609
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -2.8061
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.7702
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.7702
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.017988 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -2.9141
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.026127 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -4.1019
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -2.1899
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -2.2208
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -1.2029
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.92532
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.032742 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -2.5539
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.032742 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -2.6194
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.031412 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.50887
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.031523 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -5.2013
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.031553 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -5.3325
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.031422 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -6.6929
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.031392 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -7.1574
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.031574 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.37889
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.031574 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.56833
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.039195 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -1.9598
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.9483
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.9483
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.5308
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.5025
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.5308
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -1.6159
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.5308
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.5308
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.6442
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.6442
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.027031 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.32437
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3424
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.4143
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3424
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3424
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.4143
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3424
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.083454 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -5.508
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.047419 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -7.6345
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.047419 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -7.8716
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.047419 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -11.7599
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.047419 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -25.8908
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.047419 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -30.4904
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.049166 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -32.0071
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.049166 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -27.7296
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.049166 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -29.4996
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.047419 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.61645
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.026429 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.31715
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.93418
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.95342
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.89847
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -1.2611
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.48633
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.56051
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.54677
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.96166
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.49457
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -2.3465
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -4.0664
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -4.1861
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -4.8208
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -3.0383
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -6.8193
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -5.8065
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -5.9416
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -3.3759
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -1.2153
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -6.3467
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -4.7263
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -4.2536
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -4.8613
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -4.3752
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -6.8193
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -6.5492
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -6.9544
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -5.1314
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.4014
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.4014
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -11.5456
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2667
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.10267 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 7.854
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10823 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 8.6581
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10823 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 4.329
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.10912 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.7292
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.10803 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 8.6426
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.10344 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 8.2755
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.10194 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 8.5631
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.10912 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.7292
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -20.6118
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 14.8385
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 28.8114
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 21.0459
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -40.1387
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -33.2681
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -40.5003
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -20.7926
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -18.0805
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.12857 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.7145
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.094367 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.078013 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.11244 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.53969
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.741
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 13.5908
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 17.0675
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 15.0447
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 13.2747
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 10.1773
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.1223 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 18.3444
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 13.6971
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 18.2019
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 22.6459
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 26.1158
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.14384 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.1088 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.15155 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -3.6651
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -5.7072
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -9.6865
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -13.5119
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -5.8935
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -5.4623
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -2.7311
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -13.5119
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -5.1748
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -6.181
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -3.1624
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.2964
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.0371
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.95064
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.0371
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.2964
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.2964
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -21.2741
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.1872
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -7.9059
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.1872
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14083 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -1.6899
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.13738 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -2.0607
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.13738 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -3.1598
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.13205 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -6.3386
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.13636 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -1.0909
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.14235 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -25.6228
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.1423 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -25.6147
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14263 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -25.6738
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14263 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -25.6738
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15157 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -15.1566
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15157 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -15.1566
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.5353
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.5353
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.5353
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -2.2626
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.5353
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.5353
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.5353
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -2.1212
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15157 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15157 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -75.783
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15157 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -75.783
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15157 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.15046 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.081574 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.14777 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.14618 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK 3414 TEMP_SS_ | [7 empty] | 84.6083
Number of Bus | Name of Bus | ID | Max MW | L:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK 3414 TEMP_SS_ | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.19433 | north | Y | 0.058938 | 0.37529 | 0.071699 | 0.23387 | 0.058938 | North | N | 0.058938 | 0
239 | BOSQUESW | 1 | 149 | 0.19433 | north | Y | 0.058938 | 0.37529 | 0.071699 | 0.23387 | 0.058938 | North | N | 0.058938 | 0
244 | WHITNYDM | 1 | 15 | 0.15799 | north | N | 0.022602 | 0.33895 | 0.035363 | 0.19753 | 0.022602 | North | N | 0.022602 | 0
245 | WHITNYDM | 2 | 15 | 0.15799 | north | N | 0.022602 | 0.33895 | 0.035363 | 0.19753 | 0.022602 | North | N | 0.022602 | 0
247 | BOSQUESW | 2 | 153 | 0.19433 | north | Y | 0.058938 | 0.37529 | 0.071699 | 0.23387 | 0.058938 | North | N | 0.058938 | 0
251 | BOSQUESW | 2 | 150 | 0.16187 | north | Y | 0.026481 | 0.34283 | 0.039242 | 0.20141 | 0.026481 | North | N | 0.026481 | 0
253 | BOSQUESW | 2 | 80 | 0.16187 | north | Y | 0.026481 | 0.34283 | 0.039242 | 0.20141 | 0.026481 | North | N | 0.026481 | 0
332 | RWMILLER | 1 | 73 | 0.14073 | north | Y | 0.0053421 | 0.32169 | 0.018103 | 0.18027 | 0.0053421 | North | N | 0.0053421 | 0
333 | RWMILLER | 2 | 119 | 0.14073 | north | Y | 0.0053421 | 0.32169 | 0.018103 | 0.18027 | 0.0053421 | North | N | 0.0053421 | 0
334 | RWMILLER | 3 | 205 | 0.14073 | north | Y | 0.0053421 | 0.32169 | 0.018103 | 0.18027 | 0.0053421 | North | N | 0.0053421 | 0
335 | RWMILLER | 4 | 102 | 0.14073 | north | Y | 0.0053421 | 0.32169 | 0.018103 | 0.18027 | 0.0053421 | North | N | 0.0053421 | 0
336 | RWMILLER | 5 | 96 | 0.14073 | north | Y | 0.0053421 | 0.32169 | 0.018103 | 0.18027 | 0.0053421 | North | N | 0.0053421 | 0
344 | MRSSHPRD | 1 | 12 | 0.13945 | north | N | 0.0040641 | 0.32042 | 0.016825 | 0.179 | 0.0040641 | North | N | 0.0040641 | 0
345 | MRSSHPRD | 2 | 12 | 0.13945 | north | N | 0.0040641 | 0.32042 | 0.016825 | 0.179 | 0.0040641 | North | N | 0.0040641 | 0
366 | JNSNCNTY | 1 | 168 | 0.14912 | north | Y | 0.01373 | 0.33008 | 0.026491 | 0.18866 | 0.01373 | North | N | 0.01373 | 0
367 | JNSNCNTY | 2 | 90 | 0.14912 | north | Y | 0.01373 | 0.33008 | 0.026491 | 0.18866 | 0.01373 | North | N | 0.01373 | 0
503 | NTHTEXAS | 1 | 18 | 0.14236 | north | Y | 0.0069671 | 0.32332 | 0.019728 | 0.1819 | 0.0069671 | North | N | 0.0069671 | 0
504 | NTHTEXAS | 2 | 18 | 0.14236 | north | Y | 0.0069671 | 0.32332 | 0.019728 | 0.1819 | 0.0069671 | North | N | 0.0069671 | 0
505 | NTHTEXAS | 3 | 38 | 0.14236 | north | Y | 0.0069671 | 0.32332 | 0.019728 | 0.1819 | 0.0069671 | North | N | 0.0069671 | 0
580 | JCKCNTY8 | 1 | 288 | 0.14249 | north | Y | 0.0070951 | 0.32345 | 0.019856 | 0.18203 | 0.0070951 | North | N | 0.0070951 | 0
581 | JCKCNTY8 | 2 | 147 | 0.14249 | north | Y | 0.0070951 | 0.32345 | 0.019856 | 0.18203 | 0.0070951 | North | N | 0.0070951 | 0
582 | JCKCNTY8 | 3 | 147 | 0.14249 | north | Y | 0.0070951 | 0.32345 | 0.019856 | 0.18203 | 0.0070951 | North | N | 0.0070951 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.14218 | north | Y | 0.0067871 | 0.32314 | 0.019548 | 0.18172 | 0.0067871 | North | N | 0.0067871 | 0
837 | NEWMAN_G | 1 | 40 | 0.141 | north | Y | 0.0056131 | 0.32196 | 0.018374 | 0.18055 | 0.0056131 | North | N | 0.0056131 | 0
842 | OLINGER_ | 1 | 79 | 0.14101 | north | Y | 0.0056171 | 0.32197 | 0.018378 | 0.18055 | 0.0056171 | North | N | 0.0056171 | 0
843 | OLINGER_ | 1 | 106 | 0.14101 | north | Y | 0.0056171 | 0.32197 | 0.018378 | 0.18055 | 0.0056171 | North | N | 0.0056171 | 0
844 | OLINGER_ | 1 | 146 | 0.14101 | north | Y | 0.0056171 | 0.32197 | 0.018378 | 0.18055 | 0.0056171 | North | N | 0.0056171 | 0
845 | OLINGER_ | 1 | 76 | 0.14101 | north | Y | 0.0056171 | 0.32197 | 0.018378 | 0.18055 | 0.0056171 | North | N | 0.0056171 | 0
923 | SPENCER_ | 1 | 60 | 0.14294 | north | Y | 0.0075521 | 0.3239 | 0.020313 | 0.18248 | 0.0075521 | North | N | 0.0075521 | 0
924 | SPENCER_ | 1 | 63 | 0.14294 | north | Y | 0.0075521 | 0.3239 | 0.020313 | 0.18248 | 0.0075521 | North | N | 0.0075521 | 0
948 | STEAM1 | 1 | 20 | 0.1408 | north | Y | 0.0054071 | 0.32176 | 0.018168 | 0.18034 | 0.0054071 | North | N | 0.0054071 | 0
949 | STEAM2 | 1 | 25 | 0.1408 | north | Y | 0.0054081 | 0.32176 | 0.018169 | 0.18034 | 0.0054081 | North | N | 0.0054081 | 0
950 | STEAM3 | 1 | 41 | 0.1408 | north | Y | 0.0054081 | 0.32176 | 0.018169 | 0.18034 | 0.0054081 | North | N | 0.0054081 | 0
990 | GIBN_CRE | 1 | 463 | 0.048744 | north | Y | -0.086646 | 0.22971 | -0.073885 | 0.088286 | 0.073885 | west | Y | 0.086646 | 5.9084
1002 | PBCTAGE_ | A | 66 | 0.12045 | west | Y | -0.014942 | 0.30141 | -0.0021808 | 0.15999 | 0.0021808 | west | N | 0.0021808 | 0
1003 | PBCTBGE_ | B | 65 | 0.12045 | west | Y | -0.014942 | 0.30141 | -0.0021808 | 0.15999 | 0.0021808 | west | N | 0.0021808 | 0
1004 | PBCTCGE_ | C | 67 | 0.12045 | west | Y | -0.014942 | 0.30141 | -0.0021808 | 0.15999 | 0.0021808 | west | N | 0.0021808 | 0
1005 | PBCTDGE_ | D | 67 | 0.12045 | west | Y | -0.014942 | 0.30141 | -0.0021808 | 0.15999 | 0.0021808 | west | N | 0.0021808 | 0
1006 | PBCTEGE_ | E | 67 | 0.12045 | west | Y | -0.014942 | 0.30141 | -0.0021808 | 0.15999 | 0.0021808 | west | N | 0.0021808 | 0
1007 | PB5GEN_6 | MB | 114 | 0.12045 | west | Y | -0.014942 | 0.30141 | -0.0021808 | 0.15999 | 0.0021808 | west | N | 0.0021808 | 0
1008 | PB6GEN_7 | MB | 515 | 0.12045 | west | Y | -0.014942 | 0.30141 | -0.0021808 | 0.15999 | 0.0021808 | west | N | 0.0021808 | 0
1039 | MRGNAG_1 | A | 66 | 0.12484 | west | Y | -0.010553 | 0.3058 | 0.0022082 | 0.16438 | 0.0022082 | west | N | 0.0022082 | 0
1040 | MRGNBG_2 | B | 69 | 0.12484 | west | Y | -0.010553 | 0.3058 | 0.0022082 | 0.16438 | 0.0022082 | west | N | 0.0022082 | 0
1041 | MRGNCG_3 | C | 69 | 0.12484 | west | Y | -0.010553 | 0.3058 | 0.0022082 | 0.16438 | 0.0022082 | west | N | 0.0022082 | 0
1042 | MRGNDG_4 | D | 67 | 0.12484 | west | Y | -0.010553 | 0.3058 | 0.0022082 | 0.16438 | 0.0022082 | west | N | 0.0022082 | 0
1043 | MRGNEG_5 | E | 67 | 0.12484 | west | Y | -0.010553 | 0.3058 | 0.0022082 | 0.16438 | 0.0022082 | west | N | 0.0022082 | 0
1044 | MRGNFG_6 | F | 65 | 0.12484 | west | Y | -0.010553 | 0.3058 | 0.0022082 | 0.16438 | 0.0022082 | west | N | 0.0022082 | 0
1045 | CALENG1G | 1 | 70 | 0.12422 | west | N | -0.011173 | 0.30518 | 0.0015882 | 0.16376 | 0.0015882 | west | N | 0.0015882 | 0
1046 | CALENG2G | 2 | 73.4 | 0.12422 | west | N | -0.011173 | 0.30518 | 0.0015882 | 0.16376 | 0.0015882 | west | N | 0.0015882 | 0
1047 | CALENG3G | 3 | 70.4 | 0.12422 | west | N | -0.011173 | 0.30518 | 0.0015882 | 0.16376 | 0.0015882 | west | N | 0.0015882 | 0
1058 | LONGSHOR | 1 | 150 | 0.12457 | west | Y | -0.010817 | 0.30553 | 0.0019442 | 0.16412 | 0.0019442 | west | N | 0.0019442 | 0
1058 | LONGSHOR | 2 | 220 | 0.12457 | west | Y | -0.010817 | 0.30553 | 0.0019442 | 0.16412 | 0.0019442 | west | N | 0.0019442 | 0
1061 | CIELOGEN | 1 | 99 | 0.12508 | west | Y | -0.010311 | 0.30604 | 0.0024502 | 0.16462 | 0.0024502 | west | N | 0.0024502 | 0
1062 | CIELOGEN | 1 | 61 | 0.12508 | west | Y | -0.010311 | 0.30604 | 0.0024502 | 0.16462 | 0.0024502 | west | N | 0.0024502 | 0
1068 | SCURRYCW | 1 | 141 | 0.12504 | west | Y | -0.010346 | 0.30601 | 0.0024152 | 0.16459 | 0.0024152 | west | N | 0.0024152 | 0
1069 | KINDERMG | 1 | 25 | 0.12508 | west | N | -0.010311 | 0.30604 | 0.0024502 | 0.16462 | 0.0024502 | west | N | 0.0024502 | 0
1070 | KINDERMG | 1 | 45.7 | 0.12508 | west | N | -0.010311 | 0.30604 | 0.0024502 | 0.16462 | 0.0024502 | west | N | 0.0024502 | 0
1071 | KINDERMG | 1 | 45.7 | 0.12508 | west | N | -0.010311 | 0.30604 | 0.0024502 | 0.16462 | 0.0024502 | west | N | 0.0024502 | 0
1073 | SCURRYCW | 2 | 120 | 0.12504 | west | Y | -0.010346 | 0.30601 | 0.0024152 | 0.16459 | 0.0024152 | west | N | 0.0024152 | 0
1320 | BSP 1 | 1 | 25.8 | 0.123 | west | N | -0.012387 | 0.30396 | 0.00037419 | 0.16255 | 0.00037419 | west | N | 0.00037419 | 0
1326 | STANTONW | 1 | 100.5 | 0.12272 | west | Y | -0.012666 | 0.30369 | 9.5193e-05 | 0.16227 | 9.5193e-05 | west | N | 9.5193e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.12378 | west | Y | -0.011606 | 0.30475 | 0.0011552 | 0.16333 | 0.0011552 | west | N | 0.0011552 | 0
1328 | OCOTILLO | 1 | 58 | 0.1227 | west | Y | -0.012685 | 0.30367 | 7.6193e-05 | 0.16225 | 7.6193e-05 | west | N | 7.6193e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.123 | west | Y | -0.012387 | 0.30396 | 0.00037419 | 0.16255 | 0.00037419 | west | N | 0.00037419 | 0
1343 | TRENTIPP | 1 | 150 | 0.12547 | west | Y | -0.0099229 | 0.30643 | 0.0028382 | 0.16501 | 0.0028382 | west | N | 0.0028382 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.12118 | west | Y | -0.014215 | 0.30214 | -0.0014538 | 0.16072 | 0.0014538 | west | N | 0.0014538 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.12118 | west | Y | -0.014215 | 0.30214 | -0.0014538 | 0.16072 | 0.0014538 | west | N | 0.0014538 | 0
1354 | AEPWIND_ | 1 | 101 | 0.12547 | west | Y | -0.0099229 | 0.30643 | 0.0028382 | 0.16501 | 0.0028382 | west | N | 0.0028382 | 0
1360 | GUNSIGHT | 1 | 120 | 0.12384 | west | Y | -0.011554 | 0.3048 | 0.0012072 | 0.16338 | 0.0012072 | west | N | 0.0012072 | 0
1432 | GRHAMSES | 2 | 366 | 0.13753 | north | Y | 0.0021421 | 0.31849 | 0.014903 | 0.17707 | 0.0021421 | North | N | 0.0021421 | 0
1433 | GRHAMSES | 1 | 242 | 0.13674 | north | Y | 0.0013511 | 0.3177 | 0.014112 | 0.17628 | 0.0013511 | North | N | 0.0013511 | 0
1437 | MESQUITW | 1 | 400 | 0.13111 | west | Y | -0.0042809 | 0.31207 | 0.0084802 | 0.17065 | 0.0042809 | North | Y | 0.0084802 | 1.6797
1438 | MESQUITW | 1 | 236 | 0.13112 | west | Y | -0.0042719 | 0.31208 | 0.0084892 | 0.17066 | 0.0042719 | North | Y | 0.0084892 | 0.99527
1442 | COKFIELD | 1 | 165 | 0.13266 | west | Y | -0.0027329 | 0.31362 | 0.010028 | 0.1722 | 0.0027329 | North | Y | 0.010028 | 1.2037
1453 | WCPWRCO_ | 1 | 204 | 0.14121 | north | Y | 0.0058191 | 0.32217 | 0.01858 | 0.18075 | 0.0058191 | North | N | 0.0058191 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.14121 | north | Y | 0.0058191 | 0.32217 | 0.01858 | 0.18075 | 0.0058191 | North | N | 0.0058191 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.14121 | north | Y | 0.0058191 | 0.32217 | 0.01858 | 0.18075 | 0.0058191 | North | N | 0.0058191 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.13759 | west | Y | 0.0022001 | 0.31855 | 0.014961 | 0.17713 | 0.0022001 | North | Y | 0.014961 | 0.25522
1479 | WFCOGEN_ | 2 | 20 | 0.13759 | west | Y | 0.0022001 | 0.31855 | 0.014961 | 0.17713 | 0.0022001 | North | Y | 0.014961 | 0.25522
1482 | WFCOGEN_ | 1 | 20 | 0.13759 | west | Y | 0.0022001 | 0.31855 | 0.014961 | 0.17713 | 0.0022001 | North | Y | 0.014961 | 0.25522
1482 | WFCOGEN_ | 2 | 17 | 0.13759 | west | Y | 0.0022001 | 0.31855 | 0.014961 | 0.17713 | 0.0022001 | North | Y | 0.014961 | 0.21694
1600 | BARTNWND | 1 | 120 | 0.13931 | north | Y | 0.0039161 | 0.32027 | 0.016677 | 0.17885 | 0.0039161 | North | N | 0.0039161 | 0
1643 | SLSTR1PP | 1 | 60 | 0.13461 | north | Y | -0.00077695 | 0.31557 | 0.011984 | 0.17416 | 0.00077695 | North | N | 0.00077695 | 0
1675 | PEC_1G | 1 | 75 | 0.14108 | north | N | 0.0056881 | 0.32204 | 0.018449 | 0.18062 | 0.0056881 | North | N | 0.0056881 | 0
1676 | PEC_2G | 2 | 79.6 | 0.14108 | north | N | 0.0056881 | 0.32204 | 0.018449 | 0.18062 | 0.0056881 | North | N | 0.0056881 | 0
1677 | PEC_3G | 3 | 88.4 | 0.14108 | north | N | 0.0056881 | 0.32204 | 0.018449 | 0.18062 | 0.0056881 | North | N | 0.0056881 | 0
1678 | LAMARPWR | 1 | 160 | 0.1412 | north | Y | 0.0058081 | 0.32216 | 0.018569 | 0.18074 | 0.0058081 | North | N | 0.0058081 | 0
1679 | LAMARPWR | 2 | 156 | 0.1412 | north | Y | 0.0058081 | 0.32216 | 0.018569 | 0.18074 | 0.0058081 | North | N | 0.0058081 | 0
1680 | LAMARPWR | 3 | 196 | 0.1412 | north | Y | 0.0058081 | 0.32216 | 0.018569 | 0.18074 | 0.0058081 | North | N | 0.0058081 | 0
1681 | LAMARPWR | 4 | 156 | 0.1412 | north | Y | 0.0058081 | 0.32216 | 0.018569 | 0.18074 | 0.0058081 | North | N | 0.0058081 | 0
1682 | LAMARPWR | 5 | 157 | 0.1412 | north | Y | 0.0058081 | 0.32216 | 0.018569 | 0.18074 | 0.0058081 | North | N | 0.0058081 | 0
1683 | LAMARPWR | 6 | 198 | 0.1412 | north | Y | 0.0058081 | 0.32216 | 0.018569 | 0.18074 | 0.0058081 | North | N | 0.0058081 | 0
1687 | VALLEY_1 | 1 | 170 | 0.14145 | north | Y | 0.0060581 | 0.32241 | 0.018819 | 0.18099 | 0.0060581 | North | N | 0.0060581 | 0
1688 | VALLEY_2 | 2 | 520 | 0.14145 | north | Y | 0.0060581 | 0.32241 | 0.018819 | 0.18099 | 0.0060581 | North | N | 0.0060581 | 0
1689 | VALLEY_3 | 3 | 370 | 0.14131 | north | Y | 0.0059231 | 0.32227 | 0.018684 | 0.18086 | 0.0059231 | North | N | 0.0059231 | 0
1701 | MOSES_1G | 1 | 558 | 0.14102 | north | Y | 0.0056341 | 0.32199 | 0.018395 | 0.18057 | 0.0056341 | North | N | 0.0056341 | 0
1702 | MOSES_2G | 2 | 579 | 0.14102 | north | Y | 0.0056341 | 0.32199 | 0.018395 | 0.18057 | 0.0056341 | North | N | 0.0056341 | 0
1703 | MOSES_3G | 3 | 808 | 0.14102 | north | Y | 0.0056341 | 0.32199 | 0.018395 | 0.18057 | 0.0056341 | North | N | 0.0056341 | 0
1861 | EAGLEMNT | MB | 112 | 0.1448 | north | Y | 0.0094061 | 0.32576 | 0.022167 | 0.18434 | 0.0094061 | North | N | 0.0094061 | 0
1862 | EAGLEMNT | MB | 100 | 0.1448 | north | Y | 0.0094061 | 0.32576 | 0.022167 | 0.18434 | 0.0094061 | North | N | 0.0094061 | 0
1863 | EAGLEMNT | MB | 378 | 0.1448 | north | Y | 0.0094061 | 0.32576 | 0.022167 | 0.18434 | 0.0094061 | North | N | 0.0094061 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.14569 | north | Y | 0.010298 | 0.32665 | 0.023059 | 0.18523 | 0.010298 | North | N | 0.010298 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.14569 | north | Y | 0.010298 | 0.32665 | 0.023059 | 0.18523 | 0.010298 | North | N | 0.010298 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.14569 | north | Y | 0.010298 | 0.32665 | 0.023059 | 0.18523 | 0.010298 | North | N | 0.010298 | 0
1889 | DECRDOVA | MB | 770 | 0.14611 | north | Y | 0.010718 | 0.32707 | 0.023479 | 0.18565 | 0.010718 | North | N | 0.010718 | 0
1892 | DECRDOVA | A | 70 | 0.14552 | north | Y | 0.010128 | 0.32648 | 0.022889 | 0.18506 | 0.010128 | North | N | 0.010128 | 0
1893 | DECRDOVA | B | 69 | 0.14552 | north | Y | 0.010128 | 0.32648 | 0.022889 | 0.18506 | 0.010128 | North | N | 0.010128 | 0
1894 | DECRDOVA | C | 69 | 0.14552 | north | Y | 0.010128 | 0.32648 | 0.022889 | 0.18506 | 0.010128 | North | N | 0.010128 | 0
1895 | DECRDOVA | D | 68 | 0.14552 | north | Y | 0.010128 | 0.32648 | 0.022889 | 0.18506 | 0.010128 | North | N | 0.010128 | 0
1898 | COMCHEPK | 1 | 1157 | 0.14506 | north | N | 0.0096671 | 0.32602 | 0.022428 | 0.1846 | 0.0096671 | North | N | 0.0096671 | 0
1899 | COMCHEPK | 2 | 1158 | 0.14506 | north | N | 0.0096671 | 0.32602 | 0.022428 | 0.1846 | 0.0096671 | North | N | 0.0096671 | 0
1937 | MDLTHELP | 5 | 224 | 0.15526 | north | Y | 0.019874 | 0.33623 | 0.032635 | 0.19481 | 0.019874 | North | N | 0.019874 | 0
1938 | MDLTHELP | 6 | 226 | 0.15526 | north | Y | 0.019874 | 0.33623 | 0.032635 | 0.19481 | 0.019874 | North | N | 0.019874 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.15559 | north | Y | 0.020195 | 0.33655 | 0.032956 | 0.19513 | 0.020195 | North | N | 0.020195 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.15559 | north | Y | 0.020195 | 0.33655 | 0.032956 | 0.19513 | 0.020195 | North | N | 0.020195 | 0
1943 | MDLTHELP | 3 | 212 | 0.15526 | north | Y | 0.019874 | 0.33623 | 0.032635 | 0.19481 | 0.019874 | North | N | 0.019874 | 0
1944 | MDLTHELP | 4 | 211 | 0.15526 | north | Y | 0.019874 | 0.33623 | 0.032635 | 0.19481 | 0.019874 | North | N | 0.019874 | 0
1947 | HANDLEY_ | 3 | 395 | 0.14796 | north | Y | 0.012571 | 0.32892 | 0.025332 | 0.1875 | 0.012571 | North | N | 0.012571 | 0
1948 | HANDLEY_ | 4 | 435 | 0.14762 | north | Y | 0.012228 | 0.32858 | 0.024989 | 0.18716 | 0.012228 | North | N | 0.012228 | 0
1949 | HANDLEY_ | 5 | 435 | 0.14796 | north | Y | 0.012571 | 0.32892 | 0.025332 | 0.1875 | 0.012571 | North | N | 0.012571 | 0
2371 | COLLIN_1 | MB | 138 | 0.14235 | north | Y | 0.0069611 | 0.32331 | 0.019722 | 0.18189 | 0.0069611 | North | N | 0.0069611 | 0
2413 | MTCK6_G | 6 | 118 | 0.14388 | north | Y | 0.0084911 | 0.32484 | 0.021252 | 0.18342 | 0.0084911 | North | N | 0.0084911 | 0
2414 | MTCK7_G | 7 | 115 | 0.14388 | north | Y | 0.0084911 | 0.32484 | 0.021252 | 0.18342 | 0.0084911 | North | N | 0.0084911 | 0
2417 | MTCK8_G | 8 | 556 | 0.14388 | north | Y | 0.0084911 | 0.32484 | 0.021252 | 0.18342 | 0.0084911 | North | N | 0.0084911 | 0
2451 | LKHB1_G | 1 | 388 | 0.14104 | north | Y | 0.0056491 | 0.322 | 0.01841 | 0.18058 | 0.0056491 | North | N | 0.0056491 | 0
2452 | LKHB2_G | 2 | 515 | 0.14104 | north | Y | 0.0056491 | 0.322 | 0.01841 | 0.18058 | 0.0056491 | North | N | 0.0056491 | 0
3097 | MARTLAKE | 1 | 785 | 0.13443 | north | Y | -0.00096195 | 0.31539 | 0.011799 | 0.17397 | 0.00096195 | North | N | 0.00096195 | 0
3098 | MARTLAKE | 2 | 795 | 0.13443 | north | Y | -0.00096195 | 0.31539 | 0.011799 | 0.17397 | 0.00096195 | North | N | 0.00096195 | 0
3099 | MARTLAKE | 3 | 780 | 0.13443 | north | Y | -0.00096195 | 0.31539 | 0.011799 | 0.17397 | 0.00096195 | North | N | 0.00096195 | 0
3107 | STRYKER_ | 1 | 182 | 0.13207 | north | Y | -0.0033219 | 0.31303 | 0.0094392 | 0.17161 | 0.0033219 | North | N | 0.0033219 | 0
3108 | STRYKER_ | 2 | 484 | 0.13207 | north | Y | -0.0033219 | 0.31303 | 0.0094392 | 0.17161 | 0.0033219 | North | N | 0.0033219 | 0
3126 | TRINIDAD | 1 | 224 | 0.13603 | north | Y | 0.00063805 | 0.31699 | 0.013399 | 0.17557 | 0.00063805 | North | N | 0.00063805 | 0
3309 | ASPN_G | 1 | 50 | 0.13284 | north | Y | -0.0025499 | 0.3138 | 0.010211 | 0.17238 | 0.0025499 | North | N | 0.0025499 | 0
3348 | CHAMPION | MB | 42 | 0.13289 | north | N | -0.0025009 | 0.31385 | 0.01026 | 0.17243 | 0.0025009 | North | N | 0.0025009 | 0
3381 | BBRN_1G | 1 | 615 | 0.12455 | north | Y | -0.010836 | 0.30552 | 0.0019252 | 0.1641 | 0.0019252 | west | Y | 0.010836 | 5.4801
3382 | BBRN_2G | 2 | 587 | 0.12455 | north | Y | -0.010836 | 0.30552 | 0.0019252 | 0.1641 | 0.0019252 | west | Y | 0.010836 | 5.2306
3403 | THOUSE_1 | MB | 537 | 0.24531 | north | Y | 0.10992 | 0.42628 | 0.12269 | 0.28486 | 0.10992 | North | N | 0.10992 | 0
3404 | THOUSE_2 | 2 | 787 | 0.24531 | north | Y | 0.10992 | 0.42628 | 0.12269 | 0.28486 | 0.10992 | North | N | 0.10992 | 0
3416 | LAKE_CRK | MB | 75 | 0.14575 | north | Y | 0.010362 | 0.32671 | 0.023123 | 0.18529 | 0.010362 | North | N | 0.010362 | 0
3417 | LAKE_CRK | MB | 222 | 0.14575 | north | Y | 0.010362 | 0.32671 | 0.023123 | 0.18529 | 0.010362 | North | N | 0.010362 | 0
3432 | SANDOW_4 | 4 | 569 | -0.26963 | south | Y | -0.40502 | -0.088664 | -0.39225 | -0.23008 | 0.088664 | south | N | 0.088664 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.17257 | south | Y | -0.30796 | 0.0083909 | -0.2952 | -0.13303 | 0.0083909 | south | N | 0.0083909 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.17257 | south | Y | -0.30796 | 0.0083909 | -0.2952 | -0.13303 | 0.0083909 | south | N | 0.0083909 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.17249 | south | Y | -0.30788 | 0.0084709 | -0.29512 | -0.13295 | 0.0084709 | south | N | 0.0084709 | 0
5031 | BRA_VHBC | 1 | 46 | -0.17257 | south | Y | -0.30796 | 0.0083909 | -0.2952 | -0.13303 | 0.0083909 | south | N | 0.0083909 | 0
5032 | BRA_VHBC | 2 | 47 | -0.17257 | south | Y | -0.30796 | 0.0083909 | -0.2952 | -0.13303 | 0.0083909 | south | N | 0.0083909 | 0
5033 | BRA_VHBC | 3 | 46 | -0.17257 | south | Y | -0.30796 | 0.0083909 | -0.2952 | -0.13303 | 0.0083909 | south | N | 0.0083909 | 0
5034 | BRA_VHBC | 4 | 46 | -0.17257 | south | Y | -0.30796 | 0.0083909 | -0.2952 | -0.13303 | 0.0083909 | south | N | 0.0083909 | 0
5111 | CALAVER_ | 1 | 424 | -0.17289 | south | Y | -0.30828 | 0.0080689 | -0.29552 | -0.13335 | 0.0080689 | south | N | 0.0080689 | 0
5112 | CALAVER_ | 2 | 425 | -0.17289 | south | Y | -0.30828 | 0.0080689 | -0.29552 | -0.13335 | 0.0080689 | south | N | 0.0080689 | 0
5264 | LEON_LCP | 3 | 58 | -0.17152 | south | Y | -0.30691 | 0.0094399 | -0.29415 | -0.13198 | 0.0094399 | south | N | 0.0094399 | 0
5265 | LEON_LCP | 4 | 89 | -0.17152 | south | Y | -0.30691 | 0.0094399 | -0.29415 | -0.13198 | 0.0094399 | south | N | 0.0094399 | 0
5266 | LEON_LCP | 1 | 44 | -0.17152 | south | Y | -0.30691 | 0.0094399 | -0.29415 | -0.13198 | 0.0094399 | south | N | 0.0094399 | 0
5267 | LEON_LCP | 2 | 44 | -0.17152 | south | Y | -0.30691 | 0.0094399 | -0.29415 | -0.13198 | 0.0094399 | south | N | 0.0094399 | 0
5268 | LEON_LCP | 3 | 43 | -0.17152 | south | Y | -0.30691 | 0.0094399 | -0.29415 | -0.13198 | 0.0094399 | south | N | 0.0094399 | 0
5269 | LEON_LCP | 4 | 45 | -0.17152 | south | Y | -0.30691 | 0.0094399 | -0.29415 | -0.13198 | 0.0094399 | south | N | 0.0094399 | 0
5396 | CALAVER_ | 1 | 412 | -0.17277 | south | Y | -0.30816 | 0.0081959 | -0.29539 | -0.13322 | 0.0081959 | south | N | 0.0081959 | 0
5397 | CALAVER_ | 2 | 400 | -0.17277 | south | Y | -0.30816 | 0.0081959 | -0.29539 | -0.13322 | 0.0081959 | south | N | 0.0081959 | 0
5401 | CALAVER_ | 1 | 546 | -0.17129 | south | Y | -0.30668 | 0.0096679 | -0.29392 | -0.13175 | 0.0096679 | south | N | 0.0096679 | 0
5402 | CALAVER_ | 2 | 750 | -0.17129 | south | Y | -0.30668 | 0.0096679 | -0.29392 | -0.13175 | 0.0096679 | south | N | 0.0096679 | 0
5436 | TUTTL_WB | MB | 61 | -0.17339 | south | Y | -0.30878 | 0.0075699 | -0.29602 | -0.13385 | 0.0075699 | south | N | 0.0075699 | 0
5438 | TUTTL_WB | MB | 95 | -0.17339 | south | Y | -0.30878 | 0.0075699 | -0.29602 | -0.13385 | 0.0075699 | south | N | 0.0075699 | 0
5439 | TUTTL_WB | MB | 151 | -0.17339 | south | Y | -0.30878 | 0.0075699 | -0.29602 | -0.13385 | 0.0075699 | south | N | 0.0075699 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.17216 | south | Y | -0.30755 | 0.0087989 | -0.29479 | -0.13262 | 0.0087989 | south | N | 0.0087989 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.17216 | south | Y | -0.30755 | 0.0087989 | -0.29479 | -0.13262 | 0.0087989 | south | N | 0.0087989 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.17216 | south | Y | -0.30755 | 0.0087989 | -0.29479 | -0.13262 | 0.0087989 | south | N | 0.0087989 | 0
5503 | RAYBURNG | 1 | 22 | -0.13857 | south | Y | -0.27396 | 0.042391 | -0.2612 | -0.099029 | 0.042391 | south | N | 0.042391 | 0
5505 | RAYBURNG | 1 | 11 | -0.13857 | south | Y | -0.27396 | 0.042391 | -0.2612 | -0.099029 | 0.042391 | south | N | 0.042391 | 0
5506 | RAYBURNG | 1 | 11 | -0.13857 | south | Y | -0.27396 | 0.042391 | -0.2612 | -0.099029 | 0.042391 | south | N | 0.042391 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.13985 | south | Y | -0.27524 | 0.04111 | -0.26248 | -0.10031 | 0.04111 | south | N | 0.04111 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.13985 | south | Y | -0.27524 | 0.04111 | -0.26248 | -0.10031 | 0.04111 | south | N | 0.04111 | 0
5511 | RAYBURNC | 1 | 46 | -0.13985 | south | Y | -0.27524 | 0.04111 | -0.26248 | -0.10031 | 0.04111 | south | N | 0.04111 | 0
5512 | RAYBURNC | 1 | 48 | -0.13985 | south | Y | -0.27524 | 0.04111 | -0.26248 | -0.10031 | 0.04111 | south | N | 0.04111 | 0
5728 | FALCONHY | 2 | 12 | -0.14612 | south | N | -0.28151 | 0.034844 | -0.26875 | -0.10658 | 0.034844 | south | N | 0.034844 | 0
5729 | FALCONHY | 3 | 11 | -0.14612 | south | N | -0.28151 | 0.034844 | -0.26875 | -0.10658 | 0.034844 | south | N | 0.034844 | 0
5890 | PEARSALL | 1 | 24 | -0.15257 | south | Y | -0.28796 | 0.028389 | -0.2752 | -0.11303 | 0.028389 | south | N | 0.028389 | 0
5891 | PEARSALL | 1 | 24 | -0.15257 | south | Y | -0.28796 | 0.028389 | -0.2752 | -0.11303 | 0.028389 | south | N | 0.028389 | 0
5892 | PEARSALL | 1 | 23 | -0.15257 | south | Y | -0.28796 | 0.028389 | -0.2752 | -0.11303 | 0.028389 | south | N | 0.028389 | 0
5903 | SANMIGUE | 1 | 396 | -0.16198 | south | Y | -0.29737 | 0.018979 | -0.28461 | -0.12244 | 0.018979 | south | N | 0.018979 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.089094 | houston | N | -0.22448 | 0.091868 | -0.21172 | -0.049552 | 0.049552 | houston | N | 0.049552 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.089094 | houston | N | -0.22448 | 0.091868 | -0.21172 | -0.049552 | 0.049552 | houston | N | 0.049552 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.13539 | 0
5932 | SI_RAY9 | 9 | 38 | -0.14384 | south | Y | -0.27923 | 0.037122 | -0.26647 | -0.1043 | 0.037122 | south | N | 0.037122 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.14384 | south | Y | -0.27923 | 0.037122 | -0.26647 | -0.1043 | 0.037122 | south | N | 0.037122 | 0
5934 | SI_RAY5 | 5 | 15 | -0.14384 | south | Y | -0.27923 | 0.037122 | -0.26647 | -0.1043 | 0.037122 | south | N | 0.037122 | 0
5935 | SI_RAY10 | 10 | 47 | -0.14384 | south | Y | -0.27923 | 0.037122 | -0.26647 | -0.1043 | 0.037122 | south | N | 0.037122 | 0
6016 | SWMESA | 1 | 75 | 0.10823 | west | Y | -0.027164 | 0.28919 | -0.014403 | 0.14777 | 0.014403 | west | N | 0.014403 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.12263 | 0
6144 | MCADOO1A | 1 | 150 | 0.12679 | west | Y | -0.0085989 | 0.30775 | 0.0041622 | 0.16633 | 0.0041622 | west | N | 0.0041622 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.11984 | west | Y | -0.015552 | 0.3008 | -0.0027908 | 0.15938 | 0.0027908 | west | N | 0.0027908 | 0
6476 | LANGFORD | 1 | 150 | 0.055862 | west | Y | -0.079528 | 0.23682 | -0.066767 | 0.095404 | 0.066767 | west | N | 0.066767 | 0
6637 | SNYDERW1 | 1 | 63 | 0.12494 | west | Y | -0.01045 | 0.3059 | 0.0023112 | 0.16448 | 0.0023112 | west | N | 0.0023112 | 0
6752 | OKLA0A | 1 | 649.7 | 0.1338 | west | Y | -0.0015879 | 0.31476 | 0.011173 | 0.17334 | 0.0015879 | North | Y | 0.011173 | 6.2275
6948 | DENISNDM | 1 | 40 | 0.14158 | north | N | 0.0061921 | 0.32254 | 0.018953 | 0.18112 | 0.0061921 | North | N | 0.0061921 | 0
6948 | DENISNDM | 2 | 40 | 0.14158 | north | N | 0.0061921 | 0.32254 | 0.018953 | 0.18112 | 0.0061921 | North | N | 0.0061921 | 0
7000 | L_FERGUS | 1 | 422 | -0.19388 | south | Y | -0.32927 | -0.012914 | -0.3165 | -0.15433 | 0.012914 | south | N | 0.012914 | 0
7004 | L_SIMGID | 1 | 132 | -0.21693 | south | Y | -0.35232 | -0.035965 | -0.33956 | -0.17738 | 0.035965 | south | N | 0.035965 | 0
7005 | L_SIMGID | 2 | 134 | -0.21693 | south | Y | -0.35232 | -0.035965 | -0.33956 | -0.17738 | 0.035965 | south | N | 0.035965 | 0
7006 | L_SIMGID | 3 | 323 | -0.21693 | south | Y | -0.35232 | -0.035965 | -0.33956 | -0.17738 | 0.035965 | south | N | 0.035965 | 0
7007 | L_LOSTPI | 1 | 158 | -0.21903 | south | Y | -0.35442 | -0.038066 | -0.34166 | -0.17949 | 0.038066 | south | N | 0.038066 | 0
7008 | L_LOSTPI | 2 | 160 | -0.21903 | south | Y | -0.35442 | -0.038066 | -0.34166 | -0.17949 | 0.038066 | south | N | 0.038066 | 0
7009 | L_LOSTPI | 3 | 175 | -0.21903 | south | Y | -0.35442 | -0.038066 | -0.34166 | -0.17949 | 0.038066 | south | N | 0.038066 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.19502 | south | Y | -0.33041 | -0.014054 | -0.31764 | -0.15547 | 0.014054 | south | N | 0.014054 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.19502 | south | Y | -0.33041 | -0.014054 | -0.31764 | -0.15547 | 0.014054 | south | N | 0.014054 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.19482 | south | Y | -0.33021 | -0.01386 | -0.31745 | -0.15528 | 0.01386 | south | N | 0.01386 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.19062 | south | Y | -0.326 | -0.0096531 | -0.31324 | -0.15107 | 0.0096531 | south | N | 0.0096531 | 0
7015 | L_HAYSEN | 2 | 225 | -0.19062 | south | Y | -0.326 | -0.0096531 | -0.31324 | -0.15107 | 0.0096531 | south | N | 0.0096531 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.19062 | south | Y | -0.326 | -0.0096531 | -0.31324 | -0.15107 | 0.0096531 | south | N | 0.0096531 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.19062 | south | Y | -0.326 | -0.0096531 | -0.31324 | -0.15107 | 0.0096531 | south | N | 0.0096531 | 0
7020 | L_AUSTPL | 1 | 8 | -0.22581 | south | N | -0.36119 | -0.044843 | -0.34843 | -0.18626 | 0.044843 | south | N | 0.044843 | 0
7020 | L_AUSTPL | 2 | 8 | -0.22581 | south | N | -0.36119 | -0.044843 | -0.34843 | -0.18626 | 0.044843 | south | N | 0.044843 | 0
7022 | L_BUCHAN | 1 | 18 | -0.19245 | south | N | -0.32784 | -0.011488 | -0.31508 | -0.15291 | 0.011488 | south | N | 0.011488 | 0
7023 | L_BUCHAN | 2 | 18 | -0.19245 | south | N | -0.32784 | -0.011488 | -0.31508 | -0.15291 | 0.011488 | south | N | 0.011488 | 0
7024 | L_BUCHAN | 3 | 15 | -0.19245 | south | N | -0.32784 | -0.011488 | -0.31508 | -0.15291 | 0.011488 | south | N | 0.011488 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.18965 | south | N | -0.32504 | -0.0086931 | -0.31228 | -0.15011 | 0.0086931 | south | N | 0.0086931 | 0
7028 | L_MARBFA | 1 | 18 | -0.20133 | south | N | -0.33672 | -0.020373 | -0.32396 | -0.16179 | 0.020373 | south | N | 0.020373 | 0
7029 | L_MARBFA | 2 | 18 | -0.20133 | south | N | -0.33672 | -0.020373 | -0.32396 | -0.16179 | 0.020373 | south | N | 0.020373 | 0
7031 | L_MARSFO | 1 | 35 | -0.21825 | south | N | -0.35364 | -0.037287 | -0.34088 | -0.17871 | 0.037287 | south | N | 0.037287 | 0
7032 | L_MARSFO | 2 | 34 | -0.21825 | south | N | -0.35364 | -0.037287 | -0.34088 | -0.17871 | 0.037287 | south | N | 0.037287 | 0
7033 | L_MARSFO | 3 | 35 | -0.21825 | south | N | -0.35364 | -0.037287 | -0.34088 | -0.17871 | 0.037287 | south | N | 0.037287 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.19535 | south | N | -0.33074 | -0.014385 | -0.31798 | -0.1558 | 0.014385 | south | N | 0.014385 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.19535 | south | N | -0.33074 | -0.014385 | -0.31798 | -0.1558 | 0.014385 | south | N | 0.014385 | 0
7038 | L_DELAWA | 1 | 35 | 0.12056 | west | Y | -0.014833 | 0.30152 | -0.0020718 | 0.1601 | 0.0020718 | west | N | 0.0020718 | 0
7038 | L_DELAWA | 2 | 30 | 0.12056 | west | Y | -0.014833 | 0.30152 | -0.0020718 | 0.1601 | 0.0020718 | west | N | 0.0020718 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.19724 | south | Y | -0.33263 | -0.016281 | -0.31987 | -0.1577 | 0.016281 | south | N | 0.016281 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.19724 | south | Y | -0.33263 | -0.016281 | -0.31987 | -0.1577 | 0.016281 | south | N | 0.016281 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.19724 | south | Y | -0.33263 | -0.016281 | -0.31987 | -0.1577 | 0.016281 | south | N | 0.016281 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.19724 | south | Y | -0.33263 | -0.016281 | -0.31987 | -0.1577 | 0.016281 | south | N | 0.016281 | 0
7487 | L_CANYHY | 1 | 6 | -0.19543 | south | N | -0.33082 | -0.014467 | -0.31806 | -0.15589 | 0.014467 | south | N | 0.014467 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.18452 | south | N | -0.31991 | -0.0035621 | -0.30715 | -0.14498 | 0.0035621 | south | N | 0.0035621 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.18452 | south | N | -0.31991 | -0.0035621 | -0.30715 | -0.14498 | 0.0035621 | south | N | 0.0035621 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.18452 | south | N | -0.31991 | -0.0035621 | -0.30715 | -0.14498 | 0.0035621 | south | N | 0.0035621 | 0
7609 | L_SCHUMA | 1 | 4 | -0.18184 | south | N | -0.31723 | -0.00087711 | -0.30447 | -0.1423 | 0.00087711 | south | N | 0.00087711 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.18203 | south | N | -0.31742 | -0.0010641 | -0.30465 | -0.14248 | 0.0010641 | south | N | 0.0010641 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.18203 | south | N | -0.31742 | -0.0010641 | -0.30465 | -0.14248 | 0.0010641 | south | N | 0.0010641 | 0
7800 | L_GUADGE | 1 | 147 | -0.17726 | south | Y | -0.31265 | 0.0037019 | -0.29989 | -0.13772 | 0.0037019 | south | N | 0.0037019 | 0
7801 | L_GUADGE | 2 | 138 | -0.17726 | south | Y | -0.31265 | 0.0037019 | -0.29989 | -0.13772 | 0.0037019 | south | N | 0.0037019 | 0
7802 | L_GUADGE | 3 | 140 | -0.17726 | south | Y | -0.31265 | 0.0037019 | -0.29989 | -0.13772 | 0.0037019 | south | N | 0.0037019 | 0
7803 | L_GUADGE | 4 | 147 | -0.17726 | south | Y | -0.31265 | 0.0037019 | -0.29989 | -0.13772 | 0.0037019 | south | N | 0.0037019 | 0
7804 | L_GUADGE | 5 | 182 | -0.17726 | south | Y | -0.31265 | 0.0037019 | -0.29989 | -0.13772 | 0.0037019 | south | N | 0.0037019 | 0
7805 | L_GUADGE | 6 | 198 | -0.17726 | south | Y | -0.31265 | 0.0037019 | -0.29989 | -0.13772 | 0.0037019 | south | N | 0.0037019 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.22062 | south | Y | -0.35601 | -0.039655 | -0.34325 | -0.18107 | 0.039655 | south | N | 0.039655 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.22062 | south | Y | -0.35601 | -0.039655 | -0.34325 | -0.18107 | 0.039655 | south | N | 0.039655 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.22062 | south | Y | -0.35601 | -0.039655 | -0.34325 | -0.18107 | 0.039655 | south | N | 0.039655 | 0
7810 | L_RIONOG | 1 | 142 | -0.18377 | south | Y | -0.31915 | -0.0028031 | -0.30639 | -0.14422 | 0.0028031 | south | N | 0.0028031 | 0
7811 | L_RIONOG | 2 | 145 | -0.18377 | south | Y | -0.31915 | -0.0028031 | -0.30639 | -0.14422 | 0.0028031 | south | N | 0.0028031 | 0
7812 | L_RIONOG | 3 | 151 | -0.18377 | south | Y | -0.31915 | -0.0028031 | -0.30639 | -0.14422 | 0.0028031 | south | N | 0.0028031 | 0
7813 | L_RIONOG | 4 | 290 | -0.18377 | south | Y | -0.31915 | -0.0028031 | -0.30639 | -0.14422 | 0.0028031 | south | N | 0.0028031 | 0
8032 | AMISTADH | 1 | 33 | -0.081574 | south | N | -0.21696 | 0.099388 | -0.2042 | -0.042032 | 0.042032 | houston | Y | 0.099388 | 0
8033 | AMISTADH | 2 | 25 | -0.081574 | south | N | -0.21696 | 0.099388 | -0.2042 | -0.042032 | 0.042032 | houston | Y | 0.099388 | 0
8048 | FALCONHY | 1 | 12 | -0.14612 | south | N | -0.28151 | 0.034844 | -0.26875 | -0.10658 | 0.034844 | south | N | 0.034844 | 0
8066 | DUP1V#1 | 1 | 73 | -0.14016 | south | N | -0.27555 | 0.040805 | -0.26279 | -0.10061 | 0.040805 | south | N | 0.040805 | 0
8134 | FOR69CG0 | 1 | 79 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
8138 | FOR69CG0 | 2 | 81 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.18096 | 0
8147 | UCAR #2 | 10 | 28 | -0.13581 | south | N | -0.27119 | 0.045157 | -0.25843 | -0.096263 | 0.045157 | south | N | 0.045157 | 0
8148 | UCAR #1 | 2 | 7 | -0.13581 | south | N | -0.27119 | 0.045157 | -0.25843 | -0.096263 | 0.045157 | south | N | 0.045157 | 0
8153 | FOR69CG0 | 3 | 79 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
8154 | FOR69CG0 | 4 | 80 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
8156 | FOR69CG0 | 6 | 25 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
8157 | FOR69CG0 | 7 | 46 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
8161 | COLETOU1 | 1 | 629 | -0.1485 | south | Y | -0.28389 | 0.03246 | -0.27113 | -0.10896 | 0.03246 | south | N | 0.03246 | 0
8173 | VICEC51A | 5 | 144 | -0.14174 | south | Y | -0.27713 | 0.03922 | -0.26437 | -0.1022 | 0.03922 | south | N | 0.03922 | 0
8174 | VICEC61A | 6 | 188 | -0.14174 | south | Y | -0.27713 | 0.03922 | -0.26437 | -0.1022 | 0.03922 | south | N | 0.03922 | 0
8189 | CUERO 2 | 1 | 12 | -0.17093 | south | N | -0.30632 | 0.010036 | -0.29355 | -0.13138 | 0.010036 | south | N | 0.010036 | 0
8262 | ELPS | 1 | 6 | -0.10366 | south | N | -0.23905 | 0.077301 | -0.22629 | -0.064119 | 0.064119 | houston | Y | 0.077301 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.18096 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.18096 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.18096 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.18096 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.18096 | 0
8442 | NBEC71A | 1 | 336 | -0.1423 | south | Y | -0.27769 | 0.038658 | -0.26493 | -0.10276 | 0.038658 | south | N | 0.038658 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.18096 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.13539 | 0.18096 | -0.12263 | 0.039542 | 0.039542 | houston | Y | 0.18096 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.14263 | south | Y | -0.27802 | 0.03833 | -0.26526 | -0.10309 | 0.03833 | south | N | 0.03833 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.14263 | south | Y | -0.27802 | 0.03833 | -0.26526 | -0.10309 | 0.03833 | south | N | 0.03833 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.14283 | south | N | -0.27822 | 0.038127 | -0.26546 | -0.10329 | 0.038127 | south | N | 0.038127 | 0
8506 | VAL #1 | 1 | 25 | -0.14268 | south | N | -0.27807 | 0.038278 | -0.26531 | -0.10314 | 0.038278 | south | N | 0.038278 | 0
8507 | VAL #2 | 2 | 25 | -0.14268 | south | N | -0.27807 | 0.038278 | -0.26531 | -0.10314 | 0.038278 | south | N | 0.038278 | 0
8511 | OXY_CC0A | 1 | 38 | -0.14283 | south | N | -0.27822 | 0.038136 | -0.26545 | -0.10328 | 0.038136 | south | N | 0.038136 | 0
8517 | CELANEBI | 1 | 29 | -0.14352 | south | N | -0.27891 | 0.037444 | -0.26615 | -0.10398 | 0.037444 | south | N | 0.037444 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.14232 | south | N | -0.27771 | 0.038641 | -0.26495 | -0.10278 | 0.038641 | south | N | 0.038641 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.14232 | south | N | -0.27771 | 0.038641 | -0.26495 | -0.10278 | 0.038641 | south | N | 0.038641 | 0
8562 | CNOPST1 | 3 | 153 | -0.14232 | south | N | -0.27771 | 0.038641 | -0.26495 | -0.10278 | 0.038641 | south | N | 0.038641 | 0
8926 | LGE_GT10 | 1 | 158 | -0.14083 | south | N | -0.27622 | 0.040134 | -0.26346 | -0.10129 | 0.040134 | south | N | 0.040134 | 0
8927 | LGE_GT20 | 2 | 153 | -0.14083 | south | N | -0.27622 | 0.040134 | -0.26346 | -0.10129 | 0.040134 | south | N | 0.040134 | 0
8928 | LGE_STG0 | 3 | 100 | -0.14083 | south | N | -0.27622 | 0.040134 | -0.26346 | -0.10129 | 0.040134 | south | N | 0.040134 | 0
8930 | ICPGN10A | 1 | 145 | -0.14083 | south | N | -0.27622 | 0.040134 | -0.26346 | -0.10129 | 0.040134 | south | N | 0.040134 | 0
8931 | ICPGN20A | 2 | 147 | -0.14083 | south | N | -0.27622 | 0.040134 | -0.26346 | -0.10129 | 0.040134 | south | N | 0.040134 | 0
8932 | ICPGN30A | 3 | 127 | -0.14083 | south | N | -0.27622 | 0.040134 | -0.26346 | -0.10129 | 0.040134 | south | N | 0.040134 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.14439 | south | Y | -0.27978 | 0.036569 | -0.26702 | -0.10485 | 0.036569 | south | N | 0.036569 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.14439 | south | Y | -0.27978 | 0.036569 | -0.26702 | -0.10485 | 0.036569 | south | N | 0.036569 | 0
8935 | FGNTS201 | 3 | 173 | -0.14439 | south | Y | -0.27978 | 0.036569 | -0.26702 | -0.10485 | 0.036569 | south | N | 0.036569 | 0
8936 | MVGN#1 | 1 | 207 | -0.14412 | south | Y | -0.27951 | 0.036845 | -0.26675 | -0.10457 | 0.036845 | south | N | 0.036845 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.14412 | south | Y | -0.27951 | 0.036845 | -0.26675 | -0.10457 | 0.036845 | south | N | 0.036845 | 0
8938 | MVGN#3 | 3 | 242 | -0.14412 | south | Y | -0.27951 | 0.036845 | -0.26675 | -0.10457 | 0.036845 | south | N | 0.036845 | 0
8981 | HECN1 | 1 | 144 | -0.14411 | south | Y | -0.2795 | 0.03685 | -0.26674 | -0.10457 | 0.03685 | south | N | 0.03685 | 0
8982 | HECN2 | 2 | 144 | -0.14411 | south | Y | -0.2795 | 0.03685 | -0.26674 | -0.10457 | 0.03685 | south | N | 0.03685 | 0
8983 | HECN3 | 3 | 171 | -0.14411 | south | Y | -0.2795 | 0.03685 | -0.26674 | -0.10457 | 0.03685 | south | N | 0.03685 | 0
9000 | DECKR_G1 | 1 | 310 | -0.22672 | south | Y | -0.36211 | -0.045754 | -0.34934 | -0.18717 | 0.045754 | south | N | 0.045754 | 0
9001 | DECKR_G2 | 2 | 413 | -0.22672 | south | Y | -0.36211 | -0.045754 | -0.34934 | -0.18717 | 0.045754 | south | N | 0.045754 | 0
9002 | DECKR_G3 | 3 | 42 | -0.22912 | south | Y | -0.36451 | -0.048159 | -0.35175 | -0.18958 | 0.048159 | south | N | 0.048159 | 0
9003 | DECKR_G4 | 4 | 44 | -0.22912 | south | Y | -0.36451 | -0.048159 | -0.35175 | -0.18958 | 0.048159 | south | N | 0.048159 | 0
9004 | DECKR_G5 | 5 | 44 | -0.22912 | south | Y | -0.36451 | -0.048159 | -0.35175 | -0.18958 | 0.048159 | south | N | 0.048159 | 0
9005 | DECKR_G6 | 6 | 47 | -0.22912 | south | Y | -0.36451 | -0.048159 | -0.35175 | -0.18958 | 0.048159 | south | N | 0.048159 | 0
9016 | SANDH_G1 | 1 | 49 | -0.22415 | south | Y | -0.35954 | -0.04319 | -0.34678 | -0.18461 | 0.04319 | south | N | 0.04319 | 0
9017 | SANDH_G2 | 2 | 46 | -0.22415 | south | Y | -0.35954 | -0.04319 | -0.34678 | -0.18461 | 0.04319 | south | N | 0.04319 | 0
9018 | SANDH_G3 | 3 | 46 | -0.22415 | south | Y | -0.35954 | -0.04319 | -0.34678 | -0.18461 | 0.04319 | south | N | 0.04319 | 0
9019 | SANDH_G4 | 4 | 47 | -0.22415 | south | Y | -0.35954 | -0.04319 | -0.34678 | -0.18461 | 0.04319 | south | N | 0.04319 | 0
9020 | SANDHG5A | 5A | 154 | -0.22415 | south | Y | -0.35954 | -0.04319 | -0.34678 | -0.18461 | 0.04319 | south | N | 0.04319 | 0
9021 | SANDHG5C | 5C | 148 | -0.22415 | south | Y | -0.35954 | -0.04319 | -0.34678 | -0.18461 | 0.04319 | south | N | 0.04319 | 0
9022 | SANDH_G6 | 6 | 48 | -0.22415 | south | Y | -0.35954 | -0.04319 | -0.34678 | -0.18461 | 0.04319 | south | N | 0.04319 | 0
9023 | SANDH_G7 | 7 | 48 | -0.22415 | south | Y | -0.35954 | -0.04319 | -0.34678 | -0.18461 | 0.04319 | south | N | 0.04319 | 0
11001 | NAV1CT | 1 | 70 | 0.12265 | west | Y | -0.012737 | 0.30361 | 2.4193e-05 | 0.1622 | 2.4193e-05 | west | N | 2.4193e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.12265 | west | Y | -0.012737 | 0.30361 | 2.4193e-05 | 0.1622 | 2.4193e-05 | west | N | 2.4193e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.12265 | west | Y | -0.012737 | 0.30361 | 2.4193e-05 | 0.1622 | 2.4193e-05 | west | N | 2.4193e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.12265 | west | Y | -0.012737 | 0.30361 | 2.4193e-05 | 0.1622 | 2.4193e-05 | west | N | 2.4193e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.12265 | west | Y | -0.012737 | 0.30361 | 2.4193e-05 | 0.1622 | 2.4193e-05 | west | N | 2.4193e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.12265 | west | Y | -0.012737 | 0.30361 | 2.4193e-05 | 0.1622 | 2.4193e-05 | west | N | 2.4193e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.12263 | west | Y | -0.012758 | 0.30359 | 3.1933e-06 | 0.16217 | 3.1933e-06 | west | N | 3.1933e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.12263 | west | Y | -0.012758 | 0.30359 | 3.1933e-06 | 0.16217 | 3.1933e-06 | west | N | 3.1933e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.12263 | west | Y | -0.012758 | 0.30359 | 3.1933e-06 | 0.16217 | 3.1933e-06 | west | N | 3.1933e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.12263 | west | Y | -0.012758 | 0.30359 | 3.1933e-06 | 0.16217 | 3.1933e-06 | west | N | 3.1933e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.12263 | west | Y | -0.012758 | 0.30359 | 3.1933e-06 | 0.16217 | 3.1933e-06 | west | N | 3.1933e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.12263 | west | Y | -0.012758 | 0.30359 | 3.1933e-06 | 0.16217 | 3.1933e-06 | west | N | 3.1933e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.12671 | west | Y | -0.0086819 | 0.30767 | 0.0040792 | 0.16625 | 0.0040792 | west | N | 0.0040792 | 0
11057 | CHAMPION | 1 | 126.5 | 0.12671 | west | Y | -0.0086819 | 0.30767 | 0.0040792 | 0.16625 | 0.0040792 | west | N | 0.0040792 | 0
11058 | PYRON_1G | 1 | 249 | 0.12671 | west | Y | -0.0086819 | 0.30767 | 0.0040792 | 0.16625 | 0.0040792 | west | N | 0.0040792 | 0
11059 | INADALE_ | 1 | 197 | 0.12671 | west | Y | -0.0086819 | 0.30767 | 0.0040792 | 0.16625 | 0.0040792 | west | N | 0.0040792 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.12457 | west | Y | -0.010817 | 0.30553 | 0.0019442 | 0.16412 | 0.0019442 | west | N | 0.0019442 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.12457 | west | Y | -0.010817 | 0.30553 | 0.0019442 | 0.16412 | 0.0019442 | west | N | 0.0019442 | 0
11147 | NOTREES_ | 1 | 149 | 0.12093 | west | Y | -0.01446 | 0.30189 | -0.0016988 | 0.16047 | 0.0016988 | west | N | 0.0016988 | 0
11309 | BULLCREK | 1 | 180 | 0.12421 | west | Y | -0.011179 | 0.30517 | 0.0015822 | 0.16375 | 0.0015822 | west | N | 0.0015822 | 0
11310 | BULLCREK | 1 | 180 | 0.12421 | west | Y | -0.011179 | 0.30517 | 0.0015822 | 0.16375 | 0.0015822 | west | N | 0.0015822 | 0
11320 | COYOTE_1 | 1 | 225 | 0.12409 | west | Y | -0.011295 | 0.30506 | 0.0014662 | 0.16364 | 0.0014662 | west | N | 0.0014662 | 0
11415 | LORAINE_ | 1 | 125 | 0.12579 | west | Y | -0.0095949 | 0.30676 | 0.0031662 | 0.16534 | 0.0031662 | west | N | 0.0031662 | 0
11416 | LORAINE_ | 1 | 125 | 0.12579 | west | Y | -0.0095949 | 0.30676 | 0.0031662 | 0.16534 | 0.0031662 | west | N | 0.0031662 | 0
11691 | KMICHICT | 1 | 140 | 0.14131 | north | N | 0.0059231 | 0.32227 | 0.018684 | 0.18086 | 0.0059231 | North | N | 0.0059231 | 0
11692 | KMICHICT | 2 | 141 | 0.14131 | north | N | 0.0059231 | 0.32227 | 0.018684 | 0.18086 | 0.0059231 | North | N | 0.0059231 | 0
11693 | KMICHIST | 3 | 309 | 0.14131 | north | N | 0.0059231 | 0.32227 | 0.018684 | 0.18086 | 0.0059231 | North | N | 0.0059231 | 0
11694 | KMICHICT | 4 | 143 | 0.14131 | north | N | 0.0059231 | 0.32227 | 0.018684 | 0.18086 | 0.0059231 | North | N | 0.0059231 | 0
11695 | KMICHICT | 5 | 144 | 0.14131 | north | N | 0.0059231 | 0.32227 | 0.018684 | 0.18086 | 0.0059231 | North | N | 0.0059231 | 0
11696 | KMICHIST | 6 | 310 | 0.14131 | north | N | 0.0059231 | 0.32227 | 0.018684 | 0.18086 | 0.0059231 | North | N | 0.0059231 | 0
12322 | ENNSTRAC | 1 | 196 | 0.14286 | north | Y | 0.0074731 | 0.32382 | 0.020234 | 0.18241 | 0.0074731 | North | N | 0.0074731 | 0
12323 | ENNSTRAC | 2 | 111 | 0.14286 | north | Y | 0.0074731 | 0.32382 | 0.020234 | 0.18241 | 0.0074731 | North | N | 0.0074731 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.14241 | north | N | 0.0070241 | 0.32338 | 0.019785 | 0.18196 | 0.0070241 | North | N | 0.0070241 | 0
12411 | FPLEFR1A | 1 | 161 | 0.13975 | north | Y | 0.0043571 | 0.32071 | 0.017118 | 0.17929 | 0.0043571 | North | N | 0.0043571 | 0
12412 | FPLEFR1B | 2 | 164 | 0.13975 | north | Y | 0.0043571 | 0.32071 | 0.017118 | 0.17929 | 0.0043571 | North | N | 0.0043571 | 0
12413 | FPLEFR1C | 3 | 164 | 0.13975 | north | Y | 0.0043571 | 0.32071 | 0.017118 | 0.17929 | 0.0043571 | North | N | 0.0043571 | 0
12414 | FPLEFR1S | 4 | 414 | 0.13975 | north | Y | 0.0043571 | 0.32071 | 0.017118 | 0.17929 | 0.0043571 | North | N | 0.0043571 | 0
12421 | FPLEFR2A | 1 | 162 | 0.13975 | north | Y | 0.0043571 | 0.32071 | 0.017118 | 0.17929 | 0.0043571 | North | N | 0.0043571 | 0
12422 | FPLEFR2B | 2 | 161 | 0.13975 | north | Y | 0.0043571 | 0.32071 | 0.017118 | 0.17929 | 0.0043571 | North | N | 0.0043571 | 0
12423 | FPLEFR2C | 3 | 163 | 0.13975 | north | Y | 0.0043571 | 0.32071 | 0.017118 | 0.17929 | 0.0043571 | North | N | 0.0043571 | 0
12424 | FPLEFR2S | 4 | 409 | 0.13975 | north | Y | 0.0043571 | 0.32071 | 0.017118 | 0.17929 | 0.0043571 | North | N | 0.0043571 | 0
12440 | PARKD_1S | 1 | 0 | 0.14165 | north | N | 0.0062601 | 0.32261 | 0.019021 | 0.18119 | 0.0062601 | North | N | 0.0062601 | 0
12449 | PARKD_2S | 1 | 0 | 0.14165 | north | N | 0.0062601 | 0.32261 | 0.019021 | 0.18119 | 0.0062601 | North | N | 0.0062601 | 0
13116 | TGATEWAY | 1 | 148 | 0.13376 | north | N | -0.0016289 | 0.31472 | 0.011132 | 0.1733 | 0.0016289 | North | N | 0.0016289 | 0
13117 | TGATEWAY | 2 | 130 | 0.13376 | north | N | -0.0016289 | 0.31472 | 0.011132 | 0.1733 | 0.0016289 | North | N | 0.0016289 | 0
13118 | TGATEWAY | 3 | 145 | 0.13376 | north | N | -0.0016289 | 0.31472 | 0.011132 | 0.1733 | 0.0016289 | North | N | 0.0016289 | 0
13119 | TGATEWAY | 4 | 399 | 0.13376 | north | N | -0.0016289 | 0.31472 | 0.011132 | 0.1733 | 0.0016289 | North | N | 0.0016289 | 0
13131 | CALFREST | 1 | 150.7 | 0.12625 | north | Y | -0.0091419 | 0.30721 | 0.0036192 | 0.16579 | 0.0036192 | west | Y | 0.0091419 | 0.83228
13132 | CALFREST | 2 | 151 | 0.12625 | north | Y | -0.0091419 | 0.30721 | 0.0036192 | 0.16579 | 0.0036192 | west | Y | 0.0091419 | 0.83394
13133 | CALFREST | 3 | 177.4 | 0.12625 | north | Y | -0.0091419 | 0.30721 | 0.0036192 | 0.16579 | 0.0036192 | west | Y | 0.0091419 | 0.97974
13134 | CALFREST | 4 | 151.5 | 0.12646 | north | Y | -0.0089309 | 0.30742 | 0.0038302 | 0.166 | 0.0038302 | west | Y | 0.0089309 | 0.77276
13135 | CALFREST | 5 | 152.3 | 0.12646 | north | Y | -0.0089309 | 0.30742 | 0.0038302 | 0.166 | 0.0038302 | west | Y | 0.0089309 | 0.77684
13136 | CALFREST | 6 | 177.5 | 0.12646 | north | Y | -0.0089309 | 0.30742 | 0.0038302 | 0.166 | 0.0038302 | west | Y | 0.0089309 | 0.90538
13432 | SANDOW_5 | 5 | 581 | -0.26963 | south | Y | -0.40502 | -0.088664 | -0.39225 | -0.23008 | 0.088664 | south | N | 0.088664 | 0
13691 | OAKGROVE | 1 | 855 | 0.085657 | north | Y | -0.049733 | 0.26662 | -0.036972 | 0.1252 | 0.036972 | west | Y | 0.049733 | 10.9108
13692 | OAKGROVE | 2 | 855 | 0.085657 | north | Y | -0.049733 | 0.26662 | -0.036972 | 0.1252 | 0.036972 | west | Y | 0.049733 | 10.9108
32798 | BRYN_TAM | 1 | 32 | 0.039834 | north | N | -0.095556 | 0.2208 | -0.082795 | 0.079376 | 0.079376 | houston | Y | 0.095556 | 0
32883 | BRYN_DNS | 1 | 48 | 0.035852 | north | Y | -0.099538 | 0.21681 | -0.086777 | 0.075394 | 0.075394 | houston | Y | 0.099538 | 1.1589
32884 | BRYN_DNS | 1 | 46 | 0.035852 | north | Y | -0.099538 | 0.21681 | -0.086777 | 0.075394 | 0.075394 | houston | Y | 0.099538 | 1.1106
32886 | BRYN_ATK | MB | 12 | 0.039912 | north | Y | -0.095478 | 0.22087 | -0.082717 | 0.079454 | 0.079454 | houston | Y | 0.095478 | 0
32887 | BRYN_ATK | MB | 51 | 0.039912 | north | Y | -0.095478 | 0.22087 | -0.082717 | 0.079454 | 0.079454 | houston | Y | 0.095478 | 0
32888 | BRYN_ATK | 1 | 17 | 0.039912 | north | Y | -0.095478 | 0.22087 | -0.082717 | 0.079454 | 0.079454 | houston | Y | 0.095478 | 0.27241
32890 | BRYN_ATK | MB | 22 | 0.039912 | north | Y | -0.095478 | 0.22087 | -0.082717 | 0.079454 | 0.079454 | houston | Y | 0.095478 | 0
32891 | BRYN_ATK | MB | 25 | 0.039912 | north | Y | -0.095478 | 0.22087 | -0.082717 | 0.079454 | 0.079454 | houston | Y | 0.095478 | 0
32892 | BRYN_DNS | 1 | 105 | 0.035852 | north | Y | -0.099538 | 0.21681 | -0.086777 | 0.075394 | 0.075394 | houston | Y | 0.099538 | 2.5351
36998 | RDCNYNG1 | 1 | 84 | 0.1254 | west | Y | -0.0099929 | 0.30636 | 0.0027682 | 0.16494 | 0.0027682 | west | N | 0.0027682 | 0
38332 | WDWRDU2 | 1 | 80 | 0.10801 | west | Y | -0.027383 | 0.28897 | -0.014622 | 0.14755 | 0.014622 | west | N | 0.014622 | 0
38437 | TNSRBNMS | 1 | 150 | 0.10789 | west | Y | -0.027496 | 0.28886 | -0.014735 | 0.14744 | 0.014735 | west | N | 0.014735 | 0
38438 | TNSRBNMS | 1 | 150 | 0.10789 | west | Y | -0.027496 | 0.28886 | -0.014735 | 0.14744 | 0.014735 | west | N | 0.014735 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.041577 | houston | N | -0.17697 | 0.13938 | -0.16421 | -0.002035 | 0.002035 | houston | N | 0.002035 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.041577 | houston | N | -0.17697 | 0.13938 | -0.16421 | -0.002035 | 0.002035 | houston | N | 0.002035 | 0
38600 | TNBP_CGN | 5 | 53 | -0.041577 | houston | N | -0.17697 | 0.13938 | -0.16421 | -0.002035 | 0.002035 | houston | N | 0.002035 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.041577 | houston | N | -0.17697 | 0.13938 | -0.16421 | -0.002035 | 0.002035 | houston | N | 0.002035 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.041577 | houston | N | -0.17697 | 0.13938 | -0.16421 | -0.002035 | 0.002035 | houston | N | 0.002035 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.041577 | houston | N | -0.17697 | 0.13938 | -0.16421 | -0.002035 | 0.002035 | houston | N | 0.002035 | 0
38614 | TNBPAMCG | 4 | 96 | -0.041577 | houston | N | -0.17697 | 0.13938 | -0.16421 | -0.002035 | 0.002035 | houston | N | 0.002035 | 0
38615 | TNBPAMCG | 1 | 244 | -0.041577 | houston | N | -0.17697 | 0.13938 | -0.16421 | -0.002035 | 0.002035 | houston | N | 0.002035 | 0
38690 | TNBP_CGN | 3 | 40 | -0.041577 | houston | N | -0.17697 | 0.13938 | -0.16421 | -0.002035 | 0.002035 | houston | N | 0.002035 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.041607 | houston | N | -0.177 | 0.13935 | -0.16424 | -0.002065 | 0.002065 | houston | N | 0.002065 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.041607 | houston | N | -0.177 | 0.13935 | -0.16424 | -0.002065 | 0.002065 | houston | N | 0.002065 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.041607 | houston | N | -0.177 | 0.13935 | -0.16424 | -0.002065 | 0.002065 | houston | N | 0.002065 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.041607 | houston | N | -0.177 | 0.13935 | -0.16424 | -0.002065 | 0.002065 | houston | N | 0.002065 | 0
39470 | TNDOWCGN | 1 | 32 | -0.041606 | houston | N | -0.177 | 0.13936 | -0.16423 | -0.002064 | 0.002064 | houston | N | 0.002064 | 0
39480 | TNDOWCGN | 1 | 30 | -0.041606 | houston | N | -0.177 | 0.13936 | -0.16423 | -0.002064 | 0.002064 | houston | N | 0.002064 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.060608 | houston | N | -0.196 | 0.12035 | -0.18324 | -0.021066 | 0.021066 | houston | N | 0.021066 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.060608 | houston | N | -0.196 | 0.12035 | -0.18324 | -0.021066 | 0.021066 | houston | N | 0.021066 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.060608 | houston | N | -0.196 | 0.12035 | -0.18324 | -0.021066 | 0.021066 | houston | N | 0.021066 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.060608 | houston | N | -0.196 | 0.12035 | -0.18324 | -0.021066 | 0.021066 | houston | N | 0.021066 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.085657 | north | Y | -0.049733 | 0.26662 | -0.036972 | 0.1252 | 0.036972 | west | Y | 0.049733 | 1.9435
39970 | TNTNPONE | 1 | 153 | 0.085657 | north | Y | -0.049733 | 0.26662 | -0.036972 | 0.1252 | 0.036972 | west | Y | 0.049733 | 1.9525
48500 | APD_GT1_ | 1 | 136 | -0.029996 | houston | N | -0.16539 | 0.15097 | -0.15262 | 0.009546 | 0.009546 | houston | N | 0.009546 | 0
48510 | AK_GT1__ | 1 | 33 | -0.047916 | houston | N | -0.18331 | 0.13305 | -0.17054 | -0.008374 | 0.008374 | houston | N | 0.008374 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.029928 | houston | Y | -0.16532 | 0.15103 | -0.15256 | 0.009614 | 0.009614 | houston | N | 0.009614 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.029928 | houston | Y | -0.16532 | 0.15103 | -0.15256 | 0.009614 | 0.009614 | houston | N | 0.009614 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.029928 | houston | Y | -0.16532 | 0.15103 | -0.15256 | 0.009614 | 0.009614 | houston | N | 0.009614 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.029928 | houston | Y | -0.16532 | 0.15103 | -0.15256 | 0.009614 | 0.009614 | houston | N | 0.009614 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.063658 | houston | N | -0.19905 | 0.1173 | -0.18629 | -0.024116 | 0.024116 | houston | N | 0.024116 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.063658 | houston | N | -0.19905 | 0.1173 | -0.18629 | -0.024116 | 0.024116 | houston | N | 0.024116 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.049073 | houston | N | -0.18446 | 0.13189 | -0.1717 | -0.009531 | 0.009531 | houston | N | 0.009531 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.049073 | houston | N | -0.18446 | 0.13189 | -0.1717 | -0.009531 | 0.009531 | houston | N | 0.009531 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.049073 | houston | N | -0.18446 | 0.13189 | -0.1717 | -0.009531 | 0.009531 | houston | N | 0.009531 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.03432 | houston | N | -0.16971 | 0.14664 | -0.15695 | 0.005222 | 0.005222 | houston | N | 0.005222 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.03432 | houston | N | -0.16971 | 0.14664 | -0.15695 | 0.005222 | 0.005222 | houston | N | 0.005222 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.03432 | houston | N | -0.16971 | 0.14664 | -0.15695 | 0.005222 | 0.005222 | houston | N | 0.005222 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.03432 | houston | N | -0.16971 | 0.14664 | -0.15695 | 0.005222 | 0.005222 | houston | N | 0.005222 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.0315 | houston | N | -0.16689 | 0.14946 | -0.15413 | 0.008042 | 0.008042 | houston | N | 0.008042 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.0315 | houston | N | -0.16689 | 0.14946 | -0.15413 | 0.008042 | 0.008042 | houston | N | 0.008042 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.03517 | houston | N | -0.17056 | 0.14579 | -0.1578 | 0.004372 | 0.004372 | houston | N | 0.004372 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.03517 | houston | N | -0.17056 | 0.14579 | -0.1578 | 0.004372 | 0.004372 | houston | N | 0.004372 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.03517 | houston | N | -0.17056 | 0.14579 | -0.1578 | 0.004372 | 0.004372 | houston | N | 0.004372 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.03517 | houston | N | -0.17056 | 0.14579 | -0.1578 | 0.004372 | 0.004372 | houston | N | 0.004372 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.03517 | houston | N | -0.17056 | 0.14579 | -0.1578 | 0.004372 | 0.004372 | houston | N | 0.004372 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.026389 | houston | Y | -0.16178 | 0.15457 | -0.14902 | 0.013153 | 0.013153 | houston | N | 0.013153 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.027825 | houston | Y | -0.16321 | 0.15314 | -0.15045 | 0.011717 | 0.011717 | houston | N | 0.011717 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.025956 | houston | Y | -0.16135 | 0.15501 | -0.14858 | 0.013586 | 0.013586 | houston | N | 0.013586 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.025956 | houston | Y | -0.16135 | 0.15501 | -0.14858 | 0.013586 | 0.013586 | houston | N | 0.013586 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.025956 | houston | Y | -0.16135 | 0.15501 | -0.14858 | 0.013586 | 0.013586 | houston | N | 0.013586 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.017988 | houston | N | -0.15338 | 0.16297 | -0.14062 | 0.021554 | 0.021554 | houston | N | 0.021554 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.029711 | houston | N | -0.1651 | 0.15125 | -0.15234 | 0.009831 | 0.009831 | houston | N | 0.009831 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.029711 | houston | N | -0.1651 | 0.15125 | -0.15234 | 0.009831 | 0.009831 | houston | N | 0.009831 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.024941 | houston | N | -0.16033 | 0.15602 | -0.14757 | 0.014601 | 0.014601 | houston | N | 0.014601 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.024941 | houston | N | -0.16033 | 0.15602 | -0.14757 | 0.014601 | 0.014601 | houston | N | 0.014601 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.024941 | houston | N | -0.16033 | 0.15602 | -0.14757 | 0.014601 | 0.014601 | houston | N | 0.014601 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.024941 | houston | N | -0.16033 | 0.15602 | -0.14757 | 0.014601 | 0.014601 | houston | N | 0.014601 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.031405 | houston | N | -0.16679 | 0.14956 | -0.15403 | 0.008137 | 0.008137 | houston | N | 0.008137 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.031405 | houston | N | -0.16679 | 0.14956 | -0.15403 | 0.008137 | 0.008137 | houston | N | 0.008137 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.031405 | houston | N | -0.16679 | 0.14956 | -0.15403 | 0.008137 | 0.008137 | houston | N | 0.008137 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.031405 | houston | N | -0.16679 | 0.14956 | -0.15403 | 0.008137 | 0.008137 | houston | N | 0.008137 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.032306 | houston | N | -0.1677 | 0.14866 | -0.15493 | 0.007236 | 0.007236 | houston | N | 0.007236 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.032306 | houston | N | -0.1677 | 0.14866 | -0.15493 | 0.007236 | 0.007236 | houston | N | 0.007236 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.032306 | houston | N | -0.1677 | 0.14866 | -0.15493 | 0.007236 | 0.007236 | houston | N | 0.007236 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.032306 | houston | N | -0.1677 | 0.14866 | -0.15493 | 0.007236 | 0.007236 | houston | N | 0.007236 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.032306 | houston | N | -0.1677 | 0.14866 | -0.15493 | 0.007236 | 0.007236 | houston | N | 0.007236 | 0
48651 | EP_1_2 | 1 | 5 | -0.026465 | houston | N | -0.16185 | 0.1545 | -0.14909 | 0.013077 | 0.013077 | houston | N | 0.013077 | 0
48651 | EP_1_2 | 2 | 21 | -0.026465 | houston | N | -0.16185 | 0.1545 | -0.14909 | 0.013077 | 0.013077 | houston | N | 0.013077 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.0382 | north | N | -0.09719 | 0.21916 | -0.084429 | 0.077742 | 0.077742 | houston | Y | 0.09719 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.0382 | north | N | -0.09719 | 0.21916 | -0.084429 | 0.077742 | 0.077742 | houston | Y | 0.09719 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.0382 | north | N | -0.09719 | 0.21916 | -0.084429 | 0.077742 | 0.077742 | houston | Y | 0.09719 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.0382 | north | N | -0.09719 | 0.21916 | -0.084429 | 0.077742 | 0.077742 | houston | Y | 0.09719 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.024589 | houston | Y | -0.15998 | 0.15637 | -0.14722 | 0.014953 | 0.014953 | houston | N | 0.014953 | 0
48691 | GBY_7374 | A | 46 | -0.033057 | houston | Y | -0.16845 | 0.1479 | -0.15569 | 0.006485 | 0.006485 | houston | N | 0.006485 | 0
48691 | GBY_7374 | B | 46 | -0.033057 | houston | Y | -0.16845 | 0.1479 | -0.15569 | 0.006485 | 0.006485 | houston | N | 0.006485 | 0
48692 | GBY_8182 | C | 46 | -0.033057 | houston | Y | -0.16845 | 0.1479 | -0.15569 | 0.006485 | 0.006485 | houston | N | 0.006485 | 0
48692 | GBY_8182 | D | 55 | -0.033057 | houston | Y | -0.16845 | 0.1479 | -0.15569 | 0.006485 | 0.006485 | houston | N | 0.006485 | 0
48693 | GBY_8384 | E | 55 | -0.033057 | houston | Y | -0.16845 | 0.1479 | -0.15569 | 0.006485 | 0.006485 | houston | N | 0.006485 | 0
48693 | GBY_8384 | F | 54 | -0.033057 | houston | Y | -0.16845 | 0.1479 | -0.15569 | 0.006485 | 0.006485 | houston | N | 0.006485 | 0
48721 | LEG_1___ | 1 | 827 | 0.10149 | north | Y | -0.033903 | 0.28245 | -0.021142 | 0.14103 | 0.021142 | west | Y | 0.033903 | 10.5535
48722 | LEG_2___ | 2 | 819 | 0.10149 | north | Y | -0.033903 | 0.28245 | -0.021142 | 0.14103 | 0.021142 | west | Y | 0.033903 | 10.4514
48730 | MNS_GT | 1 | 46.1 | -0.049565 | houston | N | -0.18495 | 0.1314 | -0.17219 | -0.010023 | 0.010023 | houston | N | 0.010023 | 0
48731 | CBE_GT1 | 1 | 76 | -0.088511 | houston | Y | -0.2239 | 0.092451 | -0.21114 | -0.048969 | 0.048969 | houston | N | 0.048969 | 0
48732 | CBE_GT2 | 1 | 76 | -0.088511 | houston | Y | -0.2239 | 0.092451 | -0.21114 | -0.048969 | 0.048969 | houston | N | 0.048969 | 0
48733 | CBE_ST12 | 1 | 105 | -0.088511 | houston | Y | -0.2239 | 0.092451 | -0.21114 | -0.048969 | 0.048969 | houston | N | 0.048969 | 0
48734 | CBE_GT3 | 1 | 74 | -0.088511 | houston | Y | -0.2239 | 0.092451 | -0.21114 | -0.048969 | 0.048969 | houston | N | 0.048969 | 0
48735 | CBE_GT4 | 1 | 74 | -0.088511 | houston | Y | -0.2239 | 0.092451 | -0.21114 | -0.048969 | 0.048969 | houston | N | 0.048969 | 0
48736 | CBE_ST34 | 1 | 102 | -0.088511 | houston | Y | -0.2239 | 0.092451 | -0.21114 | -0.048969 | 0.048969 | houston | N | 0.048969 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.031379 | houston | N | -0.16677 | 0.14958 | -0.15401 | 0.008163 | 0.008163 | houston | N | 0.008163 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.031379 | houston | N | -0.16677 | 0.14958 | -0.15401 | 0.008163 | 0.008163 | houston | N | 0.008163 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.031379 | houston | N | -0.16677 | 0.14958 | -0.15401 | 0.008163 | 0.008163 | houston | N | 0.008163 | 0
48761 | PR_GT1__ | 1 | 35 | -0.031953 | houston | N | -0.16734 | 0.14901 | -0.15458 | 0.007589 | 0.007589 | houston | N | 0.007589 | 0
48772 | PHR_GN2_ | MB | 459 | -0.037337 | houston | Y | -0.17273 | 0.14362 | -0.15997 | 0.002205 | 0.002205 | houston | N | 0.002205 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.026456 | houston | N | -0.16185 | 0.15451 | -0.14908 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.026456 | houston | N | -0.16185 | 0.15451 | -0.14908 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.026456 | houston | N | -0.16185 | 0.15451 | -0.14908 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.026456 | houston | N | -0.16185 | 0.15451 | -0.14908 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.026456 | houston | N | -0.16185 | 0.15451 | -0.14908 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.026456 | houston | N | -0.16185 | 0.15451 | -0.14908 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.026456 | houston | N | -0.16185 | 0.15451 | -0.14908 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.017988 | houston | N | -0.15338 | 0.16297 | -0.14062 | 0.021554 | 0.021554 | houston | N | 0.021554 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.017988 | houston | N | -0.15338 | 0.16297 | -0.14062 | 0.021554 | 0.021554 | houston | N | 0.021554 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.017988 | houston | N | -0.15338 | 0.16297 | -0.14062 | 0.021554 | 0.021554 | houston | N | 0.021554 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.017988 | houston | N | -0.15338 | 0.16297 | -0.14062 | 0.021554 | 0.021554 | houston | N | 0.021554 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.026127 | houston | N | -0.16152 | 0.15483 | -0.14876 | 0.013415 | 0.013415 | houston | N | 0.013415 | 0
48820 | SHELLG1_ | 1 | 71 | -0.030844 | houston | N | -0.16623 | 0.15012 | -0.15347 | 0.008698 | 0.008698 | houston | N | 0.008698 | 0
48821 | SHELLG2 | 2 | 72 | -0.030844 | houston | N | -0.16623 | 0.15012 | -0.15347 | 0.008698 | 0.008698 | houston | N | 0.008698 | 0
48822 | SHELLG3_ | 1 | 39 | -0.030844 | houston | N | -0.16623 | 0.15012 | -0.15347 | 0.008698 | 0.008698 | houston | N | 0.008698 | 0
48822 | SHELLG3_ | 2 | 30 | -0.030844 | houston | N | -0.16623 | 0.15012 | -0.15347 | 0.008698 | 0.008698 | houston | N | 0.008698 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.032742 | houston | N | -0.16813 | 0.14822 | -0.15537 | 0.0068 | 0.0068 | houston | N | 0.0068 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.032742 | houston | N | -0.16813 | 0.14822 | -0.15537 | 0.0068 | 0.0068 | houston | N | 0.0068 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.031412 | houston | N | -0.1668 | 0.14955 | -0.15404 | 0.00813 | 0.00813 | houston | N | 0.00813 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.031523 | houston | Y | -0.16691 | 0.14944 | -0.15415 | 0.008019 | 0.008019 | houston | N | 0.008019 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.031553 | houston | Y | -0.16694 | 0.14941 | -0.15418 | 0.007989 | 0.007989 | houston | N | 0.007989 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.031422 | houston | Y | -0.16681 | 0.14954 | -0.15405 | 0.00812 | 0.00812 | houston | N | 0.00812 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.031392 | houston | Y | -0.16678 | 0.14957 | -0.15402 | 0.00815 | 0.00815 | houston | N | 0.00815 | 0
48855 | SRB_GT21 | B2 | 12 | -0.031574 | houston | Y | -0.16696 | 0.14939 | -0.1542 | 0.007968 | 0.007968 | houston | N | 0.007968 | 0
48855 | SRB_GT21 | MB | 18 | -0.031574 | houston | Y | -0.16696 | 0.14939 | -0.1542 | 0.007968 | 0.007968 | houston | N | 0.007968 | 0
48865 | TECO_GT1 | 1 | 50 | -0.039195 | houston | Y | -0.17458 | 0.14177 | -0.16182 | 0.00034703 | 0.00034703 | houston | N | 0.00034703 | 0
48873 | THW_ST3_ | 3 | 104 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48874 | THW_ST4_ | 4 | 104 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48875 | THW_3132 | A | 54 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48875 | THW_3132 | B | 53 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48877 | THW_3334 | C | 54 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48877 | THW_3334 | D | 57 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48879 | THW_4142 | E | 54 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48879 | THW_4142 | F | 54 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48881 | THW_4344 | G | 58 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48881 | THW_4344 | H | 58 | -0.028349 | houston | Y | -0.16374 | 0.15261 | -0.15098 | 0.011193 | 0.011193 | houston | N | 0.011193 | 0
48883 | THW_GT1_ | B2 | 12 | -0.027031 | houston | Y | -0.16242 | 0.15393 | -0.14966 | 0.012511 | 0.012511 | houston | N | 0.012511 | 0
48885 | THW_5152 | A | 56 | -0.023971 | houston | Y | -0.15936 | 0.15699 | -0.1466 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48885 | THW_5152 | B | 59 | -0.023971 | houston | Y | -0.15936 | 0.15699 | -0.1466 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48886 | THW_5354 | C | 56 | -0.023971 | houston | Y | -0.15936 | 0.15699 | -0.1466 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48886 | THW_5354 | D | 56 | -0.023971 | houston | Y | -0.15936 | 0.15699 | -0.1466 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48887 | THW_5556 | E | 59 | -0.023971 | houston | Y | -0.15936 | 0.15699 | -0.1466 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48887 | THW_5556 | F | 56 | -0.023971 | houston | Y | -0.15936 | 0.15699 | -0.1466 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.083454 | houston | Y | -0.21884 | 0.097508 | -0.20608 | -0.043912 | 0.043912 | houston | N | 0.043912 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.047419 | houston | Y | -0.18281 | 0.13354 | -0.17005 | -0.007877 | 0.007877 | houston | N | 0.007877 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.047419 | houston | Y | -0.18281 | 0.13354 | -0.17005 | -0.007877 | 0.007877 | houston | N | 0.007877 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.047419 | houston | Y | -0.18281 | 0.13354 | -0.17005 | -0.007877 | 0.007877 | houston | N | 0.007877 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.047419 | houston | Y | -0.18281 | 0.13354 | -0.17005 | -0.007877 | 0.007877 | houston | N | 0.007877 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.047419 | houston | N | -0.18281 | 0.13354 | -0.17005 | -0.007877 | 0.007877 | houston | N | 0.007877 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.049166 | houston | Y | -0.18456 | 0.1318 | -0.17179 | -0.009624 | 0.009624 | houston | N | 0.009624 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.049166 | houston | Y | -0.18456 | 0.1318 | -0.17179 | -0.009624 | 0.009624 | houston | N | 0.009624 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.049166 | houston | Y | -0.18456 | 0.1318 | -0.17179 | -0.009624 | 0.009624 | houston | N | 0.009624 | 0
48929 | WAPGT21_ | B1 | 13 | -0.047419 | houston | Y | -0.18281 | 0.13354 | -0.17005 | -0.007877 | 0.007877 | houston | N | 0.007877 | 0
48940 | WARVUE_G | G1 | 12 | -0.026429 | houston | Y | -0.16182 | 0.15453 | -0.14906 | 0.013113 | 0.013113 | houston | N | 0.013113 | 0
49803 | EXN_15GT | 1 | 34 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49826 | EXN938GT | 5 | 45.9 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49828 | EXN941GT | 10 | 17.7 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49829 | EXN942GT | 11 | 20.4 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49830 | EXN943GT | 12 | 19.9 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49831 | EXN944GT | 13 | 35 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49832 | EXN945GT | 9 | 18 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49837 | EXN_GT | 4 | 85.4 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49838 | EXN_14GT | 14 | 148 | -0.027476 | houston | N | -0.16287 | 0.15349 | -0.1501 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49851 | DOW17000 | 37 | 62 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49858 | DOW38100 | 31 | 71.4 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49859 | DOW38200 | 33 | 45 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49860 | DOW38300 | 32 | 101 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49862 | DOW39100 | 36 | 86 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49863 | DOW39200 | 35 | 88 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49865 | DOW41000 | 41 | 50 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49866 | DOW42000 | 42 | 18 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49869 | DOW49000 | 45 | 94 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49870 | DOW61000 | 61 | 70 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49871 | DOW62000 | 62 | 63 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49872 | DOW63000 | 63 | 72 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49873 | DOW64000 | 64 | 64.8 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49876 | DOW65000 | 65 | 101 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49877 | DOW66000 | 66 | 97 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49878 | DOW67000 | 67 | 103 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49882 | DOW81000 | 81 | 76 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49884 | DOW82000 | 82 | 80 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49885 | DOW83000 | 83 | 80 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
49886 | DOW84000 | 84 | 171 | -0.067518 | houston | N | -0.20291 | 0.11344 | -0.19015 | -0.027976 | 0.027976 | houston | N | 0.027976 | 0
58909 | PEARSALL | 1 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58909 | PEARSALL | 2 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58909 | PEARSALL | 3 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58909 | PEARSALL | 4 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58909 | PEARSALL | 5 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58909 | PEARSALL | 6 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58919 | PEARSALL | 1 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58919 | PEARSALL | 2 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58919 | PEARSALL | 3 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58919 | PEARSALL | 4 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58919 | PEARSALL | 5 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58919 | PEARSALL | 6 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58929 | PEARSALL | 1 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58929 | PEARSALL | 2 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58929 | PEARSALL | 3 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58929 | PEARSALL | 4 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58929 | PEARSALL | 5 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58929 | PEARSALL | 6 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58949 | PEARSALL | 1 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58949 | PEARSALL | 2 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58949 | PEARSALL | 3 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58949 | PEARSALL | 4 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58949 | PEARSALL | 5 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
58949 | PEARSALL | 6 | 8.4 | -0.1508 | south | Y | -0.28619 | 0.030163 | -0.27343 | -0.11126 | 0.030163 | south | N | 0.030163 | 0
60000 | DSKY2 | 1 | 76.5 | 0.10267 | west | Y | -0.032723 | 0.28363 | -0.019962 | 0.14221 | 0.019962 | west | N | 0.019962 | 0
60003 | KING_NE1 | 1 | 80 | 0.10823 | west | Y | -0.027164 | 0.28919 | -0.014403 | 0.14777 | 0.014403 | west | N | 0.014403 | 0
60005 | KING_SE1 | 1 | 40 | 0.10823 | west | Y | -0.027164 | 0.28919 | -0.014403 | 0.14777 | 0.014403 | west | N | 0.014403 | 0
60007 | KING_SW1 | 1 | 80 | 0.10912 | west | Y | -0.026275 | 0.29008 | -0.013514 | 0.14866 | 0.013514 | west | N | 0.013514 | 0
60016 | WOODWRD1 | 1 | 80 | 0.10803 | west | Y | -0.027357 | 0.28899 | -0.014596 | 0.14758 | 0.014596 | west | N | 0.014596 | 0
60017 | ORNNWP1 | 1 | 80 | 0.10344 | west | Y | -0.031946 | 0.28441 | -0.019185 | 0.14299 | 0.019185 | west | N | 0.019185 | 0
60018 | DSKY1 | 1 | 84 | 0.10194 | west | Y | -0.033448 | 0.2829 | -0.020687 | 0.14148 | 0.020687 | west | N | 0.020687 | 0
60019 | KING_NW1 | 1 | 80 | 0.10912 | west | Y | -0.026275 | 0.29008 | -0.013514 | 0.14866 | 0.013514 | west | N | 0.013514 | 0
60057 | CALLAHAN | 1 | 114 | -0.1808 | south | Y | -0.31619 | 0.00015689 | -0.30343 | -0.14126 | 0.00015689 | south | N | 0.00015689 | 0
60058 | BUFF_GAP | 1 | 120 | 0.12365 | west | Y | -0.011736 | 0.30462 | 0.0010252 | 0.1632 | 0.0010252 | west | N | 0.0010252 | 0
60060 | CIRELLO | 1 | 233 | 0.12365 | west | Y | -0.011736 | 0.30462 | 0.0010252 | 0.1632 | 0.0010252 | west | N | 0.0010252 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.12365 | west | Y | -0.011736 | 0.30462 | 0.0010252 | 0.1632 | 0.0010252 | west | N | 0.0010252 | 0
60066 | H_HOLLOW | 1 | 222 | -0.1808 | south | Y | -0.31619 | 0.00015689 | -0.30343 | -0.14126 | 0.00015689 | south | N | 0.00015689 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.1808 | south | Y | -0.31619 | 0.00015689 | -0.30343 | -0.14126 | 0.00015689 | south | N | 0.00015689 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.1808 | south | Y | -0.31619 | 0.00015689 | -0.30343 | -0.14126 | 0.00015689 | south | N | 0.00015689 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.1808 | south | Y | -0.31619 | 0.00015689 | -0.30343 | -0.14126 | 0.00015689 | south | N | 0.00015689 | 0
60074 | HORSH5 | 1 | 100 | -0.1808 | south | Y | -0.31619 | 0.00015689 | -0.30343 | -0.14126 | 0.00015689 | south | N | 0.00015689 | 0
60081 | WHRLWIND | 1 | 60 | 0.12857 | west | Y | -0.0068149 | 0.30954 | 0.0059462 | 0.16812 | 0.0059462 | west | N | 0.0059462 | 0
60201 | RIO DRCS | F | 0 | -0.094367 | south | N | -0.22976 | 0.086595 | -0.217 | -0.054825 | 0.054825 | houston | Y | 0.086595 | 0
60202 | FRIEND_R | F | 0 | 0.078013 | west | N | -0.057377 | 0.25897 | -0.044616 | 0.11756 | 0.044616 | west | N | 0.044616 | 0
60203 | PRES0A | BT | 4.8 | 0.11244 | west | N | -0.022954 | 0.2934 | -0.010193 | 0.15198 | 0.010193 | west | N | 0.010193 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.12643 | west | Y | -0.0089639 | 0.30739 | 0.0037972 | 0.16597 | 0.0037972 | west | N | 0.0037972 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.12643 | west | Y | -0.0089639 | 0.30739 | 0.0037972 | 0.16597 | 0.0037972 | west | N | 0.0037972 | 0
71057 | L_SWEETW | W1 | 135 | 0.12643 | west | Y | -0.0089639 | 0.30739 | 0.0037972 | 0.16597 | 0.0037972 | west | N | 0.0037972 | 0
71059 | L_SWEETW | W1 | 119 | 0.12643 | west | Y | -0.0089639 | 0.30739 | 0.0037972 | 0.16597 | 0.0037972 | west | N | 0.0037972 | 0
71060 | L_SWEETW | W1 | 105 | 0.12643 | west | Y | -0.0089639 | 0.30739 | 0.0037972 | 0.16597 | 0.0037972 | west | N | 0.0037972 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.12643 | west | Y | -0.0089639 | 0.30739 | 0.0037972 | 0.16597 | 0.0037972 | west | N | 0.0037972 | 0
76031 | L_GASCCR | W1 | 150 | 0.1223 | west | Y | -0.013094 | 0.30326 | -0.00033281 | 0.16184 | 0.00033281 | west | N | 0.00033281 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.12175 | west | Y | -0.013638 | 0.30271 | -0.00087681 | 0.16129 | 0.00087681 | west | N | 0.00087681 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.12175 | west | Y | -0.013638 | 0.30271 | -0.00087681 | 0.16129 | 0.00087681 | west | N | 0.00087681 | 0
76096 | L_CAPRSI | W1 | 186 | 0.12175 | west | Y | -0.013638 | 0.30271 | -0.00087681 | 0.16129 | 0.00087681 | west | N | 0.00087681 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.12175 | west | Y | -0.013638 | 0.30271 | -0.00087681 | 0.16129 | 0.00087681 | west | N | 0.00087681 | 0
80003 | MILHWYS | F | 0 | -0.14384 | south | N | -0.27923 | 0.037121 | -0.26647 | -0.1043 | 0.037121 | south | N | 0.037121 | 0
80010 | EPLVT1 | F | 0 | -0.1088 | south | N | -0.24419 | 0.072164 | -0.23143 | -0.069256 | 0.069256 | houston | Y | 0.072164 | 0
80012 | LAR | F | 0 | -0.15155 | south | N | -0.28694 | 0.029409 | -0.27418 | -0.11201 | 0.029409 | south | N | 0.029409 | 0
80051 | FORPVCM0 | 8 | 28 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
80053 | FOR69CG0 | 10 | 74 | -0.1309 | south | N | -0.26629 | 0.050064 | -0.25353 | -0.091356 | 0.050064 | south | N | 0.050064 | 0
80080 | GWINDT11 | 1 | 94 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80080 | GWINDT11 | 2 | 41 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80080 | GWINDT11 | 3 | 38 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80080 | GWINDT11 | 4 | 19 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80081 | GWINDT21 | 1 | 94 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80081 | GWINDT21 | 2 | 36 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80081 | GWINDT21 | 3 | 43 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80081 | GWINDT21 | 4 | 22 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80137 | CSDR89 | 8 | 39 | -0.13581 | south | N | -0.27119 | 0.045157 | -0.25843 | -0.096263 | 0.045157 | south | N | 0.045157 | 0
80137 | CSDR89 | 9 | 15 | -0.13581 | south | N | -0.27119 | 0.045157 | -0.25843 | -0.096263 | 0.045157 | south | N | 0.045157 | 0
80138 | CSDR7 | 7 | 7 | -0.13581 | south | N | -0.27119 | 0.045157 | -0.25843 | -0.096263 | 0.045157 | south | N | 0.045157 | 0
80139 | CSDR56 | 5 | 15 | -0.13581 | south | N | -0.27119 | 0.045157 | -0.25843 | -0.096263 | 0.045157 | south | N | 0.045157 | 0
80139 | CSDR56 | 6 | 39 | -0.13581 | south | N | -0.27119 | 0.045157 | -0.25843 | -0.096263 | 0.045157 | south | N | 0.045157 | 0
80140 | CSDR11 | 11 | 39 | -0.13581 | south | N | -0.27119 | 0.045157 | -0.25843 | -0.096263 | 0.045157 | south | N | 0.045157 | 0
80180 | PNSCALT1 | 1 | 148 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80180 | PNSCALT1 | 2 | 50 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80181 | PNSCALT2 | 1 | 55 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80181 | PNSCALT2 | 2 | 50 | -0.14374 | south | Y | -0.27913 | 0.037218 | -0.26637 | -0.1042 | 0.037218 | south | N | 0.037218 | 0
80223 | REYSHR G | 1 | 12 | -0.14083 | south | N | -0.27622 | 0.040134 | -0.26346 | -0.10129 | 0.040134 | south | N | 0.040134 | 0
80224 | VISTRONG | 1 | 15 | -0.13738 | south | N | -0.27277 | 0.043581 | -0.26001 | -0.097839 | 0.043581 | south | N | 0.043581 | 0
80225 | VISTRONG | 2 | 23 | -0.13738 | south | N | -0.27277 | 0.043581 | -0.26001 | -0.097839 | 0.043581 | south | N | 0.043581 | 0
80226 | ALCOA G | 1 | 48 | -0.13205 | south | N | -0.26744 | 0.048908 | -0.25468 | -0.092512 | 0.048908 | south | N | 0.048908 | 0
80227 | AIRCO G | 1 | 8 | -0.13636 | south | N | -0.27175 | 0.044599 | -0.25899 | -0.096821 | 0.044599 | south | N | 0.044599 | 0
80261 | NBEC81A | 1 | 180 | -0.14235 | south | Y | -0.27774 | 0.038613 | -0.26498 | -0.10281 | 0.038613 | south | N | 0.038613 | 0
80262 | NBEC91A | 1 | 180 | -0.1423 | south | Y | -0.27769 | 0.038658 | -0.26493 | -0.10276 | 0.038658 | south | N | 0.038658 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.14263 | south | Y | -0.27802 | 0.03833 | -0.26526 | -0.10309 | 0.03833 | south | N | 0.03833 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.14263 | south | Y | -0.27802 | 0.03833 | -0.26526 | -0.10309 | 0.03833 | south | N | 0.03833 | 0
80265 | LARECU40 | 4 | 100 | -0.15157 | south | Y | -0.28696 | 0.029396 | -0.27419 | -0.11202 | 0.029396 | south | N | 0.029396 | 0
80266 | LARECU50 | 5 | 100 | -0.15157 | south | Y | -0.28696 | 0.029396 | -0.27419 | -0.11202 | 0.029396 | south | N | 0.029396 | 0
80291 | PAPALOTE | 1 | 25 | -0.14141 | south | Y | -0.2768 | 0.039552 | -0.26404 | -0.10187 | 0.039552 | south | N | 0.039552 | 0
80291 | PAPALOTE | 2 | 25 | -0.14141 | south | Y | -0.2768 | 0.039552 | -0.26404 | -0.10187 | 0.039552 | south | N | 0.039552 | 0
80291 | PAPALOTE | 3 | 25 | -0.14141 | south | Y | -0.2768 | 0.039552 | -0.26404 | -0.10187 | 0.039552 | south | N | 0.039552 | 0
80291 | PAPALOTE | 4 | 16 | -0.14141 | south | Y | -0.2768 | 0.039552 | -0.26404 | -0.10187 | 0.039552 | south | N | 0.039552 | 0
80294 | PAPALOTE | 5 | 25 | -0.14141 | south | Y | -0.2768 | 0.039552 | -0.26404 | -0.10187 | 0.039552 | south | N | 0.039552 | 0
80294 | PAPALOTE | 6 | 25 | -0.14141 | south | Y | -0.2768 | 0.039552 | -0.26404 | -0.10187 | 0.039552 | south | N | 0.039552 | 0
80294 | PAPALOTE | 7 | 25 | -0.14141 | south | Y | -0.2768 | 0.039552 | -0.26404 | -0.10187 | 0.039552 | south | N | 0.039552 | 0
80294 | PAPALOTE | 8 | 15 | -0.14141 | south | Y | -0.2768 | 0.039552 | -0.26404 | -0.10187 | 0.039552 | south | N | 0.039552 | 0
86104 | CID-138 | EQ | 0 | -0.15157 | south | N | -0.28696 | 0.029396 | -0.27419 | -0.11202 | 0.029396 | south | N | 0.029396 | 0
86105 | CID-230 | EQ | 500 | -0.15157 | south | N | -0.28696 | 0.029396 | -0.27419 | -0.11202 | 0.029396 | south | N | 0.029396 | 0
86106 | CUF-230 | EQ | 500 | -0.15157 | south | N | -0.28696 | 0.029396 | -0.27419 | -0.11202 | 0.029396 | south | N | 0.029396 | 0
86107 | CUF-138 | EQ | 0 | -0.15157 | south | N | -0.28696 | 0.029396 | -0.27419 | -0.11202 | 0.029396 | south | N | 0.029396 | 0
88198 | BEEVILLE | F | 0 | -0.15046 | south | N | -0.28585 | 0.030504 | -0.27309 | -0.11092 | 0.030504 | south | N | 0.030504 | 0
88253 | HAMILTON | F | 0 | -0.081574 | south | N | -0.21696 | 0.099388 | -0.2042 | -0.042032 | 0.042032 | houston | Y | 0.099388 | 0
88299 | ZAPATA | F | 0 | -0.14777 | south | N | -0.28316 | 0.033193 | -0.2704 | -0.10823 | 0.033193 | south | N | 0.033193 | 0
88508 | FALFURRI | F | 0 | -0.14618 | south | N | -0.28157 | 0.03478 | -0.26881 | -0.10664 | 0.03478 | south | N | 0.03478 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.24531 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.42298 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.24531 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 193.0621 | 787 | 0.42298 | 332.8824 | 787 | 332.8824
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.19433 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 49.5536 | 255 | 0.37199 | 94.8576 | 1042 | 427.74
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.19433 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 28.9549 | 149 | 0.37199 | 55.4266 | 1191 | 483.1666 | Weighted Shift Factors
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.19433 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 29.7322 | 153 | 0.37199 | 56.9145 | 1344 | 540.0811 | North | 0.13539
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.16187 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2807 | 150 | 0.33953 | 50.93 | 1494 | 591.0111 | South | -0.17766
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.16187 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9497 | 80 | 0.33953 | 27.1627 | 1574 | 618.1738 |  | 0.31305
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.15799 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3699 | 0 | 0.33565 | 0 | 1574 | 618.1738
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.15799 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3699 | 0 | 0.33565 | 0 | 1574 | 618.1738 | Line Rating | 1239.6
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.15559 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.6686 | 216.4 | 0.33325 | 72.1147 | 1790.4 | 690.2885 | Conc Gen | 2456.5
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.15559 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.6219 | 216.1 | 0.33325 | 72.0148 | 2006.5 | 762.3033 | Weighted Imp. | 912.1202
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7791 | 224 | 0.33293 | 74.5755 | 2230.5 | 836.8788 | PTDF | 0.37131
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.0897 | 226 | 0.33293 | 75.2414 | 2456.5 | 912.1202
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.916 | 212 | 0.33293 | 70.5804 |  |  | Concentration | 1.1861
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.7607 | 211 | 0.33293 | 70.2475
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.14912 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.0522 | 168 | 0.32678 | 54.8994
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.14912 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.4208 | 90 | 0.32678 | 29.4104
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.14796 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 58.4446 | 395 | 0.32562 | 128.6212
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.14796 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 64.363 | 435 | 0.32562 | 141.6462
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.14762 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 64.2138 | 435 | 0.32528 | 141.497
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.14611 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32377 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.14575 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32341 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.14575 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32341 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.14569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.658 | 217.3 | 0.32335 | 70.264
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.14569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.866 | 205 | 0.32335 | 66.2868
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.14569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 39.6854 | 272.4 | 0.32335 | 88.0807
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1863 | 70 | 0.32318 | 22.6226
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.0407 | 69 | 0.32318 | 22.2994
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.0407 | 69 | 0.32318 | 22.2994
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.8952 | 68 | 0.32318 | 21.9763
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.14506 | north | 3 | N | N | Nnorth | Nnorth | 1 | 167.8309 | 0 | 0.32272 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.14506 | north | 3 | N | N | Nnorth | Nnorth | 1 | 167.976 | 0 | 0.32272 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.1448 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32246 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.1448 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32246 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.1448 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32246 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14388 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.978 | 118 | 0.32154 | 37.9421
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14388 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.5463 | 115 | 0.32154 | 36.9775
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14388 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 79.9978 | 556 | 0.32154 | 178.7781
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14294 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.5765 | 60 | 0.3206 | 19.2363
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14294 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.0053 | 63 | 0.3206 | 20.1981
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0011 | 196 | 0.32053 | 62.823
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.8578 | 111 | 0.32053 | 35.5783
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.14249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.0357 | 288 | 0.32015 | 92.2025
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.14249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9453 | 147 | 0.32015 | 47.0617
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.14249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9453 | 147 | 0.32015 | 47.0617
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14241 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.32008 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.14236 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.5624 | 18 | 0.32002 | 5.7603
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.14236 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.5624 | 18 | 0.32002 | 5.7603
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.14236 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.4096 | 38 | 0.32002 | 12.1607
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14235 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32001 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.14218 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.9949 | 112.5 | 0.31984 | 35.9819
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14165 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31931 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14165 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31931 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14158 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.6633 | 0 | 0.31924 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14158 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.6633 | 0 | 0.31924 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14145 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 24.0462 | 170 | 0.31911 | 54.2488
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14145 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 73.553 | 520 | 0.31911 | 165.9374
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14131 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 52.2858 | 370 | 0.31898 | 118.0209
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.7838 | 0 | 0.31898 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.9251 | 0 | 0.31898 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 43.6657 | 0 | 0.31898 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.2078 | 0 | 0.31898 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.3491 | 0 | 0.31898 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 43.807 | 0 | 0.31898 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.14121 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8066 | 204 | 0.31887 | 65.0498
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.14121 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.383 | 201 | 0.31887 | 64.0932
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.14121 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.1726 | 242 | 0.31887 | 77.1669
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5917 | 160 | 0.31886 | 51.0177
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0269 | 156 | 0.31886 | 49.7422
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.6748 | 196 | 0.31886 | 62.4966
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0269 | 156 | 0.31886 | 49.7422
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1681 | 157 | 0.31886 | 50.0611
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.9572 | 198 | 0.31886 | 63.1344
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.14108 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.5808 | 0 | 0.31874 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.14108 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.2298 | 0 | 0.31874 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.14108 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.4713 | 0 | 0.31874 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14104 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 54.7231 | 388 | 0.3187 | 123.6561
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14104 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 72.6351 | 515 | 0.3187 | 164.1312
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14102 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.6914 | 558 | 0.31869 | 177.827
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14102 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.6529 | 579 | 0.31869 | 184.5194
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14102 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 113.9474 | 808 | 0.31869 | 257.4986
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14101 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.1396 | 79 | 0.31867 | 25.1749
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14101 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.9467 | 106 | 0.31867 | 33.779
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14101 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.587 | 146 | 0.31867 | 46.5257
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14101 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.7165 | 76 | 0.31867 | 24.2189
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.141 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.6401 | 40 | 0.31867 | 12.7466
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.1408 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.52 | 25 | 0.31846 | 7.9615
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.1408 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7727 | 41 | 0.31846 | 13.0569
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.1408 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8159 | 20 | 0.31846 | 6.3692
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.14073 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.2734 | 73 | 0.31839 | 23.2428
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.14073 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.7471 | 119 | 0.31839 | 37.8889
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.14073 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 28.8501 | 205 | 0.31839 | 65.2709
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.14073 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.3547 | 102 | 0.31839 | 32.4762
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.14073 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.5103 | 96 | 0.31839 | 30.5659
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4993 | 161 | 0.31741 | 51.1029
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9185 | 164 | 0.31741 | 52.0551
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9185 | 164 | 0.31741 | 52.0551
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 57.8553 | 414 | 0.31741 | 131.4075
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.639 | 162 | 0.31741 | 51.4203
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4993 | 161 | 0.31741 | 51.1029
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7788 | 163 | 0.31741 | 51.7377
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 57.1565 | 409 | 0.31741 | 129.8204
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13945 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6734 | 0 | 0.31712 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13945 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6734 | 0 | 0.31712 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.13931 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.7167 | 120 | 0.31697 | 38.0362
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7518 | 20 | 0.31525 | 6.305
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7518 | 20 | 0.31525 | 6.305
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7518 | 20 | 0.31525 | 6.305
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.339 | 17 | 0.31525 | 5.3593
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.13753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 50.3367 | 366 | 0.31519 | 115.3612
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.13674 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.0913 | 242 | 0.3144 | 76.0856
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.13603 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 30.4703 | 224 | 0.31369 | 70.2667
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.13461 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.0768 | 60 | 0.31228 | 18.7365
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.13443 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 105.526 | 785 | 0.31209 | 244.991
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.13443 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 106.8703 | 795 | 0.31209 | 248.1119
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.13443 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 104.8538 | 780 | 0.31209 | 243.4305
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.1338 | west | 4 | Y | N | Ywest | Nwest | 1 | 86.9312 | 649.7 | 0.31146 | 202.3584
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.7966 | 0 | 0.31142 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.3889 | 0 | 0.31142 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.3953 | 0 | 0.31142 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | 1 | 53.3706 | 0 | 0.31142 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.13289 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.31055 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.13284 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.642 | 50 | 0.3105 | 15.5251
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13266 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.8884 | 165 | 0.31032 | 51.2027
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13207 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.0364 | 182 | 0.30973 | 56.3709
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13207 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 63.9209 | 484 | 0.30973 | 149.9095
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13112 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.9438 | 236 | 0.30878 | 72.8722
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13111 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.4436 | 400 | 0.30877 | 123.5086
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.12857 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7145 | 60 | 0.30624 | 18.3742
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12679 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0187 | 150 | 0.30445 | 45.668
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.482 | 209 | 0.30437 | 63.6134
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0286 | 126.5 | 0.30437 | 38.5029
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.5503 | 249 | 0.30437 | 75.7882
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.9615 | 197 | 0.30437 | 59.961
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.12646 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.1585 | 151.5 | 0.30412 | 46.0744
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.12646 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2597 | 152.3 | 0.30412 | 46.3177
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.12646 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4465 | 177.5 | 0.30412 | 53.9816
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.741 | 37.5 | 0.30409 | 11.4033
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.5908 | 107.5 | 0.30409 | 32.6895
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.0675 | 135 | 0.30409 | 41.0519
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0447 | 119 | 0.30409 | 36.1865
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2747 | 105 | 0.30409 | 31.9293
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.1773 | 80.5 | 0.30409 | 24.4791
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.12625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.0256 | 150.7 | 0.30391 | 45.7993
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.12625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.0634 | 151 | 0.30391 | 45.8905
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.12625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.3964 | 177.4 | 0.30391 | 53.9137
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12579 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7244 | 125 | 0.30346 | 37.9322
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12579 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7244 | 125 | 0.30346 | 37.9322
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12547 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.82 | 150 | 0.30313 | 45.4694
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12547 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6722 | 101 | 0.30313 | 30.6161
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.1254 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5333 | 84 | 0.30306 | 25.457
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12508 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3828 | 99 | 0.30274 | 29.9714
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12508 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6298 | 61 | 0.30274 | 18.4672
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12508 | west | 7 | N | N | Nwest | Nwest | 1 | 3.127 | 0 | 0.30274 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12508 | west | 7 | N | N | Nwest | Nwest | 1 | 5.7161 | 0 | 0.30274 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12508 | west | 7 | N | N | Nwest | Nwest | 1 | 5.7161 | 0 | 0.30274 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12504 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6312 | 141 | 0.30271 | 42.6816
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12504 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0053 | 120 | 0.30271 | 36.3248
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12494 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8712 | 63 | 0.3026 | 19.064
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2392 | 66 | 0.3025 | 19.965
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.6138 | 69 | 0.3025 | 20.8725
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.6138 | 69 | 0.3025 | 20.8725
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3641 | 67 | 0.3025 | 20.2675
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3641 | 67 | 0.3025 | 20.2675
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1144 | 65 | 0.3025 | 19.6625
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.6859 | 150 | 0.30224 | 45.3353
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.4061 | 220 | 0.30224 | 66.4918
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.9146 | 200 | 0.30224 | 60.4471
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1854 | 121.9 | 0.30224 | 36.8425
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.12455 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 76.6007 | 615 | 0.30222 | 185.8631
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.12455 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.1132 | 587 | 0.30222 | 177.401
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12422 | west | 8 | N | N | Nwest | Nwest | 1 | 8.6952 | 0 | 0.30188 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12422 | west | 8 | N | N | Nwest | Nwest | 1 | 9.1175 | 0 | 0.30188 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12422 | west | 8 | N | N | Nwest | Nwest | 1 | 8.7449 | 0 | 0.30188 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12421 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.358 | 180 | 0.30187 | 54.3372
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12421 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.358 | 180 | 0.30187 | 54.3372
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12409 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.9214 | 225 | 0.30176 | 67.8954
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12384 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8603 | 120 | 0.3015 | 36.1798
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12378 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8541 | 120 | 0.30145 | 36.1736
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8385 | 120 | 0.30132 | 36.158
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.8114 | 233 | 0.30132 | 70.2067
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0459 | 170.2 | 0.30132 | 51.2841
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.123 | west | 8 | N | N | Nwest | Nwest | 1 | 3.1735 | 0 | 0.30067 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.123 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.3472 | 214.2 | 0.30067 | 64.4025
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12272 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3338 | 100.5 | 0.30039 | 30.1888
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.1227 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1169 | 58 | 0.30037 | 17.4213
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.5857 | 70 | 0.30032 | 21.0221
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.5857 | 70 | 0.30032 | 21.0221
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.3822 | 92.8 | 0.30032 | 27.8693
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.8122 | 80 | 0.30032 | 24.0252
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.8122 | 80 | 0.30032 | 24.0252
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.1051 | 115 | 0.30032 | 34.5363
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.532 | 208.2 | 0.30029 | 62.5213
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.426 | 142.1 | 0.30029 | 42.6718
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.2365 | 132.4 | 0.30029 | 39.759
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.678 | 136 | 0.30029 | 40.84
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.0269 | 147 | 0.30029 | 44.1433
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.7527 | 210 | 0.30029 | 63.0618
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.1223 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.3444 | 150 | 0.29996 | 44.9938
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6971 | 112.5 | 0.29941 | 33.6841
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.2019 | 149.5 | 0.29941 | 44.7625
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6459 | 186 | 0.29941 | 55.6911
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.1158 | 214.5 | 0.29941 | 64.2244
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12118 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.79975 | 6.6 | 0.29884 | 1.9723
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12118 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1563 | 34.3 | 0.29884 | 10.2501
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.12093 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.0186 | 149 | 0.29859 | 44.4903
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12056 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2195 | 35 | 0.29822 | 10.4377
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12056 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6167 | 30 | 0.29822 | 8.9466
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.9496 | 66 | 0.29811 | 19.6753
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8291 | 65 | 0.29811 | 19.3772
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.07 | 67 | 0.29811 | 19.9734
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.07 | 67 | 0.29811 | 19.9734
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.07 | 67 | 0.29811 | 19.9734
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12045 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29811 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12045 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29811 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.11984 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.3125 | 169.5 | 0.2975 | 50.4263
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11244 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.53969 | 0 | 0.2901 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10912 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7292 | 80 | 0.28678 | 22.9422
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10912 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7292 | 80 | 0.28678 | 22.9422
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.10823 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1169 | 75 | 0.28589 | 21.4416
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10823 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6581 | 80 | 0.28589 | 22.8711
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.10823 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.329 | 40 | 0.28589 | 11.4355
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10803 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6426 | 80 | 0.2857 | 22.8556
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.10801 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6406 | 80 | 0.28567 | 22.8536
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.10789 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1841 | 150 | 0.28556 | 42.8335
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.10789 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1841 | 150 | 0.28556 | 42.8335
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10344 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2755 | 80 | 0.28111 | 22.4885
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10267 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.854 | 76.5 | 0.28033 | 21.4452
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10194 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5631 | 84 | 0.2796 | 23.4868
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.10149 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.9297 | 827 | 0.27915 | 230.8566
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.10149 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.1179 | 819 | 0.27915 | 228.6234
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.2367 | 855 | 0.26332 | 225.1381
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.2367 | 855 | 0.26332 | 225.1381
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.0456 | 152.3 | 0.26332 | 40.1035
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1055 | 153 | 0.26332 | 40.2879
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.078013 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.25568 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.055862 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3793 | 150 | 0.23352 | 35.0287
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.048744 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.5685 | 463 | 0.22641 | 104.8262
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21757 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21757 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.039912 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.6785 | 17 | 0.21757 | 3.6988
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21757 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21757 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.039834 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.2747 | 0 | 0.2175 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.8904 | 0 | 0.21586 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.9592 | 0 | 0.21586 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.9592 | 0 | 0.21586 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.516 | 0 | 0.21586 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.035852 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7209 | 48 | 0.21351 | 10.2487
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.035852 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6492 | 46 | 0.21351 | 9.8217
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.035852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.7645 | 105 | 0.21351 | 22.419
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17766 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17766 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.094367 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.083295 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -18.0805 | 100 | -0.0031426 | -0.31426
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13539 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13539 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.1119 | 0 | -0.15338 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8061 | 0 | -0.15338 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7702 | 0 | -0.15338 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7702 | 0 | -0.15338 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.017988 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9141 | 0 | -0.15338 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3424 | 56 | -0.15936 | -8.9242
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4143 | 59 | -0.15936 | -9.4023
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3424 | 56 | -0.15936 | -8.9242
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3424 | 56 | -0.15936 | -8.9242
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4143 | 59 | -0.15936 | -9.4023
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3424 | 56 | -0.15936 | -8.9242
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.024589 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.7864 | 398 | -0.15998 | -63.6716
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0604 | 0 | -0.16033 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0255 | 0 | -0.16033 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9631 | 0 | -0.16033 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.7141 | 0 | -0.16033 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.025956 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.4644 | 172 | -0.16135 | -27.7515
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.025956 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.4644 | 172 | -0.16135 | -27.7515
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.025956 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.4644 | 172 | -0.16135 | -27.7515
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.026127 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1019 | 0 | -0.16152 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.026389 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -19.607 | 743 | -0.16178 | -120.2018
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.026429 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.31715 | 12 | -0.16182 | -1.9418
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7196 | 0 | -0.16185 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7461 | 0 | -0.16185 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8519 | 0 | -0.16185 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6667 | 0 | -0.16185 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6403 | 0 | -0.16185 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7514 | 0 | -0.16185 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5609 | 0 | -0.16185 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.026465 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13232 | 0 | -0.16185 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.026465 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55576 | 0 | -0.16185 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.027031 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.32437 | 12 | -0.16242 | -1.9491
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93418 | 0 | -0.16287 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.95342 | 0 | -0.16287 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89847 | 0 | -0.16287 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2611 | 0 | -0.16287 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48633 | 0 | -0.16287 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56051 | 0 | -0.16287 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54677 | 0 | -0.16287 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.96166 | 0 | -0.16287 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49457 | 0 | -0.16287 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3465 | 0 | -0.16287 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0664 | 0 | -0.16287 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.027825 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -20.4514 | 735 | -0.16321 | -119.963
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.9483 | 104 | -0.16374 | -17.0289
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.9483 | 104 | -0.16374 | -17.0289
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5308 | 54 | -0.16374 | -8.8419
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5025 | 53 | -0.16374 | -8.6782
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5308 | 54 | -0.16374 | -8.8419
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.6159 | 57 | -0.16374 | -9.3331
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5308 | 54 | -0.16374 | -8.8419
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5308 | 54 | -0.16374 | -8.8419
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.6442 | 58 | -0.16374 | -9.4969
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.6442 | 58 | -0.16374 | -9.4969
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.029711 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.14 | 0 | -0.1651 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.029711 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.011 | 0 | -0.1651 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.257 | 42 | -0.16532 | -6.9434
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.257 | 42 | -0.16532 | -6.9434
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1373 | 38 | -0.16532 | -6.2821
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1373 | 38 | -0.16532 | -6.2821
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.029996 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0795 | 0 | -0.16539 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1899 | 0 | -0.16623 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2208 | 0 | -0.16623 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2029 | 0 | -0.16623 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92532 | 0 | -0.16623 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.031379 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.6482 | 0 | -0.16677 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.031379 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9767 | 0 | -0.16677 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.031379 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9265 | 0 | -0.16677 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.031392 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.1574 | 228 | -0.16678 | -38.0263
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0099 | 0 | -0.16679 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9848 | 0 | -0.16679 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5941 | 0 | -0.16679 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3114 | 0 | -0.16679 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.031412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50887 | 0 | -0.1668 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.031422 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.6929 | 213 | -0.16681 | -35.5309
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.0315 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6935 | 0 | -0.16689 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.0315 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0507 | 0 | -0.16689 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.031523 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.2013 | 165 | -0.16691 | -27.5406
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.031553 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.3325 | 169 | -0.16694 | -28.2134
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.031574 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.37889 | 12 | -0.16696 | -2.0036
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.031574 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16696 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.031953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1184 | 0 | -0.16734 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.2723 | 0 | -0.1677 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.0753 | 0 | -0.1677 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.0882 | 0 | -0.1677 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.072 | 0 | -0.1677 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.6903 | 0 | -0.1677 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.032742 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5539 | 0 | -0.16813 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.032742 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6194 | 0 | -0.16813 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5206 | 46 | -0.16845 | -7.7486
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5206 | 46 | -0.16845 | -7.7486
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5206 | 46 | -0.16845 | -7.7486
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8181 | 55 | -0.16845 | -9.2646
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8181 | 55 | -0.16845 | -9.2646
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7851 | 54 | -0.16845 | -9.0961
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2308 | 0 | -0.16971 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0592 | 0 | -0.16971 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2308 | 0 | -0.16971 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2308 | 0 | -0.16971 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2005 | 0 | -0.17056 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0809 | 0 | -0.17056 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0598 | 0 | -0.17056 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9168 | 0 | -0.17056 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42907 | 0 | -0.17056 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.037337 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17273 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.039195 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9598 | 50 | -0.17458 | -8.7292
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9437 | 0 | -0.17697 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7732 | 0 | -0.17697 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2036 | 0 | -0.17697 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3696 | 0 | -0.17697 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3821 | 0 | -0.17697 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3322 | 0 | -0.17697 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.9914 | 0 | -0.17697 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1448 | 0 | -0.17697 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6631 | 0 | -0.17697 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.041606 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3314 | 0 | -0.177 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.041606 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2482 | 0 | -0.177 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1732 | 0 | -0.177 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8653 | 0 | -0.177 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.273 | 0 | -0.177 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2439 | 0 | -0.177 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.047419 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.6345 | 161 | -0.18281 | -29.4322
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.047419 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.8716 | 166 | -0.18281 | -30.3463
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.047419 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.7599 | 248 | -0.18281 | -45.3366
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.047419 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -25.8908 | 546 | -0.18281 | -99.8137
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.047419 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -30.4904 | 0 | -0.18281 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.047419 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.61645 | 13 | -0.18281 | -2.3765
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.047916 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5812 | 0 | -0.18331 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.049073 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9989 | 0 | -0.18446 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.049073 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9989 | 0 | -0.18446 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.049073 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.0229 | 0 | -0.18446 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.049166 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -32.0071 | 651 | -0.18456 | -120.1459
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.049166 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -27.7296 | 564 | -0.18456 | -104.0896
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.049166 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -29.4996 | 600 | -0.18456 | -110.7336
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.049565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2849 | 0 | -0.18495 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7275 | 0 | -0.196 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7275 | 0 | -0.196 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2124 | 0 | -0.196 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.6366 | 0 | -0.196 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.063658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5197 | 0 | -0.19905 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.063658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63658 | 0 | -0.19905 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1861 | 0 | -0.20291 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8208 | 0 | -0.20291 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0383 | 0 | -0.20291 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8193 | 0 | -0.20291 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8065 | 0 | -0.20291 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9416 | 0 | -0.20291 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3759 | 0 | -0.20291 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2153 | 0 | -0.20291 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3467 | 0 | -0.20291 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7263 | 0 | -0.20291 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2536 | 0 | -0.20291 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8613 | 0 | -0.20291 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3752 | 0 | -0.20291 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8193 | 0 | -0.20291 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5492 | 0 | -0.20291 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.9544 | 0 | -0.20291 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.1314 | 0 | -0.20291 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4014 | 0 | -0.20291 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4014 | 0 | -0.20291 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5456 | 0 | -0.20291 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.081574 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.6919 | 0 | -0.21696 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.081574 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0394 | 0 | -0.21696 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.081574 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21696 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.083454 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.508 | 66 | -0.21884 | -14.4437
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.7268 | 76 | -0.2239 | -17.0165
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.7268 | 76 | -0.2239 | -17.0165
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2937 | 105 | -0.2239 | -23.5096
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.5498 | 74 | -0.2239 | -16.5687
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.5498 | 74 | -0.2239 | -16.5687
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.0281 | 102 | -0.2239 | -22.8379
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.089094 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -118.7623 | 0 | -0.22448 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.089094 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -118.3168 | 0 | -0.22448 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.10366 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62197 | 0 | -0.23905 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.1088 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24419 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.3409 | 0 | -0.26629 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.6027 | 0 | -0.26629 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.3409 | 0 | -0.26629 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.4718 | 0 | -0.26629 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.2624 | 0 | -0.26629 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2725 | 0 | -0.26629 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0213 | 0 | -0.26629 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6651 | 0 | -0.26629 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7072 | 0 | -0.26629 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6865 | 0 | -0.26629 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.13205 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.3386 | 0 | -0.26744 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8025 | 0 | -0.27119 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.95064 | 0 | -0.27119 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2964 | 0 | -0.27119 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0371 | 0 | -0.27119 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.95064 | 0 | -0.27119 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0371 | 0 | -0.27119 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2964 | 0 | -0.27119 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2964 | 0 | -0.27119 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.13636 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0909 | 0 | -0.27175 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.13738 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0607 | 0 | -0.27277 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.13738 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.1598 | 0 | -0.27277 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.13857 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.0486 | 22 | -0.27396 | -6.0271
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.13857 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5243 | 11 | -0.27396 | -3.0136
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.13857 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5243 | 11 | -0.27396 | -3.0136
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6709 | 47.7 | -0.27524 | -13.129
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.2165 | 37.3 | -0.27524 | -10.2665
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4332 | 46 | -0.27524 | -12.6611
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7129 | 48 | -0.27524 | -13.2116
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.14016 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.2315 | 0 | -0.27555 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.2508 | 0 | -0.27622 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.5467 | 0 | -0.27622 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -14.0828 | 0 | -0.27622 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.4201 | 0 | -0.27622 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.7017 | 0 | -0.27622 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -17.8852 | 0 | -0.27622 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.14083 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6899 | 0 | -0.27622 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 25 | -0.2768 | -6.92
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 25 | -0.2768 | -6.92
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 25 | -0.2768 | -6.92
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2626 | 16 | -0.2768 | -4.4288
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 25 | -0.2768 | -6.92
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 25 | -0.2768 | -6.92
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 25 | -0.2768 | -6.92
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.1212 | 15 | -0.2768 | -4.152
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.14174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.4108 | 144 | -0.27713 | -39.907
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.14174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6475 | 188 | -0.27713 | -52.1008
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.1423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -47.8141 | 336 | -0.27769 | -93.3052
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.1423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.6147 | 180 | -0.27769 | -49.9849
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.14232 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.1062 | 0 | -0.27771 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.14232 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.1489 | 0 | -0.27771 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.14232 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.7751 | 0 | -0.27771 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.14235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.6228 | 180 | -0.27774 | -49.993
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.14263 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.6391 | 334 | -0.27802 | -92.8593
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.14263 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -48.4949 | 340 | -0.27802 | -94.5275
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.14263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.6738 | 180 | -0.27802 | -50.044
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.14263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.6738 | 180 | -0.27802 | -50.044
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.14268 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5671 | 0 | -0.27807 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.14268 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5671 | 0 | -0.27807 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.14283 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4274 | 0 | -0.27822 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.14283 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4277 | 0 | -0.27822 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.14352 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.162 | 0 | -0.27891 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.5119 | 94 | -0.27913 | -26.2386
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8935 | 41 | -0.27913 | -11.4445
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4623 | 38 | -0.27913 | -10.6071
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7311 | 19 | -0.27913 | -5.3035
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.5119 | 94 | -0.27913 | -26.2386
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.1748 | 36 | -0.27913 | -10.0488
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.181 | 43 | -0.27913 | -12.0028
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1624 | 22 | -0.27913 | -6.1409
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.2741 | 148 | -0.27913 | -41.3118
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1872 | 50 | -0.27913 | -13.9567
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.9059 | 55 | -0.27913 | -15.3524
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1872 | 50 | -0.27913 | -13.9567
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.14384 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.4659 | 38 | -0.27923 | -10.6107
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.14384 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7761 | 19.3 | -0.27923 | -5.3891
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.14384 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.1576 | 15 | -0.27923 | -4.1884
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.14384 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.7605 | 47 | -0.27923 | -13.1238
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.14384 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.27923 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.14411 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.7521 | 144 | -0.2795 | -40.2483
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.14411 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.7521 | 144 | -0.2795 | -40.2483
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.14411 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6432 | 171 | -0.2795 | -47.7948
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.14412 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.8322 | 207 | -0.27951 | -57.8579
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.14412 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.2302 | 216.7 | -0.27951 | -60.5692
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.14412 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.8763 | 242 | -0.27951 | -67.6407
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.14439 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.1536 | 146.5 | -0.27978 | -40.9882
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.14439 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.3557 | 147.9 | -0.27978 | -41.3799
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.14439 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.98 | 173 | -0.27978 | -48.4024
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.14612 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7534 | 0 | -0.28151 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.14612 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6073 | 0 | -0.28151 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.14612 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7534 | 0 | -0.28151 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.14618 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28157 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.14777 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28316 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.1485 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -93.4078 | 629 | -0.28389 | -178.568
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.15046 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28585 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.15155 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28694 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.15157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.1566 | 100 | -0.28696 | -28.6956
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.15157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.1566 | 100 | -0.28696 | -28.6956
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.15157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28696 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.15157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28696 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.15157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28696 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.15157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28696 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15257 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.6618 | 24 | -0.28796 | -6.9111
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15257 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.6618 | 24 | -0.28796 | -6.9111
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.15257 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.5092 | 23 | -0.28796 | -6.6231
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.16198 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -64.1453 | 396 | -0.29737 | -117.7597
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.17093 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0511 | 0 | -0.30632 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.17129 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -93.5265 | 546 | -0.30668 | -167.4494
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.17129 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -128.4705 | 750 | -0.30668 | -230.013
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.17152 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.9483 | 58 | -0.30691 | -17.8009
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.17152 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.2655 | 89 | -0.30691 | -27.3152
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.547 | 44 | -0.30691 | -13.5041
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.547 | 44 | -0.30691 | -13.5041
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3754 | 43 | -0.30691 | -13.1972
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7185 | 45 | -0.30691 | -13.811
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6853 | 155 | -0.30755 | -47.6707
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.17216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.2677 | 170 | -0.30755 | -52.284
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6853 | 155 | -0.30755 | -47.6707
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.17249 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -70.2038 | 407 | -0.30788 | -125.3075
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.17257 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.0673 | 209 | -0.30796 | -64.3638
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.17257 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -37.2753 | 216 | -0.30796 | -66.5196
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9383 | 46 | -0.30796 | -14.1662
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.1108 | 47 | -0.30796 | -14.4742
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9383 | 46 | -0.30796 | -14.1662
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9383 | 46 | -0.30796 | -14.1662
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.17277 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -71.1796 | 412 | -0.30816 | -126.9603
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.17277 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -69.1064 | 400 | -0.30816 | -123.2624
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.17289 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -73.3066 | 424 | -0.30828 | -130.712
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.17289 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -73.4795 | 425 | -0.30828 | -131.0203
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.17339 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.30878 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.17339 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.30878 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.17339 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.30878 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0572 | 147 | -0.31265 | -45.9595
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.4619 | 138 | -0.31265 | -43.1457
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.8164 | 140 | -0.31265 | -43.771
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0572 | 147 | -0.31265 | -45.9595
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.2613 | 182 | -0.31265 | -56.9023
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.0975 | 198 | -0.31265 | -61.9047
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.6118 | 114 | -0.31619 | -36.0462
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -40.1387 | 222 | -0.31619 | -70.1953
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -33.2681 | 184 | -0.31619 | -58.1799
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -40.5003 | 224 | -0.31619 | -70.8277
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.7926 | 115 | -0.31619 | -36.3624
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.18184 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.72736 | 0 | -0.31723 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.18203 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43686 | 0 | -0.31742 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.18203 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43686 | 0 | -0.31742 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0946 | 142 | -0.31915 | -45.32
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6459 | 145 | -0.31915 | -46.2775
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.7485 | 151 | -0.31915 | -48.1924
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -53.2918 | 290 | -0.31915 | -92.5549
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.18452 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.44286 | 0 | -0.31991 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.18452 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.44286 | 0 | -0.31991 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.18452 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.51667 | 0 | -0.31991 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.18965 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.5983 | 0 | -0.32504 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.6787 | 223.9 | -0.326 | -72.9925
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.8884 | 225 | -0.326 | -73.3511
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.8121 | 224.6 | -0.326 | -73.2207
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -43.2124 | 226.7 | -0.326 | -73.9053
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.19245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.4641 | 0 | -0.32784 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.19245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.4641 | 0 | -0.32784 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.19245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8868 | 0 | -0.32784 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.19388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -81.8157 | 422 | -0.32927 | -138.9502
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.19482 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -84.3579 | 433 | -0.33021 | -142.9818
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.19502 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -113.8893 | 584 | -0.33041 | -192.9571
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.19502 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -116.0345 | 595 | -0.33041 | -196.5915
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.19535 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.4697 | 0 | -0.33074 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.19535 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.6651 | 0 | -0.33074 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.19543 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1726 | 0 | -0.33082 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8621 | 50 | -0.33263 | -16.6316
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8621 | 50 | -0.33263 | -16.6316
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8621 | 50 | -0.33263 | -16.6316
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8621 | 50 | -0.33263 | -16.6316
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.20133 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.624 | 0 | -0.33672 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.20133 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.624 | 0 | -0.33672 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.21693 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -28.6344 | 132 | -0.35232 | -46.5058
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.21693 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -29.0682 | 134 | -0.35232 | -47.2105
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.21693 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -70.0674 | 323 | -0.35232 | -113.7984
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.21825 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.6387 | 0 | -0.35364 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.21825 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.4205 | 0 | -0.35364 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.21825 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.6387 | 0 | -0.35364 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.21903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.6064 | 158 | -0.35442 | -55.998
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.21903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.0445 | 160 | -0.35442 | -56.7069
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.21903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -38.3299 | 175 | -0.35442 | -62.0231
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.22062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.6441 | 152.5 | -0.35601 | -54.2911
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.22062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.9822 | 149.5 | -0.35601 | -53.223
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.22062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -51.3155 | 232.6 | -0.35601 | -82.8072
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.9834 | 49 | -0.35954 | -17.6176
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.311 | 46 | -0.35954 | -16.5389
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.311 | 46 | -0.35954 | -16.5389
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5351 | 47 | -0.35954 | -16.8985
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.22415 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.5194 | 154 | -0.35954 | -55.3695
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.22415 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.1745 | 148 | -0.35954 | -53.2122
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7593 | 48 | -0.35954 | -17.258
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7593 | 48 | -0.35954 | -17.258
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.22581 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8064 | 0 | -0.36119 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.22581 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8064 | 0 | -0.36119 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.22672 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -70.282 | 310 | -0.36211 | -112.2528
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.22672 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -93.6337 | 413 | -0.36211 | -149.5498
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.6231 | 42 | -0.36451 | -15.3095
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.0813 | 44 | -0.36451 | -16.0385
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.0813 | 44 | -0.36451 | -16.0385
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7687 | 47 | -0.36451 | -17.132
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.26963 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -153.4172 | 569 | -0.40502 | -230.4541
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.26963 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -156.6527 | 581 | -0.40502 | -235.3143

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.26963 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -153.4172 | 0 | -0.40502 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.26963 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -156.6527 | 0 | -0.40502 | 0 | 0 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.6231 | 42 | -0.36451 | -15.3095 | 42 | 15.3095
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.0813 | 44 | -0.36451 | -16.0385 | 86 | 31.3479 | Weighted Shift Factors
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.0813 | 44 | -0.36451 | -16.0385 | 130 | 47.3864 | North | 0.13539
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.22912 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7687 | 47 | -0.36451 | -17.132 | 177 | 64.5184 | South | -0.17766
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.22672 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -70.282 | 310 | -0.36211 | -112.2528 | 487 | 176.7713 |  | 0.31305
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.22672 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -93.6337 | 413 | -0.36211 | -149.5498 | 900 | 326.321
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.22581 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8064 | 0 | -0.36119 | 0 | 900 | 326.321 | Line Rating | 1239.6
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.22581 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8064 | 0 | -0.36119 | 0 | 900 | 326.321 | Conc Gen | 2338.6
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.9834 | 49 | -0.35954 | -17.6176 | 949 | 343.9386 | Weighted Imp. | 840.0388
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.311 | 46 | -0.35954 | -16.5389 | 995 | 360.4775 | PTDF | 0.35921
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.311 | 46 | -0.35954 | -16.5389 | 1041 | 377.0165
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5351 | 47 | -0.35954 | -16.8985 | 1088 | 393.9149 | Concentration | 1.1474
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.22415 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.5194 | 154 | -0.35954 | -55.3695 | 1242 | 449.2844
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.22415 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.1745 | 148 | -0.35954 | -53.2122 | 1390 | 502.4966
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7593 | 48 | -0.35954 | -17.258 | 1438 | 519.7546
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.22415 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7593 | 48 | -0.35954 | -17.258 | 1486 | 537.0126
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.22062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.6441 | 152.5 | -0.35601 | -54.2911 | 1638.5 | 591.3037
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.22062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.9822 | 149.5 | -0.35601 | -53.223 | 1788 | 644.5267
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.22062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -51.3155 | 232.6 | -0.35601 | -82.8072 | 2020.6 | 727.3339
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.21903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.6064 | 158 | -0.35442 | -55.998 | 2178.6 | 783.332
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.21903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.0445 | 160 | -0.35442 | -56.7069 | 2338.6 | 840.0388
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.21903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -38.3299 | 175 | -0.35442 | -62.0231
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.21825 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.6387 | 0 | -0.35364 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.21825 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.4205 | 0 | -0.35364 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.21825 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.6387 | 0 | -0.35364 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.21693 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -28.6344 | 132 | -0.35232 | -46.5058
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.21693 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -29.0682 | 134 | -0.35232 | -47.2105
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.21693 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -70.0674 | 323 | -0.35232 | -113.7984
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.20133 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.624 | 0 | -0.33672 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.20133 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.624 | 0 | -0.33672 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8621 | 50 | -0.33263 | -16.6316
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8621 | 50 | -0.33263 | -16.6316
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8621 | 50 | -0.33263 | -16.6316
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.19724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8621 | 50 | -0.33263 | -16.6316
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.19543 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1726 | 0 | -0.33082 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.19535 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.4697 | 0 | -0.33074 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.19535 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.6651 | 0 | -0.33074 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.19502 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -113.8893 | 0 | -0.33041 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.19502 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -116.0345 | 0 | -0.33041 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.19482 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -84.3579 | 0 | -0.33021 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.19388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -81.8157 | 422 | -0.32927 | -138.9502
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.19245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.4641 | 0 | -0.32784 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.19245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.4641 | 0 | -0.32784 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.19245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8868 | 0 | -0.32784 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.6787 | 223.9 | -0.326 | -72.9925
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.8884 | 225 | -0.326 | -73.3511
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.8121 | 224.6 | -0.326 | -73.2207
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.19062 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -43.2124 | 226.7 | -0.326 | -73.9053
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.18965 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.5983 | 0 | -0.32504 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.18452 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.44286 | 0 | -0.31991 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.18452 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.44286 | 0 | -0.31991 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.18452 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.51667 | 0 | -0.31991 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0946 | 142 | -0.31915 | -45.32
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6459 | 145 | -0.31915 | -46.2775
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.7485 | 151 | -0.31915 | -48.1924
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.18377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -53.2918 | 290 | -0.31915 | -92.5549
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.18203 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43686 | 0 | -0.31742 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.18203 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43686 | 0 | -0.31742 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.18184 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.72736 | 0 | -0.31723 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.6118 | 0 | -0.31619 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -40.1387 | 0 | -0.31619 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -33.2681 | 0 | -0.31619 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -40.5003 | 0 | -0.31619 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.7926 | 0 | -0.31619 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0572 | 147 | -0.31265 | -45.9595
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.4619 | 138 | -0.31265 | -43.1457
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.8164 | 140 | -0.31265 | -43.771
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0572 | 147 | -0.31265 | -45.9595
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.2613 | 182 | -0.31265 | -56.9023
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.17726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.0975 | 198 | -0.31265 | -61.9047
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.17339 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.30878 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.17339 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.30878 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.17339 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.30878 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.17289 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -73.3066 | 0 | -0.30828 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.17289 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -73.4795 | 0 | -0.30828 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.17277 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -71.1796 | 412 | -0.30816 | -126.9603
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.17277 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -69.1064 | 400 | -0.30816 | -123.2624
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.17257 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.0673 | 209 | -0.30796 | -64.3638
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.17257 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -37.2753 | 216 | -0.30796 | -66.5196
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9383 | 46 | -0.30796 | -14.1662
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.1108 | 47 | -0.30796 | -14.4742
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9383 | 46 | -0.30796 | -14.1662
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.17257 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9383 | 46 | -0.30796 | -14.1662
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.17249 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -70.2038 | 407 | -0.30788 | -125.3075
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6853 | 155 | -0.30755 | -47.6707
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.17216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.2677 | 170 | -0.30755 | -52.284
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6853 | 155 | -0.30755 | -47.6707
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.17152 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.9483 | 58 | -0.30691 | -17.8009
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.17152 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.2655 | 89 | -0.30691 | -27.3152
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.547 | 44 | -0.30691 | -13.5041
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.547 | 44 | -0.30691 | -13.5041
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3754 | 43 | -0.30691 | -13.1972
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.17152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7185 | 45 | -0.30691 | -13.811
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.17129 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -93.5265 | 0 | -0.30668 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.17129 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -128.4705 | 0 | -0.30668 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.17093 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0511 | 0 | -0.30632 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.16198 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -64.1453 | 0 | -0.29737 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15257 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.6618 | 24 | -0.28796 | -6.9111
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15257 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.6618 | 24 | -0.28796 | -6.9111
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.15257 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.5092 | 23 | -0.28796 | -6.6231
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.15157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.1566 | 100 | -0.28696 | -28.6956
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.15157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.1566 | 100 | -0.28696 | -28.6956
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.15157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28696 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.15157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28696 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.15157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28696 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.15157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28696 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.15155 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28694 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.1508 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2667 | 8.4 | -0.28619 | -2.404
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.15046 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28585 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.1485 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -93.4078 | 0 | -0.28389 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.14777 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28316 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.14618 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28157 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.14612 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7534 | 0 | -0.28151 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.14612 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6073 | 0 | -0.28151 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.14612 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7534 | 0 | -0.28151 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.14439 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.1536 | 146.5 | -0.27978 | -40.9882
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.14439 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.3557 | 147.9 | -0.27978 | -41.3799
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.14439 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.98 | 173 | -0.27978 | -48.4024
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.14412 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.8322 | 207 | -0.27951 | -57.8579
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.14412 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.2302 | 216.7 | -0.27951 | -60.5692
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.14412 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.8763 | 242 | -0.27951 | -67.6407
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.14411 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.7521 | 144 | -0.2795 | -40.2483
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.14411 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.7521 | 144 | -0.2795 | -40.2483
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.14411 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6432 | 171 | -0.2795 | -47.7948
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.14384 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.27923 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.14384 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.4659 | 38 | -0.27923 | -10.6107
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.14384 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7761 | 19.3 | -0.27923 | -5.3891
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.14384 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.1576 | 15 | -0.27923 | -4.1884
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.14384 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.7605 | 47 | -0.27923 | -13.1238
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.5119 | 0 | -0.27913 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8935 | 0 | -0.27913 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4623 | 0 | -0.27913 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7311 | 0 | -0.27913 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.5119 | 0 | -0.27913 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.1748 | 0 | -0.27913 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.181 | 0 | -0.27913 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1624 | 0 | -0.27913 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.2741 | 0 | -0.27913 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1872 | 0 | -0.27913 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.9059 | 0 | -0.27913 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.14374 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1872 | 0 | -0.27913 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.14352 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.162 | 0 | -0.27891 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.14283 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4277 | 0 | -0.27822 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.14283 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4274 | 0 | -0.27822 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.14268 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5671 | 0 | -0.27807 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.14268 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5671 | 0 | -0.27807 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.14263 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.6391 | 334 | -0.27802 | -92.8593
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.14263 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -48.4949 | 340 | -0.27802 | -94.5275
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.14263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.6738 | 180 | -0.27802 | -50.044
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.14263 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.6738 | 180 | -0.27802 | -50.044
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.14235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.6228 | 180 | -0.27774 | -49.993
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.14232 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.1062 | 0 | -0.27771 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.14232 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.1489 | 0 | -0.27771 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.14232 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.7751 | 0 | -0.27771 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.1423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -47.8141 | 336 | -0.27769 | -93.3052
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.1423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.6147 | 180 | -0.27769 | -49.9849
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.14174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.4108 | 144 | -0.27713 | -39.907
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.14174 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6475 | 188 | -0.27713 | -52.1008
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 0 | -0.2768 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 0 | -0.2768 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 0 | -0.2768 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2626 | 0 | -0.2768 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 0 | -0.2768 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 0 | -0.2768 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5353 | 0 | -0.2768 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.14141 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.1212 | 0 | -0.2768 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.2508 | 0 | -0.27622 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.5467 | 0 | -0.27622 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -14.0828 | 0 | -0.27622 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.4201 | 0 | -0.27622 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.7017 | 0 | -0.27622 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.14083 | south | 8 | N | N | Nsouth | Nsouth | -1 | -17.8852 | 0 | -0.27622 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.14083 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6899 | 0 | -0.27622 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.14016 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.2315 | 0 | -0.27555 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6709 | 47.7 | -0.27524 | -13.129
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.2165 | 37.3 | -0.27524 | -10.2665
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4332 | 46 | -0.27524 | -12.6611
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.13985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7129 | 48 | -0.27524 | -13.2116
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.13857 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.0486 | 22 | -0.27396 | -6.0271
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.13857 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5243 | 11 | -0.27396 | -3.0136
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.13857 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5243 | 11 | -0.27396 | -3.0136
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.13738 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0607 | 0 | -0.27277 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.13738 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.1598 | 0 | -0.27277 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.13636 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0909 | 0 | -0.27175 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8025 | 0 | -0.27119 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.95064 | 0 | -0.27119 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2964 | 0 | -0.27119 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0371 | 0 | -0.27119 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.95064 | 0 | -0.27119 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0371 | 0 | -0.27119 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2964 | 0 | -0.27119 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.13581 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2964 | 0 | -0.27119 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.13205 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.3386 | 0 | -0.26744 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.3409 | 0 | -0.26629 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.6027 | 0 | -0.26629 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.3409 | 0 | -0.26629 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.4718 | 0 | -0.26629 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.2624 | 0 | -0.26629 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2725 | 0 | -0.26629 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0213 | 0 | -0.26629 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6651 | 0 | -0.26629 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7072 | 0 | -0.26629 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.1309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6865 | 0 | -0.26629 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.1088 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24419 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.10366 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62197 | 0 | -0.23905 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.089094 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -118.7623 | 0 | -0.22448 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.089094 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -118.3168 | 0 | -0.22448 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.7268 | 76 | -0.2239 | -17.0165
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.7268 | 76 | -0.2239 | -17.0165
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2937 | 105 | -0.2239 | -23.5096
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.5498 | 74 | -0.2239 | -16.5687
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.5498 | 74 | -0.2239 | -16.5687
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.088511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.0281 | 102 | -0.2239 | -22.8379
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.083454 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.508 | 66 | -0.21884 | -14.4437
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.081574 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.6919 | 0 | -0.21696 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.081574 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0394 | 0 | -0.21696 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.081574 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21696 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1861 | 0 | -0.20291 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8208 | 0 | -0.20291 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0383 | 0 | -0.20291 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8193 | 0 | -0.20291 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8065 | 0 | -0.20291 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9416 | 0 | -0.20291 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3759 | 0 | -0.20291 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2153 | 0 | -0.20291 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3467 | 0 | -0.20291 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7263 | 0 | -0.20291 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2536 | 0 | -0.20291 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8613 | 0 | -0.20291 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3752 | 0 | -0.20291 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8193 | 0 | -0.20291 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5492 | 0 | -0.20291 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.9544 | 0 | -0.20291 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.1314 | 0 | -0.20291 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4014 | 0 | -0.20291 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4014 | 0 | -0.20291 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.067518 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5456 | 0 | -0.20291 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.063658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5197 | 0 | -0.19905 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.063658 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63658 | 0 | -0.19905 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7275 | 0 | -0.196 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7275 | 0 | -0.196 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2124 | 0 | -0.196 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.060608 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.6366 | 0 | -0.196 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.049565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2849 | 0 | -0.18495 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.049166 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -32.0071 | 0 | -0.18456 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.049166 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -27.7296 | 0 | -0.18456 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.049166 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -29.4996 | 0 | -0.18456 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.049073 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9989 | 0 | -0.18446 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.049073 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.9989 | 0 | -0.18446 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.049073 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.0229 | 0 | -0.18446 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.047916 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5812 | 0 | -0.18331 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.047419 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.6345 | 161 | -0.18281 | -29.4322
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.047419 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.8716 | 166 | -0.18281 | -30.3463
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.047419 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.7599 | 248 | -0.18281 | -45.3366
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.047419 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -25.8908 | 546 | -0.18281 | -99.8137
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.047419 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -30.4904 | 0 | -0.18281 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.047419 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.61645 | 13 | -0.18281 | -2.3765
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1732 | 0 | -0.177 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8653 | 0 | -0.177 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.273 | 0 | -0.177 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.041607 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2439 | 0 | -0.177 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.041606 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3314 | 0 | -0.177 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.041606 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2482 | 0 | -0.177 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9437 | 0 | -0.17697 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7732 | 0 | -0.17697 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2036 | 0 | -0.17697 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3696 | 0 | -0.17697 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3821 | 0 | -0.17697 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3322 | 0 | -0.17697 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.9914 | 0 | -0.17697 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.041577 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1448 | 0 | -0.17697 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.041577 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6631 | 0 | -0.17697 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.039195 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9598 | 50 | -0.17458 | -8.7292
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.037337 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17273 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2005 | 0 | -0.17056 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0809 | 0 | -0.17056 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0598 | 0 | -0.17056 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9168 | 0 | -0.17056 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.03517 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42907 | 0 | -0.17056 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2308 | 0 | -0.16971 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0592 | 0 | -0.16971 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2308 | 0 | -0.16971 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03432 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2308 | 0 | -0.16971 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5206 | 46 | -0.16845 | -7.7486
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5206 | 46 | -0.16845 | -7.7486
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5206 | 46 | -0.16845 | -7.7486
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8181 | 55 | -0.16845 | -9.2646
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8181 | 55 | -0.16845 | -9.2646
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.033057 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7851 | 54 | -0.16845 | -9.0961
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.032742 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5539 | 0 | -0.16813 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.032742 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6194 | 0 | -0.16813 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.2723 | 0 | -0.1677 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.0753 | 0 | -0.1677 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.0882 | 0 | -0.1677 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.072 | 0 | -0.1677 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.032306 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.6903 | 0 | -0.1677 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.031953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1184 | 0 | -0.16734 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.031574 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.37889 | 12 | -0.16696 | -2.0036
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.031574 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16696 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.031553 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.3325 | 169 | -0.16694 | -28.2134
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.031523 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.2013 | 165 | -0.16691 | -27.5406
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.0315 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6935 | 0 | -0.16689 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.0315 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0507 | 0 | -0.16689 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.031422 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.6929 | 213 | -0.16681 | -35.5309
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.031412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50887 | 0 | -0.1668 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0099 | 0 | -0.16679 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9848 | 0 | -0.16679 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5941 | 0 | -0.16679 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.031405 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3114 | 0 | -0.16679 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.031392 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.1574 | 228 | -0.16678 | -38.0263
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.031379 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.6482 | 0 | -0.16677 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.031379 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9767 | 0 | -0.16677 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.031379 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9265 | 0 | -0.16677 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1899 | 0 | -0.16623 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2208 | 0 | -0.16623 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2029 | 0 | -0.16623 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92532 | 0 | -0.16623 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.029996 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0795 | 0 | -0.16539 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.257 | 42 | -0.16532 | -6.9434
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.257 | 42 | -0.16532 | -6.9434
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1373 | 38 | -0.16532 | -6.2821
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.029928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1373 | 38 | -0.16532 | -6.2821
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.029711 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.14 | 0 | -0.1651 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.029711 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.011 | 0 | -0.1651 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.9483 | 104 | -0.16374 | -17.0289
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.9483 | 104 | -0.16374 | -17.0289
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5308 | 54 | -0.16374 | -8.8419
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5025 | 53 | -0.16374 | -8.6782
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5308 | 54 | -0.16374 | -8.8419
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.6159 | 57 | -0.16374 | -9.3331
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5308 | 54 | -0.16374 | -8.8419
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5308 | 54 | -0.16374 | -8.8419
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.6442 | 58 | -0.16374 | -9.4969
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.028349 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.6442 | 58 | -0.16374 | -9.4969
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.027825 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -20.4514 | 735 | -0.16321 | -119.963
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93418 | 0 | -0.16287 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.95342 | 0 | -0.16287 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89847 | 0 | -0.16287 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2611 | 0 | -0.16287 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48633 | 0 | -0.16287 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56051 | 0 | -0.16287 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54677 | 0 | -0.16287 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.96166 | 0 | -0.16287 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49457 | 0 | -0.16287 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3465 | 0 | -0.16287 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.027476 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0664 | 0 | -0.16287 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.027031 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.32437 | 12 | -0.16242 | -1.9491
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.026465 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13232 | 0 | -0.16185 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.026465 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55576 | 0 | -0.16185 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7196 | 0 | -0.16185 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7461 | 0 | -0.16185 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8519 | 0 | -0.16185 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6667 | 0 | -0.16185 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6403 | 0 | -0.16185 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7514 | 0 | -0.16185 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.026456 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5609 | 0 | -0.16185 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.026429 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.31715 | 0 | -0.16182 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.026389 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -19.607 | 743 | -0.16178 | -120.2018
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.026127 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1019 | 0 | -0.16152 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.025956 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.4644 | 172 | -0.16135 | -27.7515
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.025956 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.4644 | 172 | -0.16135 | -27.7515
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.025956 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.4644 | 172 | -0.16135 | -27.7515
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0604 | 0 | -0.16033 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0255 | 0 | -0.16033 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9631 | 0 | -0.16033 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.024941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.7141 | 0 | -0.16033 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.024589 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.7864 | 398 | -0.15998 | -63.6716
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3424 | 56 | -0.15936 | -8.9242
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4143 | 59 | -0.15936 | -9.4023
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3424 | 56 | -0.15936 | -8.9242
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3424 | 56 | -0.15936 | -8.9242
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4143 | 59 | -0.15936 | -9.4023
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.023971 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3424 | 56 | -0.15936 | -8.9242
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.1119 | 0 | -0.15338 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8061 | 0 | -0.15338 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7702 | 0 | -0.15338 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.017988 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7702 | 0 | -0.15338 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.017988 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9141 | 0 | -0.15338 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13539 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13539 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13539 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.1808 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -18.0805 | 0 | -0.0031426 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.094367 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.083295 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17766 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17766 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.035852 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7209 | 48 | 0.21351 | 10.2487
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.035852 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6492 | 46 | 0.21351 | 9.8217
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.035852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.7645 | 105 | 0.21351 | 22.419
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.8904 | 0 | 0.21586 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.9592 | 0 | 0.21586 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.9592 | 0 | 0.21586 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.0382 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.516 | 0 | 0.21586 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.039834 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.2747 | 0 | 0.2175 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21757 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21757 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.039912 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.6785 | 17 | 0.21757 | 3.6988
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21757 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.039912 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21757 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.048744 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.5685 | 0 | 0.22641 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.055862 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3793 | 0 | 0.23352 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.078013 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.25568 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.2367 | 0 | 0.26332 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.2367 | 0 | 0.26332 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.0456 | 0 | 0.26332 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.085657 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1055 | 0 | 0.26332 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.10149 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.9297 | 0 | 0.27915 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.10149 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.1179 | 0 | 0.27915 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10194 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5631 | 0 | 0.2796 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10267 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.854 | 0 | 0.28033 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10344 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2755 | 0 | 0.28111 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.10789 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1841 | 0 | 0.28556 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.10789 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1841 | 0 | 0.28556 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.10801 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6406 | 0 | 0.28567 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10803 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6426 | 0 | 0.2857 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.10823 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1169 | 0 | 0.28589 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10823 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6581 | 0 | 0.28589 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.10823 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.329 | 0 | 0.28589 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10912 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7292 | 0 | 0.28678 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10912 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7292 | 0 | 0.28678 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11244 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.53969 | 0 | 0.2901 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.11984 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.3125 | 0 | 0.2975 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.9496 | 66 | 0.29811 | 19.6753
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8291 | 65 | 0.29811 | 19.3772
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.07 | 67 | 0.29811 | 19.9734
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.07 | 67 | 0.29811 | 19.9734
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12045 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.07 | 67 | 0.29811 | 19.9734
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12045 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29811 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12045 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29811 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12056 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2195 | 0 | 0.29822 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12056 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6167 | 0 | 0.29822 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.12093 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.0186 | 0 | 0.29859 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12118 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.79975 | 0 | 0.29884 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12118 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1563 | 0 | 0.29884 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6971 | 0 | 0.29941 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.2019 | 0 | 0.29941 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6459 | 0 | 0.29941 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12175 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.1158 | 0 | 0.29941 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.1223 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.3444 | 0 | 0.29996 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.532 | 208.2 | 0.30029 | 62.5213
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.426 | 142.1 | 0.30029 | 42.6718
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.2365 | 132.4 | 0.30029 | 39.759
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.678 | 136 | 0.30029 | 40.84
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.0269 | 147 | 0.30029 | 44.1433
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12263 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.7527 | 210 | 0.30029 | 63.0618
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.5857 | 70 | 0.30032 | 21.0221
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.5857 | 70 | 0.30032 | 21.0221
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.3822 | 92.8 | 0.30032 | 27.8693
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.8122 | 80 | 0.30032 | 24.0252
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.8122 | 80 | 0.30032 | 24.0252
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12265 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.1051 | 115 | 0.30032 | 34.5363
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.1227 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1169 | 0 | 0.30037 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12272 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3338 | 0 | 0.30039 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.123 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.3472 | 0 | 0.30067 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.123 | west | 8 | N | N | Nwest | Nwest | 1 | 3.1735 | 0 | 0.30067 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8385 | 0 | 0.30132 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.8114 | 0 | 0.30132 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12365 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0459 | 0 | 0.30132 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12378 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8541 | 0 | 0.30145 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12384 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8603 | 0 | 0.3015 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12409 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.9214 | 0 | 0.30176 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12421 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.358 | 0 | 0.30187 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12421 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.358 | 0 | 0.30187 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12422 | west | 8 | N | N | Nwest | Nwest | 1 | 8.6952 | 0 | 0.30188 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12422 | west | 8 | N | N | Nwest | Nwest | 1 | 9.1175 | 0 | 0.30188 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12422 | west | 8 | N | N | Nwest | Nwest | 1 | 8.7449 | 0 | 0.30188 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.12455 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 76.6007 | 0 | 0.30222 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.12455 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.1132 | 0 | 0.30222 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.6859 | 0 | 0.30224 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.4061 | 0 | 0.30224 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.9146 | 0 | 0.30224 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12457 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1854 | 0 | 0.30224 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2392 | 66 | 0.3025 | 19.965
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.6138 | 69 | 0.3025 | 20.8725
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.6138 | 69 | 0.3025 | 20.8725
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3641 | 67 | 0.3025 | 20.2675
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3641 | 67 | 0.3025 | 20.2675
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12484 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1144 | 65 | 0.3025 | 19.6625
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12494 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8712 | 0 | 0.3026 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12504 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6312 | 0 | 0.30271 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12504 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0053 | 0 | 0.30271 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12508 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3828 | 0 | 0.30274 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12508 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6298 | 0 | 0.30274 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12508 | west | 7 | N | N | Nwest | Nwest | 1 | 3.127 | 0 | 0.30274 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12508 | west | 7 | N | N | Nwest | Nwest | 1 | 5.7161 | 0 | 0.30274 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12508 | west | 7 | N | N | Nwest | Nwest | 1 | 5.7161 | 0 | 0.30274 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.1254 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5333 | 0 | 0.30306 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12547 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.82 | 0 | 0.30313 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12547 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6722 | 0 | 0.30313 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12579 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7244 | 0 | 0.30346 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12579 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7244 | 0 | 0.30346 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.12625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.0256 | 150.7 | 0.30391 | 45.7993
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.12625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.0634 | 151 | 0.30391 | 45.8905
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.12625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.3964 | 177.4 | 0.30391 | 53.9137
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.741 | 0 | 0.30409 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.5908 | 0 | 0.30409 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.0675 | 0 | 0.30409 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0447 | 0 | 0.30409 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2747 | 0 | 0.30409 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.1773 | 0 | 0.30409 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.12646 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.1585 | 151.5 | 0.30412 | 46.0744
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.12646 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2597 | 152.3 | 0.30412 | 46.3177
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.12646 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4465 | 177.5 | 0.30412 | 53.9816
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.482 | 0 | 0.30437 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0286 | 0 | 0.30437 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.5503 | 0 | 0.30437 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12671 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.9615 | 0 | 0.30437 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12679 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0187 | 0 | 0.30445 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.12857 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7145 | 0 | 0.30624 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13111 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.4436 | 0 | 0.30877 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13112 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.9438 | 0 | 0.30878 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13207 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.0364 | 182 | 0.30973 | 56.3709
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13207 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 63.9209 | 484 | 0.30973 | 149.9095
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13266 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.8884 | 0 | 0.31032 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.13284 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.642 | 0 | 0.3105 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.13289 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.31055 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.7966 | 0 | 0.31142 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.3889 | 0 | 0.31142 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.3953 | 0 | 0.31142 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.13376 | north | 1 | N | N | Nnorth | Nnorth | 1 | 53.3706 | 0 | 0.31142 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.1338 | west | 4 | Y | N | Ywest | Nwest | 1 | 86.9312 | 0 | 0.31146 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.13443 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 105.526 | 0 | 0.31209 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.13443 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 106.8703 | 0 | 0.31209 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.13443 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 104.8538 | 0 | 0.31209 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.13461 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.0768 | 0 | 0.31228 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.13603 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 30.4703 | 224 | 0.31369 | 70.2667
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.13674 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.0913 | 242 | 0.3144 | 76.0856
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.13753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 50.3367 | 366 | 0.31519 | 115.3612
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7518 | 20 | 0.31525 | 6.305
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7518 | 20 | 0.31525 | 6.305
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7518 | 20 | 0.31525 | 6.305
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.13759 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.339 | 17 | 0.31525 | 5.3593
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.13931 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.7167 | 0 | 0.31697 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13945 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6734 | 0 | 0.31712 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13945 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6734 | 0 | 0.31712 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4993 | 161 | 0.31741 | 51.1029
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9185 | 164 | 0.31741 | 52.0551
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9185 | 164 | 0.31741 | 52.0551
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 57.8553 | 414 | 0.31741 | 131.4075
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.639 | 162 | 0.31741 | 51.4203
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4993 | 161 | 0.31741 | 51.1029
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7788 | 163 | 0.31741 | 51.7377
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.13975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 57.1565 | 409 | 0.31741 | 129.8204
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.14073 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.2734 | 73 | 0.31839 | 23.2428
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.14073 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.7471 | 119 | 0.31839 | 37.8889
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.14073 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 28.8501 | 205 | 0.31839 | 65.2709
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.14073 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.3547 | 102 | 0.31839 | 32.4762
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.14073 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.5103 | 96 | 0.31839 | 30.5659
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.1408 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8159 | 20 | 0.31846 | 6.3692
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.1408 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.52 | 25 | 0.31846 | 7.9615
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.1408 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7727 | 41 | 0.31846 | 13.0569
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.141 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.6401 | 40 | 0.31867 | 12.7466
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14101 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.1396 | 79 | 0.31867 | 25.1749
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14101 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.9467 | 106 | 0.31867 | 33.779
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14101 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.587 | 146 | 0.31867 | 46.5257
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14101 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.7165 | 76 | 0.31867 | 24.2189
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14102 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.6914 | 0 | 0.31869 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14102 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.6529 | 0 | 0.31869 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14102 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 113.9474 | 0 | 0.31869 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14104 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 54.7231 | 388 | 0.3187 | 123.6561
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14104 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 72.6351 | 515 | 0.3187 | 164.1312
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.14108 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.5808 | 0 | 0.31874 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.14108 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.2298 | 0 | 0.31874 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.14108 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.4713 | 0 | 0.31874 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5917 | 160 | 0.31886 | 51.0177
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0269 | 156 | 0.31886 | 49.7422
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.6748 | 196 | 0.31886 | 62.4966
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0269 | 156 | 0.31886 | 49.7422
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1681 | 157 | 0.31886 | 50.0611
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.1412 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.9572 | 198 | 0.31886 | 63.1344
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.14121 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8066 | 204 | 0.31887 | 65.0498
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.14121 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.383 | 201 | 0.31887 | 64.0932
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.14121 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.1726 | 242 | 0.31887 | 77.1669
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14131 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 52.2858 | 370 | 0.31898 | 118.0209
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.7838 | 0 | 0.31898 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.9251 | 0 | 0.31898 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 43.6657 | 0 | 0.31898 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.2078 | 0 | 0.31898 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.3491 | 0 | 0.31898 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14131 | north | 1 | N | N | Nnorth | Nnorth | 1 | 43.807 | 0 | 0.31898 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14145 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 24.0462 | 170 | 0.31911 | 54.2488
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14145 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 73.553 | 520 | 0.31911 | 165.9374
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14158 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.6633 | 0 | 0.31924 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14158 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.6633 | 0 | 0.31924 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14165 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31931 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14165 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31931 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.14218 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.9949 | 0 | 0.31984 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14235 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32001 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.14236 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.5624 | 18 | 0.32002 | 5.7603
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.14236 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.5624 | 18 | 0.32002 | 5.7603
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.14236 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.4096 | 38 | 0.32002 | 12.1607
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14241 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.32008 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.14249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.0357 | 288 | 0.32015 | 92.2025
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.14249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9453 | 147 | 0.32015 | 47.0617
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.14249 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9453 | 147 | 0.32015 | 47.0617
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0011 | 196 | 0.32053 | 62.823
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.8578 | 111 | 0.32053 | 35.5783
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14294 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.5765 | 60 | 0.3206 | 19.2363
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14294 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.0053 | 63 | 0.3206 | 20.1981
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14388 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.978 | 118 | 0.32154 | 37.9421
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14388 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.5463 | 115 | 0.32154 | 36.9775
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14388 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 79.9978 | 556 | 0.32154 | 178.7781
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.1448 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32246 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.1448 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32246 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.1448 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32246 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.14506 | north | 3 | N | N | Nnorth | Nnorth | 1 | 167.8309 | 0 | 0.32272 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.14506 | north | 3 | N | N | Nnorth | Nnorth | 1 | 167.976 | 0 | 0.32272 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1863 | 70 | 0.32318 | 22.6226
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.0407 | 69 | 0.32318 | 22.2994
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.0407 | 69 | 0.32318 | 22.2994
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.14552 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.8952 | 68 | 0.32318 | 21.9763
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.14569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.658 | 217.3 | 0.32335 | 70.264
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.14569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.866 | 205 | 0.32335 | 66.2868
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.14569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 39.6854 | 272.4 | 0.32335 | 88.0807
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.14575 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32341 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.14575 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32341 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.14611 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32377 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.14762 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 64.2138 | 435 | 0.32528 | 141.497
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.14796 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 58.4446 | 395 | 0.32562 | 128.6212
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.14796 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 64.363 | 435 | 0.32562 | 141.6462
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.14912 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.0522 | 168 | 0.32678 | 54.8994
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.14912 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.4208 | 90 | 0.32678 | 29.4104
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7791 | 224 | 0.33293 | 74.5755
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.0897 | 226 | 0.33293 | 75.2414
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.916 | 212 | 0.33293 | 70.5804
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.15526 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.7607 | 211 | 0.33293 | 70.2475
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.15559 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.6686 | 216.4 | 0.33325 | 72.1147
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.15559 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.6219 | 216.1 | 0.33325 | 72.0148
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.15799 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3699 | 0 | 0.33565 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.15799 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3699 | 0 | 0.33565 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.16187 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2807 | 150 | 0.33953 | 50.93
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.16187 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9497 | 80 | 0.33953 | 27.1627
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.19433 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 49.5536 | 255 | 0.37199 | 94.8576
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.19433 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 28.9549 | 149 | 0.37199 | 55.4266
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.19433 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 29.7322 | 153 | 0.37199 | 56.9145
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.24531 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.42298 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.24531 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 193.0621 | 787 | 0.42298 | 332.8824

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1334
| 65 | 1307
| 70 | 1280
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| Max | 1340
| Min | 994
| Avg | 1239.6