## test results
CRE test for: |  | 3668 RNDROCK1 - 3670 RNDRCKNE_ctg2 | [5 empty] | FAIL
Line Rating: |  | 247.95
Direction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3668 RNDROCK1 - 3670 RNDRCKNE_ctg2
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.023142
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.032018
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.019864
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0055568
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3668 RNDROCK1 - 3670 RNDRCKNE_ctg2
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.024811
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.039229
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.019986
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.0050617
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3668 RNDROCK1 - 3670 RNDRCKNE_ctg2
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.062372
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.0031559
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.028204
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.052005
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.026462
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.024925
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.062372 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.062372 | -0.062372
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.12227
[6 empty] | Concentration |  | -1.9603 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.075056
[6 empty] | Concentration |  | -1.2034 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 78.947
| Percent of line rating => | [6 empty] | 31.84% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -6.444
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | -0.0037231 | 0.016614 | 0.020337 | -0.0037231
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.037404 | 0.21915 | 0.18175 | 0.037404
[7 empty] | B4 (S-W) | -0.054462 | -0.38958 | -0.33512 | -0.054462
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.016526 | -0.18705 | -0.17052 | -0.016526
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.041175 | 0.20179 | 0.16062 | 0.041175
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | -0.9263%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 9.306%
[7 empty] | B4 | -13.55%
[7 empty] | B5 | -4.112%
[7 empty] | B6 | 10.24%
[7 empty] | Max Abs Error | 13.55% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg2 C:7334 L_MCNEIL - 7336 L_GILLCR | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg2 C:7334 L_MCNEIL - 7336 L_GILLCR
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.034638 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -8.8327
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.034638 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -5.1611
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.032023 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.48035
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.032023 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.48035
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.034638 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -5.2996
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.033621 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -5.0431
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.033621 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -2.6897
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.024146 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -1.7627
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.024146 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -2.8734
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.024146 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -4.9499
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.024146 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -2.4629
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.024146 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -2.318
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.023423 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.28108
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.023423 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.28108
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.025482 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -4.281
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.025482 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -2.2934
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.024062 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.43312
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.024062 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.43312
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.024062 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.91436
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.023909 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -6.8858
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.023909 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.5146
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.023909 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.5146
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.02377 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -2.6741
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.02377 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.9508
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.023757 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -1.8768
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.023757 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -2.5182
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.023757 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -3.4685
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.023757 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -1.8055
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.023861 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -1.4317
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.023861 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -1.5032
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.023735 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.4747
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.023735 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.59337
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.023735 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.97313
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.010737 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -4.9712
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -1.284
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -1.2646
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.3035
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.3035
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.3035
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -2.2179
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -10.0193
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -1.34
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -1.4009
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -1.4009
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -1.3603
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -1.3603
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -1.3197
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.020177 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -1.4124
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.020177 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -1.481
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.020177 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -1.4205
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -3.0368
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -4.4539
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020359 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -2.0155
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020359 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -1.2419
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.020352 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -2.8696
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020359 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -0.50897
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020359 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -0.93041
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020359 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -0.93041
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.020352 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -2.4422
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.019953 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -0.51479
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.019895 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -1.9994
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.020103 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -2.4124
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.019892 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -1.1537
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.019949 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -4.2731
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.020473 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -3.0709
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.019603 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -0.12938
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.019603 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -0.67238
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.020473 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -2.0678
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.020114 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -2.4137
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.022721 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -8.3159
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.02273 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -5.5007
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.0215 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -8.6
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.021502 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -5.0745
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.021794 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -3.596
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.023397 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -4.773
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.023397 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -4.7028
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.023397 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -5.6621
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.45562
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.45562
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.45562
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.38728
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.023404 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -2.8085
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.023554 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -1.4132
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.02374 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -1.7805
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.02374 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -1.8897
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.02374 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -2.0986
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -3.8
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.705
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -4.655
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.705
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -3.7287
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -4.7025
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.023772 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -4.0412
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.023772 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -12.3614
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.02376 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -8.7912
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.023734 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -13.2436
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.023734 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -13.742
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.023734 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -19.1771
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.024081 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -2.6971
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.024081 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -2.4081
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.024081 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -9.1026
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.024162 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -5.2504
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.024162 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -4.9532
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.024162 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -6.5817
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.024277 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -18.6933
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -1.7251
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -1.7005
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -1.7005
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -1.6759
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.024076 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -27.8559
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.024076 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -27.88
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -5.693
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -5.7438
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.025393 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -5.495
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.025393 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -5.4874
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -5.388
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -5.3626
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.024514 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -9.683
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.024489 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -10.6527
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.024514 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -10.6636
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.023856 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -3.2921
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.024085 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -2.842
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.024085 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -2.7698
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.024085 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -13.3913
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.023753 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -9.2162
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.023753 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -12.2328
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.023027 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -18.0762
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.023027 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -18.3065
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.023027 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -17.9611
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.022849 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -4.1585
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.022849 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -11.0589
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.024086 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -5.3953
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.022855 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -1.1427
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.022865 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.96033
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.021658 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -13.3197
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.021658 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -12.7132
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.035827 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -19.2391
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.035827 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -28.1958
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.036333 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -2.725
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.036333 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -8.0659
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.047161 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -26.8346
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.033399 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 6.9804
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.033399 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 7.2142
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.033317 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 13.56
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 1.5364
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 1.5698
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 1.5364
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 1.5364
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.033349 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 14.14
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.033349 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 14.1733
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.033199 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 1.9255
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.033199 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 2.9547
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 1.4608
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 1.4608
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 1.4276
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 1.494
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.033422 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 13.7699
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.033422 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 13.3688
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.032725 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 17.8679
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.032725 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 24.5437
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.033369 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 2.0355
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.033369 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 3.1701
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.033369 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 5.0387
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.033058 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 5.124
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.033058 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 5.6199
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.033058 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 5.124
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.025628 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.56382
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.025628 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.28191
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.025628 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.28191
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 1.2367
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.96708
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 1.1926
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 1.2445
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.027393 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.32872
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.027393 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.30132
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.02929 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.70296
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.02929 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.70296
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.02929 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.67367
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.030538 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 12.093
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.0149 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 19.8617
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.0149 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 19.7872
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.026805 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 1.0186
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.026805 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.51734
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.026805 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.40208
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.026805 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 1.2598
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.01711 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -1.2833
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.020715 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -3.1073
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.019279 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -3.2678
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.006147 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -0.92205
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.020331 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -1.2809
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.022031 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -14.3135
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.023783 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.95132
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.023783 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.95132
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.064594 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 27.2587
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.037711 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 4.9779
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.037711 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 5.0533
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.037711 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 12.1807
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.027245 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 4.3047
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.027245 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 4.3592
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.027245 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 4.7679
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.029107 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 16.9985
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.029107 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 17.3187
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.029143 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 12.6189
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 7.8614
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 7.9
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 7.8859
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 7.9597
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.10474 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.83789
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.10474 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.83789
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.05856 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 1.0541
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.05856 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 1.0541
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.05856 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.8784
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.057862 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.79271
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.073935 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 1.3308
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.073935 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 1.3308
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.095117 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 3.3291
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.095117 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 3.234
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.095117 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 3.3291
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.065705 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 1.8397
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.065705 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 1.9054
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.019477 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -0.6817
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.019477 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -0.58431
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.6376
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.6376
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.6376
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.6376
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.047689 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.28613
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.037776 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.090662
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.037776 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.090662
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.037776 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.10577
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.036403 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.14561
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.037462 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.089909
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.037462 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.089909
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 4.8985
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 4.5986
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 4.6652
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 4.8985
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 6.0648
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 6.598
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.035061 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 5.3468
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.035061 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 5.2416
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.035061 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 8.1552
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 4.8742
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 4.9771
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 5.1831
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 9.9543
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.017036 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.56219
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.017036 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.4259
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.027393 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.32872
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.026037 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 1.9007
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.8951
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 1.943
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.70157
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.17539
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.8951
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 1.919
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 1.8807
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.5997
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 1.1034
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.027848 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 17.5164
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.026389 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 3.8
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.026389 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 4.9611
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.033981 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.40777
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.020817 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.1249
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.026471 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 8.8943
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.026541 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 8.8647
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.026541 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 9.0239
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.026592 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 1.0105
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.026557 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.66392
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.026557 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.66392
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.026584 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 1.0102
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.026732 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.77523
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.026475 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 3.9262
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.026475 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 3.9342
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.026475 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 4.0507
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 4.1319
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 4.0011
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 2.6151
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 3.7919
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 3.8442
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 3.3212
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.026944 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 3.9473
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.026944 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 3.985
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.026944 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 4.6613
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.026871 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 5.5623
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.026871 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 5.8229
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.026871 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 6.5028
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.02687 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 3.8693
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.02687 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 3.8693
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.02687 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 4.5948
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.099125 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 30.7288
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.099125 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 40.9386
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 4.0938
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 4.2887
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 4.2887
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 4.5811
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 4.4086
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 4.1387
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 4.1387
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 4.2286
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.089971 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 13.8555
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.089971 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 13.3157
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 4.3186
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 4.3186
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -1.3914
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -1.3914
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -1.8446
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -1.5902
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -1.5902
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -2.2859
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -4.1376
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -2.824
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -2.6312
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -2.7027
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -2.9213
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -4.1733
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -4.3165
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -2.6126
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -5.1426
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -4.0686
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -4.049
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -2.4679
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.019549 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -2.9128
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.020188 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -3.6338
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.020188 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -3.6338
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.020165 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -4.5371
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.020479 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -2.5599
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.020479 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -2.5599
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -3.3264
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -3.3502
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -7.3418
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -3.3977
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -3.4214
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -7.3656
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.024624 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -4.8263
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.024624 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -2.7333
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.023875 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.7999
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.8707
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.8707
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -9.7712
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -3.8235
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.7999
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -3.8471
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -9.6532
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.023817 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.023817 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -3.3953
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -2.9823
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -3.3264
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -9.1535
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.021878 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -3.297
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.021878 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -3.3036
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.021878 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -3.8812
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.021923 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -3.3213
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.021923 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -3.3389
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.021923 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -3.8913
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.047161 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -27.4005
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -14.0323
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -14.0323
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.013749 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.43997
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.014771 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.70901
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.014771 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.67947
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.16607
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.70579
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013839 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.23526
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.30446
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.34597
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.014771 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -1.551
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.020425 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -1.7157
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.017068 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -1.3654
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.017046 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -2.5569
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.017046 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -2.5569
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.42133
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.39693
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.3154
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 0.91169
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 0.91348
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 0.90634
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 0.5713
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 1.452
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.23804
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 0.59739
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 0.55331
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 0.61168
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 0.60751
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.005956 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.19059
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.005956 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.17868
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.0515
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.0515
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 1.1273
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 1.0373
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -2.4995
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -2.511
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.00381 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 0.51816
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.007124 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.23509
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.15981
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.15981
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.14459
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.14459
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.010075 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.71532
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.010075 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.10075
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.007302 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.1902
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.007302 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.1902
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.007302 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 1.789
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.29984
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.27678
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.29984
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.29984
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.004092 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 0.60971
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.004092 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.26639
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 0.43398
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.41776
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.4149
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.25991
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.058182
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.003157 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 2.3457
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.00342 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 2.5137
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.003079 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.52959
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.003079 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.52959
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.003079 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.52959
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 0.27974
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.003759 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 0.65031
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.003759 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 0.50747
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 0.47098
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 0.46693
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 0.4597
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 0.7788
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.2608
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.25754
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.33659
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.29992
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 0.69327
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 0.66736
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 0.66906
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 0.66694
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 1.1427
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.003169 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.015845
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.003169 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.066549
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -1.3223
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.3377
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.3377
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -3.2585
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.002822 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 1.1232
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.20079
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.20079
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.20079
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.24008
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.24008
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.23571
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.018647 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -15.4211
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.018647 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -15.2719
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.007431 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.34257
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 1.106
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 1.106
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 1.5281
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 1.0769
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 1.0769
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 1.4844
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.00407 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 0.7326
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.00407 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 0.6455
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.00407 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 0.63899
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.004174 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.14609
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.00517 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 2.373
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.20572
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.20889
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.22155
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.19939
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.19623
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 0.32916
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.18674
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 0.25225
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.24902
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.24902
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.001617 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 0.26195
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.003105 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 0.48749
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.28201
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.28598
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.15491
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.11916
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.004322 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.33712
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.004322 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.34576
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.004077 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.066047
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.004097 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 0.676
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.004102 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 0.69324
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.004079 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 0.86883
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.004073 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 0.92864
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.004106 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.049272
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.004106 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.073908
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.005488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.2744
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.3639
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.3639
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.18895
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.18545
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.18895
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.19944
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.18895
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.18895
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.20294
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.20294
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.00326 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.03912
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.15154
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.15965
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.15154
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.15154
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.15965
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.15154
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.013781 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.90955
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.006957 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 1.1201
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.006957 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 1.1549
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.006957 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 1.7253
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.006957 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 3.7985
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.006957 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 4.4734
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.007319 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 4.7647
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.007319 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 4.1279
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.007319 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 4.3914
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.006957 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.090441
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.003163 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.037956
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.11407
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.11642
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.10971
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.15399
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.059383
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.068442
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.066765
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.11743
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.06039
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.28652
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 0.49654
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.67059
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.77226
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.48672
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.0924
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.93018
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.95181
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.5408
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.19469
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 1.0167
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.75712
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.68141
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.77875
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.70088
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.0924
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 1.0492
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 1.114
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.82202
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.86528
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.86528
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 1.8495
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.24368
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.016042 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -1.2272
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.01711 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -1.3688
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.01711 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -0.6844
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.01728 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -1.3824
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.017073 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -1.3658
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.016193 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -1.2954
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.015906 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -1.3361
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.01728 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -1.3824
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 4.2304
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.020067 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -2.408
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.020067 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -4.6756
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.020067 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -3.4154
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 8.2382
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 6.8281
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 8.3124
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 4.2675
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 3.7109
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.021071 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -1.2643
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.03115 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.01132 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.017918 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.086006
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -0.77269
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -2.215
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -2.7817
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -2.452
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -2.1635
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -1.6587
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.019794 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -2.9691
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -2.2148
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -2.9432
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -3.6618
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -4.2229
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.026805 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.021697 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.0287 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.67166
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 1.0459
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 1.7751
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 2.5175
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 1.0981
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 1.0177
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.50886
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 2.5175
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.96415
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 1.1516
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.5892
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.97718
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.37584
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.17539
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.37584
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.97718
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.97718
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 3.9637
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 1.3391
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 1.473
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 1.3391
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026151 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.31381
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.025415 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.38122
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.025415 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.58454
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.024243 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 1.1637
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.025186 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.20149
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.026481 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 4.7666
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.026471 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 4.7648
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.026541 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 4.7774
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.026541 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 4.7774
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.028703 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 2.8703
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.028703 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 2.8703
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.6569
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.6569
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.6569
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.42042
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.6569
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.6569
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.6569
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.39414
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.028703 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.028703 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 14.3515
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.028703 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 14.3515
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.028703 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.028472 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.017036 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.027824 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.027329 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg2 C:7334 L_MCNEIL - 7336 L_GILLCR | [7 empty] | 78.947
Number of Bus | Name of Bus | ID | Max MW | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg2 C:7334 L_MCNEIL - 7336 L_GILLCR | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.034638 | north | Y | -0.011496 | -0.066656 | -0.014774 | -0.040195 | 0.011496 | North | N | 0.011496 | 0
239 | BOSQUESW | 1 | 149 | -0.034638 | north | Y | -0.011496 | -0.066656 | -0.014774 | -0.040195 | 0.011496 | North | N | 0.011496 | 0
244 | WHITNYDM | 1 | 15 | -0.032023 | north | N | -0.0088806 | -0.064041 | -0.012159 | -0.03758 | 0.0088806 | North | N | 0.0088806 | 0
245 | WHITNYDM | 2 | 15 | -0.032023 | north | N | -0.0088806 | -0.064041 | -0.012159 | -0.03758 | 0.0088806 | North | N | 0.0088806 | 0
247 | BOSQUESW | 2 | 153 | -0.034638 | north | Y | -0.011496 | -0.066656 | -0.014774 | -0.040195 | 0.011496 | North | N | 0.011496 | 0
251 | BOSQUESW | 2 | 150 | -0.033621 | north | Y | -0.010479 | -0.065639 | -0.013757 | -0.039178 | 0.010479 | North | N | 0.010479 | 0
253 | BOSQUESW | 2 | 80 | -0.033621 | north | Y | -0.010479 | -0.065639 | -0.013757 | -0.039178 | 0.010479 | North | N | 0.010479 | 0
332 | RWMILLER | 1 | 73 | -0.024146 | north | Y | -0.0010036 | -0.056164 | -0.0042824 | -0.029703 | 0.0010036 | North | N | 0.0010036 | 0
333 | RWMILLER | 2 | 119 | -0.024146 | north | Y | -0.0010036 | -0.056164 | -0.0042824 | -0.029703 | 0.0010036 | North | N | 0.0010036 | 0
334 | RWMILLER | 3 | 205 | -0.024146 | north | Y | -0.0010036 | -0.056164 | -0.0042824 | -0.029703 | 0.0010036 | North | N | 0.0010036 | 0
335 | RWMILLER | 4 | 102 | -0.024146 | north | Y | -0.0010036 | -0.056164 | -0.0042824 | -0.029703 | 0.0010036 | North | N | 0.0010036 | 0
336 | RWMILLER | 5 | 96 | -0.024146 | north | Y | -0.0010036 | -0.056164 | -0.0042824 | -0.029703 | 0.0010036 | North | N | 0.0010036 | 0
344 | MRSSHPRD | 1 | 12 | -0.023423 | north | N | -0.00028059 | -0.055441 | -0.0035594 | -0.02898 | 0.00028059 | North | N | 0.00028059 | 0
345 | MRSSHPRD | 2 | 12 | -0.023423 | north | N | -0.00028059 | -0.055441 | -0.0035594 | -0.02898 | 0.00028059 | North | N | 0.00028059 | 0
366 | JNSNCNTY | 1 | 168 | -0.025482 | north | Y | -0.0023396 | -0.0575 | -0.0056184 | -0.031039 | 0.0023396 | North | N | 0.0023396 | 0
367 | JNSNCNTY | 2 | 90 | -0.025482 | north | Y | -0.0023396 | -0.0575 | -0.0056184 | -0.031039 | 0.0023396 | North | N | 0.0023396 | 0
503 | NTHTEXAS | 1 | 18 | -0.024062 | north | Y | -0.00091959 | -0.05608 | -0.0041984 | -0.029619 | 0.00091959 | North | N | 0.00091959 | 0
504 | NTHTEXAS | 2 | 18 | -0.024062 | north | Y | -0.00091959 | -0.05608 | -0.0041984 | -0.029619 | 0.00091959 | North | N | 0.00091959 | 0
505 | NTHTEXAS | 3 | 38 | -0.024062 | north | Y | -0.00091959 | -0.05608 | -0.0041984 | -0.029619 | 0.00091959 | North | N | 0.00091959 | 0
580 | JCKCNTY8 | 1 | 288 | -0.023909 | north | Y | -0.00076659 | -0.055927 | -0.0040454 | -0.029466 | 0.00076659 | North | N | 0.00076659 | 0
581 | JCKCNTY8 | 2 | 147 | -0.023909 | north | Y | -0.00076659 | -0.055927 | -0.0040454 | -0.029466 | 0.00076659 | North | N | 0.00076659 | 0
582 | JCKCNTY8 | 3 | 147 | -0.023909 | north | Y | -0.00076659 | -0.055927 | -0.0040454 | -0.029466 | 0.00076659 | North | N | 0.00076659 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.02377 | north | Y | -0.00062759 | -0.055788 | -0.0039064 | -0.029327 | 0.00062759 | North | N | 0.00062759 | 0
837 | NEWMAN_G | 1 | 40 | -0.02377 | north | Y | -0.00062759 | -0.055788 | -0.0039064 | -0.029327 | 0.00062759 | North | N | 0.00062759 | 0
842 | OLINGER_ | 1 | 79 | -0.023757 | north | Y | -0.00061459 | -0.055775 | -0.0038934 | -0.029314 | 0.00061459 | North | N | 0.00061459 | 0
843 | OLINGER_ | 1 | 106 | -0.023757 | north | Y | -0.00061459 | -0.055775 | -0.0038934 | -0.029314 | 0.00061459 | North | N | 0.00061459 | 0
844 | OLINGER_ | 1 | 146 | -0.023757 | north | Y | -0.00061459 | -0.055775 | -0.0038934 | -0.029314 | 0.00061459 | North | N | 0.00061459 | 0
845 | OLINGER_ | 1 | 76 | -0.023757 | north | Y | -0.00061459 | -0.055775 | -0.0038934 | -0.029314 | 0.00061459 | North | N | 0.00061459 | 0
923 | SPENCER_ | 1 | 60 | -0.023861 | north | Y | -0.00071859 | -0.055879 | -0.0039974 | -0.029418 | 0.00071859 | North | N | 0.00071859 | 0
924 | SPENCER_ | 1 | 63 | -0.023861 | north | Y | -0.00071859 | -0.055879 | -0.0039974 | -0.029418 | 0.00071859 | North | N | 0.00071859 | 0
948 | STEAM1 | 1 | 20 | -0.023735 | north | Y | -0.00059259 | -0.055753 | -0.0038714 | -0.029292 | 0.00059259 | North | N | 0.00059259 | 0
949 | STEAM2 | 1 | 25 | -0.023735 | north | Y | -0.00059259 | -0.055753 | -0.0038714 | -0.029292 | 0.00059259 | North | N | 0.00059259 | 0
950 | STEAM3 | 1 | 41 | -0.023735 | north | Y | -0.00059259 | -0.055753 | -0.0038714 | -0.029292 | 0.00059259 | North | N | 0.00059259 | 0
990 | GIBN_CRE | 1 | 463 | -0.010737 | north | Y | 0.012405 | -0.042755 | 0.0091266 | -0.016294 | 0.0091266 | west | Y | 0.012405 | 1.5181
1002 | PBCTAGE_ | A | 66 | -0.019455 | west | Y | 0.0036874 | -0.051473 | 0.00040857 | -0.025012 | 0.00040857 | west | N | 0.00040857 | 0
1003 | PBCTBGE_ | B | 65 | -0.019455 | west | Y | 0.0036874 | -0.051473 | 0.00040857 | -0.025012 | 0.00040857 | west | N | 0.00040857 | 0
1004 | PBCTCGE_ | C | 67 | -0.019455 | west | Y | 0.0036874 | -0.051473 | 0.00040857 | -0.025012 | 0.00040857 | west | N | 0.00040857 | 0
1005 | PBCTDGE_ | D | 67 | -0.019455 | west | Y | 0.0036874 | -0.051473 | 0.00040857 | -0.025012 | 0.00040857 | west | N | 0.00040857 | 0
1006 | PBCTEGE_ | E | 67 | -0.019455 | west | Y | 0.0036874 | -0.051473 | 0.00040857 | -0.025012 | 0.00040857 | west | N | 0.00040857 | 0
1007 | PB5GEN_6 | MB | 114 | -0.019455 | west | Y | 0.0036874 | -0.051473 | 0.00040857 | -0.025012 | 0.00040857 | west | N | 0.00040857 | 0
1008 | PB6GEN_7 | MB | 515 | -0.019455 | west | Y | 0.0036874 | -0.051473 | 0.00040857 | -0.025012 | 0.00040857 | west | N | 0.00040857 | 0
1039 | MRGNAG_1 | A | 66 | -0.020303 | west | Y | 0.0028394 | -0.052321 | -0.00043943 | -0.02586 | 0.00043943 | west | N | 0.00043943 | 0
1040 | MRGNBG_2 | B | 69 | -0.020303 | west | Y | 0.0028394 | -0.052321 | -0.00043943 | -0.02586 | 0.00043943 | west | N | 0.00043943 | 0
1041 | MRGNCG_3 | C | 69 | -0.020303 | west | Y | 0.0028394 | -0.052321 | -0.00043943 | -0.02586 | 0.00043943 | west | N | 0.00043943 | 0
1042 | MRGNDG_4 | D | 67 | -0.020303 | west | Y | 0.0028394 | -0.052321 | -0.00043943 | -0.02586 | 0.00043943 | west | N | 0.00043943 | 0
1043 | MRGNEG_5 | E | 67 | -0.020303 | west | Y | 0.0028394 | -0.052321 | -0.00043943 | -0.02586 | 0.00043943 | west | N | 0.00043943 | 0
1044 | MRGNFG_6 | F | 65 | -0.020303 | west | Y | 0.0028394 | -0.052321 | -0.00043943 | -0.02586 | 0.00043943 | west | N | 0.00043943 | 0
1045 | CALENG1G | 1 | 70 | -0.020177 | west | N | 0.0029654 | -0.052195 | -0.00031343 | -0.025734 | 0.00031343 | west | N | 0.00031343 | 0
1046 | CALENG2G | 2 | 73.4 | -0.020177 | west | N | 0.0029654 | -0.052195 | -0.00031343 | -0.025734 | 0.00031343 | west | N | 0.00031343 | 0
1047 | CALENG3G | 3 | 70.4 | -0.020177 | west | N | 0.0029654 | -0.052195 | -0.00031343 | -0.025734 | 0.00031343 | west | N | 0.00031343 | 0
1058 | LONGSHOR | 1 | 150 | -0.020245 | west | Y | 0.0028974 | -0.052263 | -0.00038143 | -0.025802 | 0.00038143 | west | N | 0.00038143 | 0
1058 | LONGSHOR | 2 | 220 | -0.020245 | west | Y | 0.0028974 | -0.052263 | -0.00038143 | -0.025802 | 0.00038143 | west | N | 0.00038143 | 0
1061 | CIELOGEN | 1 | 99 | -0.020359 | west | Y | 0.0027834 | -0.052377 | -0.00049543 | -0.025916 | 0.00049543 | west | N | 0.00049543 | 0
1062 | CIELOGEN | 1 | 61 | -0.020359 | west | Y | 0.0027834 | -0.052377 | -0.00049543 | -0.025916 | 0.00049543 | west | N | 0.00049543 | 0
1068 | SCURRYCW | 1 | 141 | -0.020352 | west | Y | 0.0027904 | -0.05237 | -0.00048843 | -0.025909 | 0.00048843 | west | N | 0.00048843 | 0
1069 | KINDERMG | 1 | 25 | -0.020359 | west | N | 0.0027834 | -0.052377 | -0.00049543 | -0.025916 | 0.00049543 | west | N | 0.00049543 | 0
1070 | KINDERMG | 1 | 45.7 | -0.020359 | west | N | 0.0027834 | -0.052377 | -0.00049543 | -0.025916 | 0.00049543 | west | N | 0.00049543 | 0
1071 | KINDERMG | 1 | 45.7 | -0.020359 | west | N | 0.0027834 | -0.052377 | -0.00049543 | -0.025916 | 0.00049543 | west | N | 0.00049543 | 0
1073 | SCURRYCW | 2 | 120 | -0.020352 | west | Y | 0.0027904 | -0.05237 | -0.00048843 | -0.025909 | 0.00048843 | west | N | 0.00048843 | 0
1320 | BSP 1 | 1 | 25.8 | -0.019953 | west | N | 0.0031894 | -0.051971 | -8.943e-05 | -0.02551 | 8.943e-05 | west | N | 8.943e-05 | 0
1326 | STANTONW | 1 | 100.5 | -0.019895 | west | Y | 0.0032474 | -0.051913 | -3.143e-05 | -0.025452 | 3.143e-05 | west | N | 3.143e-05 | 0
1327 | WILDHRSE | 1 | 120 | -0.020103 | west | Y | 0.0030394 | -0.052121 | -0.00023943 | -0.02566 | 0.00023943 | west | N | 0.00023943 | 0
1328 | OCOTILLO | 1 | 58 | -0.019892 | west | Y | 0.0032504 | -0.05191 | -2.843e-05 | -0.025449 | 2.843e-05 | west | N | 2.843e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.019949 | west | Y | 0.0031934 | -0.051967 | -8.543e-05 | -0.025506 | 8.543e-05 | west | N | 8.543e-05 | 0
1343 | TRENTIPP | 1 | 150 | -0.020473 | west | Y | 0.0026694 | -0.052491 | -0.00060943 | -0.02603 | 0.00060943 | west | N | 0.00060943 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.019603 | west | Y | 0.0035394 | -0.051621 | 0.00026057 | -0.02516 | 0.00026057 | west | N | 0.00026057 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.019603 | west | Y | 0.0035394 | -0.051621 | 0.00026057 | -0.02516 | 0.00026057 | west | N | 0.00026057 | 0
1354 | AEPWIND_ | 1 | 101 | -0.020473 | west | Y | 0.0026694 | -0.052491 | -0.00060943 | -0.02603 | 0.00060943 | west | N | 0.00060943 | 0
1360 | GUNSIGHT | 1 | 120 | -0.020114 | west | Y | 0.0030284 | -0.052132 | -0.00025043 | -0.025671 | 0.00025043 | west | N | 0.00025043 | 0
1432 | GRHAMSES | 2 | 366 | -0.022721 | north | Y | 0.00042141 | -0.054739 | -0.0028574 | -0.028278 | 0.00042141 | North | N | 0.00042141 | 0
1433 | GRHAMSES | 1 | 242 | -0.02273 | north | Y | 0.00041241 | -0.054748 | -0.0028664 | -0.028287 | 0.00041241 | North | N | 0.00041241 | 0
1437 | MESQUITW | 1 | 400 | -0.0215 | west | Y | 0.0016424 | -0.053518 | -0.0016364 | -0.027057 | 0.0016364 | west | N | 0.0016364 | 0
1438 | MESQUITW | 1 | 236 | -0.021502 | west | Y | 0.0016404 | -0.05352 | -0.0016384 | -0.027059 | 0.0016384 | west | N | 0.0016384 | 0
1442 | COKFIELD | 1 | 165 | -0.021794 | west | Y | 0.0013484 | -0.053812 | -0.0019304 | -0.027351 | 0.0013484 | North | Y | 0.0019304 | 0.096033
1453 | WCPWRCO_ | 1 | 204 | -0.023397 | north | Y | -0.00025459 | -0.055415 | -0.0035334 | -0.028954 | 0.00025459 | North | N | 0.00025459 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.023397 | north | Y | -0.00025459 | -0.055415 | -0.0035334 | -0.028954 | 0.00025459 | North | N | 0.00025459 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.023397 | north | Y | -0.00025459 | -0.055415 | -0.0035334 | -0.028954 | 0.00025459 | North | N | 0.00025459 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.022781 | west | Y | 0.00036141 | -0.054799 | -0.0029174 | -0.028338 | 0.00036141 | North | Y | 0.0029174 | 0.05112
1479 | WFCOGEN_ | 2 | 20 | -0.022781 | west | Y | 0.00036141 | -0.054799 | -0.0029174 | -0.028338 | 0.00036141 | North | Y | 0.0029174 | 0.05112
1482 | WFCOGEN_ | 1 | 20 | -0.022781 | west | Y | 0.00036141 | -0.054799 | -0.0029174 | -0.028338 | 0.00036141 | North | Y | 0.0029174 | 0.05112
1482 | WFCOGEN_ | 2 | 17 | -0.022781 | west | Y | 0.00036141 | -0.054799 | -0.0029174 | -0.028338 | 0.00036141 | North | Y | 0.0029174 | 0.043452
1600 | BARTNWND | 1 | 120 | -0.023404 | north | Y | -0.00026159 | -0.055422 | -0.0035404 | -0.028961 | 0.00026159 | North | N | 0.00026159 | 0
1643 | SLSTR1PP | 1 | 60 | -0.023554 | north | Y | -0.00041159 | -0.055572 | -0.0036904 | -0.029111 | 0.00041159 | North | N | 0.00041159 | 0
1675 | PEC_1G | 1 | 75 | -0.02374 | north | N | -0.00059759 | -0.055758 | -0.0038764 | -0.029297 | 0.00059759 | North | N | 0.00059759 | 0
1676 | PEC_2G | 2 | 79.6 | -0.02374 | north | N | -0.00059759 | -0.055758 | -0.0038764 | -0.029297 | 0.00059759 | North | N | 0.00059759 | 0
1677 | PEC_3G | 3 | 88.4 | -0.02374 | north | N | -0.00059759 | -0.055758 | -0.0038764 | -0.029297 | 0.00059759 | North | N | 0.00059759 | 0
1678 | LAMARPWR | 1 | 160 | -0.02375 | north | Y | -0.00060759 | -0.055768 | -0.0038864 | -0.029307 | 0.00060759 | North | N | 0.00060759 | 0
1679 | LAMARPWR | 2 | 156 | -0.02375 | north | Y | -0.00060759 | -0.055768 | -0.0038864 | -0.029307 | 0.00060759 | North | N | 0.00060759 | 0
1680 | LAMARPWR | 3 | 196 | -0.02375 | north | Y | -0.00060759 | -0.055768 | -0.0038864 | -0.029307 | 0.00060759 | North | N | 0.00060759 | 0
1681 | LAMARPWR | 4 | 156 | -0.02375 | north | Y | -0.00060759 | -0.055768 | -0.0038864 | -0.029307 | 0.00060759 | North | N | 0.00060759 | 0
1682 | LAMARPWR | 5 | 157 | -0.02375 | north | Y | -0.00060759 | -0.055768 | -0.0038864 | -0.029307 | 0.00060759 | North | N | 0.00060759 | 0
1683 | LAMARPWR | 6 | 198 | -0.02375 | north | Y | -0.00060759 | -0.055768 | -0.0038864 | -0.029307 | 0.00060759 | North | N | 0.00060759 | 0
1687 | VALLEY_1 | 1 | 170 | -0.023772 | north | Y | -0.00062959 | -0.05579 | -0.0039084 | -0.029329 | 0.00062959 | North | N | 0.00062959 | 0
1688 | VALLEY_2 | 2 | 520 | -0.023772 | north | Y | -0.00062959 | -0.05579 | -0.0039084 | -0.029329 | 0.00062959 | North | N | 0.00062959 | 0
1689 | VALLEY_3 | 3 | 370 | -0.02376 | north | Y | -0.00061759 | -0.055778 | -0.0038964 | -0.029317 | 0.00061759 | North | N | 0.00061759 | 0
1701 | MOSES_1G | 1 | 558 | -0.023734 | north | Y | -0.00059159 | -0.055752 | -0.0038704 | -0.029291 | 0.00059159 | North | N | 0.00059159 | 0
1702 | MOSES_2G | 2 | 579 | -0.023734 | north | Y | -0.00059159 | -0.055752 | -0.0038704 | -0.029291 | 0.00059159 | North | N | 0.00059159 | 0
1703 | MOSES_3G | 3 | 808 | -0.023734 | north | Y | -0.00059159 | -0.055752 | -0.0038704 | -0.029291 | 0.00059159 | North | N | 0.00059159 | 0
1861 | EAGLEMNT | MB | 112 | -0.024081 | north | Y | -0.00093859 | -0.056099 | -0.0042174 | -0.029638 | 0.00093859 | North | N | 0.00093859 | 0
1862 | EAGLEMNT | MB | 100 | -0.024081 | north | Y | -0.00093859 | -0.056099 | -0.0042174 | -0.029638 | 0.00093859 | North | N | 0.00093859 | 0
1863 | EAGLEMNT | MB | 378 | -0.024081 | north | Y | -0.00093859 | -0.056099 | -0.0042174 | -0.029638 | 0.00093859 | North | N | 0.00093859 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.024162 | north | Y | -0.0010196 | -0.05618 | -0.0042984 | -0.029719 | 0.0010196 | North | N | 0.0010196 | 0
1878 | WLFHOLW_ | 2 | 205 | -0.024162 | north | Y | -0.0010196 | -0.05618 | -0.0042984 | -0.029719 | 0.0010196 | North | N | 0.0010196 | 0
1879 | WLFHOLW_ | 3 | 272.4 | -0.024162 | north | Y | -0.0010196 | -0.05618 | -0.0042984 | -0.029719 | 0.0010196 | North | N | 0.0010196 | 0
1889 | DECRDOVA | MB | 770 | -0.024277 | north | Y | -0.0011346 | -0.056295 | -0.0044134 | -0.029834 | 0.0011346 | North | N | 0.0011346 | 0
1892 | DECRDOVA | A | 70 | -0.024645 | north | Y | -0.0015026 | -0.056663 | -0.0047814 | -0.030202 | 0.0015026 | North | N | 0.0015026 | 0
1893 | DECRDOVA | B | 69 | -0.024645 | north | Y | -0.0015026 | -0.056663 | -0.0047814 | -0.030202 | 0.0015026 | North | N | 0.0015026 | 0
1894 | DECRDOVA | C | 69 | -0.024645 | north | Y | -0.0015026 | -0.056663 | -0.0047814 | -0.030202 | 0.0015026 | North | N | 0.0015026 | 0
1895 | DECRDOVA | D | 68 | -0.024645 | north | Y | -0.0015026 | -0.056663 | -0.0047814 | -0.030202 | 0.0015026 | North | N | 0.0015026 | 0
1898 | COMCHEPK | 1 | 1157 | -0.024076 | north | N | -0.00093359 | -0.056094 | -0.0042124 | -0.029633 | 0.00093359 | North | N | 0.00093359 | 0
1899 | COMCHEPK | 2 | 1158 | -0.024076 | north | N | -0.00093359 | -0.056094 | -0.0042124 | -0.029633 | 0.00093359 | North | N | 0.00093359 | 0
1937 | MDLTHELP | 5 | 224 | -0.025415 | north | Y | -0.0022726 | -0.057433 | -0.0055514 | -0.030972 | 0.0022726 | North | N | 0.0022726 | 0
1938 | MDLTHELP | 6 | 226 | -0.025415 | north | Y | -0.0022726 | -0.057433 | -0.0055514 | -0.030972 | 0.0022726 | North | N | 0.0022726 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.025393 | north | Y | -0.0022506 | -0.057411 | -0.0055294 | -0.03095 | 0.0022506 | North | N | 0.0022506 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.025393 | north | Y | -0.0022506 | -0.057411 | -0.0055294 | -0.03095 | 0.0022506 | North | N | 0.0022506 | 0
1943 | MDLTHELP | 3 | 212 | -0.025415 | north | Y | -0.0022726 | -0.057433 | -0.0055514 | -0.030972 | 0.0022726 | North | N | 0.0022726 | 0
1944 | MDLTHELP | 4 | 211 | -0.025415 | north | Y | -0.0022726 | -0.057433 | -0.0055514 | -0.030972 | 0.0022726 | North | N | 0.0022726 | 0
1947 | HANDLEY_ | 3 | 395 | -0.024514 | north | Y | -0.0013716 | -0.056532 | -0.0046504 | -0.030071 | 0.0013716 | North | N | 0.0013716 | 0
1948 | HANDLEY_ | 4 | 435 | -0.024489 | north | Y | -0.0013466 | -0.056507 | -0.0046254 | -0.030046 | 0.0013466 | North | N | 0.0013466 | 0
1949 | HANDLEY_ | 5 | 435 | -0.024514 | north | Y | -0.0013716 | -0.056532 | -0.0046504 | -0.030071 | 0.0013716 | North | N | 0.0013716 | 0
2371 | COLLIN_1 | MB | 138 | -0.023856 | north | Y | -0.00071359 | -0.055874 | -0.0039924 | -0.029413 | 0.00071359 | North | N | 0.00071359 | 0
2413 | MTCK6_G | 6 | 118 | -0.024085 | north | Y | -0.00094259 | -0.056103 | -0.0042214 | -0.029642 | 0.00094259 | North | N | 0.00094259 | 0
2414 | MTCK7_G | 7 | 115 | -0.024085 | north | Y | -0.00094259 | -0.056103 | -0.0042214 | -0.029642 | 0.00094259 | North | N | 0.00094259 | 0
2417 | MTCK8_G | 8 | 556 | -0.024085 | north | Y | -0.00094259 | -0.056103 | -0.0042214 | -0.029642 | 0.00094259 | North | N | 0.00094259 | 0
2451 | LKHB1_G | 1 | 388 | -0.023753 | north | Y | -0.00061059 | -0.055771 | -0.0038894 | -0.02931 | 0.00061059 | North | N | 0.00061059 | 0
2452 | LKHB2_G | 2 | 515 | -0.023753 | north | Y | -0.00061059 | -0.055771 | -0.0038894 | -0.02931 | 0.00061059 | North | N | 0.00061059 | 0
3097 | MARTLAKE | 1 | 785 | -0.023027 | north | Y | 0.00011541 | -0.055045 | -0.0031634 | -0.028584 | 0.00011541 | North | N | 0.00011541 | 0
3098 | MARTLAKE | 2 | 795 | -0.023027 | north | Y | 0.00011541 | -0.055045 | -0.0031634 | -0.028584 | 0.00011541 | North | N | 0.00011541 | 0
3099 | MARTLAKE | 3 | 780 | -0.023027 | north | Y | 0.00011541 | -0.055045 | -0.0031634 | -0.028584 | 0.00011541 | North | N | 0.00011541 | 0
3107 | STRYKER_ | 1 | 182 | -0.022849 | north | Y | 0.00029341 | -0.054867 | -0.0029854 | -0.028406 | 0.00029341 | North | N | 0.00029341 | 0
3108 | STRYKER_ | 2 | 484 | -0.022849 | north | Y | 0.00029341 | -0.054867 | -0.0029854 | -0.028406 | 0.00029341 | North | N | 0.00029341 | 0
3126 | TRINIDAD | 1 | 224 | -0.024086 | north | Y | -0.00094359 | -0.056104 | -0.0042224 | -0.029643 | 0.00094359 | North | N | 0.00094359 | 0
3309 | ASPN_G | 1 | 50 | -0.022855 | north | Y | 0.00028741 | -0.054873 | -0.0029914 | -0.028412 | 0.00028741 | North | N | 0.00028741 | 0
3348 | CHAMPION | MB | 42 | -0.022865 | north | N | 0.00027741 | -0.054883 | -0.0030014 | -0.028422 | 0.00027741 | North | N | 0.00027741 | 0
3381 | BBRN_1G | 1 | 615 | -0.021658 | north | Y | 0.0014844 | -0.053676 | -0.0017944 | -0.027215 | 0.0014844 | North | N | 0.0014844 | 0
3382 | BBRN_2G | 2 | 587 | -0.021658 | north | Y | 0.0014844 | -0.053676 | -0.0017944 | -0.027215 | 0.0014844 | North | N | 0.0014844 | 0
3403 | THOUSE_1 | MB | 537 | -0.035827 | north | Y | -0.012685 | -0.067845 | -0.015963 | -0.041384 | 0.012685 | North | N | 0.012685 | 0
3404 | THOUSE_2 | 2 | 787 | -0.035827 | north | Y | -0.012685 | -0.067845 | -0.015963 | -0.041384 | 0.012685 | North | N | 0.012685 | 0
3416 | LAKE_CRK | MB | 75 | -0.036333 | north | Y | -0.013191 | -0.068351 | -0.016469 | -0.04189 | 0.013191 | North | N | 0.013191 | 0
3417 | LAKE_CRK | MB | 222 | -0.036333 | north | Y | -0.013191 | -0.068351 | -0.016469 | -0.04189 | 0.013191 | North | N | 0.013191 | 0
3432 | SANDOW_4 | 4 | 569 | -0.047161 | south | Y | -0.024019 | -0.079179 | -0.027297 | -0.052718 | 0.024019 | North | Y | 0.079179 | 31.3865
5026 | BRAUNIG_ | 1 | 209 | 0.033399 | south | Y | 0.056541 | 0.0013806 | 0.053263 | 0.027842 | 0.0013806 | south | N | 0.0013806 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.033399 | south | Y | 0.056541 | 0.0013806 | 0.053263 | 0.027842 | 0.0013806 | south | N | 0.0013806 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.033317 | south | Y | 0.056459 | 0.0012986 | 0.053181 | 0.02776 | 0.0012986 | south | N | 0.0012986 | 0
5031 | BRA_VHBC | 1 | 46 | 0.033399 | south | Y | 0.056541 | 0.0013806 | 0.053263 | 0.027842 | 0.0013806 | south | N | 0.0013806 | 0
5032 | BRA_VHBC | 2 | 47 | 0.033399 | south | Y | 0.056541 | 0.0013806 | 0.053263 | 0.027842 | 0.0013806 | south | N | 0.0013806 | 0
5033 | BRA_VHBC | 3 | 46 | 0.033399 | south | Y | 0.056541 | 0.0013806 | 0.053263 | 0.027842 | 0.0013806 | south | N | 0.0013806 | 0
5034 | BRA_VHBC | 4 | 46 | 0.033399 | south | Y | 0.056541 | 0.0013806 | 0.053263 | 0.027842 | 0.0013806 | south | N | 0.0013806 | 0
5111 | CALAVER_ | 1 | 424 | 0.033349 | south | Y | 0.056491 | 0.0013306 | 0.053213 | 0.027792 | 0.0013306 | south | N | 0.0013306 | 0
5112 | CALAVER_ | 2 | 425 | 0.033349 | south | Y | 0.056491 | 0.0013306 | 0.053213 | 0.027792 | 0.0013306 | south | N | 0.0013306 | 0
5264 | LEON_LCP | 3 | 58 | 0.033199 | south | Y | 0.056341 | 0.0011806 | 0.053063 | 0.027642 | 0.0011806 | south | N | 0.0011806 | 0
5265 | LEON_LCP | 4 | 89 | 0.033199 | south | Y | 0.056341 | 0.0011806 | 0.053063 | 0.027642 | 0.0011806 | south | N | 0.0011806 | 0
5266 | LEON_LCP | 1 | 44 | 0.033199 | south | Y | 0.056341 | 0.0011806 | 0.053063 | 0.027642 | 0.0011806 | south | N | 0.0011806 | 0
5267 | LEON_LCP | 2 | 44 | 0.033199 | south | Y | 0.056341 | 0.0011806 | 0.053063 | 0.027642 | 0.0011806 | south | N | 0.0011806 | 0
5268 | LEON_LCP | 3 | 43 | 0.033199 | south | Y | 0.056341 | 0.0011806 | 0.053063 | 0.027642 | 0.0011806 | south | N | 0.0011806 | 0
5269 | LEON_LCP | 4 | 45 | 0.033199 | south | Y | 0.056341 | 0.0011806 | 0.053063 | 0.027642 | 0.0011806 | south | N | 0.0011806 | 0
5396 | CALAVER_ | 1 | 412 | 0.033422 | south | Y | 0.056564 | 0.0014036 | 0.053286 | 0.027865 | 0.0014036 | south | N | 0.0014036 | 0
5397 | CALAVER_ | 2 | 400 | 0.033422 | south | Y | 0.056564 | 0.0014036 | 0.053286 | 0.027865 | 0.0014036 | south | N | 0.0014036 | 0
5401 | CALAVER_ | 1 | 546 | 0.032725 | south | Y | 0.055867 | 0.00070659 | 0.052589 | 0.027168 | 0.00070659 | south | N | 0.00070659 | 0
5402 | CALAVER_ | 2 | 750 | 0.032725 | south | Y | 0.055867 | 0.00070659 | 0.052589 | 0.027168 | 0.00070659 | south | N | 0.00070659 | 0
5436 | TUTTL_WB | MB | 61 | 0.033369 | south | Y | 0.056511 | 0.0013506 | 0.053233 | 0.027812 | 0.0013506 | south | N | 0.0013506 | 0
5438 | TUTTL_WB | MB | 95 | 0.033369 | south | Y | 0.056511 | 0.0013506 | 0.053233 | 0.027812 | 0.0013506 | south | N | 0.0013506 | 0
5439 | TUTTL_WB | MB | 151 | 0.033369 | south | Y | 0.056511 | 0.0013506 | 0.053233 | 0.027812 | 0.0013506 | south | N | 0.0013506 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.033058 | south | Y | 0.0562 | 0.0010396 | 0.052922 | 0.027501 | 0.0010396 | south | N | 0.0010396 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.033058 | south | Y | 0.0562 | 0.0010396 | 0.052922 | 0.027501 | 0.0010396 | south | N | 0.0010396 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.033058 | south | Y | 0.0562 | 0.0010396 | 0.052922 | 0.027501 | 0.0010396 | south | N | 0.0010396 | 0
5503 | RAYBURNG | 1 | 22 | 0.025628 | south | Y | 0.04877 | -0.0063904 | 0.045492 | 0.020071 | 0.0063904 | south | N | 0.0063904 | 0
5505 | RAYBURNG | 1 | 11 | 0.025628 | south | Y | 0.04877 | -0.0063904 | 0.045492 | 0.020071 | 0.0063904 | south | N | 0.0063904 | 0
5506 | RAYBURNG | 1 | 11 | 0.025628 | south | Y | 0.04877 | -0.0063904 | 0.045492 | 0.020071 | 0.0063904 | south | N | 0.0063904 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.025927 | south | Y | 0.049069 | -0.0060914 | 0.045791 | 0.02037 | 0.0060914 | south | N | 0.0060914 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.025927 | south | Y | 0.049069 | -0.0060914 | 0.045791 | 0.02037 | 0.0060914 | south | N | 0.0060914 | 0
5511 | RAYBURNC | 1 | 46 | 0.025927 | south | Y | 0.049069 | -0.0060914 | 0.045791 | 0.02037 | 0.0060914 | south | N | 0.0060914 | 0
5512 | RAYBURNC | 1 | 48 | 0.025927 | south | Y | 0.049069 | -0.0060914 | 0.045791 | 0.02037 | 0.0060914 | south | N | 0.0060914 | 0
5728 | FALCONHY | 2 | 12 | 0.027393 | south | N | 0.050535 | -0.0046254 | 0.047257 | 0.021836 | 0.0046254 | south | N | 0.0046254 | 0
5729 | FALCONHY | 3 | 11 | 0.027393 | south | N | 0.050535 | -0.0046254 | 0.047257 | 0.021836 | 0.0046254 | south | N | 0.0046254 | 0
5890 | PEARSALL | 1 | 24 | 0.02929 | south | Y | 0.052432 | -0.0027284 | 0.049154 | 0.023733 | 0.0027284 | south | N | 0.0027284 | 0
5891 | PEARSALL | 1 | 24 | 0.02929 | south | Y | 0.052432 | -0.0027284 | 0.049154 | 0.023733 | 0.0027284 | south | N | 0.0027284 | 0
5892 | PEARSALL | 1 | 23 | 0.02929 | south | Y | 0.052432 | -0.0027284 | 0.049154 | 0.023733 | 0.0027284 | south | N | 0.0027284 | 0
5903 | SANMIGUE | 1 | 396 | 0.030538 | south | Y | 0.05368 | -0.0014804 | 0.050402 | 0.024981 | 0.0014804 | south | N | 0.0014804 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.0149 | houston | N | 0.038042 | -0.017118 | 0.034764 | 0.0093432 | 0.0093432 | houston | N | 0.0093432 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.0149 | houston | N | 0.038042 | -0.017118 | 0.034764 | 0.0093432 | 0.0093432 | houston | N | 0.0093432 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.023142 | 0
5932 | SI_RAY9 | 9 | 38 | 0.026805 | south | Y | 0.049947 | -0.0052134 | 0.046669 | 0.021248 | 0.0052134 | south | N | 0.0052134 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.026805 | south | Y | 0.049947 | -0.0052134 | 0.046669 | 0.021248 | 0.0052134 | south | N | 0.0052134 | 0
5934 | SI_RAY5 | 5 | 15 | 0.026805 | south | Y | 0.049947 | -0.0052134 | 0.046669 | 0.021248 | 0.0052134 | south | N | 0.0052134 | 0
5935 | SI_RAY10 | 10 | 47 | 0.026805 | south | Y | 0.049947 | -0.0052134 | 0.046669 | 0.021248 | 0.0052134 | south | N | 0.0052134 | 0
6016 | SWMESA | 1 | 75 | -0.01711 | west | Y | 0.0060324 | -0.049128 | 0.0027536 | -0.022667 | 0.0027536 | west | N | 0.0027536 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.019864 | 0
6144 | MCADOO1A | 1 | 150 | -0.020715 | west | Y | 0.0024274 | -0.052733 | -0.00085143 | -0.026272 | 0.00085143 | west | N | 0.00085143 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.019279 | west | Y | 0.0038634 | -0.051297 | 0.00058457 | -0.024836 | 0.00058457 | west | N | 0.00058457 | 0
6476 | LANGFORD | 1 | 150 | -0.006147 | west | Y | 0.016995 | -0.038165 | 0.013717 | -0.011704 | 0.011704 | houston | Y | 0.013717 | 0.30192
6637 | SNYDERW1 | 1 | 63 | -0.020331 | west | Y | 0.0028114 | -0.052349 | -0.00046743 | -0.025888 | 0.00046743 | west | N | 0.00046743 | 0
6752 | OKLA0A | 1 | 649.7 | -0.022031 | west | Y | 0.0011114 | -0.054049 | -0.0021674 | -0.027588 | 0.0011114 | North | Y | 0.0021674 | 0.6861
6948 | DENISNDM | 1 | 40 | -0.023783 | north | N | -0.00064059 | -0.055801 | -0.0039194 | -0.02934 | 0.00064059 | North | N | 0.00064059 | 0
6948 | DENISNDM | 2 | 40 | -0.023783 | north | N | -0.00064059 | -0.055801 | -0.0039194 | -0.02934 | 0.00064059 | North | N | 0.00064059 | 0
7000 | L_FERGUS | 1 | 422 | 0.064594 | south | Y | 0.087736 | 0.032576 | 0.084458 | 0.059037 | 0.032576 | south | N | 0.032576 | 0
7004 | L_SIMGID | 1 | 132 | 0.037711 | south | Y | 0.060853 | 0.0056926 | 0.057575 | 0.032154 | 0.0056926 | south | N | 0.0056926 | 0
7005 | L_SIMGID | 2 | 134 | 0.037711 | south | Y | 0.060853 | 0.0056926 | 0.057575 | 0.032154 | 0.0056926 | south | N | 0.0056926 | 0
7006 | L_SIMGID | 3 | 323 | 0.037711 | south | Y | 0.060853 | 0.0056926 | 0.057575 | 0.032154 | 0.0056926 | south | N | 0.0056926 | 0
7007 | L_LOSTPI | 1 | 158 | 0.027245 | south | Y | 0.050387 | -0.0047734 | 0.047109 | 0.021688 | 0.0047734 | south | N | 0.0047734 | 0
7008 | L_LOSTPI | 2 | 160 | 0.027245 | south | Y | 0.050387 | -0.0047734 | 0.047109 | 0.021688 | 0.0047734 | south | N | 0.0047734 | 0
7009 | L_LOSTPI | 3 | 175 | 0.027245 | south | Y | 0.050387 | -0.0047734 | 0.047109 | 0.021688 | 0.0047734 | south | N | 0.0047734 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.029107 | south | Y | 0.052249 | -0.0029114 | 0.048971 | 0.02355 | 0.0029114 | south | N | 0.0029114 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.029107 | south | Y | 0.052249 | -0.0029114 | 0.048971 | 0.02355 | 0.0029114 | south | N | 0.0029114 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.029143 | south | Y | 0.052285 | -0.0028754 | 0.049007 | 0.023586 | 0.0028754 | south | N | 0.0028754 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.035111 | south | Y | 0.058253 | 0.0030926 | 0.054975 | 0.029554 | 0.0030926 | south | N | 0.0030926 | 0
7015 | L_HAYSEN | 2 | 225 | 0.035111 | south | Y | 0.058253 | 0.0030926 | 0.054975 | 0.029554 | 0.0030926 | south | N | 0.0030926 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.035111 | south | Y | 0.058253 | 0.0030926 | 0.054975 | 0.029554 | 0.0030926 | south | N | 0.0030926 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.035111 | south | Y | 0.058253 | 0.0030926 | 0.054975 | 0.029554 | 0.0030926 | south | N | 0.0030926 | 0
7020 | L_AUSTPL | 1 | 8 | 0.10474 | south | N | 0.12788 | 0.072718 | 0.1246 | 0.099179 | 0.072718 | south | N | 0.072718 | 0
7020 | L_AUSTPL | 2 | 8 | 0.10474 | south | N | 0.12788 | 0.072718 | 0.1246 | 0.099179 | 0.072718 | south | N | 0.072718 | 0
7022 | L_BUCHAN | 1 | 18 | 0.05856 | south | N | 0.081702 | 0.026542 | 0.078424 | 0.053003 | 0.026542 | south | N | 0.026542 | 0
7023 | L_BUCHAN | 2 | 18 | 0.05856 | south | N | 0.081702 | 0.026542 | 0.078424 | 0.053003 | 0.026542 | south | N | 0.026542 | 0
7024 | L_BUCHAN | 3 | 15 | 0.05856 | south | N | 0.081702 | 0.026542 | 0.078424 | 0.053003 | 0.026542 | south | N | 0.026542 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.057862 | south | N | 0.081004 | 0.025844 | 0.077726 | 0.052305 | 0.025844 | south | N | 0.025844 | 0
7028 | L_MARBFA | 1 | 18 | 0.073935 | south | N | 0.097077 | 0.041917 | 0.093799 | 0.068378 | 0.041917 | south | N | 0.041917 | 0
7029 | L_MARBFA | 2 | 18 | 0.073935 | south | N | 0.097077 | 0.041917 | 0.093799 | 0.068378 | 0.041917 | south | N | 0.041917 | 0
7031 | L_MARSFO | 1 | 35 | 0.095117 | south | N | 0.11826 | 0.063099 | 0.11498 | 0.08956 | 0.063099 | south | N | 0.063099 | 0
7032 | L_MARSFO | 2 | 34 | 0.095117 | south | N | 0.11826 | 0.063099 | 0.11498 | 0.08956 | 0.063099 | south | N | 0.063099 | 0
7033 | L_MARSFO | 3 | 35 | 0.095117 | south | N | 0.11826 | 0.063099 | 0.11498 | 0.08956 | 0.063099 | south | N | 0.063099 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.065705 | south | N | 0.088847 | 0.033687 | 0.085569 | 0.060148 | 0.033687 | south | N | 0.033687 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.065705 | south | N | 0.088847 | 0.033687 | 0.085569 | 0.060148 | 0.033687 | south | N | 0.033687 | 0
7038 | L_DELAWA | 1 | 35 | -0.019477 | west | Y | 0.0036654 | -0.051495 | 0.00038657 | -0.025034 | 0.00038657 | west | N | 0.00038657 | 0
7038 | L_DELAWA | 2 | 30 | -0.019477 | west | Y | 0.0036654 | -0.051495 | 0.00038657 | -0.025034 | 0.00038657 | west | N | 0.00038657 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.032751 | south | Y | 0.055893 | 0.00073259 | 0.052615 | 0.027194 | 0.00073259 | south | N | 0.00073259 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.032751 | south | Y | 0.055893 | 0.00073259 | 0.052615 | 0.027194 | 0.00073259 | south | N | 0.00073259 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.032751 | south | Y | 0.055893 | 0.00073259 | 0.052615 | 0.027194 | 0.00073259 | south | N | 0.00073259 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.032751 | south | Y | 0.055893 | 0.00073259 | 0.052615 | 0.027194 | 0.00073259 | south | N | 0.00073259 | 0
7487 | L_CANYHY | 1 | 6 | 0.047689 | south | N | 0.070831 | 0.015671 | 0.067553 | 0.042132 | 0.015671 | south | N | 0.015671 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.037776 | south | N | 0.060918 | 0.0057576 | 0.05764 | 0.032219 | 0.0057576 | south | N | 0.0057576 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.037776 | south | N | 0.060918 | 0.0057576 | 0.05764 | 0.032219 | 0.0057576 | south | N | 0.0057576 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.037776 | south | N | 0.060918 | 0.0057576 | 0.05764 | 0.032219 | 0.0057576 | south | N | 0.0057576 | 0
7609 | L_SCHUMA | 1 | 4 | 0.036403 | south | N | 0.059545 | 0.0043846 | 0.056267 | 0.030846 | 0.0043846 | south | N | 0.0043846 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.037462 | south | N | 0.060604 | 0.0054436 | 0.057326 | 0.031905 | 0.0054436 | south | N | 0.0054436 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.037462 | south | N | 0.060604 | 0.0054436 | 0.057326 | 0.031905 | 0.0054436 | south | N | 0.0054436 | 0
7800 | L_GUADGE | 1 | 147 | 0.033323 | south | Y | 0.056465 | 0.0013046 | 0.053187 | 0.027766 | 0.0013046 | south | N | 0.0013046 | 0
7801 | L_GUADGE | 2 | 138 | 0.033323 | south | Y | 0.056465 | 0.0013046 | 0.053187 | 0.027766 | 0.0013046 | south | N | 0.0013046 | 0
7802 | L_GUADGE | 3 | 140 | 0.033323 | south | Y | 0.056465 | 0.0013046 | 0.053187 | 0.027766 | 0.0013046 | south | N | 0.0013046 | 0
7803 | L_GUADGE | 4 | 147 | 0.033323 | south | Y | 0.056465 | 0.0013046 | 0.053187 | 0.027766 | 0.0013046 | south | N | 0.0013046 | 0
7804 | L_GUADGE | 5 | 182 | 0.033323 | south | Y | 0.056465 | 0.0013046 | 0.053187 | 0.027766 | 0.0013046 | south | N | 0.0013046 | 0
7805 | L_GUADGE | 6 | 198 | 0.033323 | south | Y | 0.056465 | 0.0013046 | 0.053187 | 0.027766 | 0.0013046 | south | N | 0.0013046 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.035061 | south | Y | 0.058203 | 0.0030426 | 0.054925 | 0.029504 | 0.0030426 | south | N | 0.0030426 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.035061 | south | Y | 0.058203 | 0.0030426 | 0.054925 | 0.029504 | 0.0030426 | south | N | 0.0030426 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.035061 | south | Y | 0.058203 | 0.0030426 | 0.054925 | 0.029504 | 0.0030426 | south | N | 0.0030426 | 0
7810 | L_RIONOG | 1 | 142 | 0.034325 | south | Y | 0.057467 | 0.0023066 | 0.054189 | 0.028768 | 0.0023066 | south | N | 0.0023066 | 0
7811 | L_RIONOG | 2 | 145 | 0.034325 | south | Y | 0.057467 | 0.0023066 | 0.054189 | 0.028768 | 0.0023066 | south | N | 0.0023066 | 0
7812 | L_RIONOG | 3 | 151 | 0.034325 | south | Y | 0.057467 | 0.0023066 | 0.054189 | 0.028768 | 0.0023066 | south | N | 0.0023066 | 0
7813 | L_RIONOG | 4 | 290 | 0.034325 | south | Y | 0.057467 | 0.0023066 | 0.054189 | 0.028768 | 0.0023066 | south | N | 0.0023066 | 0
8032 | AMISTADH | 1 | 33 | 0.017036 | south | N | 0.040178 | -0.014982 | 0.0369 | 0.011479 | 0.011479 | houston | Y | 0.014982 | 0
8033 | AMISTADH | 2 | 25 | 0.017036 | south | N | 0.040178 | -0.014982 | 0.0369 | 0.011479 | 0.011479 | houston | Y | 0.014982 | 0
8048 | FALCONHY | 1 | 12 | 0.027393 | south | N | 0.050535 | -0.0046254 | 0.047257 | 0.021836 | 0.0046254 | south | N | 0.0046254 | 0
8066 | DUP1V#1 | 1 | 73 | 0.026037 | south | N | 0.049179 | -0.0059814 | 0.045901 | 0.02048 | 0.0059814 | south | N | 0.0059814 | 0
8134 | FOR69CG0 | 1 | 79 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
8138 | FOR69CG0 | 2 | 81 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.032018 | 0
8147 | UCAR #2 | 10 | 28 | 0.025056 | south | N | 0.048198 | -0.0069624 | 0.04492 | 0.019499 | 0.0069624 | south | N | 0.0069624 | 0
8148 | UCAR #1 | 2 | 7 | 0.025056 | south | N | 0.048198 | -0.0069624 | 0.04492 | 0.019499 | 0.0069624 | south | N | 0.0069624 | 0
8153 | FOR69CG0 | 3 | 79 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
8154 | FOR69CG0 | 4 | 80 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
8156 | FOR69CG0 | 6 | 25 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
8157 | FOR69CG0 | 7 | 46 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
8161 | COLETOU1 | 1 | 629 | 0.027848 | south | Y | 0.05099 | -0.0041704 | 0.047712 | 0.022291 | 0.0041704 | south | N | 0.0041704 | 0
8173 | VICEC51A | 5 | 144 | 0.026389 | south | Y | 0.049531 | -0.0056294 | 0.046253 | 0.020832 | 0.0056294 | south | N | 0.0056294 | 0
8174 | VICEC61A | 6 | 188 | 0.026389 | south | Y | 0.049531 | -0.0056294 | 0.046253 | 0.020832 | 0.0056294 | south | N | 0.0056294 | 0
8189 | CUERO 2 | 1 | 12 | 0.033981 | south | N | 0.057123 | 0.0019626 | 0.053845 | 0.028424 | 0.0019626 | south | N | 0.0019626 | 0
8262 | ELPS | 1 | 6 | 0.020817 | south | N | 0.043959 | -0.011201 | 0.040681 | 0.01526 | 0.011201 | south | N | 0.011201 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.032018 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.032018 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.032018 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.032018 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.032018 | 0
8442 | NBEC71A | 1 | 336 | 0.026471 | south | Y | 0.049613 | -0.0055474 | 0.046335 | 0.020914 | 0.0055474 | south | N | 0.0055474 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.032018 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | 0.023142 | -0.032018 | 0.019864 | -0.0055568 | 0.0055568 | houston | Y | 0.032018 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.026541 | south | Y | 0.049683 | -0.0054774 | 0.046405 | 0.020984 | 0.0054774 | south | N | 0.0054774 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.026541 | south | Y | 0.049683 | -0.0054774 | 0.046405 | 0.020984 | 0.0054774 | south | N | 0.0054774 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.026592 | south | N | 0.049734 | -0.0054264 | 0.046456 | 0.021035 | 0.0054264 | south | N | 0.0054264 | 0
8506 | VAL #1 | 1 | 25 | 0.026557 | south | N | 0.049699 | -0.0054614 | 0.046421 | 0.021 | 0.0054614 | south | N | 0.0054614 | 0
8507 | VAL #2 | 2 | 25 | 0.026557 | south | N | 0.049699 | -0.0054614 | 0.046421 | 0.021 | 0.0054614 | south | N | 0.0054614 | 0
8511 | OXY_CC0A | 1 | 38 | 0.026584 | south | N | 0.049726 | -0.0054344 | 0.046448 | 0.021027 | 0.0054344 | south | N | 0.0054344 | 0
8517 | CELANEBI | 1 | 29 | 0.026732 | south | N | 0.049874 | -0.0052864 | 0.046596 | 0.021175 | 0.0052864 | south | N | 0.0052864 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.026475 | south | N | 0.049617 | -0.0055434 | 0.046339 | 0.020918 | 0.0055434 | south | N | 0.0055434 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.026475 | south | N | 0.049617 | -0.0055434 | 0.046339 | 0.020918 | 0.0055434 | south | N | 0.0055434 | 0
8562 | CNOPST1 | 3 | 153 | 0.026475 | south | N | 0.049617 | -0.0055434 | 0.046339 | 0.020918 | 0.0055434 | south | N | 0.0055434 | 0
8926 | LGE_GT10 | 1 | 158 | 0.026151 | south | N | 0.049293 | -0.0058674 | 0.046015 | 0.020594 | 0.0058674 | south | N | 0.0058674 | 0
8927 | LGE_GT20 | 2 | 153 | 0.026151 | south | N | 0.049293 | -0.0058674 | 0.046015 | 0.020594 | 0.0058674 | south | N | 0.0058674 | 0
8928 | LGE_STG0 | 3 | 100 | 0.026151 | south | N | 0.049293 | -0.0058674 | 0.046015 | 0.020594 | 0.0058674 | south | N | 0.0058674 | 0
8930 | ICPGN10A | 1 | 145 | 0.026151 | south | N | 0.049293 | -0.0058674 | 0.046015 | 0.020594 | 0.0058674 | south | N | 0.0058674 | 0
8931 | ICPGN20A | 2 | 147 | 0.026151 | south | N | 0.049293 | -0.0058674 | 0.046015 | 0.020594 | 0.0058674 | south | N | 0.0058674 | 0
8932 | ICPGN30A | 3 | 127 | 0.026151 | south | N | 0.049293 | -0.0058674 | 0.046015 | 0.020594 | 0.0058674 | south | N | 0.0058674 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.026944 | south | Y | 0.050086 | -0.0050744 | 0.046808 | 0.021387 | 0.0050744 | south | N | 0.0050744 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.026944 | south | Y | 0.050086 | -0.0050744 | 0.046808 | 0.021387 | 0.0050744 | south | N | 0.0050744 | 0
8935 | FGNTS201 | 3 | 173 | 0.026944 | south | Y | 0.050086 | -0.0050744 | 0.046808 | 0.021387 | 0.0050744 | south | N | 0.0050744 | 0
8936 | MVGN#1 | 1 | 207 | 0.026871 | south | Y | 0.050013 | -0.0051474 | 0.046735 | 0.021314 | 0.0051474 | south | N | 0.0051474 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.026871 | south | Y | 0.050013 | -0.0051474 | 0.046735 | 0.021314 | 0.0051474 | south | N | 0.0051474 | 0
8938 | MVGN#3 | 3 | 242 | 0.026871 | south | Y | 0.050013 | -0.0051474 | 0.046735 | 0.021314 | 0.0051474 | south | N | 0.0051474 | 0
8981 | HECN1 | 1 | 144 | 0.02687 | south | Y | 0.050012 | -0.0051484 | 0.046734 | 0.021313 | 0.0051484 | south | N | 0.0051484 | 0
8982 | HECN2 | 2 | 144 | 0.02687 | south | Y | 0.050012 | -0.0051484 | 0.046734 | 0.021313 | 0.0051484 | south | N | 0.0051484 | 0
8983 | HECN3 | 3 | 171 | 0.02687 | south | Y | 0.050012 | -0.0051484 | 0.046734 | 0.021313 | 0.0051484 | south | N | 0.0051484 | 0
9000 | DECKR_G1 | 1 | 310 | 0.099125 | south | Y | 0.12227 | 0.067107 | 0.11899 | 0.093568 | 0.067107 | south | N | 0.067107 | 0
9001 | DECKR_G2 | 2 | 413 | 0.099125 | south | Y | 0.12227 | 0.067107 | 0.11899 | 0.093568 | 0.067107 | south | N | 0.067107 | 0
9002 | DECKR_G3 | 3 | 42 | 0.097471 | south | Y | 0.12061 | 0.065453 | 0.11733 | 0.091914 | 0.065453 | south | N | 0.065453 | 0
9003 | DECKR_G4 | 4 | 44 | 0.097471 | south | Y | 0.12061 | 0.065453 | 0.11733 | 0.091914 | 0.065453 | south | N | 0.065453 | 0
9004 | DECKR_G5 | 5 | 44 | 0.097471 | south | Y | 0.12061 | 0.065453 | 0.11733 | 0.091914 | 0.065453 | south | N | 0.065453 | 0
9005 | DECKR_G6 | 6 | 47 | 0.097471 | south | Y | 0.12061 | 0.065453 | 0.11733 | 0.091914 | 0.065453 | south | N | 0.065453 | 0
9016 | SANDH_G1 | 1 | 49 | 0.089971 | south | Y | 0.11311 | 0.057953 | 0.10983 | 0.084414 | 0.057953 | south | N | 0.057953 | 0
9017 | SANDH_G2 | 2 | 46 | 0.089971 | south | Y | 0.11311 | 0.057953 | 0.10983 | 0.084414 | 0.057953 | south | N | 0.057953 | 0
9018 | SANDH_G3 | 3 | 46 | 0.089971 | south | Y | 0.11311 | 0.057953 | 0.10983 | 0.084414 | 0.057953 | south | N | 0.057953 | 0
9019 | SANDH_G4 | 4 | 47 | 0.089971 | south | Y | 0.11311 | 0.057953 | 0.10983 | 0.084414 | 0.057953 | south | N | 0.057953 | 0
9020 | SANDHG5A | 5A | 154 | 0.089971 | south | Y | 0.11311 | 0.057953 | 0.10983 | 0.084414 | 0.057953 | south | N | 0.057953 | 0
9021 | SANDHG5C | 5C | 148 | 0.089971 | south | Y | 0.11311 | 0.057953 | 0.10983 | 0.084414 | 0.057953 | south | N | 0.057953 | 0
9022 | SANDH_G6 | 6 | 48 | 0.089971 | south | Y | 0.11311 | 0.057953 | 0.10983 | 0.084414 | 0.057953 | south | N | 0.057953 | 0
9023 | SANDH_G7 | 7 | 48 | 0.089971 | south | Y | 0.11311 | 0.057953 | 0.10983 | 0.084414 | 0.057953 | south | N | 0.057953 | 0
11001 | NAV1CT | 1 | 70 | -0.019877 | west | Y | 0.0032654 | -0.051895 | -1.343e-05 | -0.025434 | 1.343e-05 | west | N | 1.343e-05 | 0
11009 | NAV2CT | 1 | 70 | -0.019877 | west | Y | 0.0032654 | -0.051895 | -1.343e-05 | -0.025434 | 1.343e-05 | west | N | 1.343e-05 | 0
11011 | NAV3ST | 1 | 92.8 | -0.019877 | west | Y | 0.0032654 | -0.051895 | -1.343e-05 | -0.025434 | 1.343e-05 | west | N | 1.343e-05 | 0
11012 | NAV4CT | 1 | 80 | -0.019877 | west | Y | 0.0032654 | -0.051895 | -1.343e-05 | -0.025434 | 1.343e-05 | west | N | 1.343e-05 | 0
11013 | NAV5CT | 1 | 80 | -0.019877 | west | Y | 0.0032654 | -0.051895 | -1.343e-05 | -0.025434 | 1.343e-05 | west | N | 1.343e-05 | 0
11014 | NAV6ST | 1 | 115 | -0.019877 | west | Y | 0.0032654 | -0.051895 | -1.343e-05 | -0.025434 | 1.343e-05 | west | N | 1.343e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.019873 | west | Y | 0.0032694 | -0.051891 | -9.43e-06 | -0.02543 | 9.43e-06 | west | N | 9.43e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.019873 | west | Y | 0.0032694 | -0.051891 | -9.43e-06 | -0.02543 | 9.43e-06 | west | N | 9.43e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.019873 | west | Y | 0.0032694 | -0.051891 | -9.43e-06 | -0.02543 | 9.43e-06 | west | N | 9.43e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.019873 | west | Y | 0.0032694 | -0.051891 | -9.43e-06 | -0.02543 | 9.43e-06 | west | N | 9.43e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.019873 | west | Y | 0.0032694 | -0.051891 | -9.43e-06 | -0.02543 | 9.43e-06 | west | N | 9.43e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.019873 | west | Y | 0.0032694 | -0.051891 | -9.43e-06 | -0.02543 | 9.43e-06 | west | N | 9.43e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.020653 | west | Y | 0.0024894 | -0.052671 | -0.00078943 | -0.02621 | 0.00078943 | west | N | 0.00078943 | 0
11057 | CHAMPION | 1 | 126.5 | -0.020653 | west | Y | 0.0024894 | -0.052671 | -0.00078943 | -0.02621 | 0.00078943 | west | N | 0.00078943 | 0
11058 | PYRON_1G | 1 | 249 | -0.020653 | west | Y | 0.0024894 | -0.052671 | -0.00078943 | -0.02621 | 0.00078943 | west | N | 0.00078943 | 0
11059 | INADALE_ | 1 | 197 | -0.020653 | west | Y | 0.0024894 | -0.052671 | -0.00078943 | -0.02621 | 0.00078943 | west | N | 0.00078943 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.020245 | west | Y | 0.0028974 | -0.052263 | -0.00038143 | -0.025802 | 0.00038143 | west | N | 0.00038143 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.020245 | west | Y | 0.0028974 | -0.052263 | -0.00038143 | -0.025802 | 0.00038143 | west | N | 0.00038143 | 0
11147 | NOTREES_ | 1 | 149 | -0.019549 | west | Y | 0.0035934 | -0.051567 | 0.00031457 | -0.025106 | 0.00031457 | west | N | 0.00031457 | 0
11309 | BULLCREK | 1 | 180 | -0.020188 | west | Y | 0.0029544 | -0.052206 | -0.00032443 | -0.025745 | 0.00032443 | west | N | 0.00032443 | 0
11310 | BULLCREK | 1 | 180 | -0.020188 | west | Y | 0.0029544 | -0.052206 | -0.00032443 | -0.025745 | 0.00032443 | west | N | 0.00032443 | 0
11320 | COYOTE_1 | 1 | 225 | -0.020165 | west | Y | 0.0029774 | -0.052183 | -0.00030143 | -0.025722 | 0.00030143 | west | N | 0.00030143 | 0
11415 | LORAINE_ | 1 | 125 | -0.020479 | west | Y | 0.0026634 | -0.052497 | -0.00061543 | -0.026036 | 0.00061543 | west | N | 0.00061543 | 0
11416 | LORAINE_ | 1 | 125 | -0.020479 | west | Y | 0.0026634 | -0.052497 | -0.00061543 | -0.026036 | 0.00061543 | west | N | 0.00061543 | 0
11691 | KMICHICT | 1 | 140 | -0.02376 | north | N | -0.00061759 | -0.055778 | -0.0038964 | -0.029317 | 0.00061759 | North | N | 0.00061759 | 0
11692 | KMICHICT | 2 | 141 | -0.02376 | north | N | -0.00061759 | -0.055778 | -0.0038964 | -0.029317 | 0.00061759 | North | N | 0.00061759 | 0
11693 | KMICHIST | 3 | 309 | -0.02376 | north | N | -0.00061759 | -0.055778 | -0.0038964 | -0.029317 | 0.00061759 | North | N | 0.00061759 | 0
11694 | KMICHICT | 4 | 143 | -0.02376 | north | N | -0.00061759 | -0.055778 | -0.0038964 | -0.029317 | 0.00061759 | North | N | 0.00061759 | 0
11695 | KMICHICT | 5 | 144 | -0.02376 | north | N | -0.00061759 | -0.055778 | -0.0038964 | -0.029317 | 0.00061759 | North | N | 0.00061759 | 0
11696 | KMICHIST | 6 | 310 | -0.02376 | north | N | -0.00061759 | -0.055778 | -0.0038964 | -0.029317 | 0.00061759 | North | N | 0.00061759 | 0
12322 | ENNSTRAC | 1 | 196 | -0.024624 | north | Y | -0.0014816 | -0.056642 | -0.0047604 | -0.030181 | 0.0014816 | North | N | 0.0014816 | 0
12323 | ENNSTRAC | 2 | 111 | -0.024624 | north | Y | -0.0014816 | -0.056642 | -0.0047604 | -0.030181 | 0.0014816 | North | N | 0.0014816 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.023875 | north | N | -0.00073259 | -0.055893 | -0.0040114 | -0.029432 | 0.00073259 | North | N | 0.00073259 | 0
12411 | FPLEFR1A | 1 | 161 | -0.023602 | north | Y | -0.00045959 | -0.05562 | -0.0037384 | -0.029159 | 0.00045959 | North | N | 0.00045959 | 0
12412 | FPLEFR1B | 2 | 164 | -0.023602 | north | Y | -0.00045959 | -0.05562 | -0.0037384 | -0.029159 | 0.00045959 | North | N | 0.00045959 | 0
12413 | FPLEFR1C | 3 | 164 | -0.023602 | north | Y | -0.00045959 | -0.05562 | -0.0037384 | -0.029159 | 0.00045959 | North | N | 0.00045959 | 0
12414 | FPLEFR1S | 4 | 414 | -0.023602 | north | Y | -0.00045959 | -0.05562 | -0.0037384 | -0.029159 | 0.00045959 | North | N | 0.00045959 | 0
12421 | FPLEFR2A | 1 | 162 | -0.023602 | north | Y | -0.00045959 | -0.05562 | -0.0037384 | -0.029159 | 0.00045959 | North | N | 0.00045959 | 0
12422 | FPLEFR2B | 2 | 161 | -0.023602 | north | Y | -0.00045959 | -0.05562 | -0.0037384 | -0.029159 | 0.00045959 | North | N | 0.00045959 | 0
12423 | FPLEFR2C | 3 | 163 | -0.023602 | north | Y | -0.00045959 | -0.05562 | -0.0037384 | -0.029159 | 0.00045959 | North | N | 0.00045959 | 0
12424 | FPLEFR2S | 4 | 409 | -0.023602 | north | Y | -0.00045959 | -0.05562 | -0.0037384 | -0.029159 | 0.00045959 | North | N | 0.00045959 | 0
12440 | PARKD_1S | 1 | 0 | -0.023817 | north | N | -0.00067459 | -0.055835 | -0.0039534 | -0.029374 | 0.00067459 | North | N | 0.00067459 | 0
12449 | PARKD_2S | 1 | 0 | -0.023817 | north | N | -0.00067459 | -0.055835 | -0.0039534 | -0.029374 | 0.00067459 | North | N | 0.00067459 | 0
13116 | TGATEWAY | 1 | 148 | -0.022941 | north | N | 0.00020141 | -0.054959 | -0.0030774 | -0.028498 | 0.00020141 | North | N | 0.00020141 | 0
13117 | TGATEWAY | 2 | 130 | -0.022941 | north | N | 0.00020141 | -0.054959 | -0.0030774 | -0.028498 | 0.00020141 | North | N | 0.00020141 | 0
13118 | TGATEWAY | 3 | 145 | -0.022941 | north | N | 0.00020141 | -0.054959 | -0.0030774 | -0.028498 | 0.00020141 | North | N | 0.00020141 | 0
13119 | TGATEWAY | 4 | 399 | -0.022941 | north | N | 0.00020141 | -0.054959 | -0.0030774 | -0.028498 | 0.00020141 | North | N | 0.00020141 | 0
13131 | CALFREST | 1 | 150.7 | -0.021878 | north | Y | 0.0012644 | -0.053896 | -0.0020144 | -0.027435 | 0.0012644 | North | N | 0.0012644 | 0
13132 | CALFREST | 2 | 151 | -0.021878 | north | Y | 0.0012644 | -0.053896 | -0.0020144 | -0.027435 | 0.0012644 | North | N | 0.0012644 | 0
13133 | CALFREST | 3 | 177.4 | -0.021878 | north | Y | 0.0012644 | -0.053896 | -0.0020144 | -0.027435 | 0.0012644 | North | N | 0.0012644 | 0
13134 | CALFREST | 4 | 151.5 | -0.021923 | north | Y | 0.0012194 | -0.053941 | -0.0020594 | -0.02748 | 0.0012194 | North | N | 0.0012194 | 0
13135 | CALFREST | 5 | 152.3 | -0.021923 | north | Y | 0.0012194 | -0.053941 | -0.0020594 | -0.02748 | 0.0012194 | North | N | 0.0012194 | 0
13136 | CALFREST | 6 | 177.5 | -0.021923 | north | Y | 0.0012194 | -0.053941 | -0.0020594 | -0.02748 | 0.0012194 | North | N | 0.0012194 | 0
13432 | SANDOW_5 | 5 | 581 | -0.047161 | south | Y | -0.024019 | -0.079179 | -0.027297 | -0.052718 | 0.024019 | North | Y | 0.079179 | 32.0484
13691 | OAKGROVE | 1 | 855 | -0.016412 | north | Y | 0.0067304 | -0.04843 | 0.0034516 | -0.021969 | 0.0034516 | west | Y | 0.0067304 | 2.8034
13692 | OAKGROVE | 2 | 855 | -0.016412 | north | Y | 0.0067304 | -0.04843 | 0.0034516 | -0.021969 | 0.0034516 | west | Y | 0.0067304 | 2.8034
32798 | BRYN_TAM | 1 | 32 | -0.013749 | north | N | 0.0093934 | -0.045767 | 0.0061146 | -0.019306 | 0.0061146 | west | Y | 0.0093934 | 0
32883 | BRYN_DNS | 1 | 48 | -0.014771 | north | Y | 0.0083714 | -0.046789 | 0.0050926 | -0.020328 | 0.0050926 | west | Y | 0.0083714 | 0.15738
32884 | BRYN_DNS | 1 | 46 | -0.014771 | north | Y | 0.0083714 | -0.046789 | 0.0050926 | -0.020328 | 0.0050926 | west | Y | 0.0083714 | 0.15083
32886 | BRYN_ATK | MB | 12 | -0.013839 | north | Y | 0.0093034 | -0.045857 | 0.0060246 | -0.019396 | 0.0060246 | west | Y | 0.0093034 | 0
32887 | BRYN_ATK | MB | 51 | -0.013839 | north | Y | 0.0093034 | -0.045857 | 0.0060246 | -0.019396 | 0.0060246 | west | Y | 0.0093034 | 0
32888 | BRYN_ATK | 1 | 17 | -0.013839 | north | Y | 0.0093034 | -0.045857 | 0.0060246 | -0.019396 | 0.0060246 | west | Y | 0.0093034 | 0.05574
32890 | BRYN_ATK | MB | 22 | -0.013839 | north | Y | 0.0093034 | -0.045857 | 0.0060246 | -0.019396 | 0.0060246 | west | Y | 0.0093034 | 0
32891 | BRYN_ATK | MB | 25 | -0.013839 | north | Y | 0.0093034 | -0.045857 | 0.0060246 | -0.019396 | 0.0060246 | west | Y | 0.0093034 | 0
32892 | BRYN_DNS | 1 | 105 | -0.014771 | north | Y | 0.0083714 | -0.046789 | 0.0050926 | -0.020328 | 0.0050926 | west | Y | 0.0083714 | 0.34428
36998 | RDCNYNG1 | 1 | 84 | -0.020425 | west | Y | 0.0027174 | -0.052443 | -0.00056143 | -0.025982 | 0.00056143 | west | N | 0.00056143 | 0
38332 | WDWRDU2 | 1 | 80 | -0.017068 | west | Y | 0.0060744 | -0.049086 | 0.0027956 | -0.022625 | 0.0027956 | west | N | 0.0027956 | 0
38437 | TNSRBNMS | 1 | 150 | -0.017046 | west | Y | 0.0060964 | -0.049064 | 0.0028176 | -0.022603 | 0.0028176 | west | N | 0.0028176 | 0
38438 | TNSRBNMS | 1 | 150 | -0.017046 | west | Y | 0.0060964 | -0.049064 | 0.0028176 | -0.022603 | 0.0028176 | west | N | 0.0028176 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.005951 | houston | N | 0.029093 | -0.026067 | 0.025815 | 0.00039422 | 0.00039422 | houston | N | 0.00039422 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.005951 | houston | N | 0.029093 | -0.026067 | 0.025815 | 0.00039422 | 0.00039422 | houston | N | 0.00039422 | 0
38600 | TNBP_CGN | 5 | 53 | 0.005951 | houston | N | 0.029093 | -0.026067 | 0.025815 | 0.00039422 | 0.00039422 | houston | N | 0.00039422 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.005951 | houston | N | 0.029093 | -0.026067 | 0.025815 | 0.00039422 | 0.00039422 | houston | N | 0.00039422 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.005951 | houston | N | 0.029093 | -0.026067 | 0.025815 | 0.00039422 | 0.00039422 | houston | N | 0.00039422 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.005951 | houston | N | 0.029093 | -0.026067 | 0.025815 | 0.00039422 | 0.00039422 | houston | N | 0.00039422 | 0
38614 | TNBPAMCG | 4 | 96 | 0.005951 | houston | N | 0.029093 | -0.026067 | 0.025815 | 0.00039422 | 0.00039422 | houston | N | 0.00039422 | 0
38615 | TNBPAMCG | 1 | 244 | 0.005951 | houston | N | 0.029093 | -0.026067 | 0.025815 | 0.00039422 | 0.00039422 | houston | N | 0.00039422 | 0
38690 | TNBP_CGN | 3 | 40 | 0.005951 | houston | N | 0.029093 | -0.026067 | 0.025815 | 0.00039422 | 0.00039422 | houston | N | 0.00039422 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.005956 | houston | N | 0.029098 | -0.026062 | 0.02582 | 0.00039922 | 0.00039922 | houston | N | 0.00039922 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.005956 | houston | N | 0.029098 | -0.026062 | 0.02582 | 0.00039922 | 0.00039922 | houston | N | 0.00039922 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.005956 | houston | N | 0.029098 | -0.026062 | 0.02582 | 0.00039922 | 0.00039922 | houston | N | 0.00039922 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.005956 | houston | N | 0.029098 | -0.026062 | 0.02582 | 0.00039922 | 0.00039922 | houston | N | 0.00039922 | 0
39470 | TNDOWCGN | 1 | 32 | 0.005956 | houston | N | 0.029098 | -0.026062 | 0.02582 | 0.00039922 | 0.00039922 | houston | N | 0.00039922 | 0
39480 | TNDOWCGN | 1 | 30 | 0.005956 | houston | N | 0.029098 | -0.026062 | 0.02582 | 0.00039922 | 0.00039922 | houston | N | 0.00039922 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.009473 | houston | N | 0.032615 | -0.022545 | 0.029337 | 0.0039162 | 0.0039162 | houston | N | 0.0039162 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.009473 | houston | N | 0.032615 | -0.022545 | 0.029337 | 0.0039162 | 0.0039162 | houston | N | 0.0039162 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.009473 | houston | N | 0.032615 | -0.022545 | 0.029337 | 0.0039162 | 0.0039162 | houston | N | 0.0039162 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.009473 | houston | N | 0.032615 | -0.022545 | 0.029337 | 0.0039162 | 0.0039162 | houston | N | 0.0039162 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.016412 | north | Y | 0.0067304 | -0.04843 | 0.0034516 | -0.021969 | 0.0034516 | west | Y | 0.0067304 | 0.49937
39970 | TNTNPONE | 1 | 153 | -0.016412 | north | Y | 0.0067304 | -0.04843 | 0.0034516 | -0.021969 | 0.0034516 | west | Y | 0.0067304 | 0.50166
48500 | APD_GT1_ | 1 | 136 | 0.00381 | houston | N | 0.026952 | -0.028208 | 0.023674 | -0.0017468 | 0.0017468 | houston | N | 0.0017468 | 0
48510 | AK_GT1__ | 1 | 33 | 0.007124 | houston | N | 0.030266 | -0.024894 | 0.026988 | 0.0015672 | 0.0015672 | houston | N | 0.0015672 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.003805 | houston | Y | 0.026947 | -0.028213 | 0.023669 | -0.0017518 | 0.0017518 | houston | N | 0.0017518 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.003805 | houston | Y | 0.026947 | -0.028213 | 0.023669 | -0.0017518 | 0.0017518 | houston | N | 0.0017518 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.003805 | houston | Y | 0.026947 | -0.028213 | 0.023669 | -0.0017518 | 0.0017518 | houston | N | 0.0017518 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.003805 | houston | Y | 0.026947 | -0.028213 | 0.023669 | -0.0017518 | 0.0017518 | houston | N | 0.0017518 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.010075 | houston | N | 0.033217 | -0.021943 | 0.029939 | 0.0045182 | 0.0045182 | houston | N | 0.0045182 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.010075 | houston | N | 0.033217 | -0.021943 | 0.029939 | 0.0045182 | 0.0045182 | houston | N | 0.0045182 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.007302 | houston | N | 0.030444 | -0.024716 | 0.027166 | 0.0017452 | 0.0017452 | houston | N | 0.0017452 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.007302 | houston | N | 0.030444 | -0.024716 | 0.027166 | 0.0017452 | 0.0017452 | houston | N | 0.0017452 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.007302 | houston | N | 0.030444 | -0.024716 | 0.027166 | 0.0017452 | 0.0017452 | houston | N | 0.0017452 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.004613 | houston | N | 0.027755 | -0.027405 | 0.024477 | -0.00094378 | 0.00094378 | houston | N | 0.00094378 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.004613 | houston | N | 0.027755 | -0.027405 | 0.024477 | -0.00094378 | 0.00094378 | houston | N | 0.00094378 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.004613 | houston | N | 0.027755 | -0.027405 | 0.024477 | -0.00094378 | 0.00094378 | houston | N | 0.00094378 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.004613 | houston | N | 0.027755 | -0.027405 | 0.024477 | -0.00094378 | 0.00094378 | houston | N | 0.00094378 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.004092 | houston | N | 0.027234 | -0.027926 | 0.023956 | -0.0014648 | 0.0014648 | houston | N | 0.0014648 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.004092 | houston | N | 0.027234 | -0.027926 | 0.023956 | -0.0014648 | 0.0014648 | houston | N | 0.0014648 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.004769 | houston | N | 0.027911 | -0.027249 | 0.024633 | -0.00078778 | 0.00078778 | houston | N | 0.00078778 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.004769 | houston | N | 0.027911 | -0.027249 | 0.024633 | -0.00078778 | 0.00078778 | houston | N | 0.00078778 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.004769 | houston | N | 0.027911 | -0.027249 | 0.024633 | -0.00078778 | 0.00078778 | houston | N | 0.00078778 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.004769 | houston | N | 0.027911 | -0.027249 | 0.024633 | -0.00078778 | 0.00078778 | houston | N | 0.00078778 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.004769 | houston | N | 0.027911 | -0.027249 | 0.024633 | -0.00078778 | 0.00078778 | houston | N | 0.00078778 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.003157 | houston | Y | 0.026299 | -0.028861 | 0.023021 | -0.0023998 | 0.0023998 | houston | N | 0.0023998 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.00342 | houston | Y | 0.026562 | -0.028598 | 0.023284 | -0.0021368 | 0.0021368 | houston | N | 0.0021368 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.003079 | houston | Y | 0.026221 | -0.028939 | 0.022943 | -0.0024778 | 0.0024778 | houston | N | 0.0024778 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.003079 | houston | Y | 0.026221 | -0.028939 | 0.022943 | -0.0024778 | 0.0024778 | houston | N | 0.0024778 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.003079 | houston | Y | 0.026221 | -0.028939 | 0.022943 | -0.0024778 | 0.0024778 | houston | N | 0.0024778 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.001617 | houston | N | 0.024759 | -0.030401 | 0.021481 | -0.0039398 | 0.0039398 | houston | N | 0.0039398 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.003759 | houston | N | 0.026901 | -0.028259 | 0.023623 | -0.0017978 | 0.0017978 | houston | N | 0.0017978 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.003759 | houston | N | 0.026901 | -0.028259 | 0.023623 | -0.0017978 | 0.0017978 | houston | N | 0.0017978 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.002893 | houston | N | 0.026035 | -0.029125 | 0.022757 | -0.0026638 | 0.0026638 | houston | N | 0.0026638 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.002893 | houston | N | 0.026035 | -0.029125 | 0.022757 | -0.0026638 | 0.0026638 | houston | N | 0.0026638 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.002893 | houston | N | 0.026035 | -0.029125 | 0.022757 | -0.0026638 | 0.0026638 | houston | N | 0.0026638 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.002893 | houston | N | 0.026035 | -0.029125 | 0.022757 | -0.0026638 | 0.0026638 | houston | N | 0.0026638 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.004075 | houston | N | 0.027217 | -0.027943 | 0.023939 | -0.0014818 | 0.0014818 | houston | N | 0.0014818 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.004075 | houston | N | 0.027217 | -0.027943 | 0.023939 | -0.0014818 | 0.0014818 | houston | N | 0.0014818 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.004075 | houston | N | 0.027217 | -0.027943 | 0.023939 | -0.0014818 | 0.0014818 | houston | N | 0.0014818 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.004075 | houston | N | 0.027217 | -0.027943 | 0.023939 | -0.0014818 | 0.0014818 | houston | N | 0.0014818 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.004248 | houston | N | 0.02739 | -0.02777 | 0.024112 | -0.0013088 | 0.0013088 | houston | N | 0.0013088 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.004248 | houston | N | 0.02739 | -0.02777 | 0.024112 | -0.0013088 | 0.0013088 | houston | N | 0.0013088 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.004248 | houston | N | 0.02739 | -0.02777 | 0.024112 | -0.0013088 | 0.0013088 | houston | N | 0.0013088 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.004248 | houston | N | 0.02739 | -0.02777 | 0.024112 | -0.0013088 | 0.0013088 | houston | N | 0.0013088 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.004248 | houston | N | 0.02739 | -0.02777 | 0.024112 | -0.0013088 | 0.0013088 | houston | N | 0.0013088 | 0
48651 | EP_1_2 | 1 | 5 | 0.003169 | houston | N | 0.026311 | -0.028849 | 0.023033 | -0.0023878 | 0.0023878 | houston | N | 0.0023878 | 0
48651 | EP_1_2 | 2 | 21 | 0.003169 | houston | N | 0.026311 | -0.028849 | 0.023033 | -0.0023878 | 0.0023878 | houston | N | 0.0023878 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.008575 | north | N | 0.014567 | -0.040593 | 0.011289 | -0.014132 | 0.011289 | west | Y | 0.014567 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.008575 | north | N | 0.014567 | -0.040593 | 0.011289 | -0.014132 | 0.011289 | west | Y | 0.014567 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.008575 | north | N | 0.014567 | -0.040593 | 0.011289 | -0.014132 | 0.011289 | west | Y | 0.014567 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.008575 | north | N | 0.014567 | -0.040593 | 0.011289 | -0.014132 | 0.011289 | west | Y | 0.014567 | 0
48690 | GBY_GN5_ | 5 | 398 | 0.002822 | houston | Y | 0.025964 | -0.029196 | 0.022686 | -0.0027348 | 0.0027348 | houston | N | 0.0027348 | 0
48691 | GBY_7374 | A | 46 | 0.004365 | houston | Y | 0.027507 | -0.027653 | 0.024229 | -0.0011918 | 0.0011918 | houston | N | 0.0011918 | 0
48691 | GBY_7374 | B | 46 | 0.004365 | houston | Y | 0.027507 | -0.027653 | 0.024229 | -0.0011918 | 0.0011918 | houston | N | 0.0011918 | 0
48692 | GBY_8182 | C | 46 | 0.004365 | houston | Y | 0.027507 | -0.027653 | 0.024229 | -0.0011918 | 0.0011918 | houston | N | 0.0011918 | 0
48692 | GBY_8182 | D | 55 | 0.004365 | houston | Y | 0.027507 | -0.027653 | 0.024229 | -0.0011918 | 0.0011918 | houston | N | 0.0011918 | 0
48693 | GBY_8384 | E | 55 | 0.004365 | houston | Y | 0.027507 | -0.027653 | 0.024229 | -0.0011918 | 0.0011918 | houston | N | 0.0011918 | 0
48693 | GBY_8384 | F | 54 | 0.004365 | houston | Y | 0.027507 | -0.027653 | 0.024229 | -0.0011918 | 0.0011918 | houston | N | 0.0011918 | 0
48721 | LEG_1___ | 1 | 827 | -0.018647 | north | Y | 0.0044954 | -0.050665 | 0.0012166 | -0.024204 | 0.0012166 | west | Y | 0.0044954 | 2.7116
48722 | LEG_2___ | 2 | 819 | -0.018647 | north | Y | 0.0044954 | -0.050665 | 0.0012166 | -0.024204 | 0.0012166 | west | Y | 0.0044954 | 2.6854
48730 | MNS_GT | 1 | 46.1 | 0.007431 | houston | N | 0.030573 | -0.024587 | 0.027295 | 0.0018742 | 0.0018742 | houston | N | 0.0018742 | 0
48731 | CBE_GT1 | 1 | 76 | 0.014553 | houston | Y | 0.037695 | -0.017465 | 0.034417 | 0.0089962 | 0.0089962 | houston | N | 0.0089962 | 0
48732 | CBE_GT2 | 1 | 76 | 0.014553 | houston | Y | 0.037695 | -0.017465 | 0.034417 | 0.0089962 | 0.0089962 | houston | N | 0.0089962 | 0
48733 | CBE_ST12 | 1 | 105 | 0.014553 | houston | Y | 0.037695 | -0.017465 | 0.034417 | 0.0089962 | 0.0089962 | houston | N | 0.0089962 | 0
48734 | CBE_GT3 | 1 | 74 | 0.014553 | houston | Y | 0.037695 | -0.017465 | 0.034417 | 0.0089962 | 0.0089962 | houston | N | 0.0089962 | 0
48735 | CBE_GT4 | 1 | 74 | 0.014553 | houston | Y | 0.037695 | -0.017465 | 0.034417 | 0.0089962 | 0.0089962 | houston | N | 0.0089962 | 0
48736 | CBE_ST34 | 1 | 102 | 0.014553 | houston | Y | 0.037695 | -0.017465 | 0.034417 | 0.0089962 | 0.0089962 | houston | N | 0.0089962 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.00407 | houston | N | 0.027212 | -0.027948 | 0.023934 | -0.0014868 | 0.0014868 | houston | N | 0.0014868 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.00407 | houston | N | 0.027212 | -0.027948 | 0.023934 | -0.0014868 | 0.0014868 | houston | N | 0.0014868 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.00407 | houston | N | 0.027212 | -0.027948 | 0.023934 | -0.0014868 | 0.0014868 | houston | N | 0.0014868 | 0
48761 | PR_GT1__ | 1 | 35 | 0.004174 | houston | N | 0.027316 | -0.027844 | 0.024038 | -0.0013828 | 0.0013828 | houston | N | 0.0013828 | 0
48772 | PHR_GN2_ | MB | 459 | 0.00517 | houston | Y | 0.028312 | -0.026848 | 0.025034 | -0.00038678 | 0.00038678 | houston | N | 0.00038678 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.003165 | houston | N | 0.026307 | -0.028853 | 0.023029 | -0.0023918 | 0.0023918 | houston | N | 0.0023918 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.003165 | houston | N | 0.026307 | -0.028853 | 0.023029 | -0.0023918 | 0.0023918 | houston | N | 0.0023918 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.003165 | houston | N | 0.026307 | -0.028853 | 0.023029 | -0.0023918 | 0.0023918 | houston | N | 0.0023918 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.003165 | houston | N | 0.026307 | -0.028853 | 0.023029 | -0.0023918 | 0.0023918 | houston | N | 0.0023918 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.003165 | houston | N | 0.026307 | -0.028853 | 0.023029 | -0.0023918 | 0.0023918 | houston | N | 0.0023918 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.003165 | houston | N | 0.026307 | -0.028853 | 0.023029 | -0.0023918 | 0.0023918 | houston | N | 0.0023918 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.003165 | houston | N | 0.026307 | -0.028853 | 0.023029 | -0.0023918 | 0.0023918 | houston | N | 0.0023918 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.001617 | houston | N | 0.024759 | -0.030401 | 0.021481 | -0.0039398 | 0.0039398 | houston | N | 0.0039398 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.001617 | houston | N | 0.024759 | -0.030401 | 0.021481 | -0.0039398 | 0.0039398 | houston | N | 0.0039398 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.001617 | houston | N | 0.024759 | -0.030401 | 0.021481 | -0.0039398 | 0.0039398 | houston | N | 0.0039398 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.001617 | houston | N | 0.024759 | -0.030401 | 0.021481 | -0.0039398 | 0.0039398 | houston | N | 0.0039398 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.003105 | houston | N | 0.026247 | -0.028913 | 0.022969 | -0.0024518 | 0.0024518 | houston | N | 0.0024518 | 0
48820 | SHELLG1_ | 1 | 71 | 0.003972 | houston | N | 0.027114 | -0.028046 | 0.023836 | -0.0015848 | 0.0015848 | houston | N | 0.0015848 | 0
48821 | SHELLG2 | 2 | 72 | 0.003972 | houston | N | 0.027114 | -0.028046 | 0.023836 | -0.0015848 | 0.0015848 | houston | N | 0.0015848 | 0
48822 | SHELLG3_ | 1 | 39 | 0.003972 | houston | N | 0.027114 | -0.028046 | 0.023836 | -0.0015848 | 0.0015848 | houston | N | 0.0015848 | 0
48822 | SHELLG3_ | 2 | 30 | 0.003972 | houston | N | 0.027114 | -0.028046 | 0.023836 | -0.0015848 | 0.0015848 | houston | N | 0.0015848 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.004322 | houston | N | 0.027464 | -0.027696 | 0.024186 | -0.0012348 | 0.0012348 | houston | N | 0.0012348 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.004322 | houston | N | 0.027464 | -0.027696 | 0.024186 | -0.0012348 | 0.0012348 | houston | N | 0.0012348 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.004077 | houston | N | 0.027219 | -0.027941 | 0.023941 | -0.0014798 | 0.0014798 | houston | N | 0.0014798 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.004097 | houston | Y | 0.027239 | -0.027921 | 0.023961 | -0.0014598 | 0.0014598 | houston | N | 0.0014598 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.004102 | houston | Y | 0.027244 | -0.027916 | 0.023966 | -0.0014548 | 0.0014548 | houston | N | 0.0014548 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.004079 | houston | Y | 0.027221 | -0.027939 | 0.023943 | -0.0014778 | 0.0014778 | houston | N | 0.0014778 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.004073 | houston | Y | 0.027215 | -0.027945 | 0.023937 | -0.0014838 | 0.0014838 | houston | N | 0.0014838 | 0
48855 | SRB_GT21 | B2 | 12 | 0.004106 | houston | Y | 0.027248 | -0.027912 | 0.02397 | -0.0014508 | 0.0014508 | houston | N | 0.0014508 | 0
48855 | SRB_GT21 | MB | 18 | 0.004106 | houston | Y | 0.027248 | -0.027912 | 0.02397 | -0.0014508 | 0.0014508 | houston | N | 0.0014508 | 0
48865 | TECO_GT1 | 1 | 50 | 0.005488 | houston | Y | 0.02863 | -0.02653 | 0.025352 | -6.8775e-05 | 6.8775e-05 | houston | N | 6.8775e-05 | 0
48873 | THW_ST3_ | 3 | 104 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48874 | THW_ST4_ | 4 | 104 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48875 | THW_3132 | A | 54 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48875 | THW_3132 | B | 53 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48877 | THW_3334 | C | 54 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48877 | THW_3334 | D | 57 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48879 | THW_4142 | E | 54 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48879 | THW_4142 | F | 54 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48881 | THW_4344 | G | 58 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48881 | THW_4344 | H | 58 | 0.003499 | houston | Y | 0.026641 | -0.028519 | 0.023363 | -0.0020578 | 0.0020578 | houston | N | 0.0020578 | 0
48883 | THW_GT1_ | B2 | 12 | 0.00326 | houston | Y | 0.026402 | -0.028758 | 0.023124 | -0.0022968 | 0.0022968 | houston | N | 0.0022968 | 0
48885 | THW_5152 | A | 56 | 0.002706 | houston | Y | 0.025848 | -0.029312 | 0.02257 | -0.0028508 | 0.0028508 | houston | N | 0.0028508 | 0
48885 | THW_5152 | B | 59 | 0.002706 | houston | Y | 0.025848 | -0.029312 | 0.02257 | -0.0028508 | 0.0028508 | houston | N | 0.0028508 | 0
48886 | THW_5354 | C | 56 | 0.002706 | houston | Y | 0.025848 | -0.029312 | 0.02257 | -0.0028508 | 0.0028508 | houston | N | 0.0028508 | 0
48886 | THW_5354 | D | 56 | 0.002706 | houston | Y | 0.025848 | -0.029312 | 0.02257 | -0.0028508 | 0.0028508 | houston | N | 0.0028508 | 0
48887 | THW_5556 | E | 59 | 0.002706 | houston | Y | 0.025848 | -0.029312 | 0.02257 | -0.0028508 | 0.0028508 | houston | N | 0.0028508 | 0
48887 | THW_5556 | F | 56 | 0.002706 | houston | Y | 0.025848 | -0.029312 | 0.02257 | -0.0028508 | 0.0028508 | houston | N | 0.0028508 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.013781 | houston | Y | 0.036923 | -0.018237 | 0.033645 | 0.0082242 | 0.0082242 | houston | N | 0.0082242 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.006957 | houston | Y | 0.030099 | -0.025061 | 0.026821 | 0.0014002 | 0.0014002 | houston | N | 0.0014002 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.006957 | houston | Y | 0.030099 | -0.025061 | 0.026821 | 0.0014002 | 0.0014002 | houston | N | 0.0014002 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.006957 | houston | Y | 0.030099 | -0.025061 | 0.026821 | 0.0014002 | 0.0014002 | houston | N | 0.0014002 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.006957 | houston | Y | 0.030099 | -0.025061 | 0.026821 | 0.0014002 | 0.0014002 | houston | N | 0.0014002 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.006957 | houston | N | 0.030099 | -0.025061 | 0.026821 | 0.0014002 | 0.0014002 | houston | N | 0.0014002 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.007319 | houston | Y | 0.030461 | -0.024699 | 0.027183 | 0.0017622 | 0.0017622 | houston | N | 0.0017622 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.007319 | houston | Y | 0.030461 | -0.024699 | 0.027183 | 0.0017622 | 0.0017622 | houston | N | 0.0017622 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.007319 | houston | Y | 0.030461 | -0.024699 | 0.027183 | 0.0017622 | 0.0017622 | houston | N | 0.0017622 | 0
48929 | WAPGT21_ | B1 | 13 | 0.006957 | houston | Y | 0.030099 | -0.025061 | 0.026821 | 0.0014002 | 0.0014002 | houston | N | 0.0014002 | 0
48940 | WARVUE_G | G1 | 12 | 0.003163 | houston | Y | 0.026305 | -0.028855 | 0.023027 | -0.0023938 | 0.0023938 | houston | N | 0.0023938 | 0
49803 | EXN_15GT | 1 | 34 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49826 | EXN938GT | 5 | 45.9 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49828 | EXN941GT | 10 | 17.7 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49829 | EXN942GT | 11 | 20.4 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49830 | EXN943GT | 12 | 19.9 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49831 | EXN944GT | 13 | 35 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49832 | EXN945GT | 9 | 18 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49837 | EXN_GT | 4 | 85.4 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49838 | EXN_14GT | 14 | 148 | 0.003355 | houston | N | 0.026497 | -0.028663 | 0.023219 | -0.0022018 | 0.0022018 | houston | N | 0.0022018 | 0
49851 | DOW17000 | 37 | 62 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49858 | DOW38100 | 31 | 71.4 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49859 | DOW38200 | 33 | 45 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49860 | DOW38300 | 32 | 101 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49862 | DOW39100 | 36 | 86 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49863 | DOW39200 | 35 | 88 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49865 | DOW41000 | 41 | 50 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49866 | DOW42000 | 42 | 18 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49869 | DOW49000 | 45 | 94 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49870 | DOW61000 | 61 | 70 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49871 | DOW62000 | 62 | 63 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49872 | DOW63000 | 63 | 72 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49873 | DOW64000 | 64 | 64.8 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49876 | DOW65000 | 65 | 101 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49877 | DOW66000 | 66 | 97 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49878 | DOW67000 | 67 | 103 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49882 | DOW81000 | 81 | 76 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49884 | DOW82000 | 82 | 80 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49885 | DOW83000 | 83 | 80 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
49886 | DOW84000 | 84 | 171 | 0.010816 | houston | N | 0.033958 | -0.021202 | 0.03068 | 0.0052592 | 0.0052592 | houston | N | 0.0052592 | 0
58909 | PEARSALL | 1 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58909 | PEARSALL | 2 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58909 | PEARSALL | 3 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58909 | PEARSALL | 4 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58909 | PEARSALL | 5 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58909 | PEARSALL | 6 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58919 | PEARSALL | 1 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58919 | PEARSALL | 2 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58919 | PEARSALL | 3 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58919 | PEARSALL | 4 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58919 | PEARSALL | 5 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58919 | PEARSALL | 6 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58929 | PEARSALL | 1 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58929 | PEARSALL | 2 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58929 | PEARSALL | 3 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58929 | PEARSALL | 4 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58929 | PEARSALL | 5 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58929 | PEARSALL | 6 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58949 | PEARSALL | 1 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58949 | PEARSALL | 2 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58949 | PEARSALL | 3 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58949 | PEARSALL | 4 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58949 | PEARSALL | 5 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
58949 | PEARSALL | 6 | 8.4 | 0.029009 | south | Y | 0.052151 | -0.0030094 | 0.048873 | 0.023452 | 0.0030094 | south | N | 0.0030094 | 0
60000 | DSKY2 | 1 | 76.5 | -0.016042 | west | Y | 0.0071004 | -0.04806 | 0.0038216 | -0.021599 | 0.0038216 | west | N | 0.0038216 | 0
60003 | KING_NE1 | 1 | 80 | -0.01711 | west | Y | 0.0060324 | -0.049128 | 0.0027536 | -0.022667 | 0.0027536 | west | N | 0.0027536 | 0
60005 | KING_SE1 | 1 | 40 | -0.01711 | west | Y | 0.0060324 | -0.049128 | 0.0027536 | -0.022667 | 0.0027536 | west | N | 0.0027536 | 0
60007 | KING_SW1 | 1 | 80 | -0.01728 | west | Y | 0.0058624 | -0.049298 | 0.0025836 | -0.022837 | 0.0025836 | west | N | 0.0025836 | 0
60016 | WOODWRD1 | 1 | 80 | -0.017073 | west | Y | 0.0060694 | -0.049091 | 0.0027906 | -0.02263 | 0.0027906 | west | N | 0.0027906 | 0
60017 | ORNNWP1 | 1 | 80 | -0.016193 | west | Y | 0.0069494 | -0.048211 | 0.0036706 | -0.02175 | 0.0036706 | west | N | 0.0036706 | 0
60018 | DSKY1 | 1 | 84 | -0.015906 | west | Y | 0.0072364 | -0.047924 | 0.0039576 | -0.021463 | 0.0039576 | west | N | 0.0039576 | 0
60019 | KING_NW1 | 1 | 80 | -0.01728 | west | Y | 0.0058624 | -0.049298 | 0.0025836 | -0.022837 | 0.0025836 | west | N | 0.0025836 | 0
60057 | CALLAHAN | 1 | 114 | 0.037109 | south | Y | 0.060251 | 0.0050906 | 0.056973 | 0.031552 | 0.0050906 | south | N | 0.0050906 | 0
60058 | BUFF_GAP | 1 | 120 | -0.020067 | west | Y | 0.0030754 | -0.052085 | -0.00020343 | -0.025624 | 0.00020343 | west | N | 0.00020343 | 0
60060 | CIRELLO | 1 | 233 | -0.020067 | west | Y | 0.0030754 | -0.052085 | -0.00020343 | -0.025624 | 0.00020343 | west | N | 0.00020343 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.020067 | west | Y | 0.0030754 | -0.052085 | -0.00020343 | -0.025624 | 0.00020343 | west | N | 0.00020343 | 0
60066 | H_HOLLOW | 1 | 222 | 0.037109 | south | Y | 0.060251 | 0.0050906 | 0.056973 | 0.031552 | 0.0050906 | south | N | 0.0050906 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.037109 | south | Y | 0.060251 | 0.0050906 | 0.056973 | 0.031552 | 0.0050906 | south | N | 0.0050906 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.037109 | south | Y | 0.060251 | 0.0050906 | 0.056973 | 0.031552 | 0.0050906 | south | N | 0.0050906 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.037109 | south | Y | 0.060251 | 0.0050906 | 0.056973 | 0.031552 | 0.0050906 | south | N | 0.0050906 | 0
60074 | HORSH5 | 1 | 100 | 0.037109 | south | Y | 0.060251 | 0.0050906 | 0.056973 | 0.031552 | 0.0050906 | south | N | 0.0050906 | 0
60081 | WHRLWIND | 1 | 60 | -0.021071 | west | Y | 0.0020714 | -0.053089 | -0.0012074 | -0.026628 | 0.0012074 | west | N | 0.0012074 | 0
60201 | RIO DRCS | F | 0 | 0.03115 | south | N | 0.054292 | -0.00086841 | 0.051014 | 0.025593 | 0.00086841 | south | N | 0.00086841 | 0
60202 | FRIEND_R | F | 0 | -0.01132 | west | N | 0.011822 | -0.043338 | 0.0085436 | -0.016877 | 0.0085436 | west | N | 0.0085436 | 0
60203 | PRES0A | BT | 4.8 | -0.017918 | west | N | 0.0052244 | -0.049936 | 0.0019456 | -0.023475 | 0.0019456 | west | N | 0.0019456 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.020605 | west | Y | 0.0025374 | -0.052623 | -0.00074143 | -0.026162 | 0.00074143 | west | N | 0.00074143 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.020605 | west | Y | 0.0025374 | -0.052623 | -0.00074143 | -0.026162 | 0.00074143 | west | N | 0.00074143 | 0
71057 | L_SWEETW | W1 | 135 | -0.020605 | west | Y | 0.0025374 | -0.052623 | -0.00074143 | -0.026162 | 0.00074143 | west | N | 0.00074143 | 0
71059 | L_SWEETW | W1 | 119 | -0.020605 | west | Y | 0.0025374 | -0.052623 | -0.00074143 | -0.026162 | 0.00074143 | west | N | 0.00074143 | 0
71060 | L_SWEETW | W1 | 105 | -0.020605 | west | Y | 0.0025374 | -0.052623 | -0.00074143 | -0.026162 | 0.00074143 | west | N | 0.00074143 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.020605 | west | Y | 0.0025374 | -0.052623 | -0.00074143 | -0.026162 | 0.00074143 | west | N | 0.00074143 | 0
76031 | L_GASCCR | W1 | 150 | -0.019794 | west | Y | 0.0033484 | -0.051812 | 6.957e-05 | -0.025351 | 6.957e-05 | west | N | 6.957e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.019687 | west | Y | 0.0034554 | -0.051705 | 0.00017657 | -0.025244 | 0.00017657 | west | N | 0.00017657 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.019687 | west | Y | 0.0034554 | -0.051705 | 0.00017657 | -0.025244 | 0.00017657 | west | N | 0.00017657 | 0
76096 | L_CAPRSI | W1 | 186 | -0.019687 | west | Y | 0.0034554 | -0.051705 | 0.00017657 | -0.025244 | 0.00017657 | west | N | 0.00017657 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.019687 | west | Y | 0.0034554 | -0.051705 | 0.00017657 | -0.025244 | 0.00017657 | west | N | 0.00017657 | 0
80003 | MILHWYS | F | 0 | 0.026805 | south | N | 0.049947 | -0.0052134 | 0.046669 | 0.021248 | 0.0052134 | south | N | 0.0052134 | 0
80010 | EPLVT1 | F | 0 | 0.021697 | south | N | 0.044839 | -0.010321 | 0.041561 | 0.01614 | 0.010321 | south | N | 0.010321 | 0
80012 | LAR | F | 0 | 0.0287 | south | N | 0.051842 | -0.0033184 | 0.048564 | 0.023143 | 0.0033184 | south | N | 0.0033184 | 0
80051 | FORPVCM0 | 8 | 28 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
80053 | FOR69CG0 | 10 | 74 | 0.023988 | south | N | 0.04713 | -0.0080304 | 0.043852 | 0.018431 | 0.0080304 | south | N | 0.0080304 | 0
80080 | GWINDT11 | 1 | 94 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80080 | GWINDT11 | 2 | 41 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80080 | GWINDT11 | 3 | 38 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80080 | GWINDT11 | 4 | 19 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80081 | GWINDT21 | 1 | 94 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80081 | GWINDT21 | 2 | 36 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80081 | GWINDT21 | 3 | 43 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80081 | GWINDT21 | 4 | 22 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80137 | CSDR89 | 8 | 39 | 0.025056 | south | N | 0.048198 | -0.0069624 | 0.04492 | 0.019499 | 0.0069624 | south | N | 0.0069624 | 0
80137 | CSDR89 | 9 | 15 | 0.025056 | south | N | 0.048198 | -0.0069624 | 0.04492 | 0.019499 | 0.0069624 | south | N | 0.0069624 | 0
80138 | CSDR7 | 7 | 7 | 0.025056 | south | N | 0.048198 | -0.0069624 | 0.04492 | 0.019499 | 0.0069624 | south | N | 0.0069624 | 0
80139 | CSDR56 | 5 | 15 | 0.025056 | south | N | 0.048198 | -0.0069624 | 0.04492 | 0.019499 | 0.0069624 | south | N | 0.0069624 | 0
80139 | CSDR56 | 6 | 39 | 0.025056 | south | N | 0.048198 | -0.0069624 | 0.04492 | 0.019499 | 0.0069624 | south | N | 0.0069624 | 0
80140 | CSDR11 | 11 | 39 | 0.025056 | south | N | 0.048198 | -0.0069624 | 0.04492 | 0.019499 | 0.0069624 | south | N | 0.0069624 | 0
80180 | PNSCALT1 | 1 | 148 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80180 | PNSCALT1 | 2 | 50 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80181 | PNSCALT2 | 1 | 55 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80181 | PNSCALT2 | 2 | 50 | 0.026782 | south | Y | 0.049924 | -0.0052364 | 0.046646 | 0.021225 | 0.0052364 | south | N | 0.0052364 | 0
80223 | REYSHR G | 1 | 12 | 0.026151 | south | N | 0.049293 | -0.0058674 | 0.046015 | 0.020594 | 0.0058674 | south | N | 0.0058674 | 0
80224 | VISTRONG | 1 | 15 | 0.025415 | south | N | 0.048557 | -0.0066034 | 0.045279 | 0.019858 | 0.0066034 | south | N | 0.0066034 | 0
80225 | VISTRONG | 2 | 23 | 0.025415 | south | N | 0.048557 | -0.0066034 | 0.045279 | 0.019858 | 0.0066034 | south | N | 0.0066034 | 0
80226 | ALCOA G | 1 | 48 | 0.024243 | south | N | 0.047385 | -0.0077754 | 0.044107 | 0.018686 | 0.0077754 | south | N | 0.0077754 | 0
80227 | AIRCO G | 1 | 8 | 0.025186 | south | N | 0.048328 | -0.0068324 | 0.04505 | 0.019629 | 0.0068324 | south | N | 0.0068324 | 0
80261 | NBEC81A | 1 | 180 | 0.026481 | south | Y | 0.049623 | -0.0055374 | 0.046345 | 0.020924 | 0.0055374 | south | N | 0.0055374 | 0
80262 | NBEC91A | 1 | 180 | 0.026471 | south | Y | 0.049613 | -0.0055474 | 0.046335 | 0.020914 | 0.0055474 | south | N | 0.0055474 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.026541 | south | Y | 0.049683 | -0.0054774 | 0.046405 | 0.020984 | 0.0054774 | south | N | 0.0054774 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.026541 | south | Y | 0.049683 | -0.0054774 | 0.046405 | 0.020984 | 0.0054774 | south | N | 0.0054774 | 0
80265 | LARECU40 | 4 | 100 | 0.028703 | south | Y | 0.051845 | -0.0033154 | 0.048567 | 0.023146 | 0.0033154 | south | N | 0.0033154 | 0
80266 | LARECU50 | 5 | 100 | 0.028703 | south | Y | 0.051845 | -0.0033154 | 0.048567 | 0.023146 | 0.0033154 | south | N | 0.0033154 | 0
80291 | PAPALOTE | 1 | 25 | 0.026276 | south | Y | 0.049418 | -0.0057424 | 0.04614 | 0.020719 | 0.0057424 | south | N | 0.0057424 | 0
80291 | PAPALOTE | 2 | 25 | 0.026276 | south | Y | 0.049418 | -0.0057424 | 0.04614 | 0.020719 | 0.0057424 | south | N | 0.0057424 | 0
80291 | PAPALOTE | 3 | 25 | 0.026276 | south | Y | 0.049418 | -0.0057424 | 0.04614 | 0.020719 | 0.0057424 | south | N | 0.0057424 | 0
80291 | PAPALOTE | 4 | 16 | 0.026276 | south | Y | 0.049418 | -0.0057424 | 0.04614 | 0.020719 | 0.0057424 | south | N | 0.0057424 | 0
80294 | PAPALOTE | 5 | 25 | 0.026276 | south | Y | 0.049418 | -0.0057424 | 0.04614 | 0.020719 | 0.0057424 | south | N | 0.0057424 | 0
80294 | PAPALOTE | 6 | 25 | 0.026276 | south | Y | 0.049418 | -0.0057424 | 0.04614 | 0.020719 | 0.0057424 | south | N | 0.0057424 | 0
80294 | PAPALOTE | 7 | 25 | 0.026276 | south | Y | 0.049418 | -0.0057424 | 0.04614 | 0.020719 | 0.0057424 | south | N | 0.0057424 | 0
80294 | PAPALOTE | 8 | 15 | 0.026276 | south | Y | 0.049418 | -0.0057424 | 0.04614 | 0.020719 | 0.0057424 | south | N | 0.0057424 | 0
86104 | CID-138 | EQ | 0 | 0.028703 | south | N | 0.051845 | -0.0033154 | 0.048567 | 0.023146 | 0.0033154 | south | N | 0.0033154 | 0
86105 | CID-230 | EQ | 500 | 0.028703 | south | N | 0.051845 | -0.0033154 | 0.048567 | 0.023146 | 0.0033154 | south | N | 0.0033154 | 0
86106 | CUF-230 | EQ | 500 | 0.028703 | south | N | 0.051845 | -0.0033154 | 0.048567 | 0.023146 | 0.0033154 | south | N | 0.0033154 | 0
86107 | CUF-138 | EQ | 0 | 0.028703 | south | N | 0.051845 | -0.0033154 | 0.048567 | 0.023146 | 0.0033154 | south | N | 0.0033154 | 0
88198 | BEEVILLE | F | 0 | 0.028472 | south | N | 0.051614 | -0.0035464 | 0.048336 | 0.022915 | 0.0035464 | south | N | 0.0035464 | 0
88253 | HAMILTON | F | 0 | 0.017036 | south | N | 0.040178 | -0.014982 | 0.0369 | 0.011479 | 0.011479 | houston | Y | 0.014982 | 0
88299 | ZAPATA | F | 0 | 0.027824 | south | N | 0.050966 | -0.0041944 | 0.047688 | 0.022267 | 0.0041944 | south | N | 0.0041944 | 0
88508 | FALFURRI | F | 0 | 0.027329 | south | N | 0.050471 | -0.0046894 | 0.047193 | 0.021772 | 0.0046894 | south | N | 0.0046894 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg2 C:7334 L_MCNEIL - 7336 L_GILLCR | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.10474 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.83789 | 0 | 0.12788 | 0 | 0 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.10474 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.83789 | 0 | 0.12788 | 0 | 0 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.099125 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 30.7288 | 310 | 0.12227 | 37.9029 | 310 | 37.9029
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.099125 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 40.9386 | 413 | 0.12227 | 50.4964 |  |  | Weighted Shift Factors
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.0938 | 42 | 0.12061 | 5.0658 |  |  | North | -0.023142
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2887 | 44 | 0.12061 | 5.307 |  |  | South | 0.039229
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2887 | 44 | 0.12061 | 5.307 |  |  |  | -0.062372
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5811 | 47 | 0.12061 | 5.6688
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.095117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.3291 | 0 | 0.11826 | 0 |  |  | Line Rating | 247.95
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.095117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.234 | 0 | 0.11826 | 0 |  |  | Conc Gen | 310
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.095117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.3291 | 0 | 0.11826 | 0 |  |  | Weighted Imp. | 37.9029
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.4086 | 49 | 0.11311 | 5.5426 |  |  | PTDF | 0.12227
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.1387 | 46 | 0.11311 | 5.2032
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.1387 | 46 | 0.11311 | 5.2032 |  |  | Concentration | -1.9603
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2286 | 47 | 0.11311 | 5.3163
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.089971 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.8555 | 154 | 0.11311 | 17.4195
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.089971 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.3157 | 148 | 0.11311 | 16.7408
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3186 | 48 | 0.11311 | 5.4294
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3186 | 48 | 0.11311 | 5.4294
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.073935 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3308 | 0 | 0.097077 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.073935 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3308 | 0 | 0.097077 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.065705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8397 | 0 | 0.088847 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.065705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.9054 | 0 | 0.088847 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.064594 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 27.2587 | 422 | 0.087736 | 37.0248
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.05856 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0541 | 0 | 0.081702 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.05856 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0541 | 0 | 0.081702 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.05856 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.8784 | 0 | 0.081702 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.057862 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.79271 | 0 | 0.081004 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.047689 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.28613 | 0 | 0.070831 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.037776 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.090662 | 0 | 0.060918 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.037776 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.090662 | 0 | 0.060918 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.037776 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10577 | 0 | 0.060918 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.037711 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.9779 | 132 | 0.060853 | 8.0327
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.037711 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.0533 | 134 | 0.060853 | 8.1544
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.037711 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.1807 | 323 | 0.060853 | 19.6557
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.037462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.089909 | 0 | 0.060604 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.037462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.089909 | 0 | 0.060604 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.2304 | 114 | 0.060251 | 6.8687
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 8.2382 | 222 | 0.060251 | 13.3758
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.8281 | 184 | 0.060251 | 11.0863
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 8.3124 | 224 | 0.060251 | 13.4963
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.2675 | 115 | 0.060251 | 6.9289
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.036403 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14561 | 0 | 0.059545 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.8614 | 223.9 | 0.058253 | 13.0429
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.9 | 225 | 0.058253 | 13.107
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.8859 | 224.6 | 0.058253 | 13.0837
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.9597 | 226.7 | 0.058253 | 13.206
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.035061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.3468 | 152.5 | 0.058203 | 8.876
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.035061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.2416 | 149.5 | 0.058203 | 8.7014
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.035061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.1552 | 232.6 | 0.058203 | 13.5381
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8742 | 142 | 0.057467 | 8.1604
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9771 | 145 | 0.057467 | 8.3328
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.1831 | 151 | 0.057467 | 8.6776
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.9543 | 290 | 0.057467 | 16.6655
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.033981 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.40777 | 0 | 0.057123 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.033422 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.7699 | 412 | 0.056564 | 23.3045
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.033422 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.3688 | 400 | 0.056564 | 22.6258
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.033399 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.9804 | 209 | 0.056541 | 11.8172
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.033399 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.2142 | 216 | 0.056541 | 12.2129
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5364 | 46 | 0.056541 | 2.6009
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5698 | 47 | 0.056541 | 2.6574
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5364 | 46 | 0.056541 | 2.6009
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5364 | 46 | 0.056541 | 2.6009
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.033369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.056511 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.033369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.056511 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.033369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.056511 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.033349 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 14.14 | 424 | 0.056491 | 23.9524
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.033349 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 14.1733 | 425 | 0.056491 | 24.0088
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8985 | 147 | 0.056465 | 8.3004
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.5986 | 138 | 0.056465 | 7.7922
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.6652 | 140 | 0.056465 | 7.9052
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8985 | 147 | 0.056465 | 8.3004
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0648 | 182 | 0.056465 | 10.2767
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.598 | 198 | 0.056465 | 11.1802
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.033317 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.56 | 407 | 0.056459 | 22.979
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.033199 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.9255 | 58 | 0.056341 | 3.2678
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.033199 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.9547 | 89 | 0.056341 | 5.0144
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4608 | 44 | 0.056341 | 2.479
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4608 | 44 | 0.056341 | 2.479
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4276 | 43 | 0.056341 | 2.4227
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.494 | 45 | 0.056341 | 2.5354
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.033058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.124 | 155 | 0.0562 | 8.7111
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.033058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.6199 | 170 | 0.0562 | 9.5541
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.033058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.124 | 155 | 0.0562 | 8.7111
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6376 | 50 | 0.055893 | 2.7947
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6376 | 50 | 0.055893 | 2.7947
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6376 | 50 | 0.055893 | 2.7947
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6376 | 50 | 0.055893 | 2.7947
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.032725 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.8679 | 546 | 0.055867 | 30.5036
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.032725 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 24.5437 | 750 | 0.055867 | 41.9006
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.030538 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 12.093 | 396 | 0.05368 | 21.2574
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.02929 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.70296 | 24 | 0.052432 | 1.2584
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.02929 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.70296 | 24 | 0.052432 | 1.2584
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.02929 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.67367 | 23 | 0.052432 | 1.2059
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.029143 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 12.6189 | 433 | 0.052285 | 22.6396
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.029107 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 16.9985 | 584 | 0.052249 | 30.5137
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.029107 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.3187 | 595 | 0.052249 | 31.0884
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.028703 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.8703 | 100 | 0.051845 | 5.1845
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.028703 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.8703 | 100 | 0.051845 | 5.1845
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.028703 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051845 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.028703 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051845 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.028703 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051845 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.028703 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051845 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.0287 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051842 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.028472 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051614 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.027848 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.5164 | 629 | 0.05099 | 32.073
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.027824 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050966 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.027393 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.32872 | 0 | 0.050535 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.027393 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.30132 | 0 | 0.050535 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.027393 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.32872 | 0 | 0.050535 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.027329 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050471 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.027245 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3047 | 158 | 0.050387 | 7.9612
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.027245 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3592 | 160 | 0.050387 | 8.062
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.027245 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7679 | 175 | 0.050387 | 8.8178
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.026944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9473 | 146.5 | 0.050086 | 7.3377
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.026944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.985 | 147.9 | 0.050086 | 7.4078
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.026944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.6613 | 173 | 0.050086 | 8.6649
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.026871 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.5623 | 207 | 0.050013 | 10.3528
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.026871 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.8229 | 216.7 | 0.050013 | 10.8379
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.026871 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.5028 | 242 | 0.050013 | 12.1032
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.02687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8693 | 144 | 0.050012 | 7.2018
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.02687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8693 | 144 | 0.050012 | 7.2018
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.02687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.5948 | 171 | 0.050012 | 8.5521
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.026805 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.049947 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.026805 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0186 | 38 | 0.049947 | 1.898
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.026805 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.51734 | 19.3 | 0.049947 | 0.96399
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.026805 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.40208 | 15 | 0.049947 | 0.74921
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.026805 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2598 | 47 | 0.049947 | 2.3475
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5175 | 94 | 0.049924 | 4.6929
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0981 | 41 | 0.049924 | 2.0469
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0177 | 38 | 0.049924 | 1.8971
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.50886 | 19 | 0.049924 | 0.94856
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5175 | 94 | 0.049924 | 4.6929
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.96415 | 36 | 0.049924 | 1.7973
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1516 | 43 | 0.049924 | 2.1467
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.5892 | 22 | 0.049924 | 1.0983
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.9637 | 148 | 0.049924 | 7.3888
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.3391 | 50 | 0.049924 | 2.4962
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.473 | 55 | 0.049924 | 2.7458
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.3391 | 50 | 0.049924 | 2.4962
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.026732 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.77523 | 0 | 0.049874 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.026592 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0105 | 0 | 0.049734 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.026584 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0102 | 0 | 0.049726 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.026557 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.66392 | 0 | 0.049699 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.026557 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.66392 | 0 | 0.049699 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.026541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.8647 | 334 | 0.049683 | 16.5943
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.026541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 9.0239 | 340 | 0.049683 | 16.8924
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.026541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7774 | 180 | 0.049683 | 8.943
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.026541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7774 | 180 | 0.049683 | 8.943
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.026481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7666 | 180 | 0.049623 | 8.9322
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.026475 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.9262 | 0 | 0.049617 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.026475 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.9342 | 0 | 0.049617 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.026475 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.0507 | 0 | 0.049617 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.026471 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.8943 | 336 | 0.049613 | 16.6701
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.026471 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7648 | 180 | 0.049613 | 8.9304
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.026389 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8 | 144 | 0.049531 | 7.1325
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.026389 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9611 | 188 | 0.049531 | 9.3119
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 25 | 0.049418 | 1.2355
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 25 | 0.049418 | 1.2355
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 25 | 0.049418 | 1.2355
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.42042 | 16 | 0.049418 | 0.79069
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 25 | 0.049418 | 1.2355
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 25 | 0.049418 | 1.2355
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 25 | 0.049418 | 1.2355
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.39414 | 15 | 0.049418 | 0.74128
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.1319 | 0 | 0.049293 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.0011 | 0 | 0.049293 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6151 | 0 | 0.049293 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.7919 | 0 | 0.049293 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.8442 | 0 | 0.049293 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.3212 | 0 | 0.049293 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.026151 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.31381 | 0 | 0.049293 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.026037 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9007 | 0 | 0.049179 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2367 | 47.7 | 0.049069 | 2.3406
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.96708 | 37.3 | 0.049069 | 1.8303
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.1926 | 46 | 0.049069 | 2.2572
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2445 | 48 | 0.049069 | 2.3553
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.025628 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56382 | 22 | 0.04877 | 1.0729
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.025628 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28191 | 11 | 0.04877 | 0.53647
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.025628 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28191 | 11 | 0.04877 | 0.53647
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.025415 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38122 | 0 | 0.048557 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.025415 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.58454 | 0 | 0.048557 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.025186 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.20149 | 0 | 0.048328 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.70157 | 0 | 0.048198 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.17539 | 0 | 0.048198 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97718 | 0 | 0.048198 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.37584 | 0 | 0.048198 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.17539 | 0 | 0.048198 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.37584 | 0 | 0.048198 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97718 | 0 | 0.048198 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97718 | 0 | 0.048198 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.024243 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1637 | 0 | 0.047385 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8951 | 0 | 0.04713 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.943 | 0 | 0.04713 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8951 | 0 | 0.04713 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.919 | 0 | 0.04713 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8807 | 0 | 0.04713 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5997 | 0 | 0.04713 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1034 | 0 | 0.04713 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67166 | 0 | 0.04713 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0459 | 0 | 0.04713 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.7751 | 0 | 0.04713 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.021697 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.044839 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.020817 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1249 | 0 | 0.043959 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.017036 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.56219 | 0 | 0.040178 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.017036 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.4259 | 0 | 0.040178 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.017036 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040178 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.0149 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 19.8617 | 0 | 0.038042 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.0149 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 19.7872 | 0 | 0.038042 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.106 | 76 | 0.037695 | 2.8649
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.106 | 76 | 0.037695 | 2.8649
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.5281 | 105 | 0.037695 | 3.958
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0769 | 74 | 0.037695 | 2.7895
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0769 | 74 | 0.037695 | 2.7895
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4844 | 102 | 0.037695 | 3.8449
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.013781 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.90955 | 66 | 0.036923 | 2.4369
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67059 | 0 | 0.033958 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77226 | 0 | 0.033958 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.48672 | 0 | 0.033958 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0924 | 0 | 0.033958 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93018 | 0 | 0.033958 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95181 | 0 | 0.033958 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5408 | 0 | 0.033958 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19469 | 0 | 0.033958 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0167 | 0 | 0.033958 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75712 | 0 | 0.033958 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68141 | 0 | 0.033958 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77875 | 0 | 0.033958 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.70088 | 0 | 0.033958 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0924 | 0 | 0.033958 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0492 | 0 | 0.033958 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.114 | 0 | 0.033958 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82202 | 0 | 0.033958 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.86528 | 0 | 0.033958 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.86528 | 0 | 0.033958 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8495 | 0 | 0.033958 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.010075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71532 | 0 | 0.033217 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.010075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10075 | 0 | 0.033217 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0515 | 0 | 0.032615 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0515 | 0 | 0.032615 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1273 | 0 | 0.032615 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0373 | 0 | 0.032615 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.007431 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34257 | 0 | 0.030573 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.007319 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.7647 | 651 | 0.030461 | 19.8304
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.007319 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.1279 | 564 | 0.030461 | 17.1802
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.007319 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.3914 | 600 | 0.030461 | 18.2768
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.007302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1902 | 0 | 0.030444 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.007302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1902 | 0 | 0.030444 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.007302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.789 | 0 | 0.030444 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.007124 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23509 | 0 | 0.030266 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.006957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.1201 | 161 | 0.030099 | 4.846
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.006957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.1549 | 166 | 0.030099 | 4.9965
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.006957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7253 | 248 | 0.030099 | 7.4647
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.006957 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.7985 | 546 | 0.030099 | 16.4343
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.006957 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 4.4734 | 0 | 0.030099 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.006957 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.090441 | 13 | 0.030099 | 0.39129
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.005956 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19059 | 0 | 0.029098 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.005956 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17868 | 0 | 0.029098 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.59739 | 0 | 0.029098 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.55331 | 0 | 0.029098 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.61168 | 0 | 0.029098 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.60751 | 0 | 0.029098 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42133 | 0 | 0.029093 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39693 | 0 | 0.029093 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3154 | 0 | 0.029093 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91169 | 0 | 0.029093 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91348 | 0 | 0.029093 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90634 | 0 | 0.029093 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5713 | 0 | 0.029093 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.452 | 0 | 0.029093 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23804 | 0 | 0.029093 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.005488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2744 | 50 | 0.02863 | 1.4315
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.00517 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.028312 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43398 | 0 | 0.027911 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.41776 | 0 | 0.027911 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4149 | 0 | 0.027911 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25991 | 0 | 0.027911 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.058182 | 0 | 0.027911 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.29984 | 0 | 0.027755 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.27678 | 0 | 0.027755 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.29984 | 0 | 0.027755 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.29984 | 0 | 0.027755 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20079 | 46 | 0.027507 | 1.2653
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20079 | 46 | 0.027507 | 1.2653
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20079 | 46 | 0.027507 | 1.2653
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.24008 | 55 | 0.027507 | 1.5129
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.24008 | 55 | 0.027507 | 1.5129
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.23571 | 54 | 0.027507 | 1.4854
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.004322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.33712 | 0 | 0.027464 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.004322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.34576 | 0 | 0.027464 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.69327 | 0 | 0.02739 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66736 | 0 | 0.02739 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66906 | 0 | 0.02739 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66694 | 0 | 0.02739 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1427 | 0 | 0.02739 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.004174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14609 | 0 | 0.027316 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.004106 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.049272 | 12 | 0.027248 | 0.32698
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.004106 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.027248 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.004102 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.69324 | 169 | 0.027244 | 4.6043
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.004097 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.676 | 165 | 0.027239 | 4.4945
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.004092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60971 | 0 | 0.027234 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.004092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.26639 | 0 | 0.027234 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.004079 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.86883 | 213 | 0.027221 | 5.7982
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.004077 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.066047 | 0 | 0.027219 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2608 | 0 | 0.027217 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25754 | 0 | 0.027217 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33659 | 0 | 0.027217 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29992 | 0 | 0.027217 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.004073 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.92864 | 228 | 0.027215 | 6.2051
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.00407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.7326 | 0 | 0.027212 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.00407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.6455 | 0 | 0.027212 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.00407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.63899 | 0 | 0.027212 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28201 | 0 | 0.027114 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28598 | 0 | 0.027114 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15491 | 0 | 0.027114 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11916 | 0 | 0.027114 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.00381 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51816 | 0 | 0.026952 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15981 | 42 | 0.026947 | 1.1318
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15981 | 42 | 0.026947 | 1.1318
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14459 | 38 | 0.026947 | 1.024
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14459 | 38 | 0.026947 | 1.024
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.003759 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65031 | 0 | 0.026901 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.003759 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.50747 | 0 | 0.026901 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.3639 | 104 | 0.026641 | 2.7707
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.3639 | 104 | 0.026641 | 2.7707
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18895 | 54 | 0.026641 | 1.4386
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18545 | 53 | 0.026641 | 1.412
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18895 | 54 | 0.026641 | 1.4386
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.19944 | 57 | 0.026641 | 1.5186
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18895 | 54 | 0.026641 | 1.4386
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18895 | 54 | 0.026641 | 1.4386
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20294 | 58 | 0.026641 | 1.5452
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20294 | 58 | 0.026641 | 1.5452
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.00342 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 2.5137 | 735 | 0.026562 | 19.5234
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11407 | 0 | 0.026497 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11642 | 0 | 0.026497 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10971 | 0 | 0.026497 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15399 | 0 | 0.026497 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.059383 | 0 | 0.026497 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.068442 | 0 | 0.026497 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.066765 | 0 | 0.026497 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11743 | 0 | 0.026497 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.06039 | 0 | 0.026497 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28652 | 0 | 0.026497 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49654 | 0 | 0.026497 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.00326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.03912 | 12 | 0.026402 | 0.31683
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.003169 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.015845 | 0 | 0.026311 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.003169 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.066549 | 0 | 0.026311 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20572 | 0 | 0.026307 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20889 | 0 | 0.026307 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22155 | 0 | 0.026307 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19939 | 0 | 0.026307 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19623 | 0 | 0.026307 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32916 | 0 | 0.026307 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18674 | 0 | 0.026307 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.003163 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.037956 | 12 | 0.026305 | 0.31566
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.003157 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 2.3457 | 743 | 0.026299 | 19.5405
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.003105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.48749 | 0 | 0.026247 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.003079 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52959 | 172 | 0.026221 | 4.5101
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.003079 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52959 | 172 | 0.026221 | 4.5101
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.003079 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52959 | 172 | 0.026221 | 4.5101
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47098 | 0 | 0.026035 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.46693 | 0 | 0.026035 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4597 | 0 | 0.026035 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7788 | 0 | 0.026035 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.002822 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.1232 | 398 | 0.025964 | 10.3338
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15154 | 56 | 0.025848 | 1.4475
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15965 | 59 | 0.025848 | 1.5251
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15154 | 56 | 0.025848 | 1.4475
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15154 | 56 | 0.025848 | 1.4475
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15965 | 59 | 0.025848 | 1.5251
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15154 | 56 | 0.025848 | 1.4475
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.27974 | 0 | 0.024759 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.25225 | 0 | 0.024759 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24902 | 0 | 0.024759 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24902 | 0 | 0.024759 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.001617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.26195 | 0 | 0.024759 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023142 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023142 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 3.7109 | 100 | -0.0021204 | -0.21204
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.03115 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.0080794 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.047161 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -26.8346 | 569 | -0.024019 | -13.6666
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.047161 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -27.4005 | 581 | -0.024019 | -13.9548
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039229 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.039229 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.006147 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.92205 | 150 | -0.045376 | -6.8065
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.3223 | 0 | -0.047804 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.3377 | 0 | -0.047804 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.3377 | 0 | -0.047804 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2585 | 0 | -0.047804 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.010737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.9712 | 463 | -0.049966 | -23.1344
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.01132 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.050549 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.013749 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.43997 | 0 | -0.052978 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053068 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053068 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.013839 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.23526 | 17 | -0.053068 | -0.90216
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053068 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053068 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.014771 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.70901 | 48 | -0.054 | -2.592
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.014771 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.67947 | 46 | -0.054 | -2.484
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.014771 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.551 | 105 | -0.054 | -5.67
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.015906 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3361 | 84 | -0.055135 | -4.6314
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.016042 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2272 | 76.5 | -0.055271 | -4.2283
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.016193 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2954 | 80 | -0.055422 | -4.4338
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.0323 | 855 | -0.055641 | -47.5734
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.0323 | 855 | -0.055641 | -47.5734
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.4995 | 152.3 | -0.055641 | -8.4742
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.511 | 153 | -0.055641 | -8.5131
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.017046 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5569 | 150 | -0.056275 | -8.4413
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.017046 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5569 | 150 | -0.056275 | -8.4413
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.017068 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3654 | 80 | -0.056297 | -4.5038
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017073 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3658 | 80 | -0.056302 | -4.5042
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.01711 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2833 | 75 | -0.056339 | -4.2255
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.01711 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3688 | 80 | -0.056339 | -4.5071
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.01711 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.6844 | 40 | -0.056339 | -2.2536
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.01728 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3824 | 80 | -0.056509 | -4.5207
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.01728 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3824 | 80 | -0.056509 | -4.5207
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.017918 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.086006 | 0 | -0.057147 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.018647 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.4211 | 827 | -0.057876 | -47.8637
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.018647 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.2719 | 819 | -0.057876 | -47.4007
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.019279 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.2678 | 169.5 | -0.058508 | -9.9172
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.284 | 66 | -0.058684 | -3.8732
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.2646 | 65 | -0.058684 | -3.8145
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.058684 | -3.9319
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.058684 | -3.9319
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.058684 | -3.9319
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.019455 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058684 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.019455 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058684 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.019477 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.6817 | 35 | -0.058706 | -2.0547
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.019477 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.58431 | 30 | -0.058706 | -1.7612
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.019549 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9128 | 149 | -0.058778 | -8.758
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.019603 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.12938 | 6.6 | -0.058832 | -0.38829
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.019603 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.67238 | 34.3 | -0.058832 | -2.0179
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2148 | 112.5 | -0.058916 | -6.6281
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9432 | 149.5 | -0.058916 | -8.808
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6618 | 186 | -0.058916 | -10.9584
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2229 | 214.5 | -0.058916 | -12.6376
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.019794 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9691 | 150 | -0.059023 | -8.8535
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.1376 | 208.2 | -0.059102 | -12.3051
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.824 | 142.1 | -0.059102 | -8.3984
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.6312 | 132.4 | -0.059102 | -7.8252
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.7027 | 136 | -0.059102 | -8.0379
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9213 | 147 | -0.059102 | -8.688
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.1733 | 210 | -0.059102 | -12.4115
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3914 | 70 | -0.059106 | -4.1374
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3914 | 70 | -0.059106 | -4.1374
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.8446 | 92.8 | -0.059106 | -5.4851
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5902 | 80 | -0.059106 | -4.7285
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5902 | 80 | -0.059106 | -4.7285
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.2859 | 115 | -0.059106 | -6.7972
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.019892 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1537 | 58 | -0.059121 | -3.429
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.019895 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9994 | 100.5 | -0.059124 | -5.942
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.019949 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2731 | 214.2 | -0.059178 | -12.676
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.019953 | west | 8 | N | N | Nwest | Nwest | 1 | -0.51479 | 0 | -0.059182 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.020067 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.408 | 120 | -0.059296 | -7.1156
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.020067 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.6756 | 233 | -0.059296 | -13.8161
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.020067 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4154 | 170.2 | -0.059296 | -10.0922
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.020103 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4124 | 120 | -0.059332 | -7.1199
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.020114 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4137 | 120 | -0.059343 | -7.1212
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.020165 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5371 | 225 | -0.059394 | -13.3637
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.020177 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4124 | 0 | -0.059406 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.020177 | west | 8 | N | N | Nwest | Nwest | 1 | -1.481 | 0 | -0.059406 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.020177 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4205 | 0 | -0.059406 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.020188 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6338 | 180 | -0.059417 | -10.6951
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.020188 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6338 | 180 | -0.059417 | -10.6951
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0368 | 150 | -0.059474 | -8.9212
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4539 | 220 | -0.059474 | -13.0844
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.049 | 200 | -0.059474 | -11.8949
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4679 | 121.9 | -0.059474 | -7.2499
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.34 | 66 | -0.059532 | -3.9291
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4009 | 69 | -0.059532 | -4.1077
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4009 | 69 | -0.059532 | -4.1077
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3603 | 67 | -0.059532 | -3.9887
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3603 | 67 | -0.059532 | -3.9887
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3197 | 65 | -0.059532 | -3.8696
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.020331 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2809 | 63 | -0.05956 | -3.7523
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.020352 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8696 | 141 | -0.059581 | -8.401
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.020352 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4422 | 120 | -0.059581 | -7.1498
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.020359 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0155 | 99 | -0.059588 | -5.8992
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.020359 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2419 | 61 | -0.059588 | -3.6349
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.020359 | west | 7 | N | N | Nwest | Nwest | 1 | -0.50897 | 0 | -0.059588 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.020359 | west | 7 | N | N | Nwest | Nwest | 1 | -0.93041 | 0 | -0.059588 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.020359 | west | 7 | N | N | Nwest | Nwest | 1 | -0.93041 | 0 | -0.059588 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.020425 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7157 | 84 | -0.059654 | -5.011
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.020473 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0709 | 150 | -0.059702 | -8.9554
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.020473 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0678 | 101 | -0.059702 | -6.0299
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.020479 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5599 | 125 | -0.059708 | -7.4635
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.020479 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5599 | 125 | -0.059708 | -7.4635
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.77269 | 37.5 | -0.059834 | -2.2438
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.215 | 107.5 | -0.059834 | -6.4322
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7817 | 135 | -0.059834 | -8.0776
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.452 | 119 | -0.059834 | -7.1203
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1635 | 105 | -0.059834 | -6.2826
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.6587 | 80.5 | -0.059834 | -4.8167
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.3165 | 209 | -0.059882 | -12.5154
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6126 | 126.5 | -0.059882 | -7.5751
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1426 | 249 | -0.059882 | -14.9107
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0686 | 197 | -0.059882 | -11.7968
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.020715 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.1073 | 150 | -0.059944 | -8.9917
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.021071 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2643 | 60 | -0.0603 | -3.618
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.0215 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6 | 400 | -0.060729 | -24.2917
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.021502 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.0745 | 236 | -0.060731 | -14.3326
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.021658 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.3197 | 615 | -0.060887 | -37.4457
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.021658 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.7132 | 587 | -0.060887 | -35.7409
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.021794 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.596 | 165 | -0.061023 | -10.0689
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.021878 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.297 | 150.7 | -0.061107 | -9.2089
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.021878 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3036 | 151 | -0.061107 | -9.2272
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.021878 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8812 | 177.4 | -0.061107 | -10.8404
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.021923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3213 | 151.5 | -0.061152 | -9.2646
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.021923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3389 | 152.3 | -0.061152 | -9.3135
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.021923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8913 | 177.5 | -0.061152 | -10.8545
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.022031 | west | 4 | Y | N | Ywest | Nwest | 1 | -14.3135 | 649.7 | -0.06126 | -39.8009
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.022721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.3159 | 366 | -0.06195 | -22.6738
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.02273 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.5007 | 242 | -0.061959 | -14.9942
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.45562 | 20 | -0.06201 | -1.2402
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.45562 | 20 | -0.06201 | -1.2402
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.45562 | 20 | -0.06201 | -1.2402
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.38728 | 17 | -0.06201 | -1.0542
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.022849 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.1585 | 182 | -0.062078 | -11.2983
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.022849 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.0589 | 484 | -0.062078 | -30.0459
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.022855 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.1427 | 50 | -0.062084 | -3.1042
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.022865 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.062094 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3953 | 0 | -0.06217 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.9823 | 0 | -0.06217 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3264 | 0 | -0.06217 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | 1 | -9.1535 | 0 | -0.06217 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.023027 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -18.0762 | 785 | -0.062256 | -48.8712
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.023027 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -18.3065 | 795 | -0.062256 | -49.4938
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.023027 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.9611 | 780 | -0.062256 | -48.56
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.023397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.773 | 204 | -0.062626 | -12.7758
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.023397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.7028 | 201 | -0.062626 | -12.5879
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.023397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.6621 | 242 | -0.062626 | -15.1556
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.023404 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.8085 | 120 | -0.062633 | -7.516
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.023423 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.28108 | 0 | -0.062652 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.023423 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.28108 | 0 | -0.062652 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.023554 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.4132 | 60 | -0.062783 | -3.767
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7999 | 161 | -0.062831 | -10.1158
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8707 | 164 | -0.062831 | -10.3043
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8707 | 164 | -0.062831 | -10.3043
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.7712 | 414 | -0.062831 | -26.0122
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8235 | 162 | -0.062831 | -10.1787
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7999 | 161 | -0.062831 | -10.1158
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8471 | 163 | -0.062831 | -10.2415
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.6532 | 409 | -0.062831 | -25.698
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.023734 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.2436 | 558 | -0.062963 | -35.1336
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.023734 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.742 | 579 | -0.062963 | -36.4558
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.023734 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -19.1771 | 808 | -0.062963 | -50.8744
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.023735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.4747 | 20 | -0.062964 | -1.2593
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.023735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.59337 | 25 | -0.062964 | -1.5741
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.023735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.97313 | 41 | -0.062964 | -2.5815
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.02374 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7805 | 0 | -0.062969 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.02374 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.8897 | 0 | -0.062969 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.02374 | north | 8 | N | N | Nnorth | Nnorth | 1 | -2.0986 | 0 | -0.062969 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8 | 160 | -0.062979 | -10.0767
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.705 | 156 | -0.062979 | -9.8248
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.655 | 196 | -0.062979 | -12.344
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.705 | 156 | -0.062979 | -9.8248
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7287 | 157 | -0.062979 | -9.8878
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.7025 | 198 | -0.062979 | -12.4699
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.023753 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.2162 | 388 | -0.062982 | -24.4372
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.023753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.2328 | 515 | -0.062982 | -32.4359
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.023757 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.8768 | 79 | -0.062986 | -4.9759
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.023757 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.5182 | 106 | -0.062986 | -6.6766
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.023757 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.4685 | 146 | -0.062986 | -9.196
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.023757 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.8055 | 76 | -0.062986 | -4.787
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.02376 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.7912 | 370 | -0.062989 | -23.3061
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3264 | 0 | -0.062989 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3502 | 0 | -0.062989 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.3418 | 0 | -0.062989 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3977 | 0 | -0.062989 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.4214 | 0 | -0.062989 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.3656 | 0 | -0.062989 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.02377 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.9508 | 40 | -0.062999 | -2.52
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.02377 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.6741 | 112.5 | -0.062999 | -7.0874
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.023772 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.0412 | 170 | -0.063001 | -10.7102
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.023772 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.3614 | 520 | -0.063001 | -32.7607
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.023783 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.95132 | 0 | -0.063012 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.023783 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.95132 | 0 | -0.063012 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.023817 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.063046 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.023817 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.063046 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.023856 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.063085 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.023861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4317 | 60 | -0.06309 | -3.7854
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.023861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5032 | 63 | -0.06309 | -3.9747
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.023875 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.063104 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.023909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.8858 | 288 | -0.063138 | -18.1838
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.023909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5146 | 147 | -0.063138 | -9.2813
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.023909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5146 | 147 | -0.063138 | -9.2813
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.024062 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.43312 | 18 | -0.063291 | -1.1392
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.024062 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.43312 | 18 | -0.063291 | -1.1392
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.024062 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.91436 | 38 | -0.063291 | -2.4051
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.024076 | north | 3 | N | N | Nnorth | Nnorth | 1 | -27.8559 | 0 | -0.063305 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.024076 | north | 3 | N | N | Nnorth | Nnorth | 1 | -27.88 | 0 | -0.063305 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.024081 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.06331 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.024081 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.06331 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.024081 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.06331 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.024085 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.842 | 118 | -0.063314 | -7.4711
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.024085 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.7698 | 115 | -0.063314 | -7.2812
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.024085 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -13.3913 | 556 | -0.063314 | -35.2028
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.024086 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.3953 | 224 | -0.063315 | -14.1826
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.024146 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.7627 | 73 | -0.063375 | -4.6264
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.024146 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.8734 | 119 | -0.063375 | -7.5417
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.024146 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.9499 | 205 | -0.063375 | -12.9919
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.024146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.4629 | 102 | -0.063375 | -6.4643
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.024146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.318 | 96 | -0.063375 | -6.084
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.024162 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2504 | 217.3 | -0.063391 | -13.7749
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.024162 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.9532 | 205 | -0.063391 | -12.9952
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.024162 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.5817 | 272.4 | -0.063391 | -17.2678
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.024277 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.063506 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.024489 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.6527 | 435 | -0.063718 | -27.7175
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.024514 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.683 | 395 | -0.063743 | -25.1786
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.024514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.6636 | 435 | -0.063743 | -27.7284
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.024624 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.8263 | 196 | -0.063853 | -12.5153
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.024624 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7333 | 111 | -0.063853 | -7.0877
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.7251 | 70 | -0.063874 | -4.4712
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.7005 | 69 | -0.063874 | -4.4073
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.7005 | 69 | -0.063874 | -4.4073
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6759 | 68 | -0.063874 | -4.3435
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.025393 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.495 | 216.4 | -0.064622 | -13.9843
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.025393 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4874 | 216.1 | -0.064622 | -13.9649
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.693 | 224 | -0.064644 | -14.4803
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.7438 | 226 | -0.064644 | -14.6096
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.388 | 212 | -0.064644 | -13.7046
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.3626 | 211 | -0.064644 | -13.64
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.025482 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.281 | 168 | -0.064711 | -10.8715
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.025482 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2934 | 90 | -0.064711 | -5.824
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.032023 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.48035 | 0 | -0.071252 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.032023 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.48035 | 0 | -0.071252 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.033621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.0431 | 150 | -0.07285 | -10.9276
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.033621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6897 | 80 | -0.07285 | -5.828
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.034638 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.8327 | 255 | -0.073867 | -18.8362
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.034638 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.1611 | 149 | -0.073867 | -11.0062
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.034638 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.2996 | 153 | -0.073867 | -11.3017
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.035827 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.075056 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.035827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -28.1958 | 787 | -0.075056 | -59.0694
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.036333 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.075562 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.036333 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.075562 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg2 C:7334 L_MCNEIL - 7336 L_GILLCR | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.036333 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.075562 | 0 | 0 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.036333 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.075562 | 0 | 0 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.035827 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.075056 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.035827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -28.1958 | 787 | -0.075056 | -59.0694 | 787 | 59.0694 | Weighted Shift Factors
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.034638 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.8327 | 255 | -0.073867 | -18.8362 |  |  | North | -0.023142
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.034638 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.1611 | 149 | -0.073867 | -11.0062 |  |  | South | 0.039229
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.034638 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.2996 | 153 | -0.073867 | -11.3017 |  |  |  | -0.062372
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.033621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.0431 | 150 | -0.07285 | -10.9276
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.033621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6897 | 80 | -0.07285 | -5.828 |  |  | Line Rating | 247.95
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.032023 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.48035 | 0 | -0.071252 | 0 |  |  | Conc Gen | 787
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.032023 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.48035 | 0 | -0.071252 | 0 |  |  | Weighted Imp. | 59.0694
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.025482 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.281 | 168 | -0.064711 | -10.8715 |  |  | PTDF | 0.075056
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.025482 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2934 | 90 | -0.064711 | -5.824
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.693 | 224 | -0.064644 | -14.4803 |  |  | Concentration | -1.2034
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.7438 | 226 | -0.064644 | -14.6096
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.388 | 212 | -0.064644 | -13.7046
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.025415 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.3626 | 211 | -0.064644 | -13.64
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.025393 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.495 | 216.4 | -0.064622 | -13.9843
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.025393 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4874 | 216.1 | -0.064622 | -13.9649
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.7251 | 70 | -0.063874 | -4.4712
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.7005 | 69 | -0.063874 | -4.4073
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.7005 | 69 | -0.063874 | -4.4073
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.024645 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6759 | 68 | -0.063874 | -4.3435
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.024624 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.8263 | 196 | -0.063853 | -12.5153
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.024624 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7333 | 111 | -0.063853 | -7.0877
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.024514 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.683 | 395 | -0.063743 | -25.1786
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.024514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.6636 | 435 | -0.063743 | -27.7284
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.024489 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.6527 | 435 | -0.063718 | -27.7175
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.024277 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.063506 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.024162 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2504 | 217.3 | -0.063391 | -13.7749
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.024162 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.9532 | 205 | -0.063391 | -12.9952
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.024162 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.5817 | 272.4 | -0.063391 | -17.2678
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.024146 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.7627 | 73 | -0.063375 | -4.6264
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.024146 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.8734 | 119 | -0.063375 | -7.5417
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.024146 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.9499 | 205 | -0.063375 | -12.9919
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.024146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.4629 | 102 | -0.063375 | -6.4643
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.024146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.318 | 96 | -0.063375 | -6.084
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.024086 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.3953 | 224 | -0.063315 | -14.1826
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.024085 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.842 | 118 | -0.063314 | -7.4711
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.024085 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.7698 | 115 | -0.063314 | -7.2812
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.024085 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -13.3913 | 556 | -0.063314 | -35.2028
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.024081 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.06331 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.024081 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.06331 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.024081 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.06331 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.024076 | north | 3 | N | N | Nnorth | Nnorth | 1 | -27.8559 | 0 | -0.063305 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.024076 | north | 3 | N | N | Nnorth | Nnorth | 1 | -27.88 | 0 | -0.063305 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.024062 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.43312 | 18 | -0.063291 | -1.1392
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.024062 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.43312 | 18 | -0.063291 | -1.1392
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.024062 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.91436 | 38 | -0.063291 | -2.4051
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.023909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.8858 | 288 | -0.063138 | -18.1838
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.023909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5146 | 147 | -0.063138 | -9.2813
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.023909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5146 | 147 | -0.063138 | -9.2813
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.023875 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.063104 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.023861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4317 | 60 | -0.06309 | -3.7854
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.023861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5032 | 63 | -0.06309 | -3.9747
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.023856 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.063085 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.023817 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.063046 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.023817 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.063046 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.023783 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.95132 | 0 | -0.063012 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.023783 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.95132 | 0 | -0.063012 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.023772 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.0412 | 170 | -0.063001 | -10.7102
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.023772 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.3614 | 520 | -0.063001 | -32.7607
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.02377 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.6741 | 0 | -0.062999 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.02377 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.9508 | 40 | -0.062999 | -2.52
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.02376 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.7912 | 370 | -0.062989 | -23.3061
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3264 | 0 | -0.062989 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3502 | 0 | -0.062989 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.3418 | 0 | -0.062989 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3977 | 0 | -0.062989 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.4214 | 0 | -0.062989 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.02376 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.3656 | 0 | -0.062989 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.023757 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.8768 | 79 | -0.062986 | -4.9759
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.023757 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.5182 | 106 | -0.062986 | -6.6766
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.023757 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.4685 | 146 | -0.062986 | -9.196
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.023757 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.8055 | 76 | -0.062986 | -4.787
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.023753 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.2162 | 388 | -0.062982 | -24.4372
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.023753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.2328 | 515 | -0.062982 | -32.4359
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8 | 160 | -0.062979 | -10.0767
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.705 | 156 | -0.062979 | -9.8248
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.655 | 196 | -0.062979 | -12.344
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.705 | 156 | -0.062979 | -9.8248
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7287 | 157 | -0.062979 | -9.8878
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.02375 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.7025 | 198 | -0.062979 | -12.4699
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.02374 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7805 | 0 | -0.062969 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.02374 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.8897 | 0 | -0.062969 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.02374 | north | 8 | N | N | Nnorth | Nnorth | 1 | -2.0986 | 0 | -0.062969 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.023735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.4747 | 20 | -0.062964 | -1.2593
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.023735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.59337 | 25 | -0.062964 | -1.5741
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.023735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.97313 | 41 | -0.062964 | -2.5815
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.023734 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.2436 | 0 | -0.062963 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.023734 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.742 | 0 | -0.062963 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.023734 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -19.1771 | 0 | -0.062963 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7999 | 161 | -0.062831 | -10.1158
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8707 | 164 | -0.062831 | -10.3043
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8707 | 164 | -0.062831 | -10.3043
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.7712 | 414 | -0.062831 | -26.0122
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8235 | 162 | -0.062831 | -10.1787
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7999 | 161 | -0.062831 | -10.1158
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8471 | 163 | -0.062831 | -10.2415
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.023602 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.6532 | 409 | -0.062831 | -25.698
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.023554 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.4132 | 0 | -0.062783 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.023423 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.28108 | 0 | -0.062652 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.023423 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.28108 | 0 | -0.062652 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.023404 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.8085 | 0 | -0.062633 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.023397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.773 | 204 | -0.062626 | -12.7758
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.023397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.7028 | 201 | -0.062626 | -12.5879
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.023397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.6621 | 242 | -0.062626 | -15.1556
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.023027 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -18.0762 | 0 | -0.062256 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.023027 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -18.3065 | 0 | -0.062256 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.023027 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.9611 | 0 | -0.062256 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3953 | 0 | -0.06217 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.9823 | 0 | -0.06217 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3264 | 0 | -0.06217 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.022941 | north | 1 | N | N | Nnorth | Nnorth | 1 | -9.1535 | 0 | -0.06217 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.022865 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.062094 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.022855 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.1427 | 0 | -0.062084 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.022849 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.1585 | 182 | -0.062078 | -11.2983
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.022849 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.0589 | 484 | -0.062078 | -30.0459
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.45562 | 20 | -0.06201 | -1.2402
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.45562 | 20 | -0.06201 | -1.2402
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.45562 | 20 | -0.06201 | -1.2402
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.022781 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.38728 | 17 | -0.06201 | -1.0542
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.02273 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.5007 | 242 | -0.061959 | -14.9942
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.022721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.3159 | 366 | -0.06195 | -22.6738
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.022031 | west | 4 | Y | N | Ywest | Nwest | 1 | -14.3135 | 0 | -0.06126 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.021923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3213 | 151.5 | -0.061152 | -9.2646
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.021923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3389 | 152.3 | -0.061152 | -9.3135
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.021923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8913 | 177.5 | -0.061152 | -10.8545
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.021878 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.297 | 150.7 | -0.061107 | -9.2089
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.021878 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3036 | 151 | -0.061107 | -9.2272
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.021878 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8812 | 177.4 | -0.061107 | -10.8404
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.021794 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.596 | 0 | -0.061023 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.021658 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.3197 | 0 | -0.060887 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.021658 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.7132 | 0 | -0.060887 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.021502 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.0745 | 0 | -0.060731 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.0215 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6 | 0 | -0.060729 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.021071 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2643 | 0 | -0.0603 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.020715 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.1073 | 0 | -0.059944 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.3165 | 0 | -0.059882 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6126 | 0 | -0.059882 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1426 | 0 | -0.059882 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.020653 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0686 | 0 | -0.059882 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.77269 | 0 | -0.059834 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.215 | 0 | -0.059834 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7817 | 0 | -0.059834 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.452 | 0 | -0.059834 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1635 | 0 | -0.059834 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.020605 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.6587 | 0 | -0.059834 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.020479 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5599 | 0 | -0.059708 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.020479 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5599 | 0 | -0.059708 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.020473 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0709 | 0 | -0.059702 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.020473 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0678 | 0 | -0.059702 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.020425 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7157 | 0 | -0.059654 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.020359 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0155 | 0 | -0.059588 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.020359 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2419 | 0 | -0.059588 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.020359 | west | 7 | N | N | Nwest | Nwest | 1 | -0.50897 | 0 | -0.059588 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.020359 | west | 7 | N | N | Nwest | Nwest | 1 | -0.93041 | 0 | -0.059588 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.020359 | west | 7 | N | N | Nwest | Nwest | 1 | -0.93041 | 0 | -0.059588 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.020352 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8696 | 0 | -0.059581 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.020352 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4422 | 0 | -0.059581 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.020331 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2809 | 0 | -0.05956 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.34 | 66 | -0.059532 | -3.9291
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4009 | 69 | -0.059532 | -4.1077
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4009 | 69 | -0.059532 | -4.1077
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3603 | 67 | -0.059532 | -3.9887
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3603 | 67 | -0.059532 | -3.9887
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.020303 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3197 | 65 | -0.059532 | -3.8696
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0368 | 0 | -0.059474 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4539 | 0 | -0.059474 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.049 | 0 | -0.059474 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.020245 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4679 | 0 | -0.059474 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.020188 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6338 | 0 | -0.059417 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.020188 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6338 | 0 | -0.059417 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.020177 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4124 | 0 | -0.059406 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.020177 | west | 8 | N | N | Nwest | Nwest | 1 | -1.481 | 0 | -0.059406 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.020177 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4205 | 0 | -0.059406 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.020165 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5371 | 0 | -0.059394 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.020114 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4137 | 0 | -0.059343 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.020103 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4124 | 0 | -0.059332 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.020067 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.408 | 0 | -0.059296 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.020067 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.6756 | 0 | -0.059296 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.020067 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4154 | 0 | -0.059296 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.019953 | west | 8 | N | N | Nwest | Nwest | 1 | -0.51479 | 0 | -0.059182 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.019949 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2731 | 0 | -0.059178 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.019895 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9994 | 0 | -0.059124 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.019892 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1537 | 0 | -0.059121 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3914 | 70 | -0.059106 | -4.1374
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3914 | 70 | -0.059106 | -4.1374
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.8446 | 92.8 | -0.059106 | -5.4851
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5902 | 80 | -0.059106 | -4.7285
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5902 | 80 | -0.059106 | -4.7285
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.019877 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.2859 | 115 | -0.059106 | -6.7972
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.1376 | 208.2 | -0.059102 | -12.3051
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.824 | 142.1 | -0.059102 | -8.3984
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.6312 | 132.4 | -0.059102 | -7.8252
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.7027 | 136 | -0.059102 | -8.0379
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9213 | 147 | -0.059102 | -8.688
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.019873 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.1733 | 210 | -0.059102 | -12.4115
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.019794 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9691 | 0 | -0.059023 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2148 | 0 | -0.058916 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9432 | 0 | -0.058916 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6618 | 0 | -0.058916 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.019687 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2229 | 0 | -0.058916 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.019603 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.12938 | 0 | -0.058832 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.019603 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.67238 | 0 | -0.058832 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.019549 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9128 | 0 | -0.058778 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.019477 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.6817 | 0 | -0.058706 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.019477 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.58431 | 0 | -0.058706 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.284 | 66 | -0.058684 | -3.8732
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.2646 | 65 | -0.058684 | -3.8145
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.058684 | -3.9319
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.058684 | -3.9319
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.058684 | -3.9319
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.019455 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058684 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.019455 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058684 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.019279 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.2678 | 0 | -0.058508 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.018647 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.4211 | 0 | -0.057876 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.018647 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.2719 | 0 | -0.057876 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.017918 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.086006 | 0 | -0.057147 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.01728 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3824 | 0 | -0.056509 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.01728 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3824 | 0 | -0.056509 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.01711 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2833 | 0 | -0.056339 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.01711 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3688 | 0 | -0.056339 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.01711 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.6844 | 0 | -0.056339 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017073 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3658 | 0 | -0.056302 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.017068 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3654 | 0 | -0.056297 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.017046 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5569 | 0 | -0.056275 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.017046 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5569 | 0 | -0.056275 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.0323 | 0 | -0.055641 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.0323 | 0 | -0.055641 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.4995 | 0 | -0.055641 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.016412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.511 | 0 | -0.055641 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.016193 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2954 | 0 | -0.055422 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.016042 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2272 | 0 | -0.055271 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.015906 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3361 | 0 | -0.055135 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.014771 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.70901 | 48 | -0.054 | -2.592
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.014771 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.67947 | 46 | -0.054 | -2.484
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.014771 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.551 | 105 | -0.054 | -5.67
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053068 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053068 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.013839 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.23526 | 17 | -0.053068 | -0.90216
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053068 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.013839 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053068 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.013749 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.43997 | 0 | -0.052978 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.01132 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.050549 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.010737 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.9712 | 0 | -0.049966 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.3223 | 0 | -0.047804 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.3377 | 0 | -0.047804 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.3377 | 0 | -0.047804 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.008575 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2585 | 0 | -0.047804 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.006147 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.92205 | 0 | -0.045376 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039229 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.039229 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.047161 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -26.8346 | 0 | -0.024019 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.047161 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -27.4005 | 0 | -0.024019 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.03115 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.0080794 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 3.7109 | 0 | -0.0021204 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023142 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023142 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023142 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.27974 | 0 | 0.024759 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.25225 | 0 | 0.024759 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24902 | 0 | 0.024759 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.001617 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.24902 | 0 | 0.024759 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.001617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.26195 | 0 | 0.024759 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15154 | 56 | 0.025848 | 1.4475
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15965 | 59 | 0.025848 | 1.5251
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15154 | 56 | 0.025848 | 1.4475
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15154 | 56 | 0.025848 | 1.4475
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15965 | 59 | 0.025848 | 1.5251
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.002706 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15154 | 56 | 0.025848 | 1.4475
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.002822 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.1232 | 398 | 0.025964 | 10.3338
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47098 | 0 | 0.026035 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.46693 | 0 | 0.026035 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4597 | 0 | 0.026035 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.002893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7788 | 0 | 0.026035 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.003079 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52959 | 172 | 0.026221 | 4.5101
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.003079 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52959 | 172 | 0.026221 | 4.5101
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.003079 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52959 | 172 | 0.026221 | 4.5101
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.003105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.48749 | 0 | 0.026247 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.003157 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 2.3457 | 743 | 0.026299 | 19.5405
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.003163 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.037956 | 0 | 0.026305 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20572 | 0 | 0.026307 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20889 | 0 | 0.026307 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22155 | 0 | 0.026307 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19939 | 0 | 0.026307 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19623 | 0 | 0.026307 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32916 | 0 | 0.026307 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.003165 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18674 | 0 | 0.026307 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.003169 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.015845 | 0 | 0.026311 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.003169 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.066549 | 0 | 0.026311 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.00326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.03912 | 12 | 0.026402 | 0.31683
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11407 | 0 | 0.026497 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11642 | 0 | 0.026497 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10971 | 0 | 0.026497 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15399 | 0 | 0.026497 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.059383 | 0 | 0.026497 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.068442 | 0 | 0.026497 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.066765 | 0 | 0.026497 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11743 | 0 | 0.026497 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.06039 | 0 | 0.026497 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28652 | 0 | 0.026497 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.003355 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49654 | 0 | 0.026497 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.00342 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 2.5137 | 735 | 0.026562 | 19.5234
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.3639 | 104 | 0.026641 | 2.7707
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.3639 | 104 | 0.026641 | 2.7707
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18895 | 54 | 0.026641 | 1.4386
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18545 | 53 | 0.026641 | 1.412
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18895 | 54 | 0.026641 | 1.4386
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.19944 | 57 | 0.026641 | 1.5186
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18895 | 54 | 0.026641 | 1.4386
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18895 | 54 | 0.026641 | 1.4386
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20294 | 58 | 0.026641 | 1.5452
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.003499 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.20294 | 58 | 0.026641 | 1.5452
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.003759 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65031 | 0 | 0.026901 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.003759 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.50747 | 0 | 0.026901 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15981 | 42 | 0.026947 | 1.1318
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15981 | 42 | 0.026947 | 1.1318
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14459 | 38 | 0.026947 | 1.024
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.003805 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.14459 | 38 | 0.026947 | 1.024
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.00381 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51816 | 0 | 0.026952 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28201 | 0 | 0.027114 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28598 | 0 | 0.027114 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15491 | 0 | 0.027114 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.003972 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11916 | 0 | 0.027114 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.00407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.7326 | 0 | 0.027212 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.00407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.6455 | 0 | 0.027212 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.00407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.63899 | 0 | 0.027212 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.004073 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.92864 | 228 | 0.027215 | 6.2051
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2608 | 0 | 0.027217 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25754 | 0 | 0.027217 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33659 | 0 | 0.027217 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.004075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29992 | 0 | 0.027217 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.004077 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.066047 | 0 | 0.027219 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.004079 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.86883 | 213 | 0.027221 | 5.7982
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.004092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60971 | 0 | 0.027234 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.004092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.26639 | 0 | 0.027234 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.004097 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.676 | 165 | 0.027239 | 4.4945
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.004102 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.69324 | 169 | 0.027244 | 4.6043
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.004106 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.049272 | 12 | 0.027248 | 0.32698
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.004106 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.027248 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.004174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14609 | 0 | 0.027316 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.69327 | 0 | 0.02739 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66736 | 0 | 0.02739 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66906 | 0 | 0.02739 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66694 | 0 | 0.02739 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.004248 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1427 | 0 | 0.02739 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.004322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.33712 | 0 | 0.027464 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.004322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.34576 | 0 | 0.027464 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20079 | 46 | 0.027507 | 1.2653
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20079 | 46 | 0.027507 | 1.2653
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20079 | 46 | 0.027507 | 1.2653
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.24008 | 55 | 0.027507 | 1.5129
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.24008 | 55 | 0.027507 | 1.5129
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.004365 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.23571 | 54 | 0.027507 | 1.4854
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.29984 | 0 | 0.027755 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.27678 | 0 | 0.027755 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.29984 | 0 | 0.027755 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.004613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.29984 | 0 | 0.027755 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43398 | 0 | 0.027911 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.41776 | 0 | 0.027911 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4149 | 0 | 0.027911 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25991 | 0 | 0.027911 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.004769 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.058182 | 0 | 0.027911 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.00517 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.028312 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.005488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2744 | 50 | 0.02863 | 1.4315
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42133 | 0 | 0.029093 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39693 | 0 | 0.029093 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3154 | 0 | 0.029093 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91169 | 0 | 0.029093 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91348 | 0 | 0.029093 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90634 | 0 | 0.029093 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5713 | 0 | 0.029093 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.005951 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.452 | 0 | 0.029093 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.005951 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23804 | 0 | 0.029093 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.59739 | 0 | 0.029098 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.55331 | 0 | 0.029098 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.61168 | 0 | 0.029098 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.005956 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.60751 | 0 | 0.029098 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.005956 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19059 | 0 | 0.029098 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.005956 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17868 | 0 | 0.029098 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.006957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.1201 | 161 | 0.030099 | 4.846
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.006957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.1549 | 166 | 0.030099 | 4.9965
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.006957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7253 | 248 | 0.030099 | 7.4647
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.006957 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.7985 | 546 | 0.030099 | 16.4343
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.006957 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 4.4734 | 0 | 0.030099 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.006957 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.090441 | 13 | 0.030099 | 0.39129
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.007124 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23509 | 0 | 0.030266 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.007302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1902 | 0 | 0.030444 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.007302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1902 | 0 | 0.030444 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.007302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.789 | 0 | 0.030444 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.007319 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.7647 | 0 | 0.030461 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.007319 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.1279 | 0 | 0.030461 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.007319 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.3914 | 0 | 0.030461 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.007431 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34257 | 0 | 0.030573 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0515 | 0 | 0.032615 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0515 | 0 | 0.032615 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1273 | 0 | 0.032615 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.009473 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0373 | 0 | 0.032615 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.010075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71532 | 0 | 0.033217 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.010075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10075 | 0 | 0.033217 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67059 | 0 | 0.033958 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77226 | 0 | 0.033958 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.48672 | 0 | 0.033958 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0924 | 0 | 0.033958 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93018 | 0 | 0.033958 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95181 | 0 | 0.033958 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5408 | 0 | 0.033958 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19469 | 0 | 0.033958 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0167 | 0 | 0.033958 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75712 | 0 | 0.033958 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68141 | 0 | 0.033958 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77875 | 0 | 0.033958 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.70088 | 0 | 0.033958 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0924 | 0 | 0.033958 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0492 | 0 | 0.033958 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.114 | 0 | 0.033958 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82202 | 0 | 0.033958 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.86528 | 0 | 0.033958 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.86528 | 0 | 0.033958 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.010816 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8495 | 0 | 0.033958 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.013781 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.90955 | 66 | 0.036923 | 2.4369
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.106 | 76 | 0.037695 | 2.8649
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.106 | 76 | 0.037695 | 2.8649
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.5281 | 105 | 0.037695 | 3.958
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0769 | 74 | 0.037695 | 2.7895
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0769 | 74 | 0.037695 | 2.7895
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.014553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4844 | 102 | 0.037695 | 3.8449
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.0149 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 19.8617 | 0 | 0.038042 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.0149 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 19.7872 | 0 | 0.038042 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.017036 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.56219 | 0 | 0.040178 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.017036 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.4259 | 0 | 0.040178 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.017036 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040178 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.020817 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1249 | 0 | 0.043959 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.021697 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.044839 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8951 | 0 | 0.04713 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.943 | 0 | 0.04713 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8951 | 0 | 0.04713 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.919 | 0 | 0.04713 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8807 | 0 | 0.04713 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5997 | 0 | 0.04713 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1034 | 0 | 0.04713 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67166 | 0 | 0.04713 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0459 | 0 | 0.04713 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.023988 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.7751 | 0 | 0.04713 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.024243 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1637 | 0 | 0.047385 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.70157 | 0 | 0.048198 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.17539 | 0 | 0.048198 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97718 | 0 | 0.048198 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.37584 | 0 | 0.048198 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.17539 | 0 | 0.048198 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.37584 | 0 | 0.048198 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97718 | 0 | 0.048198 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.025056 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97718 | 0 | 0.048198 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.025186 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.20149 | 0 | 0.048328 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.025415 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38122 | 0 | 0.048557 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.025415 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.58454 | 0 | 0.048557 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.025628 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56382 | 22 | 0.04877 | 1.0729
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.025628 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28191 | 11 | 0.04877 | 0.53647
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.025628 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28191 | 11 | 0.04877 | 0.53647
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2367 | 47.7 | 0.049069 | 2.3406
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.96708 | 37.3 | 0.049069 | 1.8303
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.1926 | 46 | 0.049069 | 2.2572
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.025927 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2445 | 48 | 0.049069 | 2.3553
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.026037 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9007 | 0 | 0.049179 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.1319 | 0 | 0.049293 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.0011 | 0 | 0.049293 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6151 | 0 | 0.049293 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.7919 | 0 | 0.049293 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.8442 | 0 | 0.049293 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.026151 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.3212 | 0 | 0.049293 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.026151 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.31381 | 0 | 0.049293 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 0 | 0.049418 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 0 | 0.049418 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 0 | 0.049418 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.42042 | 0 | 0.049418 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 0 | 0.049418 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 0 | 0.049418 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.6569 | 0 | 0.049418 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.026276 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.39414 | 0 | 0.049418 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.026389 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8 | 144 | 0.049531 | 7.1325
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.026389 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9611 | 188 | 0.049531 | 9.3119
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.026471 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.8943 | 336 | 0.049613 | 16.6701
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.026471 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7648 | 180 | 0.049613 | 8.9304
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.026475 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.9262 | 0 | 0.049617 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.026475 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.9342 | 0 | 0.049617 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.026475 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.0507 | 0 | 0.049617 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.026481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7666 | 180 | 0.049623 | 8.9322
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.026541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.8647 | 334 | 0.049683 | 16.5943
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.026541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 9.0239 | 340 | 0.049683 | 16.8924
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.026541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7774 | 180 | 0.049683 | 8.943
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.026541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7774 | 180 | 0.049683 | 8.943
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.026557 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.66392 | 0 | 0.049699 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.026557 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.66392 | 0 | 0.049699 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.026584 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0102 | 0 | 0.049726 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.026592 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0105 | 0 | 0.049734 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.026732 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.77523 | 0 | 0.049874 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5175 | 0 | 0.049924 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0981 | 0 | 0.049924 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0177 | 0 | 0.049924 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.50886 | 0 | 0.049924 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5175 | 0 | 0.049924 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.96415 | 0 | 0.049924 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1516 | 0 | 0.049924 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.5892 | 0 | 0.049924 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.9637 | 0 | 0.049924 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.3391 | 0 | 0.049924 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.473 | 0 | 0.049924 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.026782 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.3391 | 0 | 0.049924 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.026805 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0186 | 38 | 0.049947 | 1.898
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.026805 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.51734 | 19.3 | 0.049947 | 0.96399
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.026805 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.40208 | 15 | 0.049947 | 0.74921
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.026805 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2598 | 47 | 0.049947 | 2.3475
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.026805 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.049947 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.02687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8693 | 144 | 0.050012 | 7.2018
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.02687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8693 | 144 | 0.050012 | 7.2018
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.02687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.5948 | 171 | 0.050012 | 8.5521
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.026871 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.5623 | 207 | 0.050013 | 10.3528
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.026871 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.8229 | 216.7 | 0.050013 | 10.8379
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.026871 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.5028 | 242 | 0.050013 | 12.1032
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.026944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9473 | 146.5 | 0.050086 | 7.3377
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.026944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.985 | 147.9 | 0.050086 | 7.4078
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.026944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.6613 | 173 | 0.050086 | 8.6649
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.027245 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3047 | 158 | 0.050387 | 7.9612
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.027245 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3592 | 160 | 0.050387 | 8.062
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.027245 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7679 | 175 | 0.050387 | 8.8178
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.027329 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050471 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.027393 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.32872 | 0 | 0.050535 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.027393 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.30132 | 0 | 0.050535 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.027393 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.32872 | 0 | 0.050535 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.027824 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050966 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.027848 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.5164 | 0 | 0.05099 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.028472 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051614 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.0287 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051842 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.028703 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.8703 | 100 | 0.051845 | 5.1845
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.028703 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.8703 | 100 | 0.051845 | 5.1845
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.028703 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051845 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.028703 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051845 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.028703 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051845 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.028703 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051845 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.029009 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.24368 | 8.4 | 0.052151 | 0.43807
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.029107 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 16.9985 | 0 | 0.052249 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.029107 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.3187 | 0 | 0.052249 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.029143 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 12.6189 | 0 | 0.052285 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.02929 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.70296 | 24 | 0.052432 | 1.2584
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.02929 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.70296 | 24 | 0.052432 | 1.2584
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.02929 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.67367 | 23 | 0.052432 | 1.2059
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.030538 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 12.093 | 0 | 0.05368 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.032725 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.8679 | 0 | 0.055867 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.032725 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 24.5437 | 0 | 0.055867 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6376 | 50 | 0.055893 | 2.7947
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6376 | 50 | 0.055893 | 2.7947
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6376 | 50 | 0.055893 | 2.7947
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.032751 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6376 | 50 | 0.055893 | 2.7947
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.033058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.124 | 155 | 0.0562 | 8.7111
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.033058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.6199 | 170 | 0.0562 | 9.5541
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.033058 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.124 | 155 | 0.0562 | 8.7111
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.033199 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.9255 | 58 | 0.056341 | 3.2678
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.033199 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.9547 | 89 | 0.056341 | 5.0144
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4608 | 44 | 0.056341 | 2.479
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4608 | 44 | 0.056341 | 2.479
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4276 | 43 | 0.056341 | 2.4227
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.033199 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.494 | 45 | 0.056341 | 2.5354
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.033317 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.56 | 407 | 0.056459 | 22.979
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8985 | 147 | 0.056465 | 8.3004
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.5986 | 138 | 0.056465 | 7.7922
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.6652 | 140 | 0.056465 | 7.9052
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8985 | 147 | 0.056465 | 8.3004
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0648 | 182 | 0.056465 | 10.2767
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.033323 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.598 | 198 | 0.056465 | 11.1802
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.033349 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 14.14 | 0 | 0.056491 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.033349 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 14.1733 | 0 | 0.056491 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.033369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.056511 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.033369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.056511 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.033369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.056511 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.033399 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.9804 | 209 | 0.056541 | 11.8172
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.033399 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.2142 | 216 | 0.056541 | 12.2129
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5364 | 46 | 0.056541 | 2.6009
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5698 | 47 | 0.056541 | 2.6574
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5364 | 46 | 0.056541 | 2.6009
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.033399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5364 | 46 | 0.056541 | 2.6009
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.033422 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.7699 | 412 | 0.056564 | 23.3045
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.033422 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.3688 | 400 | 0.056564 | 22.6258
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.033981 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.40777 | 0 | 0.057123 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8742 | 142 | 0.057467 | 8.1604
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9771 | 145 | 0.057467 | 8.3328
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.1831 | 151 | 0.057467 | 8.6776
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.034325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.9543 | 290 | 0.057467 | 16.6655
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.035061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.3468 | 152.5 | 0.058203 | 8.876
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.035061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.2416 | 149.5 | 0.058203 | 8.7014
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.035061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.1552 | 232.6 | 0.058203 | 13.5381
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.8614 | 223.9 | 0.058253 | 13.0429
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.9 | 225 | 0.058253 | 13.107
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.8859 | 224.6 | 0.058253 | 13.0837
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.035111 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.9597 | 226.7 | 0.058253 | 13.206
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.036403 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14561 | 0 | 0.059545 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.2304 | 0 | 0.060251 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 8.2382 | 0 | 0.060251 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.8281 | 0 | 0.060251 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 8.3124 | 0 | 0.060251 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.037109 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.2675 | 0 | 0.060251 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.037462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.089909 | 0 | 0.060604 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.037462 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.089909 | 0 | 0.060604 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.037711 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.9779 | 132 | 0.060853 | 8.0327
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.037711 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.0533 | 134 | 0.060853 | 8.1544
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.037711 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.1807 | 323 | 0.060853 | 19.6557
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.037776 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.090662 | 0 | 0.060918 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.037776 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.090662 | 0 | 0.060918 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.037776 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10577 | 0 | 0.060918 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.047689 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.28613 | 0 | 0.070831 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.057862 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.79271 | 0 | 0.081004 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.05856 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0541 | 0 | 0.081702 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.05856 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0541 | 0 | 0.081702 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.05856 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.8784 | 0 | 0.081702 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.064594 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 27.2587 | 422 | 0.087736 | 37.0248
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.065705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8397 | 0 | 0.088847 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.065705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.9054 | 0 | 0.088847 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.073935 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3308 | 0 | 0.097077 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.073935 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3308 | 0 | 0.097077 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.4086 | 49 | 0.11311 | 5.5426
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.1387 | 46 | 0.11311 | 5.2032
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.1387 | 46 | 0.11311 | 5.2032
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2286 | 47 | 0.11311 | 5.3163
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.089971 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.8555 | 154 | 0.11311 | 17.4195
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.089971 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.3157 | 148 | 0.11311 | 16.7408
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3186 | 48 | 0.11311 | 5.4294
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.089971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3186 | 48 | 0.11311 | 5.4294
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.095117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.3291 | 0 | 0.11826 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.095117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.234 | 0 | 0.11826 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.095117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.3291 | 0 | 0.11826 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.0938 | 42 | 0.12061 | 5.0658
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2887 | 44 | 0.12061 | 5.307
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.2887 | 44 | 0.12061 | 5.307
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.097471 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5811 | 47 | 0.12061 | 5.6688
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.099125 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 30.7288 | 310 | 0.12227 | 37.9029
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.099125 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 40.9386 | 413 | 0.12227 | 50.4964
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.10474 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.83789 | 0 | 0.12788 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.10474 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.83789 | 0 | 0.12788 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 268
| 25 | 268
| 30 | 268
| 35 | 268
| 40 | 268
| 45 | 268
| 50 | 268
| 55 | 268
| 60 | 267
| 65 | 261
| 70 | 256
| 75 | 250
| 80 | 245
| 85 | 239
| 90 | 233
| 95 | 226
| 100 | 220
| 105 | 213
| 110 | 206
| 115 | 199
| Max | 268
| Min | 199
| Avg | 247.95