## test results
CRE test for: |  | 1426 FISHRDSS - 1427 FISHERRD | [5 empty] | FAIL
Line Rating: |  | 287
Direction |  | North | → | West |  | N-W
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1426 FISHRDSS - 1427 FISHERRD
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.003208
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.00051629
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.052141
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.00065273
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1426 FISHRDSS - 1427 FISHERRD
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.0035577
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.00058084
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.036952
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0006726
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 1426 FISHRDSS - 1427 FISHERRD
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.0037888
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.04016
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.0025354
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.036436
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.001169
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.052814
PTDF tests
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.04016 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.04016 | -0.0037888
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.2171
[6 empty] | Concentration |  | -5.4059 | FAIL
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.06273
[6 empty] | Concentration |  | -1.562 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 13.823
| Percent of line rating => | [6 empty] | 4.816% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -20.2881
[7 empty] | B1(N-S) | -0.036741 | 0.040127 | 0.076868 | -0.036741
[7 empty] | B2 (N-W) | 0 | 0.81477 | 0.81477 | 0
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.032463 | 0.018975 | 0.051438 | -0.032463
[7 empty] | B4 (S-W) | 0.036559 | 0.77577 | 0.73921 | 0.036559
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.0036931 | -0.020024 | -0.023717 | 0.0036931
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.27856 | -0.79294 | -1.0715 | 0.27856
[7 empty] | test | 0 | 0.81477 | 0.81477 | 0
[7 empty] | B1 | -4.509%
Deployment Error Percent | [6 empty] | B2 | 0%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -3.984%
[7 empty] | B4 | 4.487%
[7 empty] | B5 | 0.4533%
[7 empty] | B6 | 34.19%
[7 empty] | Max Abs Error | 34.19% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-W
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:1426 FISHRDSS - 1427 FISHERRD C: 1422 BOWMAN5 - 1425 FISHRDSS | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:1426 FISHRDSS - 1427 FISHERRD C: 1422 BOWMAN5 - 1425 FISHRDSS
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.001205 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -0.30728
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.001205 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -0.17955
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.001549 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.023235
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.001549 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.023235
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.001205 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -0.18437
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.001191 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -0.17865
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.001191 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -0.09528
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007026 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -0.5129
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007026 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -0.83609
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007026 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -1.4403
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007026 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -0.71665
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007026 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -0.6745
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.023127 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.27752
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.023127 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.27752
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.001761 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -0.29585
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.001761 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -0.15849
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.011125 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.20025
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.011125 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.20025
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.011125 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.42275
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.021935 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -6.3173
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.021935 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.2244
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.021935 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.2244
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.025743 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -2.8961
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.003092 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.12368
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.003125 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -0.24688
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.003125 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -0.33125
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.003125 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -0.45625
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.003125 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -0.2375
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.005928 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -0.35568
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.005928 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -0.37346
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.003102 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.06204
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.003102 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.07755
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.003102 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.12718
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.001302 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -0.60283
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 2.6091
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 2.5696
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.6486
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.6486
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.6486
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039532 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 4.5066
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039532 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 20.359
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 2.7009
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.8237
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.8237
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.7418
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.7418
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 2.66
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.039802 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 2.7861
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.039802 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 2.9215
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.039802 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 2.8021
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 5.9712
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 8.7578
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.043039 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 4.2609
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.043039 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 2.6254
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.042962 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 6.0576
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.043039 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 1.076
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.043039 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.9669
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.043039 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.9669
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.042962 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 5.1554
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.040827 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 1.0533
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.04023 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 4.0431
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.041071 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 4.9285
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.040276 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 2.336
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.040367 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 8.6466
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.045449 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 6.8174
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.040423 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.26679
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.040423 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.3865
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.045449 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 4.5903
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.041224 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 4.9469
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.002418 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 0.88499
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.019569 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -4.7357
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.034511 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 13.8044
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.034412 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 8.1212
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.026734 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 4.4111
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.004719 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -0.96268
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.004719 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -0.94852
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.004719 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -1.142
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.94982
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.94982
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.94982
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.80735
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.015651 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -1.8781
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.001407 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 0.08442
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.003489 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -0.26167
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.003489 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -0.27772
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.003489 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -0.30843
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -0.55312
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.53929
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -0.67757
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.53929
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -0.54275
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -0.68449
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.003994 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -0.67898
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.003994 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -2.0769
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003509 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -1.2983
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.003308 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -1.8459
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.003308 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -1.9153
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.003308 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -2.6729
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.004651 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -0.52091
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.004651 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -0.4651
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.004651 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -1.7581
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000319 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -0.069319
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000319 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -0.065395
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000319 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -0.086896
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.00103 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -0.7931
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -0.12026
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.11854
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.11854
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -0.11682
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -5.3e-05 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -0.061321
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -5.3e-05 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -0.061374
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -0.41395
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -0.41765
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.002095 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -0.45336
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.002095 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -0.45273
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -0.39178
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -0.38993
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.002575 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -1.0171
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.002643 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -1.1497
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.002575 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -1.1201
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.003825 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -0.52785
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.002645 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -0.31211
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.002645 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -0.30417
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.002645 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -1.4706
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.002928 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -1.1361
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.002928 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -1.5079
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.002564 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -2.0127
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.002564 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -2.0384
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.002564 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -1.9999
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.002468 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -0.44918
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.002468 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -1.1945
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.002319 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -0.51946
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.002467 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -0.12335
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.002473 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.10387
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.001974 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -1.214
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.001974 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -1.1587
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.001225 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -0.65782
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.001225 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -0.96408
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.001147 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -0.086025
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.001147 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -0.25463
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.000293 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -0.16672
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.15424
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.15941
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.000762 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 0.31013
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.033948
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.034686
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.033948
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.033948
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.000726 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 0.30782
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.000726 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 0.30855
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000831 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.048198
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000831 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.073959
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.036564
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.036564
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.035733
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.037395
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 0.30406
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 0.2952
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.000636 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 0.34726
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.000636 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 0.477
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.000674 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.041114
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.000674 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.06403
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.000674 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.10177
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.000659 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.10214
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.000659 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.11203
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.000659 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.10214
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.000422 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.009284
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.000422 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.004642
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.000422 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.004642
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.018794
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.014696
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.018124
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.018912
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000957 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.011484
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000957 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.010527
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.002169 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.052056
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.002169 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.052056
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.002169 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.049887
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.000743 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 0.29423
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.000256 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -0.34125
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.000256 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -0.33997
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000571 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.021698
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000571 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.01102
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000571 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.008565
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000571 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.026837
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.037805 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 2.8354
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.050411 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 7.5617
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.046247 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 7.8389
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.030836 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 4.6254
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.042446 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 2.6741
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.25405 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 165.0582
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.004316 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.17264
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.004316 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.17264
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.002037 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 0.85961
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.000146 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.019272
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.000146 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.019564
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.000146 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 0.047158
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 6.4e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.010112
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 6.4e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.01024
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 6.4e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 0.0112
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 5.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 0.03212
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 5.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 0.032725
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 5.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 0.023815
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.10031
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.1008
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.10062
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.10156
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.000298 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.002384
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.000298 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.002384
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.002104 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.037872
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.002104 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.037872
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.002104 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.03156
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.002576 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.035291
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.001631 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.029358
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.001631 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.029358
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000712 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.02492
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000712 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.024208
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000712 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.02492
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.001935 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.05418
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.001935 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.056115
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.039613 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.3865
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.039613 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.1884
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.00445
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.00445
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.00445
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.00445
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.000546 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.003276
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.000488 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0011712
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.000488 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0011712
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.000488 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.0013664
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.000552 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.002208
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.00042 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.001008
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.00042 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.001008
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.077175
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.07245
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.0735
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.077175
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.09555
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.10395
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.000141 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.021503
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.000141 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.02108
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.000141 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 0.032797
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.069012
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.07047
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.073386
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 0.14094
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.011896 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.39257
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.011896 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.2974
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000957 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.011484
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.000367 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.026791
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.020461
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.020979
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.00924
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.00231
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.020461
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.02072
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.020306
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.006475
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.011914
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.000514 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 0.32331
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.000382 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.055008
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.000382 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.071816
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.000416 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.004992
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.008804 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.052824
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.000515 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 0.17304
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.000521 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 0.17401
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.000521 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 0.17714
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.000529 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.020102
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.000525 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.013125
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.000525 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.013125
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.000525 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.01995
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.000544 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.015776
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.000516 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.076523
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.000516 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.076678
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.000516 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.078948
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.07663
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.074205
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.0485
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.070325
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.071295
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.061595
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.000652 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.095518
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.000652 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.096431
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.000652 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.1128
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.000602 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.12461
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.000602 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.13045
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.000602 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.14568
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.000601 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.086544
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.000601 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.086544
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.000601 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.10277
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.000259 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 0.08029
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.000259 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 0.10697
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.009534
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.009988
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.009988
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.010669
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.013181
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.012374
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.012374
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.012643
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000269 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.041426
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000269 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.039812
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.012912
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.012912
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.7776
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.7776
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 3.6823
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 3.1744
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 3.1744
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 4.5632
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 8.261
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 5.6382
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 5.2534
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 5.3962
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 5.8327
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 8.3324
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 7.3098
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 4.4243
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 8.7088
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 6.8901
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 7.9616
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 4.8526
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.03981 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 5.9317
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.041867 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 7.5361
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.041867 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 7.5361
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.041786 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 9.4018
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.039207 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 4.9009
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.039207 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 4.9009
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -0.49126
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -0.49477
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -1.0843
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -0.50179
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -0.5053
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -1.0878
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.002275 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -0.4459
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.002275 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -0.25252
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.003377 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.47189
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.48068
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.48068
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -1.2134
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -0.47482
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.47189
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -0.47775
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -1.1988
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.002856 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.002856 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -0.37207
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -0.32682
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -0.36453
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -1.0031
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.002042 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -0.30773
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.002042 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -0.30834
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.002042 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -0.36225
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.002066 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -0.313
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.002066 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -0.31465
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.002066 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -0.36672
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.000293 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -0.17023
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -1.3483
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -1.3483
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.001299 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.041568
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.001293 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.062064
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.001293 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.059478
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.015612
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.066351
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001301 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.022117
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.028622
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.032525
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.001293 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -0.13576
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.044407 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 3.7302
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.037775 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 3.022
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.037759 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 5.6639
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.037759 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 5.6639
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.045029
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.042421
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.033708
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -0.097435
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -0.097626
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -0.096863
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.061056
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -0.15518
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.02544
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.063791
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.059084
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.065317
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.064872
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.020352
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.01908
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.054168
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.054168
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -0.058072
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -0.053436
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -0.24018
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -0.24128
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.000724 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.098464
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.000587 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.019371
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.030408
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.030408
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.027512
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.027512
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.000462 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.032802
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.000462 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.00462
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.000583 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.095029
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.000583 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.095029
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.000583 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -0.14283
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.044915
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.04146
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.044915
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.044915
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.000712 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.10609
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.000712 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.046351
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.062244
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.059918
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.059508
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.037278
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.0083448
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.00075 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -0.55725
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.000739 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -0.54317
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.000753 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.12952
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.000753 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.12952
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.000753 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.12952
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.14048
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.000726 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -0.1256
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.000726 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.09801
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.12373
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.12266
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.12076
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -0.20459
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.045632
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.045062
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.058894
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.052477
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -0.11506
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -0.11076
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -0.11104
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -0.11069
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -0.18965
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.000749 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.003745
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.000749 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.015729
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -0.18782
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.19001
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.19001
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -0.46284
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.000764 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -0.30407
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.032292
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.032292
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.032292
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.03861
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.03861
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.037908
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.001689 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -1.3968
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.001689 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -1.3833
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.000574 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.026461
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.021204
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.021204
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.029295
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.020646
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.020646
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.028458
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.000713 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -0.12834
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.000713 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -0.11308
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.000713 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -0.11194
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.000709 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.024815
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.000668 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -0.30661
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.04875
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.0495
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.0525
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.04725
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.0465
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.078
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.04425
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.12667
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.12505
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.12505
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000812 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.13154
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.000752 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.11806
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.050907
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.051624
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.027963
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.02151
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.000703 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.054834
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.000703 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.05624
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.011551
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.000712 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -0.11748
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.000712 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -0.12033
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.000713 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -0.15187
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.000713 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -0.16256
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.000711 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.008532
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.000711 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.012798
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.000656 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.0328
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.076648
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.076648
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.039798
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.039061
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.039798
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.042009
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.039798
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.039798
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.042746
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.042746
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.000747 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.008964
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.043064
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.045371
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.043064
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.043064
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.045371
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.043064
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.0003 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.0198
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000599 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -0.096439
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000599 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -0.099434
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000599 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -0.14855
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000599 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -0.32705
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000599 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -0.38516
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.000582 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -0.37888
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.000582 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -0.32825
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.000582 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -0.3492
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000599 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.007787
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.00075 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.009
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.025228
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.025747
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.024263
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.034058
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.013133
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.015137
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.014766
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.02597
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.013356
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.063367
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.10982
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.02666
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.030702
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.01935
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.04343
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.03698
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.03784
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.0215
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.00774
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.04042
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.0301
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.02709
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.03096
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.027864
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.04343
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.04171
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.04429
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.03268
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.0344
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.0344
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -0.07353
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.020698
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.03702 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 2.832
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.037805 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 3.0244
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.037805 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.5122
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.037927 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.0342
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.037778 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 3.0222
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.03714 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 2.9712
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.036931 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 3.1022
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.037927 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.0342
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.1018
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.049112 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 5.8934
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.049112 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 11.4431
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.049112 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 8.3589
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.19825
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.16431
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.20003
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.10269
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.0893
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.074485 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 4.4691
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.012995 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.033614 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.0384 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.18432
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 1.8207
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 5.2193
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 6.5545
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 5.7777
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 5.098
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 3.9084
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.039207 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 5.8811
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 4.3968
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 5.8429
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 7.2694
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 8.3833
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.000571 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.008085 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.007252
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.011292
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.019166
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.052546
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.022919
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.021242
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.010621
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.052546
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.020124
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.024037
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.012298
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.01287
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.00495
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.00231
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.00495
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.01287
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.01287
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.082732
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.02795
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.030745
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.02795
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000485 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.00582
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.00519
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.007958
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.000274 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.013152
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.000341 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.002728
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.000516 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.09288
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.000515 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.0927
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.000521 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.09378
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.000521 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.09378
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001583 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.1583
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001583 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.1583
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.01245
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.01245
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.01245
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.007968
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.01245
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.01245
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.01245
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.00747
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001583 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001583 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 0.7915
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001583 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 0.7915
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001583 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.00069 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.011896 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.001248 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.000717 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:1426 FISHRDSS - 1427 FISHERRD C: 1422 BOWMAN5 - 1425 FISHRDSS | [7 empty] | 13.823
Number of Bus | Name of Bus | ID | Max MW | L:1426 FISHRDSS - 1427 FISHERRD C: 1422 BOWMAN5 - 1425 FISHRDSS | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.001205 | north | Y | 0.002003 | -0.0017213 | -0.053346 | -0.00055227 | 0.00055227 | houston | Y | 0.002003 | 0.36993
239 | BOSQUESW | 1 | 149 | -0.001205 | north | Y | 0.002003 | -0.0017213 | -0.053346 | -0.00055227 | 0.00055227 | houston | Y | 0.002003 | 0.21615
244 | WHITNYDM | 1 | 15 | -0.001549 | north | N | 0.001659 | -0.0020653 | -0.05369 | -0.00089627 | 0.00089627 | houston | Y | 0.001659 | 0
245 | WHITNYDM | 2 | 15 | -0.001549 | north | N | 0.001659 | -0.0020653 | -0.05369 | -0.00089627 | 0.00089627 | houston | Y | 0.001659 | 0
247 | BOSQUESW | 2 | 153 | -0.001205 | north | Y | 0.002003 | -0.0017213 | -0.053346 | -0.00055227 | 0.00055227 | houston | Y | 0.002003 | 0.22196
251 | BOSQUESW | 2 | 150 | -0.001191 | north | Y | 0.002017 | -0.0017073 | -0.053332 | -0.00053827 | 0.00053827 | houston | Y | 0.002017 | 0.22181
253 | BOSQUESW | 2 | 80 | -0.001191 | north | Y | 0.002017 | -0.0017073 | -0.053332 | -0.00053827 | 0.00053827 | houston | Y | 0.002017 | 0.1183
332 | RWMILLER | 1 | 73 | -0.007026 | north | Y | -0.003818 | -0.0075423 | -0.059167 | -0.0063733 | 0.003818 | North | N | 0.003818 | 0
333 | RWMILLER | 2 | 119 | -0.007026 | north | Y | -0.003818 | -0.0075423 | -0.059167 | -0.0063733 | 0.003818 | North | N | 0.003818 | 0
334 | RWMILLER | 3 | 205 | -0.007026 | north | Y | -0.003818 | -0.0075423 | -0.059167 | -0.0063733 | 0.003818 | North | N | 0.003818 | 0
335 | RWMILLER | 4 | 102 | -0.007026 | north | Y | -0.003818 | -0.0075423 | -0.059167 | -0.0063733 | 0.003818 | North | N | 0.003818 | 0
336 | RWMILLER | 5 | 96 | -0.007026 | north | Y | -0.003818 | -0.0075423 | -0.059167 | -0.0063733 | 0.003818 | North | N | 0.003818 | 0
344 | MRSSHPRD | 1 | 12 | -0.023127 | north | N | -0.019919 | -0.023643 | -0.075268 | -0.022474 | 0.019919 | North | N | 0.019919 | 0
345 | MRSSHPRD | 2 | 12 | -0.023127 | north | N | -0.019919 | -0.023643 | -0.075268 | -0.022474 | 0.019919 | North | N | 0.019919 | 0
366 | JNSNCNTY | 1 | 168 | -0.001761 | north | Y | 0.001447 | -0.0022773 | -0.053902 | -0.0011083 | 0.0011083 | houston | Y | 0.001447 | 0.056902
367 | JNSNCNTY | 2 | 90 | -0.001761 | north | Y | 0.001447 | -0.0022773 | -0.053902 | -0.0011083 | 0.0011083 | houston | Y | 0.001447 | 0.030483
503 | NTHTEXAS | 1 | 18 | -0.011125 | north | Y | -0.007917 | -0.011641 | -0.063266 | -0.010472 | 0.007917 | North | N | 0.007917 | 0
504 | NTHTEXAS | 2 | 18 | -0.011125 | north | Y | -0.007917 | -0.011641 | -0.063266 | -0.010472 | 0.007917 | North | N | 0.007917 | 0
505 | NTHTEXAS | 3 | 38 | -0.011125 | north | Y | -0.007917 | -0.011641 | -0.063266 | -0.010472 | 0.007917 | North | N | 0.007917 | 0
580 | JCKCNTY8 | 1 | 288 | -0.021935 | north | Y | -0.018727 | -0.022451 | -0.074076 | -0.021282 | 0.018727 | North | N | 0.018727 | 0
581 | JCKCNTY8 | 2 | 147 | -0.021935 | north | Y | -0.018727 | -0.022451 | -0.074076 | -0.021282 | 0.018727 | North | N | 0.018727 | 0
582 | JCKCNTY8 | 3 | 147 | -0.021935 | north | Y | -0.018727 | -0.022451 | -0.074076 | -0.021282 | 0.018727 | North | N | 0.018727 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.025743 | north | Y | -0.022535 | -0.026259 | -0.077884 | -0.02509 | 0.022535 | North | N | 0.022535 | 0
837 | NEWMAN_G | 1 | 40 | -0.003092 | north | Y | 0.00011597 | -0.0036083 | -0.055233 | -0.0024393 | 0.00011597 | North | N | 0.00011597 | 0
842 | OLINGER_ | 1 | 79 | -0.003125 | north | Y | 8.2971e-05 | -0.0036413 | -0.055266 | -0.0024723 | 8.2971e-05 | North | N | 8.2971e-05 | 0
843 | OLINGER_ | 1 | 106 | -0.003125 | north | Y | 8.2971e-05 | -0.0036413 | -0.055266 | -0.0024723 | 8.2971e-05 | North | N | 8.2971e-05 | 0
844 | OLINGER_ | 1 | 146 | -0.003125 | north | Y | 8.2971e-05 | -0.0036413 | -0.055266 | -0.0024723 | 8.2971e-05 | North | N | 8.2971e-05 | 0
845 | OLINGER_ | 1 | 76 | -0.003125 | north | Y | 8.2971e-05 | -0.0036413 | -0.055266 | -0.0024723 | 8.2971e-05 | North | N | 8.2971e-05 | 0
923 | SPENCER_ | 1 | 60 | -0.005928 | north | Y | -0.00272 | -0.0064443 | -0.058069 | -0.0052753 | 0.00272 | North | N | 0.00272 | 0
924 | SPENCER_ | 1 | 63 | -0.005928 | north | Y | -0.00272 | -0.0064443 | -0.058069 | -0.0052753 | 0.00272 | North | N | 0.00272 | 0
948 | STEAM1 | 1 | 20 | -0.003102 | north | Y | 0.00010597 | -0.0036183 | -0.055243 | -0.0024493 | 0.00010597 | North | N | 0.00010597 | 0
949 | STEAM2 | 1 | 25 | -0.003102 | north | Y | 0.00010597 | -0.0036183 | -0.055243 | -0.0024493 | 0.00010597 | North | N | 0.00010597 | 0
950 | STEAM3 | 1 | 41 | -0.003102 | north | Y | 0.00010597 | -0.0036183 | -0.055243 | -0.0024493 | 0.00010597 | North | N | 0.00010597 | 0
990 | GIBN_CRE | 1 | 463 | -0.001302 | north | Y | 0.001906 | -0.0018183 | -0.053443 | -0.00064927 | 0.00064927 | houston | Y | 0.001906 | 0.58185
1002 | PBCTAGE_ | A | 66 | 0.039532 | west | Y | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1003 | PBCTBGE_ | B | 65 | 0.039532 | west | Y | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1004 | PBCTCGE_ | C | 67 | 0.039532 | west | Y | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1005 | PBCTDGE_ | D | 67 | 0.039532 | west | Y | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1006 | PBCTEGE_ | E | 67 | 0.039532 | west | Y | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1007 | PB5GEN_6 | MB | 114 | 0.039532 | west | Y | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1008 | PB6GEN_7 | MB | 515 | 0.039532 | west | Y | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1039 | MRGNAG_1 | A | 66 | 0.040923 | west | Y | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1040 | MRGNBG_2 | B | 69 | 0.040923 | west | Y | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1041 | MRGNCG_3 | C | 69 | 0.040923 | west | Y | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1042 | MRGNDG_4 | D | 67 | 0.040923 | west | Y | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1043 | MRGNEG_5 | E | 67 | 0.040923 | west | Y | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1044 | MRGNFG_6 | F | 65 | 0.040923 | west | Y | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1045 | CALENG1G | 1 | 70 | 0.039802 | west | N | 0.04301 | 0.039286 | -0.012339 | 0.040455 | 0.012339 | west | N | 0.012339 | 0
1046 | CALENG2G | 2 | 73.4 | 0.039802 | west | N | 0.04301 | 0.039286 | -0.012339 | 0.040455 | 0.012339 | west | N | 0.012339 | 0
1047 | CALENG3G | 3 | 70.4 | 0.039802 | west | N | 0.04301 | 0.039286 | -0.012339 | 0.040455 | 0.012339 | west | N | 0.012339 | 0
1058 | LONGSHOR | 1 | 150 | 0.039808 | west | Y | 0.043016 | 0.039292 | -0.012333 | 0.040461 | 0.012333 | west | N | 0.012333 | 0
1058 | LONGSHOR | 2 | 220 | 0.039808 | west | Y | 0.043016 | 0.039292 | -0.012333 | 0.040461 | 0.012333 | west | N | 0.012333 | 0
1061 | CIELOGEN | 1 | 99 | 0.043039 | west | Y | 0.046247 | 0.042523 | -0.0091023 | 0.043692 | 0.0091023 | west | N | 0.0091023 | 0
1062 | CIELOGEN | 1 | 61 | 0.043039 | west | Y | 0.046247 | 0.042523 | -0.0091023 | 0.043692 | 0.0091023 | west | N | 0.0091023 | 0
1068 | SCURRYCW | 1 | 141 | 0.042962 | west | Y | 0.04617 | 0.042446 | -0.0091793 | 0.043615 | 0.0091793 | west | N | 0.0091793 | 0
1069 | KINDERMG | 1 | 25 | 0.043039 | west | N | 0.046247 | 0.042523 | -0.0091023 | 0.043692 | 0.0091023 | west | N | 0.0091023 | 0
1070 | KINDERMG | 1 | 45.7 | 0.043039 | west | N | 0.046247 | 0.042523 | -0.0091023 | 0.043692 | 0.0091023 | west | N | 0.0091023 | 0
1071 | KINDERMG | 1 | 45.7 | 0.043039 | west | N | 0.046247 | 0.042523 | -0.0091023 | 0.043692 | 0.0091023 | west | N | 0.0091023 | 0
1073 | SCURRYCW | 2 | 120 | 0.042962 | west | Y | 0.04617 | 0.042446 | -0.0091793 | 0.043615 | 0.0091793 | west | N | 0.0091793 | 0
1320 | BSP 1 | 1 | 25.8 | 0.040827 | west | N | 0.044035 | 0.040311 | -0.011314 | 0.04148 | 0.011314 | west | N | 0.011314 | 0
1326 | STANTONW | 1 | 100.5 | 0.04023 | west | Y | 0.043438 | 0.039714 | -0.011911 | 0.040883 | 0.011911 | west | N | 0.011911 | 0
1327 | WILDHRSE | 1 | 120 | 0.041071 | west | Y | 0.044279 | 0.040555 | -0.01107 | 0.041724 | 0.01107 | west | N | 0.01107 | 0
1328 | OCOTILLO | 1 | 58 | 0.040276 | west | Y | 0.043484 | 0.03976 | -0.011865 | 0.040929 | 0.011865 | west | N | 0.011865 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.040367 | west | Y | 0.043575 | 0.039851 | -0.011774 | 0.04102 | 0.011774 | west | N | 0.011774 | 0
1343 | TRENTIPP | 1 | 150 | 0.045449 | west | Y | 0.048657 | 0.044933 | -0.0066923 | 0.046102 | 0.0066923 | west | N | 0.0066923 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.040423 | west | Y | 0.043631 | 0.039907 | -0.011718 | 0.041076 | 0.011718 | west | N | 0.011718 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.040423 | west | Y | 0.043631 | 0.039907 | -0.011718 | 0.041076 | 0.011718 | west | N | 0.011718 | 0
1354 | AEPWIND_ | 1 | 101 | 0.045449 | west | Y | 0.048657 | 0.044933 | -0.0066923 | 0.046102 | 0.0066923 | west | N | 0.0066923 | 0
1360 | GUNSIGHT | 1 | 120 | 0.041224 | west | Y | 0.044432 | 0.040708 | -0.010917 | 0.041877 | 0.010917 | west | N | 0.010917 | 0
1432 | GRHAMSES | 2 | 366 | 0.002418 | north | Y | 0.005626 | 0.0019017 | -0.049723 | 0.0030707 | 0.0019017 | south | Y | 0.005626 | 1.3631
1433 | GRHAMSES | 1 | 242 | -0.019569 | north | Y | -0.016361 | -0.020085 | -0.07171 | -0.018916 | 0.016361 | North | N | 0.016361 | 0
1437 | MESQUITW | 1 | 400 | 0.034511 | west | Y | 0.037719 | 0.033995 | -0.01763 | 0.035164 | 0.01763 | west | N | 0.01763 | 0
1438 | MESQUITW | 1 | 236 | 0.034412 | west | Y | 0.03762 | 0.033896 | -0.017729 | 0.035065 | 0.017729 | west | N | 0.017729 | 0
1442 | COKFIELD | 1 | 165 | 0.026734 | west | Y | 0.029942 | 0.026218 | -0.025407 | 0.027387 | 0.025407 | west | N | 0.025407 | 0
1453 | WCPWRCO_ | 1 | 204 | -0.004719 | north | Y | -0.001511 | -0.0052353 | -0.05686 | -0.0040663 | 0.001511 | North | N | 0.001511 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.004719 | north | Y | -0.001511 | -0.0052353 | -0.05686 | -0.0040663 | 0.001511 | North | N | 0.001511 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.004719 | north | Y | -0.001511 | -0.0052353 | -0.05686 | -0.0040663 | 0.001511 | North | N | 0.001511 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.047491 | west | Y | -0.044283 | -0.048007 | -0.099632 | -0.046838 | 0.044283 | North | Y | 0.099632 | 1.107
1479 | WFCOGEN_ | 2 | 20 | -0.047491 | west | Y | -0.044283 | -0.048007 | -0.099632 | -0.046838 | 0.044283 | North | Y | 0.099632 | 1.107
1482 | WFCOGEN_ | 1 | 20 | -0.047491 | west | Y | -0.044283 | -0.048007 | -0.099632 | -0.046838 | 0.044283 | North | Y | 0.099632 | 1.107
1482 | WFCOGEN_ | 2 | 17 | -0.047491 | west | Y | -0.044283 | -0.048007 | -0.099632 | -0.046838 | 0.044283 | North | Y | 0.099632 | 0.94094
1600 | BARTNWND | 1 | 120 | -0.015651 | north | Y | -0.012443 | -0.016167 | -0.067792 | -0.014998 | 0.012443 | North | N | 0.012443 | 0
1643 | SLSTR1PP | 1 | 60 | 0.001407 | north | Y | 0.004615 | 0.00089071 | -0.050734 | 0.0020597 | 0.00089071 | south | Y | 0.004615 | 0.22346
1675 | PEC_1G | 1 | 75 | -0.003489 | north | N | -0.00028103 | -0.0040053 | -0.05563 | -0.0028363 | 0.00028103 | North | N | 0.00028103 | 0
1676 | PEC_2G | 2 | 79.6 | -0.003489 | north | N | -0.00028103 | -0.0040053 | -0.05563 | -0.0028363 | 0.00028103 | North | N | 0.00028103 | 0
1677 | PEC_3G | 3 | 88.4 | -0.003489 | north | N | -0.00028103 | -0.0040053 | -0.05563 | -0.0028363 | 0.00028103 | North | N | 0.00028103 | 0
1678 | LAMARPWR | 1 | 160 | -0.003457 | north | Y | -0.00024903 | -0.0039733 | -0.055598 | -0.0028043 | 0.00024903 | North | N | 0.00024903 | 0
1679 | LAMARPWR | 2 | 156 | -0.003457 | north | Y | -0.00024903 | -0.0039733 | -0.055598 | -0.0028043 | 0.00024903 | North | N | 0.00024903 | 0
1680 | LAMARPWR | 3 | 196 | -0.003457 | north | Y | -0.00024903 | -0.0039733 | -0.055598 | -0.0028043 | 0.00024903 | North | N | 0.00024903 | 0
1681 | LAMARPWR | 4 | 156 | -0.003457 | north | Y | -0.00024903 | -0.0039733 | -0.055598 | -0.0028043 | 0.00024903 | North | N | 0.00024903 | 0
1682 | LAMARPWR | 5 | 157 | -0.003457 | north | Y | -0.00024903 | -0.0039733 | -0.055598 | -0.0028043 | 0.00024903 | North | N | 0.00024903 | 0
1683 | LAMARPWR | 6 | 198 | -0.003457 | north | Y | -0.00024903 | -0.0039733 | -0.055598 | -0.0028043 | 0.00024903 | North | N | 0.00024903 | 0
1687 | VALLEY_1 | 1 | 170 | -0.003994 | north | Y | -0.00078603 | -0.0045103 | -0.056135 | -0.0033413 | 0.00078603 | North | N | 0.00078603 | 0
1688 | VALLEY_2 | 2 | 520 | -0.003994 | north | Y | -0.00078603 | -0.0045103 | -0.056135 | -0.0033413 | 0.00078603 | North | N | 0.00078603 | 0
1689 | VALLEY_3 | 3 | 370 | -0.003509 | north | Y | -0.00030103 | -0.0040253 | -0.05565 | -0.0028563 | 0.00030103 | North | N | 0.00030103 | 0
1701 | MOSES_1G | 1 | 558 | -0.003308 | north | Y | -0.00010003 | -0.0038243 | -0.055449 | -0.0026553 | 0.00010003 | North | N | 0.00010003 | 0
1702 | MOSES_2G | 2 | 579 | -0.003308 | north | Y | -0.00010003 | -0.0038243 | -0.055449 | -0.0026553 | 0.00010003 | North | N | 0.00010003 | 0
1703 | MOSES_3G | 3 | 808 | -0.003308 | north | Y | -0.00010003 | -0.0038243 | -0.055449 | -0.0026553 | 0.00010003 | North | N | 0.00010003 | 0
1861 | EAGLEMNT | MB | 112 | -0.004651 | north | Y | -0.001443 | -0.0051673 | -0.056792 | -0.0039983 | 0.001443 | North | N | 0.001443 | 0
1862 | EAGLEMNT | MB | 100 | -0.004651 | north | Y | -0.001443 | -0.0051673 | -0.056792 | -0.0039983 | 0.001443 | North | N | 0.001443 | 0
1863 | EAGLEMNT | MB | 378 | -0.004651 | north | Y | -0.001443 | -0.0051673 | -0.056792 | -0.0039983 | 0.001443 | North | N | 0.001443 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.000319 | north | Y | 0.002889 | -0.00083529 | -0.05246 | 0.00033373 | 0.00033373 | houston | Y | 0.002889 | 0.55525
1878 | WLFHOLW_ | 2 | 205 | -0.000319 | north | Y | 0.002889 | -0.00083529 | -0.05246 | 0.00033373 | 0.00033373 | houston | Y | 0.002889 | 0.52382
1879 | WLFHOLW_ | 3 | 272.4 | -0.000319 | north | Y | 0.002889 | -0.00083529 | -0.05246 | 0.00033373 | 0.00033373 | houston | Y | 0.002889 | 0.69605
1889 | DECRDOVA | MB | 770 | -0.00103 | north | Y | 0.002178 | -0.0015463 | -0.053171 | -0.00037727 | 0.00037727 | houston | Y | 0.002178 | 0
1892 | DECRDOVA | A | 70 | -0.001718 | north | Y | 0.00149 | -0.0022343 | -0.053859 | -0.0010653 | 0.0010653 | houston | Y | 0.00149 | 0.029729
1893 | DECRDOVA | B | 69 | -0.001718 | north | Y | 0.00149 | -0.0022343 | -0.053859 | -0.0010653 | 0.0010653 | houston | Y | 0.00149 | 0.029304
1894 | DECRDOVA | C | 69 | -0.001718 | north | Y | 0.00149 | -0.0022343 | -0.053859 | -0.0010653 | 0.0010653 | houston | Y | 0.00149 | 0.029304
1895 | DECRDOVA | D | 68 | -0.001718 | north | Y | 0.00149 | -0.0022343 | -0.053859 | -0.0010653 | 0.0010653 | houston | Y | 0.00149 | 0.02888
1898 | COMCHEPK | 1 | 1157 | -5.3e-05 | north | N | 0.003155 | -0.00056929 | -0.052194 | 0.00059973 | 0.00056929 | south | Y | 0.003155 | 0
1899 | COMCHEPK | 2 | 1158 | -5.3e-05 | north | N | 0.003155 | -0.00056929 | -0.052194 | 0.00059973 | 0.00056929 | south | Y | 0.003155 | 0
1937 | MDLTHELP | 5 | 224 | -0.001848 | north | Y | 0.00136 | -0.0023643 | -0.053989 | -0.0011953 | 0.0011953 | houston | Y | 0.00136 | 0.036893
1938 | MDLTHELP | 6 | 226 | -0.001848 | north | Y | 0.00136 | -0.0023643 | -0.053989 | -0.0011953 | 0.0011953 | houston | Y | 0.00136 | 0.037222
1941 | MDLTHELP | 1 | 216.4 | -0.002095 | north | Y | 0.001113 | -0.0026113 | -0.054236 | -0.0014423 | 0.001113 | North | N | 0.001113 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.002095 | north | Y | 0.001113 | -0.0026113 | -0.054236 | -0.0014423 | 0.001113 | North | N | 0.001113 | 0
1943 | MDLTHELP | 3 | 212 | -0.001848 | north | Y | 0.00136 | -0.0023643 | -0.053989 | -0.0011953 | 0.0011953 | houston | Y | 0.00136 | 0.034917
1944 | MDLTHELP | 4 | 211 | -0.001848 | north | Y | 0.00136 | -0.0023643 | -0.053989 | -0.0011953 | 0.0011953 | houston | Y | 0.00136 | 0.034752
1947 | HANDLEY_ | 3 | 395 | -0.002575 | north | Y | 0.00063297 | -0.0030913 | -0.054716 | -0.0019223 | 0.00063297 | North | N | 0.00063297 | 0
1948 | HANDLEY_ | 4 | 435 | -0.002643 | north | Y | 0.00056497 | -0.0031593 | -0.054784 | -0.0019903 | 0.00056497 | North | N | 0.00056497 | 0
1949 | HANDLEY_ | 5 | 435 | -0.002575 | north | Y | 0.00063297 | -0.0030913 | -0.054716 | -0.0019223 | 0.00063297 | North | N | 0.00063297 | 0
2371 | COLLIN_1 | MB | 138 | -0.003825 | north | Y | -0.00061703 | -0.0043413 | -0.055966 | -0.0031723 | 0.00061703 | North | N | 0.00061703 | 0
2413 | MTCK6_G | 6 | 118 | -0.002645 | north | Y | 0.00056297 | -0.0031613 | -0.054786 | -0.0019923 | 0.00056297 | North | N | 0.00056297 | 0
2414 | MTCK7_G | 7 | 115 | -0.002645 | north | Y | 0.00056297 | -0.0031613 | -0.054786 | -0.0019923 | 0.00056297 | North | N | 0.00056297 | 0
2417 | MTCK8_G | 8 | 556 | -0.002645 | north | Y | 0.00056297 | -0.0031613 | -0.054786 | -0.0019923 | 0.00056297 | North | N | 0.00056297 | 0
2451 | LKHB1_G | 1 | 388 | -0.002928 | north | Y | 0.00027997 | -0.0034443 | -0.055069 | -0.0022753 | 0.00027997 | North | N | 0.00027997 | 0
2452 | LKHB2_G | 2 | 515 | -0.002928 | north | Y | 0.00027997 | -0.0034443 | -0.055069 | -0.0022753 | 0.00027997 | North | N | 0.00027997 | 0
3097 | MARTLAKE | 1 | 785 | -0.002564 | north | Y | 0.00064397 | -0.0030803 | -0.054705 | -0.0019113 | 0.00064397 | North | N | 0.00064397 | 0
3098 | MARTLAKE | 2 | 795 | -0.002564 | north | Y | 0.00064397 | -0.0030803 | -0.054705 | -0.0019113 | 0.00064397 | North | N | 0.00064397 | 0
3099 | MARTLAKE | 3 | 780 | -0.002564 | north | Y | 0.00064397 | -0.0030803 | -0.054705 | -0.0019113 | 0.00064397 | North | N | 0.00064397 | 0
3107 | STRYKER_ | 1 | 182 | -0.002468 | north | Y | 0.00073997 | -0.0029843 | -0.054609 | -0.0018153 | 0.00073997 | North | N | 0.00073997 | 0
3108 | STRYKER_ | 2 | 484 | -0.002468 | north | Y | 0.00073997 | -0.0029843 | -0.054609 | -0.0018153 | 0.00073997 | North | N | 0.00073997 | 0
3126 | TRINIDAD | 1 | 224 | -0.002319 | north | Y | 0.00088897 | -0.0028353 | -0.05446 | -0.0016663 | 0.00088897 | North | N | 0.00088897 | 0
3309 | ASPN_G | 1 | 50 | -0.002467 | north | Y | 0.00074097 | -0.0029833 | -0.054608 | -0.0018143 | 0.00074097 | North | N | 0.00074097 | 0
3348 | CHAMPION | MB | 42 | -0.002473 | north | N | 0.00073497 | -0.0029893 | -0.054614 | -0.0018203 | 0.00073497 | North | N | 0.00073497 | 0
3381 | BBRN_1G | 1 | 615 | -0.001974 | north | Y | 0.001234 | -0.0024903 | -0.054115 | -0.0013213 | 0.001234 | North | N | 0.001234 | 0
3382 | BBRN_2G | 2 | 587 | -0.001974 | north | Y | 0.001234 | -0.0024903 | -0.054115 | -0.0013213 | 0.001234 | North | N | 0.001234 | 0
3403 | THOUSE_1 | MB | 537 | -0.001225 | north | Y | 0.001983 | -0.0017413 | -0.053366 | -0.00057227 | 0.00057227 | houston | Y | 0.001983 | 0
3404 | THOUSE_2 | 2 | 787 | -0.001225 | north | Y | 0.001983 | -0.0017413 | -0.053366 | -0.00057227 | 0.00057227 | houston | Y | 0.001983 | 1.1102
3416 | LAKE_CRK | MB | 75 | -0.001147 | north | Y | 0.002061 | -0.0016633 | -0.053288 | -0.00049427 | 0.00049427 | houston | Y | 0.002061 | 0
3417 | LAKE_CRK | MB | 222 | -0.001147 | north | Y | 0.002061 | -0.0016633 | -0.053288 | -0.00049427 | 0.00049427 | houston | Y | 0.002061 | 0
3432 | SANDOW_4 | 4 | 569 | -0.000293 | south | Y | 0.002915 | -0.00080929 | -0.052434 | 0.00035973 | 0.00035973 | houston | Y | 0.00080929 | 0.2558
5026 | BRAUNIG_ | 1 | 209 | 0.000738 | south | Y | 0.003946 | 0.00022171 | -0.051403 | 0.0013907 | 0.00022171 | south | N | 0.00022171 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.000738 | south | Y | 0.003946 | 0.00022171 | -0.051403 | 0.0013907 | 0.00022171 | south | N | 0.00022171 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.000762 | south | Y | 0.00397 | 0.00024571 | -0.051379 | 0.0014147 | 0.00024571 | south | N | 0.00024571 | 0
5031 | BRA_VHBC | 1 | 46 | 0.000738 | south | Y | 0.003946 | 0.00022171 | -0.051403 | 0.0013907 | 0.00022171 | south | N | 0.00022171 | 0
5032 | BRA_VHBC | 2 | 47 | 0.000738 | south | Y | 0.003946 | 0.00022171 | -0.051403 | 0.0013907 | 0.00022171 | south | N | 0.00022171 | 0
5033 | BRA_VHBC | 3 | 46 | 0.000738 | south | Y | 0.003946 | 0.00022171 | -0.051403 | 0.0013907 | 0.00022171 | south | N | 0.00022171 | 0
5034 | BRA_VHBC | 4 | 46 | 0.000738 | south | Y | 0.003946 | 0.00022171 | -0.051403 | 0.0013907 | 0.00022171 | south | N | 0.00022171 | 0
5111 | CALAVER_ | 1 | 424 | 0.000726 | south | Y | 0.003934 | 0.00020971 | -0.051415 | 0.0013787 | 0.00020971 | south | N | 0.00020971 | 0
5112 | CALAVER_ | 2 | 425 | 0.000726 | south | Y | 0.003934 | 0.00020971 | -0.051415 | 0.0013787 | 0.00020971 | south | N | 0.00020971 | 0
5264 | LEON_LCP | 3 | 58 | 0.000831 | south | Y | 0.004039 | 0.00031471 | -0.05131 | 0.0014837 | 0.00031471 | south | N | 0.00031471 | 0
5265 | LEON_LCP | 4 | 89 | 0.000831 | south | Y | 0.004039 | 0.00031471 | -0.05131 | 0.0014837 | 0.00031471 | south | N | 0.00031471 | 0
5266 | LEON_LCP | 1 | 44 | 0.000831 | south | Y | 0.004039 | 0.00031471 | -0.05131 | 0.0014837 | 0.00031471 | south | N | 0.00031471 | 0
5267 | LEON_LCP | 2 | 44 | 0.000831 | south | Y | 0.004039 | 0.00031471 | -0.05131 | 0.0014837 | 0.00031471 | south | N | 0.00031471 | 0
5268 | LEON_LCP | 3 | 43 | 0.000831 | south | Y | 0.004039 | 0.00031471 | -0.05131 | 0.0014837 | 0.00031471 | south | N | 0.00031471 | 0
5269 | LEON_LCP | 4 | 45 | 0.000831 | south | Y | 0.004039 | 0.00031471 | -0.05131 | 0.0014837 | 0.00031471 | south | N | 0.00031471 | 0
5396 | CALAVER_ | 1 | 412 | 0.000738 | south | Y | 0.003946 | 0.00022171 | -0.051403 | 0.0013907 | 0.00022171 | south | N | 0.00022171 | 0
5397 | CALAVER_ | 2 | 400 | 0.000738 | south | Y | 0.003946 | 0.00022171 | -0.051403 | 0.0013907 | 0.00022171 | south | N | 0.00022171 | 0
5401 | CALAVER_ | 1 | 546 | 0.000636 | south | Y | 0.003844 | 0.00011971 | -0.051505 | 0.0012887 | 0.00011971 | south | N | 0.00011971 | 0
5402 | CALAVER_ | 2 | 750 | 0.000636 | south | Y | 0.003844 | 0.00011971 | -0.051505 | 0.0012887 | 0.00011971 | south | N | 0.00011971 | 0
5436 | TUTTL_WB | MB | 61 | 0.000674 | south | Y | 0.003882 | 0.00015771 | -0.051467 | 0.0013267 | 0.00015771 | south | N | 0.00015771 | 0
5438 | TUTTL_WB | MB | 95 | 0.000674 | south | Y | 0.003882 | 0.00015771 | -0.051467 | 0.0013267 | 0.00015771 | south | N | 0.00015771 | 0
5439 | TUTTL_WB | MB | 151 | 0.000674 | south | Y | 0.003882 | 0.00015771 | -0.051467 | 0.0013267 | 0.00015771 | south | N | 0.00015771 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.000659 | south | Y | 0.003867 | 0.00014271 | -0.051482 | 0.0013117 | 0.00014271 | south | N | 0.00014271 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.000659 | south | Y | 0.003867 | 0.00014271 | -0.051482 | 0.0013117 | 0.00014271 | south | N | 0.00014271 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.000659 | south | Y | 0.003867 | 0.00014271 | -0.051482 | 0.0013117 | 0.00014271 | south | N | 0.00014271 | 0
5503 | RAYBURNG | 1 | 22 | 0.000422 | south | Y | 0.00363 | -9.4293e-05 | -0.051719 | 0.0010747 | 9.4293e-05 | south | N | 9.4293e-05 | 0
5505 | RAYBURNG | 1 | 11 | 0.000422 | south | Y | 0.00363 | -9.4293e-05 | -0.051719 | 0.0010747 | 9.4293e-05 | south | N | 9.4293e-05 | 0
5506 | RAYBURNG | 1 | 11 | 0.000422 | south | Y | 0.00363 | -9.4293e-05 | -0.051719 | 0.0010747 | 9.4293e-05 | south | N | 9.4293e-05 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.000394 | south | Y | 0.003602 | -0.00012229 | -0.051747 | 0.0010467 | 0.00012229 | south | N | 0.00012229 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.000394 | south | Y | 0.003602 | -0.00012229 | -0.051747 | 0.0010467 | 0.00012229 | south | N | 0.00012229 | 0
5511 | RAYBURNC | 1 | 46 | 0.000394 | south | Y | 0.003602 | -0.00012229 | -0.051747 | 0.0010467 | 0.00012229 | south | N | 0.00012229 | 0
5512 | RAYBURNC | 1 | 48 | 0.000394 | south | Y | 0.003602 | -0.00012229 | -0.051747 | 0.0010467 | 0.00012229 | south | N | 0.00012229 | 0
5728 | FALCONHY | 2 | 12 | 0.000957 | south | N | 0.004165 | 0.00044071 | -0.051184 | 0.0016097 | 0.00044071 | south | N | 0.00044071 | 0
5729 | FALCONHY | 3 | 11 | 0.000957 | south | N | 0.004165 | 0.00044071 | -0.051184 | 0.0016097 | 0.00044071 | south | N | 0.00044071 | 0
5890 | PEARSALL | 1 | 24 | 0.002169 | south | Y | 0.005377 | 0.0016527 | -0.049972 | 0.0028217 | 0.0016527 | south | N | 0.0016527 | 0
5891 | PEARSALL | 1 | 24 | 0.002169 | south | Y | 0.005377 | 0.0016527 | -0.049972 | 0.0028217 | 0.0016527 | south | N | 0.0016527 | 0
5892 | PEARSALL | 1 | 23 | 0.002169 | south | Y | 0.005377 | 0.0016527 | -0.049972 | 0.0028217 | 0.0016527 | south | N | 0.0016527 | 0
5903 | SANMIGUE | 1 | 396 | 0.000743 | south | Y | 0.003951 | 0.00022671 | -0.051398 | 0.0013957 | 0.00022671 | south | N | 0.00022671 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.000256 | houston | N | 0.002952 | -0.00077229 | -0.052397 | 0.00039673 | 0.00039673 | houston | N | 0.00039673 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.000256 | houston | N | 0.002952 | -0.00077229 | -0.052397 | 0.00039673 | 0.00039673 | houston | N | 0.00039673 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | Y | 0.003208 | 0
5932 | SI_RAY9 | 9 | 38 | 0.000571 | south | Y | 0.003779 | 5.4707e-05 | -0.05157 | 0.0012237 | 5.4707e-05 | south | N | 5.4707e-05 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.000571 | south | Y | 0.003779 | 5.4707e-05 | -0.05157 | 0.0012237 | 5.4707e-05 | south | N | 5.4707e-05 | 0
5934 | SI_RAY5 | 5 | 15 | 0.000571 | south | Y | 0.003779 | 5.4707e-05 | -0.05157 | 0.0012237 | 5.4707e-05 | south | N | 5.4707e-05 | 0
5935 | SI_RAY10 | 10 | 47 | 0.000571 | south | Y | 0.003779 | 5.4707e-05 | -0.05157 | 0.0012237 | 5.4707e-05 | south | N | 5.4707e-05 | 0
6016 | SWMESA | 1 | 75 | 0.037805 | west | Y | 0.041013 | 0.037289 | -0.014336 | 0.038458 | 0.014336 | west | N | 0.014336 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | Y | 0.052141 | 0
6144 | MCADOO1A | 1 | 150 | 0.050411 | west | Y | 0.053619 | 0.049895 | -0.0017303 | 0.051064 | 0.0017303 | west | N | 0.0017303 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.046247 | west | Y | 0.049455 | 0.045731 | -0.0058943 | 0.0469 | 0.0058943 | west | N | 0.0058943 | 0
6476 | LANGFORD | 1 | 150 | 0.030836 | west | Y | 0.034044 | 0.03032 | -0.021305 | 0.031489 | 0.021305 | west | N | 0.021305 | 0
6637 | SNYDERW1 | 1 | 63 | 0.042446 | west | Y | 0.045654 | 0.04193 | -0.0096953 | 0.043099 | 0.0096953 | west | N | 0.0096953 | 0
6752 | OKLA0A | 1 | 649.7 | 0.25405 | west | Y | 0.25726 | 0.25354 | 0.20191 | 0.25471 | 0.20191 | west | N | 0.20191 | 0
6948 | DENISNDM | 1 | 40 | -0.004316 | north | N | -0.001108 | -0.0048323 | -0.056457 | -0.0036633 | 0.001108 | North | N | 0.001108 | 0
6948 | DENISNDM | 2 | 40 | -0.004316 | north | N | -0.001108 | -0.0048323 | -0.056457 | -0.0036633 | 0.001108 | North | N | 0.001108 | 0
7000 | L_FERGUS | 1 | 422 | 0.002037 | south | Y | 0.005245 | 0.0015207 | -0.050104 | 0.0026897 | 0.0015207 | south | N | 0.0015207 | 0
7004 | L_SIMGID | 1 | 132 | 0.000146 | south | Y | 0.003354 | -0.00037029 | -0.051995 | 0.00079873 | 0.00037029 | south | N | 0.00037029 | 0
7005 | L_SIMGID | 2 | 134 | 0.000146 | south | Y | 0.003354 | -0.00037029 | -0.051995 | 0.00079873 | 0.00037029 | south | N | 0.00037029 | 0
7006 | L_SIMGID | 3 | 323 | 0.000146 | south | Y | 0.003354 | -0.00037029 | -0.051995 | 0.00079873 | 0.00037029 | south | N | 0.00037029 | 0
7007 | L_LOSTPI | 1 | 158 | 6.4e-05 | south | Y | 0.003272 | -0.00045229 | -0.052077 | 0.00071673 | 0.00045229 | south | N | 0.00045229 | 0
7008 | L_LOSTPI | 2 | 160 | 6.4e-05 | south | Y | 0.003272 | -0.00045229 | -0.052077 | 0.00071673 | 0.00045229 | south | N | 0.00045229 | 0
7009 | L_LOSTPI | 3 | 175 | 6.4e-05 | south | Y | 0.003272 | -0.00045229 | -0.052077 | 0.00071673 | 0.00045229 | south | N | 0.00045229 | 0
7010 | L_FPPYD1 | 1 | 584 | 5.5e-05 | south | Y | 0.003263 | -0.00046129 | -0.052086 | 0.00070773 | 0.00046129 | south | N | 0.00046129 | 0
7011 | L_FPPYD1 | 2 | 595 | 5.5e-05 | south | Y | 0.003263 | -0.00046129 | -0.052086 | 0.00070773 | 0.00046129 | south | N | 0.00046129 | 0
7012 | L_FPPYD2 | 3 | 433 | 5.5e-05 | south | Y | 0.003263 | -0.00046129 | -0.052086 | 0.00070773 | 0.00046129 | south | N | 0.00046129 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.000448 | south | Y | 0.003656 | -6.8293e-05 | -0.051693 | 0.0011007 | 6.8293e-05 | south | N | 6.8293e-05 | 0
7015 | L_HAYSEN | 2 | 225 | 0.000448 | south | Y | 0.003656 | -6.8293e-05 | -0.051693 | 0.0011007 | 6.8293e-05 | south | N | 6.8293e-05 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.000448 | south | Y | 0.003656 | -6.8293e-05 | -0.051693 | 0.0011007 | 6.8293e-05 | south | N | 6.8293e-05 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.000448 | south | Y | 0.003656 | -6.8293e-05 | -0.051693 | 0.0011007 | 6.8293e-05 | south | N | 6.8293e-05 | 0
7020 | L_AUSTPL | 1 | 8 | 0.000298 | south | N | 0.003506 | -0.00021829 | -0.051843 | 0.00095073 | 0.00021829 | south | N | 0.00021829 | 0
7020 | L_AUSTPL | 2 | 8 | 0.000298 | south | N | 0.003506 | -0.00021829 | -0.051843 | 0.00095073 | 0.00021829 | south | N | 0.00021829 | 0
7022 | L_BUCHAN | 1 | 18 | 0.002104 | south | N | 0.005312 | 0.0015877 | -0.050037 | 0.0027567 | 0.0015877 | south | N | 0.0015877 | 0
7023 | L_BUCHAN | 2 | 18 | 0.002104 | south | N | 0.005312 | 0.0015877 | -0.050037 | 0.0027567 | 0.0015877 | south | N | 0.0015877 | 0
7024 | L_BUCHAN | 3 | 15 | 0.002104 | south | N | 0.005312 | 0.0015877 | -0.050037 | 0.0027567 | 0.0015877 | south | N | 0.0015877 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.002576 | south | N | 0.005784 | 0.0020597 | -0.049565 | 0.0032287 | 0.0020597 | south | N | 0.0020597 | 0
7028 | L_MARBFA | 1 | 18 | 0.001631 | south | N | 0.004839 | 0.0011147 | -0.05051 | 0.0022837 | 0.0011147 | south | N | 0.0011147 | 0
7029 | L_MARBFA | 2 | 18 | 0.001631 | south | N | 0.004839 | 0.0011147 | -0.05051 | 0.0022837 | 0.0011147 | south | N | 0.0011147 | 0
7031 | L_MARSFO | 1 | 35 | 0.000712 | south | N | 0.00392 | 0.00019571 | -0.051429 | 0.0013647 | 0.00019571 | south | N | 0.00019571 | 0
7032 | L_MARSFO | 2 | 34 | 0.000712 | south | N | 0.00392 | 0.00019571 | -0.051429 | 0.0013647 | 0.00019571 | south | N | 0.00019571 | 0
7033 | L_MARSFO | 3 | 35 | 0.000712 | south | N | 0.00392 | 0.00019571 | -0.051429 | 0.0013647 | 0.00019571 | south | N | 0.00019571 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.001935 | south | N | 0.005143 | 0.0014187 | -0.050206 | 0.0025877 | 0.0014187 | south | N | 0.0014187 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.001935 | south | N | 0.005143 | 0.0014187 | -0.050206 | 0.0025877 | 0.0014187 | south | N | 0.0014187 | 0
7038 | L_DELAWA | 1 | 35 | 0.039613 | west | Y | 0.042821 | 0.039097 | -0.012528 | 0.040266 | 0.012528 | west | N | 0.012528 | 0
7038 | L_DELAWA | 2 | 30 | 0.039613 | west | Y | 0.042821 | 0.039097 | -0.012528 | 0.040266 | 0.012528 | west | N | 0.012528 | 0
7303 | L_WPPGS1 | 1 | 50 | 8.9e-05 | south | Y | 0.003297 | -0.00042729 | -0.052052 | 0.00074173 | 0.00042729 | south | N | 0.00042729 | 0
7303 | L_WPPGS1 | 2 | 50 | 8.9e-05 | south | Y | 0.003297 | -0.00042729 | -0.052052 | 0.00074173 | 0.00042729 | south | N | 0.00042729 | 0
7305 | L_WPPGS3 | 3 | 50 | 8.9e-05 | south | Y | 0.003297 | -0.00042729 | -0.052052 | 0.00074173 | 0.00042729 | south | N | 0.00042729 | 0
7305 | L_WPPGS3 | 4 | 50 | 8.9e-05 | south | Y | 0.003297 | -0.00042729 | -0.052052 | 0.00074173 | 0.00042729 | south | N | 0.00042729 | 0
7487 | L_CANYHY | 1 | 6 | 0.000546 | south | N | 0.003754 | 2.9707e-05 | -0.051595 | 0.0011987 | 2.9707e-05 | south | N | 2.9707e-05 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.000488 | south | N | 0.003696 | -2.8293e-05 | -0.051653 | 0.0011407 | 2.8293e-05 | south | N | 2.8293e-05 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.000488 | south | N | 0.003696 | -2.8293e-05 | -0.051653 | 0.0011407 | 2.8293e-05 | south | N | 2.8293e-05 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.000488 | south | N | 0.003696 | -2.8293e-05 | -0.051653 | 0.0011407 | 2.8293e-05 | south | N | 2.8293e-05 | 0
7609 | L_SCHUMA | 1 | 4 | 0.000552 | south | N | 0.00376 | 3.5707e-05 | -0.051589 | 0.0012047 | 3.5707e-05 | south | N | 3.5707e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.00042 | south | N | 0.003628 | -9.6293e-05 | -0.051721 | 0.0010727 | 9.6293e-05 | south | N | 9.6293e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.00042 | south | N | 0.003628 | -9.6293e-05 | -0.051721 | 0.0010727 | 9.6293e-05 | south | N | 9.6293e-05 | 0
7800 | L_GUADGE | 1 | 147 | 0.000525 | south | Y | 0.003733 | 8.707e-06 | -0.051616 | 0.0011777 | 8.707e-06 | south | N | 8.707e-06 | 0
7801 | L_GUADGE | 2 | 138 | 0.000525 | south | Y | 0.003733 | 8.707e-06 | -0.051616 | 0.0011777 | 8.707e-06 | south | N | 8.707e-06 | 0
7802 | L_GUADGE | 3 | 140 | 0.000525 | south | Y | 0.003733 | 8.707e-06 | -0.051616 | 0.0011777 | 8.707e-06 | south | N | 8.707e-06 | 0
7803 | L_GUADGE | 4 | 147 | 0.000525 | south | Y | 0.003733 | 8.707e-06 | -0.051616 | 0.0011777 | 8.707e-06 | south | N | 8.707e-06 | 0
7804 | L_GUADGE | 5 | 182 | 0.000525 | south | Y | 0.003733 | 8.707e-06 | -0.051616 | 0.0011777 | 8.707e-06 | south | N | 8.707e-06 | 0
7805 | L_GUADGE | 6 | 198 | 0.000525 | south | Y | 0.003733 | 8.707e-06 | -0.051616 | 0.0011777 | 8.707e-06 | south | N | 8.707e-06 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.000141 | south | Y | 0.003349 | -0.00037529 | -0.052 | 0.00079373 | 0.00037529 | south | N | 0.00037529 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.000141 | south | Y | 0.003349 | -0.00037529 | -0.052 | 0.00079373 | 0.00037529 | south | N | 0.00037529 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.000141 | south | Y | 0.003349 | -0.00037529 | -0.052 | 0.00079373 | 0.00037529 | south | N | 0.00037529 | 0
7810 | L_RIONOG | 1 | 142 | 0.000486 | south | Y | 0.003694 | -3.0293e-05 | -0.051655 | 0.0011387 | 3.0293e-05 | south | N | 3.0293e-05 | 0
7811 | L_RIONOG | 2 | 145 | 0.000486 | south | Y | 0.003694 | -3.0293e-05 | -0.051655 | 0.0011387 | 3.0293e-05 | south | N | 3.0293e-05 | 0
7812 | L_RIONOG | 3 | 151 | 0.000486 | south | Y | 0.003694 | -3.0293e-05 | -0.051655 | 0.0011387 | 3.0293e-05 | south | N | 3.0293e-05 | 0
7813 | L_RIONOG | 4 | 290 | 0.000486 | south | Y | 0.003694 | -3.0293e-05 | -0.051655 | 0.0011387 | 3.0293e-05 | south | N | 3.0293e-05 | 0
8032 | AMISTADH | 1 | 33 | 0.011896 | south | N | 0.015104 | 0.01138 | -0.040245 | 0.012549 | 0.01138 | south | N | 0.01138 | 0
8033 | AMISTADH | 2 | 25 | 0.011896 | south | N | 0.015104 | 0.01138 | -0.040245 | 0.012549 | 0.01138 | south | N | 0.01138 | 0
8048 | FALCONHY | 1 | 12 | 0.000957 | south | N | 0.004165 | 0.00044071 | -0.051184 | 0.0016097 | 0.00044071 | south | N | 0.00044071 | 0
8066 | DUP1V#1 | 1 | 73 | 0.000367 | south | N | 0.003575 | -0.00014929 | -0.051774 | 0.0010197 | 0.00014929 | south | N | 0.00014929 | 0
8134 | FOR69CG0 | 1 | 79 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
8138 | FOR69CG0 | 2 | 81 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | N | 0.00051629 | 0
8147 | UCAR #2 | 10 | 28 | 0.00033 | south | N | 0.003538 | -0.00018629 | -0.051811 | 0.00098273 | 0.00018629 | south | N | 0.00018629 | 0
8148 | UCAR #1 | 2 | 7 | 0.00033 | south | N | 0.003538 | -0.00018629 | -0.051811 | 0.00098273 | 0.00018629 | south | N | 0.00018629 | 0
8153 | FOR69CG0 | 3 | 79 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
8154 | FOR69CG0 | 4 | 80 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
8156 | FOR69CG0 | 6 | 25 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
8157 | FOR69CG0 | 7 | 46 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
8161 | COLETOU1 | 1 | 629 | 0.000514 | south | Y | 0.003722 | -2.293e-06 | -0.051627 | 0.0011667 | 2.293e-06 | south | N | 2.293e-06 | 0
8173 | VICEC51A | 5 | 144 | 0.000382 | south | Y | 0.00359 | -0.00013429 | -0.051759 | 0.0010347 | 0.00013429 | south | N | 0.00013429 | 0
8174 | VICEC61A | 6 | 188 | 0.000382 | south | Y | 0.00359 | -0.00013429 | -0.051759 | 0.0010347 | 0.00013429 | south | N | 0.00013429 | 0
8189 | CUERO 2 | 1 | 12 | 0.000416 | south | N | 0.003624 | -0.00010029 | -0.051725 | 0.0010687 | 0.00010029 | south | N | 0.00010029 | 0
8262 | ELPS | 1 | 6 | 0.008804 | south | N | 0.012012 | 0.0082877 | -0.043337 | 0.0094567 | 0.0082877 | south | N | 0.0082877 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | N | 0.00051629 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | N | 0.00051629 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | N | 0.00051629 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | N | 0.00051629 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | N | 0.00051629 | 0
8442 | NBEC71A | 1 | 336 | 0.000515 | south | Y | 0.003723 | -1.293e-06 | -0.051626 | 0.0011677 | 1.293e-06 | south | N | 1.293e-06 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | N | 0.00051629 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | 0.003208 | -0.00051629 | -0.052141 | 0.00065273 | 0.00051629 | south | N | 0.00051629 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.000521 | south | Y | 0.003729 | 4.707e-06 | -0.05162 | 0.0011737 | 4.707e-06 | south | N | 4.707e-06 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.000521 | south | Y | 0.003729 | 4.707e-06 | -0.05162 | 0.0011737 | 4.707e-06 | south | N | 4.707e-06 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.000529 | south | N | 0.003737 | 1.2707e-05 | -0.051612 | 0.0011817 | 1.2707e-05 | south | N | 1.2707e-05 | 0
8506 | VAL #1 | 1 | 25 | 0.000525 | south | N | 0.003733 | 8.707e-06 | -0.051616 | 0.0011777 | 8.707e-06 | south | N | 8.707e-06 | 0
8507 | VAL #2 | 2 | 25 | 0.000525 | south | N | 0.003733 | 8.707e-06 | -0.051616 | 0.0011777 | 8.707e-06 | south | N | 8.707e-06 | 0
8511 | OXY_CC0A | 1 | 38 | 0.000525 | south | N | 0.003733 | 8.707e-06 | -0.051616 | 0.0011777 | 8.707e-06 | south | N | 8.707e-06 | 0
8517 | CELANEBI | 1 | 29 | 0.000544 | south | N | 0.003752 | 2.7707e-05 | -0.051597 | 0.0011967 | 2.7707e-05 | south | N | 2.7707e-05 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.000516 | south | N | 0.003724 | -2.9301e-07 | -0.051625 | 0.0011687 | 2.9301e-07 | south | N | 2.9301e-07 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.000516 | south | N | 0.003724 | -2.9301e-07 | -0.051625 | 0.0011687 | 2.9301e-07 | south | N | 2.9301e-07 | 0
8562 | CNOPST1 | 3 | 153 | 0.000516 | south | N | 0.003724 | -2.9301e-07 | -0.051625 | 0.0011687 | 2.9301e-07 | south | N | 2.9301e-07 | 0
8926 | LGE_GT10 | 1 | 158 | 0.000485 | south | N | 0.003693 | -3.1293e-05 | -0.051656 | 0.0011377 | 3.1293e-05 | south | N | 3.1293e-05 | 0
8927 | LGE_GT20 | 2 | 153 | 0.000485 | south | N | 0.003693 | -3.1293e-05 | -0.051656 | 0.0011377 | 3.1293e-05 | south | N | 3.1293e-05 | 0
8928 | LGE_STG0 | 3 | 100 | 0.000485 | south | N | 0.003693 | -3.1293e-05 | -0.051656 | 0.0011377 | 3.1293e-05 | south | N | 3.1293e-05 | 0
8930 | ICPGN10A | 1 | 145 | 0.000485 | south | N | 0.003693 | -3.1293e-05 | -0.051656 | 0.0011377 | 3.1293e-05 | south | N | 3.1293e-05 | 0
8931 | ICPGN20A | 2 | 147 | 0.000485 | south | N | 0.003693 | -3.1293e-05 | -0.051656 | 0.0011377 | 3.1293e-05 | south | N | 3.1293e-05 | 0
8932 | ICPGN30A | 3 | 127 | 0.000485 | south | N | 0.003693 | -3.1293e-05 | -0.051656 | 0.0011377 | 3.1293e-05 | south | N | 3.1293e-05 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.000652 | south | Y | 0.00386 | 0.00013571 | -0.051489 | 0.0013047 | 0.00013571 | south | N | 0.00013571 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.000652 | south | Y | 0.00386 | 0.00013571 | -0.051489 | 0.0013047 | 0.00013571 | south | N | 0.00013571 | 0
8935 | FGNTS201 | 3 | 173 | 0.000652 | south | Y | 0.00386 | 0.00013571 | -0.051489 | 0.0013047 | 0.00013571 | south | N | 0.00013571 | 0
8936 | MVGN#1 | 1 | 207 | 0.000602 | south | Y | 0.00381 | 8.5707e-05 | -0.051539 | 0.0012547 | 8.5707e-05 | south | N | 8.5707e-05 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.000602 | south | Y | 0.00381 | 8.5707e-05 | -0.051539 | 0.0012547 | 8.5707e-05 | south | N | 8.5707e-05 | 0
8938 | MVGN#3 | 3 | 242 | 0.000602 | south | Y | 0.00381 | 8.5707e-05 | -0.051539 | 0.0012547 | 8.5707e-05 | south | N | 8.5707e-05 | 0
8981 | HECN1 | 1 | 144 | 0.000601 | south | Y | 0.003809 | 8.4707e-05 | -0.05154 | 0.0012537 | 8.4707e-05 | south | N | 8.4707e-05 | 0
8982 | HECN2 | 2 | 144 | 0.000601 | south | Y | 0.003809 | 8.4707e-05 | -0.05154 | 0.0012537 | 8.4707e-05 | south | N | 8.4707e-05 | 0
8983 | HECN3 | 3 | 171 | 0.000601 | south | Y | 0.003809 | 8.4707e-05 | -0.05154 | 0.0012537 | 8.4707e-05 | south | N | 8.4707e-05 | 0
9000 | DECKR_G1 | 1 | 310 | 0.000259 | south | Y | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
9001 | DECKR_G2 | 2 | 413 | 0.000259 | south | Y | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
9002 | DECKR_G3 | 3 | 42 | 0.000227 | south | Y | 0.003435 | -0.00028929 | -0.051914 | 0.00087973 | 0.00028929 | south | N | 0.00028929 | 0
9003 | DECKR_G4 | 4 | 44 | 0.000227 | south | Y | 0.003435 | -0.00028929 | -0.051914 | 0.00087973 | 0.00028929 | south | N | 0.00028929 | 0
9004 | DECKR_G5 | 5 | 44 | 0.000227 | south | Y | 0.003435 | -0.00028929 | -0.051914 | 0.00087973 | 0.00028929 | south | N | 0.00028929 | 0
9005 | DECKR_G6 | 6 | 47 | 0.000227 | south | Y | 0.003435 | -0.00028929 | -0.051914 | 0.00087973 | 0.00028929 | south | N | 0.00028929 | 0
9016 | SANDH_G1 | 1 | 49 | 0.000269 | south | Y | 0.003477 | -0.00024729 | -0.051872 | 0.00092173 | 0.00024729 | south | N | 0.00024729 | 0
9017 | SANDH_G2 | 2 | 46 | 0.000269 | south | Y | 0.003477 | -0.00024729 | -0.051872 | 0.00092173 | 0.00024729 | south | N | 0.00024729 | 0
9018 | SANDH_G3 | 3 | 46 | 0.000269 | south | Y | 0.003477 | -0.00024729 | -0.051872 | 0.00092173 | 0.00024729 | south | N | 0.00024729 | 0
9019 | SANDH_G4 | 4 | 47 | 0.000269 | south | Y | 0.003477 | -0.00024729 | -0.051872 | 0.00092173 | 0.00024729 | south | N | 0.00024729 | 0
9020 | SANDHG5A | 5A | 154 | 0.000269 | south | Y | 0.003477 | -0.00024729 | -0.051872 | 0.00092173 | 0.00024729 | south | N | 0.00024729 | 0
9021 | SANDHG5C | 5C | 148 | 0.000269 | south | Y | 0.003477 | -0.00024729 | -0.051872 | 0.00092173 | 0.00024729 | south | N | 0.00024729 | 0
9022 | SANDH_G6 | 6 | 48 | 0.000269 | south | Y | 0.003477 | -0.00024729 | -0.051872 | 0.00092173 | 0.00024729 | south | N | 0.00024729 | 0
9023 | SANDH_G7 | 7 | 48 | 0.000269 | south | Y | 0.003477 | -0.00024729 | -0.051872 | 0.00092173 | 0.00024729 | south | N | 0.00024729 | 0
11001 | NAV1CT | 1 | 70 | 0.03968 | west | Y | 0.042888 | 0.039164 | -0.012461 | 0.040333 | 0.012461 | west | N | 0.012461 | 0
11009 | NAV2CT | 1 | 70 | 0.03968 | west | Y | 0.042888 | 0.039164 | -0.012461 | 0.040333 | 0.012461 | west | N | 0.012461 | 0
11011 | NAV3ST | 1 | 92.8 | 0.03968 | west | Y | 0.042888 | 0.039164 | -0.012461 | 0.040333 | 0.012461 | west | N | 0.012461 | 0
11012 | NAV4CT | 1 | 80 | 0.03968 | west | Y | 0.042888 | 0.039164 | -0.012461 | 0.040333 | 0.012461 | west | N | 0.012461 | 0
11013 | NAV5CT | 1 | 80 | 0.03968 | west | Y | 0.042888 | 0.039164 | -0.012461 | 0.040333 | 0.012461 | west | N | 0.012461 | 0
11014 | NAV6ST | 1 | 115 | 0.03968 | west | Y | 0.042888 | 0.039164 | -0.012461 | 0.040333 | 0.012461 | west | N | 0.012461 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.039678 | west | Y | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.039678 | west | Y | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.039678 | west | Y | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.039678 | west | Y | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.039678 | west | Y | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.039678 | west | Y | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.034975 | west | Y | 0.038183 | 0.034459 | -0.017166 | 0.035628 | 0.017166 | west | N | 0.017166 | 0
11057 | CHAMPION | 1 | 126.5 | 0.034975 | west | Y | 0.038183 | 0.034459 | -0.017166 | 0.035628 | 0.017166 | west | N | 0.017166 | 0
11058 | PYRON_1G | 1 | 249 | 0.034975 | west | Y | 0.038183 | 0.034459 | -0.017166 | 0.035628 | 0.017166 | west | N | 0.017166 | 0
11059 | INADALE_ | 1 | 197 | 0.034975 | west | Y | 0.038183 | 0.034459 | -0.017166 | 0.035628 | 0.017166 | west | N | 0.017166 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.039808 | west | Y | 0.043016 | 0.039292 | -0.012333 | 0.040461 | 0.012333 | west | N | 0.012333 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.039808 | west | Y | 0.043016 | 0.039292 | -0.012333 | 0.040461 | 0.012333 | west | N | 0.012333 | 0
11147 | NOTREES_ | 1 | 149 | 0.03981 | west | Y | 0.043018 | 0.039294 | -0.012331 | 0.040463 | 0.012331 | west | N | 0.012331 | 0
11309 | BULLCREK | 1 | 180 | 0.041867 | west | Y | 0.045075 | 0.041351 | -0.010274 | 0.04252 | 0.010274 | west | N | 0.010274 | 0
11310 | BULLCREK | 1 | 180 | 0.041867 | west | Y | 0.045075 | 0.041351 | -0.010274 | 0.04252 | 0.010274 | west | N | 0.010274 | 0
11320 | COYOTE_1 | 1 | 225 | 0.041786 | west | Y | 0.044994 | 0.04127 | -0.010355 | 0.042439 | 0.010355 | west | N | 0.010355 | 0
11415 | LORAINE_ | 1 | 125 | 0.039207 | west | Y | 0.042415 | 0.038691 | -0.012934 | 0.03986 | 0.012934 | west | N | 0.012934 | 0
11416 | LORAINE_ | 1 | 125 | 0.039207 | west | Y | 0.042415 | 0.038691 | -0.012934 | 0.03986 | 0.012934 | west | N | 0.012934 | 0
11691 | KMICHICT | 1 | 140 | -0.003509 | north | N | -0.00030103 | -0.0040253 | -0.05565 | -0.0028563 | 0.00030103 | North | N | 0.00030103 | 0
11692 | KMICHICT | 2 | 141 | -0.003509 | north | N | -0.00030103 | -0.0040253 | -0.05565 | -0.0028563 | 0.00030103 | North | N | 0.00030103 | 0
11693 | KMICHIST | 3 | 309 | -0.003509 | north | N | -0.00030103 | -0.0040253 | -0.05565 | -0.0028563 | 0.00030103 | North | N | 0.00030103 | 0
11694 | KMICHICT | 4 | 143 | -0.003509 | north | N | -0.00030103 | -0.0040253 | -0.05565 | -0.0028563 | 0.00030103 | North | N | 0.00030103 | 0
11695 | KMICHICT | 5 | 144 | -0.003509 | north | N | -0.00030103 | -0.0040253 | -0.05565 | -0.0028563 | 0.00030103 | North | N | 0.00030103 | 0
11696 | KMICHIST | 6 | 310 | -0.003509 | north | N | -0.00030103 | -0.0040253 | -0.05565 | -0.0028563 | 0.00030103 | North | N | 0.00030103 | 0
12322 | ENNSTRAC | 1 | 196 | -0.002275 | north | Y | 0.00093297 | -0.0027913 | -0.054416 | -0.0016223 | 0.00093297 | North | N | 0.00093297 | 0
12323 | ENNSTRAC | 2 | 111 | -0.002275 | north | Y | 0.00093297 | -0.0027913 | -0.054416 | -0.0016223 | 0.00093297 | North | N | 0.00093297 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.003377 | north | N | -0.00016903 | -0.0038933 | -0.055518 | -0.0027243 | 0.00016903 | North | N | 0.00016903 | 0
12411 | FPLEFR1A | 1 | 161 | -0.002931 | north | Y | 0.00027697 | -0.0034473 | -0.055072 | -0.0022783 | 0.00027697 | North | N | 0.00027697 | 0
12412 | FPLEFR1B | 2 | 164 | -0.002931 | north | Y | 0.00027697 | -0.0034473 | -0.055072 | -0.0022783 | 0.00027697 | North | N | 0.00027697 | 0
12413 | FPLEFR1C | 3 | 164 | -0.002931 | north | Y | 0.00027697 | -0.0034473 | -0.055072 | -0.0022783 | 0.00027697 | North | N | 0.00027697 | 0
12414 | FPLEFR1S | 4 | 414 | -0.002931 | north | Y | 0.00027697 | -0.0034473 | -0.055072 | -0.0022783 | 0.00027697 | North | N | 0.00027697 | 0
12421 | FPLEFR2A | 1 | 162 | -0.002931 | north | Y | 0.00027697 | -0.0034473 | -0.055072 | -0.0022783 | 0.00027697 | North | N | 0.00027697 | 0
12422 | FPLEFR2B | 2 | 161 | -0.002931 | north | Y | 0.00027697 | -0.0034473 | -0.055072 | -0.0022783 | 0.00027697 | North | N | 0.00027697 | 0
12423 | FPLEFR2C | 3 | 163 | -0.002931 | north | Y | 0.00027697 | -0.0034473 | -0.055072 | -0.0022783 | 0.00027697 | North | N | 0.00027697 | 0
12424 | FPLEFR2S | 4 | 409 | -0.002931 | north | Y | 0.00027697 | -0.0034473 | -0.055072 | -0.0022783 | 0.00027697 | North | N | 0.00027697 | 0
12440 | PARKD_1S | 1 | 0 | -0.002856 | north | N | 0.00035197 | -0.0033723 | -0.054997 | -0.0022033 | 0.00035197 | North | N | 0.00035197 | 0
12449 | PARKD_2S | 1 | 0 | -0.002856 | north | N | 0.00035197 | -0.0033723 | -0.054997 | -0.0022033 | 0.00035197 | North | N | 0.00035197 | 0
13116 | TGATEWAY | 1 | 148 | -0.002514 | north | N | 0.00069397 | -0.0030303 | -0.054655 | -0.0018613 | 0.00069397 | North | N | 0.00069397 | 0
13117 | TGATEWAY | 2 | 130 | -0.002514 | north | N | 0.00069397 | -0.0030303 | -0.054655 | -0.0018613 | 0.00069397 | North | N | 0.00069397 | 0
13118 | TGATEWAY | 3 | 145 | -0.002514 | north | N | 0.00069397 | -0.0030303 | -0.054655 | -0.0018613 | 0.00069397 | North | N | 0.00069397 | 0
13119 | TGATEWAY | 4 | 399 | -0.002514 | north | N | 0.00069397 | -0.0030303 | -0.054655 | -0.0018613 | 0.00069397 | North | N | 0.00069397 | 0
13131 | CALFREST | 1 | 150.7 | -0.002042 | north | Y | 0.001166 | -0.0025583 | -0.054183 | -0.0013893 | 0.001166 | North | N | 0.001166 | 0
13132 | CALFREST | 2 | 151 | -0.002042 | north | Y | 0.001166 | -0.0025583 | -0.054183 | -0.0013893 | 0.001166 | North | N | 0.001166 | 0
13133 | CALFREST | 3 | 177.4 | -0.002042 | north | Y | 0.001166 | -0.0025583 | -0.054183 | -0.0013893 | 0.001166 | North | N | 0.001166 | 0
13134 | CALFREST | 4 | 151.5 | -0.002066 | north | Y | 0.001142 | -0.0025823 | -0.054207 | -0.0014133 | 0.001142 | North | N | 0.001142 | 0
13135 | CALFREST | 5 | 152.3 | -0.002066 | north | Y | 0.001142 | -0.0025823 | -0.054207 | -0.0014133 | 0.001142 | North | N | 0.001142 | 0
13136 | CALFREST | 6 | 177.5 | -0.002066 | north | Y | 0.001142 | -0.0025823 | -0.054207 | -0.0014133 | 0.001142 | North | N | 0.001142 | 0
13432 | SANDOW_5 | 5 | 581 | -0.000293 | south | Y | 0.002915 | -0.00080929 | -0.052434 | 0.00035973 | 0.00035973 | houston | Y | 0.00080929 | 0.2612
13691 | OAKGROVE | 1 | 855 | -0.001577 | north | Y | 0.001631 | -0.0020933 | -0.053718 | -0.00092427 | 0.00092427 | houston | Y | 0.001631 | 0.60423
13692 | OAKGROVE | 2 | 855 | -0.001577 | north | Y | 0.001631 | -0.0020933 | -0.053718 | -0.00092427 | 0.00092427 | houston | Y | 0.001631 | 0.60423
32798 | BRYN_TAM | 1 | 32 | -0.001299 | north | N | 0.001909 | -0.0018153 | -0.05344 | -0.00064627 | 0.00064627 | houston | Y | 0.001909 | 0
32883 | BRYN_DNS | 1 | 48 | -0.001293 | north | Y | 0.001915 | -0.0018093 | -0.053434 | -0.00064027 | 0.00064027 | houston | Y | 0.001915 | 0.061186
32884 | BRYN_DNS | 1 | 46 | -0.001293 | north | Y | 0.001915 | -0.0018093 | -0.053434 | -0.00064027 | 0.00064027 | houston | Y | 0.001915 | 0.058636
32886 | BRYN_ATK | MB | 12 | -0.001301 | north | Y | 0.001907 | -0.0018173 | -0.053442 | -0.00064827 | 0.00064827 | houston | Y | 0.001907 | 0
32887 | BRYN_ATK | MB | 51 | -0.001301 | north | Y | 0.001907 | -0.0018173 | -0.053442 | -0.00064827 | 0.00064827 | houston | Y | 0.001907 | 0
32888 | BRYN_ATK | 1 | 17 | -0.001301 | north | Y | 0.001907 | -0.0018173 | -0.053442 | -0.00064827 | 0.00064827 | houston | Y | 0.001907 | 0.021398
32890 | BRYN_ATK | MB | 22 | -0.001301 | north | Y | 0.001907 | -0.0018173 | -0.053442 | -0.00064827 | 0.00064827 | houston | Y | 0.001907 | 0
32891 | BRYN_ATK | MB | 25 | -0.001301 | north | Y | 0.001907 | -0.0018173 | -0.053442 | -0.00064827 | 0.00064827 | houston | Y | 0.001907 | 0
32892 | BRYN_DNS | 1 | 105 | -0.001293 | north | Y | 0.001915 | -0.0018093 | -0.053434 | -0.00064027 | 0.00064027 | houston | Y | 0.001915 | 0.13384
36998 | RDCNYNG1 | 1 | 84 | 0.044407 | west | Y | 0.047615 | 0.043891 | -0.0077343 | 0.04506 | 0.0077343 | west | N | 0.0077343 | 0
38332 | WDWRDU2 | 1 | 80 | 0.037775 | west | Y | 0.040983 | 0.037259 | -0.014366 | 0.038428 | 0.014366 | west | N | 0.014366 | 0
38437 | TNSRBNMS | 1 | 150 | 0.037759 | west | Y | 0.040967 | 0.037243 | -0.014382 | 0.038412 | 0.014382 | west | N | 0.014382 | 0
38438 | TNSRBNMS | 1 | 150 | 0.037759 | west | Y | 0.040967 | 0.037243 | -0.014382 | 0.038412 | 0.014382 | west | N | 0.014382 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38600 | TNBP_CGN | 5 | 53 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38614 | TNBPAMCG | 4 | 96 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38615 | TNBPAMCG | 1 | 244 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38690 | TNBP_CGN | 3 | 40 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
39470 | TNDOWCGN | 1 | 32 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
39480 | TNDOWCGN | 1 | 30 | -0.000636 | houston | N | 0.002572 | -0.0011523 | -0.052777 | 1.673e-05 | 1.673e-05 | houston | N | 1.673e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.000488 | houston | N | 0.00272 | -0.0010043 | -0.052629 | 0.00016473 | 0.00016473 | houston | N | 0.00016473 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.000488 | houston | N | 0.00272 | -0.0010043 | -0.052629 | 0.00016473 | 0.00016473 | houston | N | 0.00016473 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.000488 | houston | N | 0.00272 | -0.0010043 | -0.052629 | 0.00016473 | 0.00016473 | houston | N | 0.00016473 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.000488 | houston | N | 0.00272 | -0.0010043 | -0.052629 | 0.00016473 | 0.00016473 | houston | N | 0.00016473 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.001577 | north | Y | 0.001631 | -0.0020933 | -0.053718 | -0.00092427 | 0.00092427 | houston | Y | 0.001631 | 0.10763
39970 | TNTNPONE | 1 | 153 | -0.001577 | north | Y | 0.001631 | -0.0020933 | -0.053718 | -0.00092427 | 0.00092427 | houston | Y | 0.001631 | 0.10813
48500 | APD_GT1_ | 1 | 136 | -0.000724 | houston | N | 0.002484 | -0.0012403 | -0.052865 | -7.127e-05 | 7.127e-05 | houston | N | 7.127e-05 | 0
48510 | AK_GT1__ | 1 | 33 | -0.000587 | houston | N | 0.002621 | -0.0011033 | -0.052728 | 6.573e-05 | 6.573e-05 | houston | N | 6.573e-05 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.000724 | houston | Y | 0.002484 | -0.0012403 | -0.052865 | -7.127e-05 | 7.127e-05 | houston | N | 7.127e-05 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.000724 | houston | Y | 0.002484 | -0.0012403 | -0.052865 | -7.127e-05 | 7.127e-05 | houston | N | 7.127e-05 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.000724 | houston | Y | 0.002484 | -0.0012403 | -0.052865 | -7.127e-05 | 7.127e-05 | houston | N | 7.127e-05 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.000724 | houston | Y | 0.002484 | -0.0012403 | -0.052865 | -7.127e-05 | 7.127e-05 | houston | N | 7.127e-05 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.000462 | houston | N | 0.002746 | -0.00097829 | -0.052603 | 0.00019073 | 0.00019073 | houston | N | 0.00019073 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.000462 | houston | N | 0.002746 | -0.00097829 | -0.052603 | 0.00019073 | 0.00019073 | houston | N | 0.00019073 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.000583 | houston | N | 0.002625 | -0.0010993 | -0.052724 | 6.973e-05 | 6.973e-05 | houston | N | 6.973e-05 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.000583 | houston | N | 0.002625 | -0.0010993 | -0.052724 | 6.973e-05 | 6.973e-05 | houston | N | 6.973e-05 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.000583 | houston | N | 0.002625 | -0.0010993 | -0.052724 | 6.973e-05 | 6.973e-05 | houston | N | 6.973e-05 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.000691 | houston | N | 0.002517 | -0.0012073 | -0.052832 | -3.827e-05 | 3.827e-05 | houston | N | 3.827e-05 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.000691 | houston | N | 0.002517 | -0.0012073 | -0.052832 | -3.827e-05 | 3.827e-05 | houston | N | 3.827e-05 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.000691 | houston | N | 0.002517 | -0.0012073 | -0.052832 | -3.827e-05 | 3.827e-05 | houston | N | 3.827e-05 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.000691 | houston | N | 0.002517 | -0.0012073 | -0.052832 | -3.827e-05 | 3.827e-05 | houston | N | 3.827e-05 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.000712 | houston | N | 0.002496 | -0.0012283 | -0.052853 | -5.927e-05 | 5.927e-05 | houston | N | 5.927e-05 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.000712 | houston | N | 0.002496 | -0.0012283 | -0.052853 | -5.927e-05 | 5.927e-05 | houston | N | 5.927e-05 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.000684 | houston | N | 0.002524 | -0.0012003 | -0.052825 | -3.127e-05 | 3.127e-05 | houston | N | 3.127e-05 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.000684 | houston | N | 0.002524 | -0.0012003 | -0.052825 | -3.127e-05 | 3.127e-05 | houston | N | 3.127e-05 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.000684 | houston | N | 0.002524 | -0.0012003 | -0.052825 | -3.127e-05 | 3.127e-05 | houston | N | 3.127e-05 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.000684 | houston | N | 0.002524 | -0.0012003 | -0.052825 | -3.127e-05 | 3.127e-05 | houston | N | 3.127e-05 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.000684 | houston | N | 0.002524 | -0.0012003 | -0.052825 | -3.127e-05 | 3.127e-05 | houston | N | 3.127e-05 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.00075 | houston | Y | 0.002458 | -0.0012663 | -0.052891 | -9.727e-05 | 9.727e-05 | houston | N | 9.727e-05 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.000739 | houston | Y | 0.002469 | -0.0012553 | -0.05288 | -8.627e-05 | 8.627e-05 | houston | N | 8.627e-05 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.000753 | houston | Y | 0.002455 | -0.0012693 | -0.052894 | -0.00010027 | 0.00010027 | houston | N | 0.00010027 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.000753 | houston | Y | 0.002455 | -0.0012693 | -0.052894 | -0.00010027 | 0.00010027 | houston | N | 0.00010027 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.000753 | houston | Y | 0.002455 | -0.0012693 | -0.052894 | -0.00010027 | 0.00010027 | houston | N | 0.00010027 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.000812 | houston | N | 0.002396 | -0.0013283 | -0.052953 | -0.00015927 | 0.00015927 | houston | N | 0.00015927 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.000726 | houston | N | 0.002482 | -0.0012423 | -0.052867 | -7.327e-05 | 7.327e-05 | houston | N | 7.327e-05 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.000726 | houston | N | 0.002482 | -0.0012423 | -0.052867 | -7.327e-05 | 7.327e-05 | houston | N | 7.327e-05 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.00076 | houston | N | 0.002448 | -0.0012763 | -0.052901 | -0.00010727 | 0.00010727 | houston | N | 0.00010727 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.00076 | houston | N | 0.002448 | -0.0012763 | -0.052901 | -0.00010727 | 0.00010727 | houston | N | 0.00010727 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.00076 | houston | N | 0.002448 | -0.0012763 | -0.052901 | -0.00010727 | 0.00010727 | houston | N | 0.00010727 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.00076 | houston | N | 0.002448 | -0.0012763 | -0.052901 | -0.00010727 | 0.00010727 | houston | N | 0.00010727 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.000713 | houston | N | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.000713 | houston | N | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.000713 | houston | N | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.000713 | houston | N | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.000705 | houston | N | 0.002503 | -0.0012213 | -0.052846 | -5.227e-05 | 5.227e-05 | houston | N | 5.227e-05 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.000705 | houston | N | 0.002503 | -0.0012213 | -0.052846 | -5.227e-05 | 5.227e-05 | houston | N | 5.227e-05 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.000705 | houston | N | 0.002503 | -0.0012213 | -0.052846 | -5.227e-05 | 5.227e-05 | houston | N | 5.227e-05 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.000705 | houston | N | 0.002503 | -0.0012213 | -0.052846 | -5.227e-05 | 5.227e-05 | houston | N | 5.227e-05 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.000705 | houston | N | 0.002503 | -0.0012213 | -0.052846 | -5.227e-05 | 5.227e-05 | houston | N | 5.227e-05 | 0
48651 | EP_1_2 | 1 | 5 | -0.000749 | houston | N | 0.002459 | -0.0012653 | -0.05289 | -9.627e-05 | 9.627e-05 | houston | N | 9.627e-05 | 0
48651 | EP_1_2 | 2 | 21 | -0.000749 | houston | N | 0.002459 | -0.0012653 | -0.05289 | -9.627e-05 | 9.627e-05 | houston | N | 9.627e-05 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.001218 | north | N | 0.00199 | -0.0017343 | -0.053359 | -0.00056527 | 0.00056527 | houston | Y | 0.00199 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.001218 | north | N | 0.00199 | -0.0017343 | -0.053359 | -0.00056527 | 0.00056527 | houston | Y | 0.00199 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.001218 | north | N | 0.00199 | -0.0017343 | -0.053359 | -0.00056527 | 0.00056527 | houston | Y | 0.00199 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.001218 | north | N | 0.00199 | -0.0017343 | -0.053359 | -0.00056527 | 0.00056527 | houston | Y | 0.00199 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.000764 | houston | Y | 0.002444 | -0.0012803 | -0.052905 | -0.00011127 | 0.00011127 | houston | N | 0.00011127 | 0
48691 | GBY_7374 | A | 46 | -0.000702 | houston | Y | 0.002506 | -0.0012183 | -0.052843 | -4.927e-05 | 4.927e-05 | houston | N | 4.927e-05 | 0
48691 | GBY_7374 | B | 46 | -0.000702 | houston | Y | 0.002506 | -0.0012183 | -0.052843 | -4.927e-05 | 4.927e-05 | houston | N | 4.927e-05 | 0
48692 | GBY_8182 | C | 46 | -0.000702 | houston | Y | 0.002506 | -0.0012183 | -0.052843 | -4.927e-05 | 4.927e-05 | houston | N | 4.927e-05 | 0
48692 | GBY_8182 | D | 55 | -0.000702 | houston | Y | 0.002506 | -0.0012183 | -0.052843 | -4.927e-05 | 4.927e-05 | houston | N | 4.927e-05 | 0
48693 | GBY_8384 | E | 55 | -0.000702 | houston | Y | 0.002506 | -0.0012183 | -0.052843 | -4.927e-05 | 4.927e-05 | houston | N | 4.927e-05 | 0
48693 | GBY_8384 | F | 54 | -0.000702 | houston | Y | 0.002506 | -0.0012183 | -0.052843 | -4.927e-05 | 4.927e-05 | houston | N | 4.927e-05 | 0
48721 | LEG_1___ | 1 | 827 | -0.001689 | north | Y | 0.001519 | -0.0022053 | -0.05383 | -0.0010363 | 0.0010363 | houston | Y | 0.001519 | 0.39919
48722 | LEG_2___ | 2 | 819 | -0.001689 | north | Y | 0.001519 | -0.0022053 | -0.05383 | -0.0010363 | 0.0010363 | houston | Y | 0.001519 | 0.39533
48730 | MNS_GT | 1 | 46.1 | -0.000574 | houston | N | 0.002634 | -0.0010903 | -0.052715 | 7.873e-05 | 7.873e-05 | houston | N | 7.873e-05 | 0
48731 | CBE_GT1 | 1 | 76 | -0.000279 | houston | Y | 0.002929 | -0.00079529 | -0.05242 | 0.00037373 | 0.00037373 | houston | N | 0.00037373 | 0
48732 | CBE_GT2 | 1 | 76 | -0.000279 | houston | Y | 0.002929 | -0.00079529 | -0.05242 | 0.00037373 | 0.00037373 | houston | N | 0.00037373 | 0
48733 | CBE_ST12 | 1 | 105 | -0.000279 | houston | Y | 0.002929 | -0.00079529 | -0.05242 | 0.00037373 | 0.00037373 | houston | N | 0.00037373 | 0
48734 | CBE_GT3 | 1 | 74 | -0.000279 | houston | Y | 0.002929 | -0.00079529 | -0.05242 | 0.00037373 | 0.00037373 | houston | N | 0.00037373 | 0
48735 | CBE_GT4 | 1 | 74 | -0.000279 | houston | Y | 0.002929 | -0.00079529 | -0.05242 | 0.00037373 | 0.00037373 | houston | N | 0.00037373 | 0
48736 | CBE_ST34 | 1 | 102 | -0.000279 | houston | Y | 0.002929 | -0.00079529 | -0.05242 | 0.00037373 | 0.00037373 | houston | N | 0.00037373 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.000713 | houston | N | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.000713 | houston | N | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.000713 | houston | N | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48761 | PR_GT1__ | 1 | 35 | -0.000709 | houston | N | 0.002499 | -0.0012253 | -0.05285 | -5.627e-05 | 5.627e-05 | houston | N | 5.627e-05 | 0
48772 | PHR_GN2_ | MB | 459 | -0.000668 | houston | Y | 0.00254 | -0.0011843 | -0.052809 | -1.527e-05 | 1.527e-05 | houston | N | 1.527e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.00075 | houston | N | 0.002458 | -0.0012663 | -0.052891 | -9.727e-05 | 9.727e-05 | houston | N | 9.727e-05 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.00075 | houston | N | 0.002458 | -0.0012663 | -0.052891 | -9.727e-05 | 9.727e-05 | houston | N | 9.727e-05 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.00075 | houston | N | 0.002458 | -0.0012663 | -0.052891 | -9.727e-05 | 9.727e-05 | houston | N | 9.727e-05 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.00075 | houston | N | 0.002458 | -0.0012663 | -0.052891 | -9.727e-05 | 9.727e-05 | houston | N | 9.727e-05 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.00075 | houston | N | 0.002458 | -0.0012663 | -0.052891 | -9.727e-05 | 9.727e-05 | houston | N | 9.727e-05 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.00075 | houston | N | 0.002458 | -0.0012663 | -0.052891 | -9.727e-05 | 9.727e-05 | houston | N | 9.727e-05 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.00075 | houston | N | 0.002458 | -0.0012663 | -0.052891 | -9.727e-05 | 9.727e-05 | houston | N | 9.727e-05 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.000812 | houston | N | 0.002396 | -0.0013283 | -0.052953 | -0.00015927 | 0.00015927 | houston | N | 0.00015927 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.000812 | houston | N | 0.002396 | -0.0013283 | -0.052953 | -0.00015927 | 0.00015927 | houston | N | 0.00015927 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.000812 | houston | N | 0.002396 | -0.0013283 | -0.052953 | -0.00015927 | 0.00015927 | houston | N | 0.00015927 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.000812 | houston | N | 0.002396 | -0.0013283 | -0.052953 | -0.00015927 | 0.00015927 | houston | N | 0.00015927 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.000752 | houston | N | 0.002456 | -0.0012683 | -0.052893 | -9.927e-05 | 9.927e-05 | houston | N | 9.927e-05 | 0
48820 | SHELLG1_ | 1 | 71 | -0.000717 | houston | N | 0.002491 | -0.0012333 | -0.052858 | -6.427e-05 | 6.427e-05 | houston | N | 6.427e-05 | 0
48821 | SHELLG2 | 2 | 72 | -0.000717 | houston | N | 0.002491 | -0.0012333 | -0.052858 | -6.427e-05 | 6.427e-05 | houston | N | 6.427e-05 | 0
48822 | SHELLG3_ | 1 | 39 | -0.000717 | houston | N | 0.002491 | -0.0012333 | -0.052858 | -6.427e-05 | 6.427e-05 | houston | N | 6.427e-05 | 0
48822 | SHELLG3_ | 2 | 30 | -0.000717 | houston | N | 0.002491 | -0.0012333 | -0.052858 | -6.427e-05 | 6.427e-05 | houston | N | 6.427e-05 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.000703 | houston | N | 0.002505 | -0.0012193 | -0.052844 | -5.027e-05 | 5.027e-05 | houston | N | 5.027e-05 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.000703 | houston | N | 0.002505 | -0.0012193 | -0.052844 | -5.027e-05 | 5.027e-05 | houston | N | 5.027e-05 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.000713 | houston | N | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.000712 | houston | Y | 0.002496 | -0.0012283 | -0.052853 | -5.927e-05 | 5.927e-05 | houston | N | 5.927e-05 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.000712 | houston | Y | 0.002496 | -0.0012283 | -0.052853 | -5.927e-05 | 5.927e-05 | houston | N | 5.927e-05 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.000713 | houston | Y | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.000713 | houston | Y | 0.002495 | -0.0012293 | -0.052854 | -6.027e-05 | 6.027e-05 | houston | N | 6.027e-05 | 0
48855 | SRB_GT21 | B2 | 12 | -0.000711 | houston | Y | 0.002497 | -0.0012273 | -0.052852 | -5.827e-05 | 5.827e-05 | houston | N | 5.827e-05 | 0
48855 | SRB_GT21 | MB | 18 | -0.000711 | houston | Y | 0.002497 | -0.0012273 | -0.052852 | -5.827e-05 | 5.827e-05 | houston | N | 5.827e-05 | 0
48865 | TECO_GT1 | 1 | 50 | -0.000656 | houston | Y | 0.002552 | -0.0011723 | -0.052797 | -3.2703e-06 | 3.2703e-06 | houston | N | 3.2703e-06 | 0
48873 | THW_ST3_ | 3 | 104 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48874 | THW_ST4_ | 4 | 104 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48875 | THW_3132 | A | 54 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48875 | THW_3132 | B | 53 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48877 | THW_3334 | C | 54 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48877 | THW_3334 | D | 57 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48879 | THW_4142 | E | 54 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48879 | THW_4142 | F | 54 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48881 | THW_4344 | G | 58 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48881 | THW_4344 | H | 58 | -0.000737 | houston | Y | 0.002471 | -0.0012533 | -0.052878 | -8.427e-05 | 8.427e-05 | houston | N | 8.427e-05 | 0
48883 | THW_GT1_ | B2 | 12 | -0.000747 | houston | Y | 0.002461 | -0.0012633 | -0.052888 | -9.427e-05 | 9.427e-05 | houston | N | 9.427e-05 | 0
48885 | THW_5152 | A | 56 | -0.000769 | houston | Y | 0.002439 | -0.0012853 | -0.05291 | -0.00011627 | 0.00011627 | houston | N | 0.00011627 | 0
48885 | THW_5152 | B | 59 | -0.000769 | houston | Y | 0.002439 | -0.0012853 | -0.05291 | -0.00011627 | 0.00011627 | houston | N | 0.00011627 | 0
48886 | THW_5354 | C | 56 | -0.000769 | houston | Y | 0.002439 | -0.0012853 | -0.05291 | -0.00011627 | 0.00011627 | houston | N | 0.00011627 | 0
48886 | THW_5354 | D | 56 | -0.000769 | houston | Y | 0.002439 | -0.0012853 | -0.05291 | -0.00011627 | 0.00011627 | houston | N | 0.00011627 | 0
48887 | THW_5556 | E | 59 | -0.000769 | houston | Y | 0.002439 | -0.0012853 | -0.05291 | -0.00011627 | 0.00011627 | houston | N | 0.00011627 | 0
48887 | THW_5556 | F | 56 | -0.000769 | houston | Y | 0.002439 | -0.0012853 | -0.05291 | -0.00011627 | 0.00011627 | houston | N | 0.00011627 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.0003 | houston | Y | 0.002908 | -0.00081629 | -0.052441 | 0.00035273 | 0.00035273 | houston | N | 0.00035273 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.000599 | houston | Y | 0.002609 | -0.0011153 | -0.05274 | 5.373e-05 | 5.373e-05 | houston | N | 5.373e-05 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.000599 | houston | Y | 0.002609 | -0.0011153 | -0.05274 | 5.373e-05 | 5.373e-05 | houston | N | 5.373e-05 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.000599 | houston | Y | 0.002609 | -0.0011153 | -0.05274 | 5.373e-05 | 5.373e-05 | houston | N | 5.373e-05 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.000599 | houston | Y | 0.002609 | -0.0011153 | -0.05274 | 5.373e-05 | 5.373e-05 | houston | N | 5.373e-05 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.000599 | houston | N | 0.002609 | -0.0011153 | -0.05274 | 5.373e-05 | 5.373e-05 | houston | N | 5.373e-05 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.000582 | houston | Y | 0.002626 | -0.0010983 | -0.052723 | 7.073e-05 | 7.073e-05 | houston | N | 7.073e-05 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.000582 | houston | Y | 0.002626 | -0.0010983 | -0.052723 | 7.073e-05 | 7.073e-05 | houston | N | 7.073e-05 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.000582 | houston | Y | 0.002626 | -0.0010983 | -0.052723 | 7.073e-05 | 7.073e-05 | houston | N | 7.073e-05 | 0
48929 | WAPGT21_ | B1 | 13 | -0.000599 | houston | Y | 0.002609 | -0.0011153 | -0.05274 | 5.373e-05 | 5.373e-05 | houston | N | 5.373e-05 | 0
48940 | WARVUE_G | G1 | 12 | -0.00075 | houston | Y | 0.002458 | -0.0012663 | -0.052891 | -9.727e-05 | 9.727e-05 | houston | N | 9.727e-05 | 0
49803 | EXN_15GT | 1 | 34 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49826 | EXN938GT | 5 | 45.9 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49828 | EXN941GT | 10 | 17.7 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49829 | EXN942GT | 11 | 20.4 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49830 | EXN943GT | 12 | 19.9 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49831 | EXN944GT | 13 | 35 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49832 | EXN945GT | 9 | 18 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49837 | EXN_GT | 4 | 85.4 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49838 | EXN_14GT | 14 | 148 | -0.000742 | houston | N | 0.002466 | -0.0012583 | -0.052883 | -8.927e-05 | 8.927e-05 | houston | N | 8.927e-05 | 0
49851 | DOW17000 | 37 | 62 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49858 | DOW38100 | 31 | 71.4 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49859 | DOW38200 | 33 | 45 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49860 | DOW38300 | 32 | 101 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49862 | DOW39100 | 36 | 86 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49863 | DOW39200 | 35 | 88 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49865 | DOW41000 | 41 | 50 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49866 | DOW42000 | 42 | 18 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49869 | DOW49000 | 45 | 94 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49870 | DOW61000 | 61 | 70 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49871 | DOW62000 | 62 | 63 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49872 | DOW63000 | 63 | 72 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49873 | DOW64000 | 64 | 64.8 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49876 | DOW65000 | 65 | 101 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49877 | DOW66000 | 66 | 97 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49878 | DOW67000 | 67 | 103 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49882 | DOW81000 | 81 | 76 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49884 | DOW82000 | 82 | 80 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49885 | DOW83000 | 83 | 80 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
49886 | DOW84000 | 84 | 171 | -0.00043 | houston | N | 0.002778 | -0.00094629 | -0.052571 | 0.00022273 | 0.00022273 | houston | N | 0.00022273 | 0
58909 | PEARSALL | 1 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58909 | PEARSALL | 2 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58909 | PEARSALL | 3 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58909 | PEARSALL | 4 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58909 | PEARSALL | 5 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58909 | PEARSALL | 6 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58919 | PEARSALL | 1 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58919 | PEARSALL | 2 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58919 | PEARSALL | 3 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58919 | PEARSALL | 4 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58919 | PEARSALL | 5 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58919 | PEARSALL | 6 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58929 | PEARSALL | 1 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58929 | PEARSALL | 2 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58929 | PEARSALL | 3 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58929 | PEARSALL | 4 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58929 | PEARSALL | 5 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58929 | PEARSALL | 6 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58949 | PEARSALL | 1 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58949 | PEARSALL | 2 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58949 | PEARSALL | 3 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58949 | PEARSALL | 4 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58949 | PEARSALL | 5 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
58949 | PEARSALL | 6 | 8.4 | 0.002464 | south | Y | 0.005672 | 0.0019477 | -0.049677 | 0.0031167 | 0.0019477 | south | N | 0.0019477 | 0
60000 | DSKY2 | 1 | 76.5 | 0.03702 | west | Y | 0.040228 | 0.036504 | -0.015121 | 0.037673 | 0.015121 | west | N | 0.015121 | 0
60003 | KING_NE1 | 1 | 80 | 0.037805 | west | Y | 0.041013 | 0.037289 | -0.014336 | 0.038458 | 0.014336 | west | N | 0.014336 | 0
60005 | KING_SE1 | 1 | 40 | 0.037805 | west | Y | 0.041013 | 0.037289 | -0.014336 | 0.038458 | 0.014336 | west | N | 0.014336 | 0
60007 | KING_SW1 | 1 | 80 | 0.037927 | west | Y | 0.041135 | 0.037411 | -0.014214 | 0.03858 | 0.014214 | west | N | 0.014214 | 0
60016 | WOODWRD1 | 1 | 80 | 0.037778 | west | Y | 0.040986 | 0.037262 | -0.014363 | 0.038431 | 0.014363 | west | N | 0.014363 | 0
60017 | ORNNWP1 | 1 | 80 | 0.03714 | west | Y | 0.040348 | 0.036624 | -0.015001 | 0.037793 | 0.015001 | west | N | 0.015001 | 0
60018 | DSKY1 | 1 | 84 | 0.036931 | west | Y | 0.040139 | 0.036415 | -0.01521 | 0.037584 | 0.01521 | west | N | 0.01521 | 0
60019 | KING_NW1 | 1 | 80 | 0.037927 | west | Y | 0.041135 | 0.037411 | -0.014214 | 0.03858 | 0.014214 | west | N | 0.014214 | 0
60057 | CALLAHAN | 1 | 114 | 0.000893 | south | Y | 0.004101 | 0.00037671 | -0.051248 | 0.0015457 | 0.00037671 | south | N | 0.00037671 | 0
60058 | BUFF_GAP | 1 | 120 | 0.049112 | west | Y | 0.05232 | 0.048596 | -0.0030293 | 0.049765 | 0.0030293 | west | N | 0.0030293 | 0
60060 | CIRELLO | 1 | 233 | 0.049112 | west | Y | 0.05232 | 0.048596 | -0.0030293 | 0.049765 | 0.0030293 | west | N | 0.0030293 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.049112 | west | Y | 0.05232 | 0.048596 | -0.0030293 | 0.049765 | 0.0030293 | west | N | 0.0030293 | 0
60066 | H_HOLLOW | 1 | 222 | 0.000893 | south | Y | 0.004101 | 0.00037671 | -0.051248 | 0.0015457 | 0.00037671 | south | N | 0.00037671 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.000893 | south | Y | 0.004101 | 0.00037671 | -0.051248 | 0.0015457 | 0.00037671 | south | N | 0.00037671 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.000893 | south | Y | 0.004101 | 0.00037671 | -0.051248 | 0.0015457 | 0.00037671 | south | N | 0.00037671 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.000893 | south | Y | 0.004101 | 0.00037671 | -0.051248 | 0.0015457 | 0.00037671 | south | N | 0.00037671 | 0
60074 | HORSH5 | 1 | 100 | 0.000893 | south | Y | 0.004101 | 0.00037671 | -0.051248 | 0.0015457 | 0.00037671 | south | N | 0.00037671 | 0
60081 | WHRLWIND | 1 | 60 | 0.074485 | west | Y | 0.077693 | 0.073969 | 0.022344 | 0.075138 | 0.022344 | west | N | 0.022344 | 0
60201 | RIO DRCS | F | 0 | 0.012995 | south | N | 0.016203 | 0.012479 | -0.039146 | 0.013648 | 0.012479 | south | N | 0.012479 | 0
60202 | FRIEND_R | F | 0 | 0.033614 | west | N | 0.036822 | 0.033098 | -0.018527 | 0.034267 | 0.018527 | west | N | 0.018527 | 0
60203 | PRES0A | BT | 4.8 | 0.0384 | west | N | 0.041608 | 0.037884 | -0.013741 | 0.039053 | 0.013741 | west | N | 0.013741 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.048552 | west | Y | 0.05176 | 0.048036 | -0.0035893 | 0.049205 | 0.0035893 | west | N | 0.0035893 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.048552 | west | Y | 0.05176 | 0.048036 | -0.0035893 | 0.049205 | 0.0035893 | west | N | 0.0035893 | 0
71057 | L_SWEETW | W1 | 135 | 0.048552 | west | Y | 0.05176 | 0.048036 | -0.0035893 | 0.049205 | 0.0035893 | west | N | 0.0035893 | 0
71059 | L_SWEETW | W1 | 119 | 0.048552 | west | Y | 0.05176 | 0.048036 | -0.0035893 | 0.049205 | 0.0035893 | west | N | 0.0035893 | 0
71060 | L_SWEETW | W1 | 105 | 0.048552 | west | Y | 0.05176 | 0.048036 | -0.0035893 | 0.049205 | 0.0035893 | west | N | 0.0035893 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.048552 | west | Y | 0.05176 | 0.048036 | -0.0035893 | 0.049205 | 0.0035893 | west | N | 0.0035893 | 0
76031 | L_GASCCR | W1 | 150 | 0.039207 | west | Y | 0.042415 | 0.038691 | -0.012934 | 0.03986 | 0.012934 | west | N | 0.012934 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.039083 | west | Y | 0.042291 | 0.038567 | -0.013058 | 0.039736 | 0.013058 | west | N | 0.013058 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.039083 | west | Y | 0.042291 | 0.038567 | -0.013058 | 0.039736 | 0.013058 | west | N | 0.013058 | 0
76096 | L_CAPRSI | W1 | 186 | 0.039083 | west | Y | 0.042291 | 0.038567 | -0.013058 | 0.039736 | 0.013058 | west | N | 0.013058 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.039083 | west | Y | 0.042291 | 0.038567 | -0.013058 | 0.039736 | 0.013058 | west | N | 0.013058 | 0
80003 | MILHWYS | F | 0 | 0.000571 | south | N | 0.003779 | 5.4707e-05 | -0.05157 | 0.0012237 | 5.4707e-05 | south | N | 5.4707e-05 | 0
80010 | EPLVT1 | F | 0 | 0.008085 | south | N | 0.011293 | 0.0075687 | -0.044056 | 0.0087377 | 0.0075687 | south | N | 0.0075687 | 0
80012 | LAR | F | 0 | 0.001583 | south | N | 0.004791 | 0.0010667 | -0.050558 | 0.0022357 | 0.0010667 | south | N | 0.0010667 | 0
80051 | FORPVCM0 | 8 | 28 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
80053 | FOR69CG0 | 10 | 74 | 0.000259 | south | N | 0.003467 | -0.00025729 | -0.051882 | 0.00091173 | 0.00025729 | south | N | 0.00025729 | 0
80080 | GWINDT11 | 1 | 94 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80080 | GWINDT11 | 2 | 41 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80080 | GWINDT11 | 3 | 38 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80080 | GWINDT11 | 4 | 19 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80081 | GWINDT21 | 1 | 94 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80081 | GWINDT21 | 2 | 36 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80081 | GWINDT21 | 3 | 43 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80081 | GWINDT21 | 4 | 22 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80137 | CSDR89 | 8 | 39 | 0.00033 | south | N | 0.003538 | -0.00018629 | -0.051811 | 0.00098273 | 0.00018629 | south | N | 0.00018629 | 0
80137 | CSDR89 | 9 | 15 | 0.00033 | south | N | 0.003538 | -0.00018629 | -0.051811 | 0.00098273 | 0.00018629 | south | N | 0.00018629 | 0
80138 | CSDR7 | 7 | 7 | 0.00033 | south | N | 0.003538 | -0.00018629 | -0.051811 | 0.00098273 | 0.00018629 | south | N | 0.00018629 | 0
80139 | CSDR56 | 5 | 15 | 0.00033 | south | N | 0.003538 | -0.00018629 | -0.051811 | 0.00098273 | 0.00018629 | south | N | 0.00018629 | 0
80139 | CSDR56 | 6 | 39 | 0.00033 | south | N | 0.003538 | -0.00018629 | -0.051811 | 0.00098273 | 0.00018629 | south | N | 0.00018629 | 0
80140 | CSDR11 | 11 | 39 | 0.00033 | south | N | 0.003538 | -0.00018629 | -0.051811 | 0.00098273 | 0.00018629 | south | N | 0.00018629 | 0
80180 | PNSCALT1 | 1 | 148 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80180 | PNSCALT1 | 2 | 50 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80181 | PNSCALT2 | 1 | 55 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80181 | PNSCALT2 | 2 | 50 | 0.000559 | south | Y | 0.003767 | 4.2707e-05 | -0.051582 | 0.0012117 | 4.2707e-05 | south | N | 4.2707e-05 | 0
80223 | REYSHR G | 1 | 12 | 0.000485 | south | N | 0.003693 | -3.1293e-05 | -0.051656 | 0.0011377 | 3.1293e-05 | south | N | 3.1293e-05 | 0
80224 | VISTRONG | 1 | 15 | 0.000346 | south | N | 0.003554 | -0.00017029 | -0.051795 | 0.00099873 | 0.00017029 | south | N | 0.00017029 | 0
80225 | VISTRONG | 2 | 23 | 0.000346 | south | N | 0.003554 | -0.00017029 | -0.051795 | 0.00099873 | 0.00017029 | south | N | 0.00017029 | 0
80226 | ALCOA G | 1 | 48 | 0.000274 | south | N | 0.003482 | -0.00024229 | -0.051867 | 0.00092673 | 0.00024229 | south | N | 0.00024229 | 0
80227 | AIRCO G | 1 | 8 | 0.000341 | south | N | 0.003549 | -0.00017529 | -0.0518 | 0.00099373 | 0.00017529 | south | N | 0.00017529 | 0
80261 | NBEC81A | 1 | 180 | 0.000516 | south | Y | 0.003724 | -2.9301e-07 | -0.051625 | 0.0011687 | 2.9301e-07 | south | N | 2.9301e-07 | 0
80262 | NBEC91A | 1 | 180 | 0.000515 | south | Y | 0.003723 | -1.293e-06 | -0.051626 | 0.0011677 | 1.293e-06 | south | N | 1.293e-06 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.000521 | south | Y | 0.003729 | 4.707e-06 | -0.05162 | 0.0011737 | 4.707e-06 | south | N | 4.707e-06 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.000521 | south | Y | 0.003729 | 4.707e-06 | -0.05162 | 0.0011737 | 4.707e-06 | south | N | 4.707e-06 | 0
80265 | LARECU40 | 4 | 100 | 0.001583 | south | Y | 0.004791 | 0.0010667 | -0.050558 | 0.0022357 | 0.0010667 | south | N | 0.0010667 | 0
80266 | LARECU50 | 5 | 100 | 0.001583 | south | Y | 0.004791 | 0.0010667 | -0.050558 | 0.0022357 | 0.0010667 | south | N | 0.0010667 | 0
80291 | PAPALOTE | 1 | 25 | 0.000498 | south | Y | 0.003706 | -1.8293e-05 | -0.051643 | 0.0011507 | 1.8293e-05 | south | N | 1.8293e-05 | 0
80291 | PAPALOTE | 2 | 25 | 0.000498 | south | Y | 0.003706 | -1.8293e-05 | -0.051643 | 0.0011507 | 1.8293e-05 | south | N | 1.8293e-05 | 0
80291 | PAPALOTE | 3 | 25 | 0.000498 | south | Y | 0.003706 | -1.8293e-05 | -0.051643 | 0.0011507 | 1.8293e-05 | south | N | 1.8293e-05 | 0
80291 | PAPALOTE | 4 | 16 | 0.000498 | south | Y | 0.003706 | -1.8293e-05 | -0.051643 | 0.0011507 | 1.8293e-05 | south | N | 1.8293e-05 | 0
80294 | PAPALOTE | 5 | 25 | 0.000498 | south | Y | 0.003706 | -1.8293e-05 | -0.051643 | 0.0011507 | 1.8293e-05 | south | N | 1.8293e-05 | 0
80294 | PAPALOTE | 6 | 25 | 0.000498 | south | Y | 0.003706 | -1.8293e-05 | -0.051643 | 0.0011507 | 1.8293e-05 | south | N | 1.8293e-05 | 0
80294 | PAPALOTE | 7 | 25 | 0.000498 | south | Y | 0.003706 | -1.8293e-05 | -0.051643 | 0.0011507 | 1.8293e-05 | south | N | 1.8293e-05 | 0
80294 | PAPALOTE | 8 | 15 | 0.000498 | south | Y | 0.003706 | -1.8293e-05 | -0.051643 | 0.0011507 | 1.8293e-05 | south | N | 1.8293e-05 | 0
86104 | CID-138 | EQ | 0 | 0.001583 | south | N | 0.004791 | 0.0010667 | -0.050558 | 0.0022357 | 0.0010667 | south | N | 0.0010667 | 0
86105 | CID-230 | EQ | 500 | 0.001583 | south | N | 0.004791 | 0.0010667 | -0.050558 | 0.0022357 | 0.0010667 | south | N | 0.0010667 | 0
86106 | CUF-230 | EQ | 500 | 0.001583 | south | N | 0.004791 | 0.0010667 | -0.050558 | 0.0022357 | 0.0010667 | south | N | 0.0010667 | 0
86107 | CUF-138 | EQ | 0 | 0.001583 | south | N | 0.004791 | 0.0010667 | -0.050558 | 0.0022357 | 0.0010667 | south | N | 0.0010667 | 0
88198 | BEEVILLE | F | 0 | 0.00069 | south | N | 0.003898 | 0.00017371 | -0.051451 | 0.0013427 | 0.00017371 | south | N | 0.00017371 | 0
88253 | HAMILTON | F | 0 | 0.011896 | south | N | 0.015104 | 0.01138 | -0.040245 | 0.012549 | 0.01138 | south | N | 0.01138 | 0
88299 | ZAPATA | F | 0 | 0.001248 | south | N | 0.004456 | 0.00073171 | -0.050893 | 0.0019007 | 0.00073171 | south | N | 0.00073171 | 0
88508 | FALFURRI | F | 0 | 0.000717 | south | N | 0.003925 | 0.00020071 | -0.051424 | 0.0013697 | 0.00020071 | south | N | 0.00020071 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1426 FISHRDSS - 1427 FISHERRD C: 1422 BOWMAN5 - 1425 FISHRDSS | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.25405 | west | 4 | Y | N | Ywest | Nwest | 1 | 165.0582 | 649.7 | 0.2171 | 141.0506 | 649.7 | 141.0506
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.074485 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4691 | 60 | 0.037533 | 2.252
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.011896 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.39257 | 0 | 0.015104 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.011896 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2974 | 0 | 0.015104 | 0 |  |  | Weighted Shift Factors
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.011896 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015104 | 0 |  |  | North | -0.003208
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.050411 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5617 | 150 | 0.013459 | 2.0189 |  |  | West | 0.036952
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.049112 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8934 | 120 | 0.01216 | 1.4592 |  |  |  | -0.04016
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.049112 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.4431 | 233 | 0.01216 | 2.8333
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.049112 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3589 | 170.2 | 0.01216 | 2.0696 |  |  | Line Rating | 287
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.008804 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.052824 | 0 | 0.012012 | 0 |  |  | Conc Gen | 649.7
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8207 | 37.5 | 0.0116 | 0.435 |  |  | Weighted Imp. | 141.0506
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2193 | 107.5 | 0.0116 | 1.247 |  |  | PTDF | 0.2171
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5545 | 135 | 0.0116 | 1.566
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.7777 | 119 | 0.0116 | 1.3804 |  |  | Concentration | -5.4059
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.098 | 105 | 0.0116 | 1.218
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9084 | 80.5 | 0.0116 | 0.93381
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.008085 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011293 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.046247 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8389 | 169.5 | 0.0092951 | 1.5755
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.045449 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8174 | 150 | 0.0084971 | 1.2746
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.045449 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5903 | 101 | 0.0084971 | 0.85821
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.044407 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7302 | 84 | 0.0074551 | 0.62623
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.043039 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2609 | 99 | 0.0060871 | 0.60262
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.043039 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6254 | 61 | 0.0060871 | 0.37131
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.043039 | west | 7 | N | N | Nwest | Nwest | 1 | 1.076 | 0 | 0.0060871 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.043039 | west | 7 | N | N | Nwest | Nwest | 1 | 1.9669 | 0 | 0.0060871 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.043039 | west | 7 | N | N | Nwest | Nwest | 1 | 1.9669 | 0 | 0.0060871 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.042962 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0576 | 141 | 0.0060101 | 0.84742
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.042962 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1554 | 120 | 0.0060101 | 0.72121
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.002576 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.035291 | 0 | 0.005784 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.042446 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6741 | 63 | 0.0054941 | 0.34613
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.002169 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.052056 | 24 | 0.005377 | 0.12905
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.002169 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.052056 | 24 | 0.005377 | 0.12905
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.002169 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.049887 | 23 | 0.005377 | 0.12367
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.002104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037872 | 0 | 0.005312 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.002104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037872 | 0 | 0.005312 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.002104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03156 | 0 | 0.005312 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.002037 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.85961 | 422 | 0.005245 | 2.2134
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.001935 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.05418 | 0 | 0.005143 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.001935 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.056115 | 0 | 0.005143 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.041867 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5361 | 180 | 0.0049151 | 0.88472
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.041867 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5361 | 180 | 0.0049151 | 0.88472
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.001631 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.029358 | 0 | 0.004839 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.001631 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.029358 | 0 | 0.004839 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.041786 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4018 | 225 | 0.0048341 | 1.0877
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.001583 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1583 | 100 | 0.004791 | 0.4791
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.001583 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1583 | 100 | 0.004791 | 0.4791
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.001248 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004456 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.041224 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9469 | 120 | 0.0042721 | 0.51265
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000957 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011484 | 0 | 0.004165 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000957 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010527 | 0 | 0.004165 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000957 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011484 | 0 | 0.004165 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.041071 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9285 | 120 | 0.0041191 | 0.49429
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1018 | 114 | 0.004101 | 0.46751
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.19825 | 222 | 0.004101 | 0.91042
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.16431 | 184 | 0.004101 | 0.75458
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.20003 | 224 | 0.004101 | 0.91862
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10269 | 115 | 0.004101 | 0.47161
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000831 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.048198 | 58 | 0.004039 | 0.23426
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000831 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.073959 | 89 | 0.004039 | 0.35947
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.036564 | 44 | 0.004039 | 0.17771
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.036564 | 44 | 0.004039 | 0.17771
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035733 | 43 | 0.004039 | 0.17368
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.037395 | 45 | 0.004039 | 0.18175
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7009 | 66 | 0.0039711 | 0.26209
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.8237 | 69 | 0.0039711 | 0.27401
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.8237 | 69 | 0.0039711 | 0.27401
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7418 | 67 | 0.0039711 | 0.26606
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7418 | 67 | 0.0039711 | 0.26606
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.66 | 65 | 0.0039711 | 0.25812
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.000762 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.31013 | 407 | 0.00397 | 1.6158
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.000743 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.29423 | 396 | 0.003951 | 1.5646
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.15424 | 209 | 0.003946 | 0.82471
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.15941 | 216 | 0.003946 | 0.85233
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.033948 | 46 | 0.003946 | 0.18151
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.034686 | 47 | 0.003946 | 0.18546
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.033948 | 46 | 0.003946 | 0.18151
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.033948 | 46 | 0.003946 | 0.18151
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.30406 | 412 | 0.003946 | 1.6257
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.2952 | 400 | 0.003946 | 1.5784
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.000726 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.30782 | 424 | 0.003934 | 1.668
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.000726 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.30855 | 425 | 0.003934 | 1.6719
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.000717 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003925 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000712 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02492 | 0 | 0.00392 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000712 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.024208 | 0 | 0.00392 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000712 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02492 | 0 | 0.00392 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.00069 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003898 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.000674 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003882 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.000674 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003882 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.000674 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003882 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.040827 | west | 8 | N | N | Nwest | Nwest | 1 | 1.0533 | 0 | 0.0038751 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10214 | 155 | 0.003867 | 0.59938
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.000659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.11203 | 170 | 0.003867 | 0.65739
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10214 | 155 | 0.003867 | 0.59938
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.000652 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.095518 | 146.5 | 0.00386 | 0.56549
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.000652 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.096431 | 147.9 | 0.00386 | 0.57089
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.000652 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1128 | 173 | 0.00386 | 0.66777
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.000636 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.34726 | 546 | 0.003844 | 2.0988
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.000636 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.477 | 750 | 0.003844 | 2.883
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.000602 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12461 | 207 | 0.00381 | 0.78866
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.000602 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13045 | 216.7 | 0.00381 | 0.82562
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.000602 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14568 | 242 | 0.00381 | 0.92201
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.000601 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.086544 | 144 | 0.003809 | 0.54849
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.000601 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.086544 | 144 | 0.003809 | 0.54849
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.000601 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10277 | 171 | 0.003809 | 0.65133
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.000571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003779 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.000571 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.021698 | 38 | 0.003779 | 0.1436
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.000571 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.01102 | 19.3 | 0.003779 | 0.072934
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.000571 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.008565 | 15 | 0.003779 | 0.056685
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.000571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.026837 | 47 | 0.003779 | 0.17761
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.052546 | 94 | 0.003767 | 0.3541
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.022919 | 41 | 0.003767 | 0.15445
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.021242 | 38 | 0.003767 | 0.14314
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.010621 | 19 | 0.003767 | 0.071572
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.052546 | 94 | 0.003767 | 0.3541
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.020124 | 36 | 0.003767 | 0.13561
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.024037 | 43 | 0.003767 | 0.16198
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.012298 | 22 | 0.003767 | 0.082873
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.082732 | 148 | 0.003767 | 0.55751
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02795 | 50 | 0.003767 | 0.18835
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.030745 | 55 | 0.003767 | 0.20718
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02795 | 50 | 0.003767 | 0.18835
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.000552 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002208 | 0 | 0.00376 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.000546 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.003276 | 0 | 0.003754 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.000544 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.015776 | 0 | 0.003752 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.000529 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020102 | 0 | 0.003737 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.000525 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01995 | 0 | 0.003733 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.077175 | 147 | 0.003733 | 0.54875
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.07245 | 138 | 0.003733 | 0.51515
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0735 | 140 | 0.003733 | 0.52262
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.077175 | 147 | 0.003733 | 0.54875
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.09555 | 182 | 0.003733 | 0.6794
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10395 | 198 | 0.003733 | 0.73913
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.000525 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013125 | 0 | 0.003733 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.000525 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013125 | 0 | 0.003733 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.000521 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.17401 | 334 | 0.003729 | 1.2455
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.000521 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.17714 | 340 | 0.003729 | 1.2679
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.000521 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.09378 | 180 | 0.003729 | 0.67121
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.000521 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.09378 | 180 | 0.003729 | 0.67121
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.000516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.09288 | 180 | 0.003724 | 0.67031
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.000516 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.076523 | 0 | 0.003724 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.000516 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.076678 | 0 | 0.003724 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.000516 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.078948 | 0 | 0.003724 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.000515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17304 | 336 | 0.003723 | 1.2509
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.000515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0927 | 180 | 0.003723 | 0.67013
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.000514 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.32331 | 629 | 0.003722 | 2.3411
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 25 | 0.003706 | 0.092649
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 25 | 0.003706 | 0.092649
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 25 | 0.003706 | 0.092649
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007968 | 16 | 0.003706 | 0.059296
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 25 | 0.003706 | 0.092649
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 25 | 0.003706 | 0.092649
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 25 | 0.003706 | 0.092649
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.00747 | 15 | 0.003706 | 0.05559
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.000488 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0011712 | 0 | 0.003696 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.000488 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0011712 | 0 | 0.003696 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.000488 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0013664 | 0 | 0.003696 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.069012 | 142 | 0.003694 | 0.52454
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.07047 | 145 | 0.003694 | 0.53563
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.073386 | 151 | 0.003694 | 0.55779
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14094 | 290 | 0.003694 | 1.0713
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.07663 | 0 | 0.003693 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.074205 | 0 | 0.003693 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.0485 | 0 | 0.003693 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.070325 | 0 | 0.003693 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.071295 | 0 | 0.003693 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.061595 | 0 | 0.003693 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.000485 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00582 | 0 | 0.003693 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10031 | 223.9 | 0.003656 | 0.81857
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1008 | 225 | 0.003656 | 0.82259
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10062 | 224.6 | 0.003656 | 0.82113
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10156 | 226.7 | 0.003656 | 0.82881
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.000422 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.009284 | 22 | 0.00363 | 0.079859
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.000422 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.004642 | 11 | 0.00363 | 0.03993
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.000422 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.004642 | 11 | 0.00363 | 0.03993
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.00042 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001008 | 0 | 0.003628 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.00042 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001008 | 0 | 0.003628 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000416 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.004992 | 0 | 0.003624 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.018794 | 47.7 | 0.003602 | 0.17181
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.014696 | 37.3 | 0.003602 | 0.13435
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.018124 | 46 | 0.003602 | 0.16569
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.018912 | 48 | 0.003602 | 0.17289
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.000382 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.055008 | 144 | 0.00359 | 0.51696
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.000382 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.071816 | 188 | 0.00359 | 0.67491
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.000367 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.026791 | 0 | 0.003575 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00519 | 0 | 0.003554 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.007958 | 0 | 0.003554 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.000341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.002728 | 0 | 0.003549 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00924 | 0 | 0.003538 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00231 | 0 | 0.003538 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01287 | 0 | 0.003538 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00495 | 0 | 0.003538 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00231 | 0 | 0.003538 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00495 | 0 | 0.003538 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01287 | 0 | 0.003538 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01287 | 0 | 0.003538 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.000298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002384 | 0 | 0.003506 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.000298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002384 | 0 | 0.003506 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.000274 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013152 | 0 | 0.003482 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.013181 | 49 | 0.003477 | 0.17037
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012374 | 46 | 0.003477 | 0.15994
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012374 | 46 | 0.003477 | 0.15994
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012643 | 47 | 0.003477 | 0.16342
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.000269 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.041426 | 154 | 0.003477 | 0.53545
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.000269 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.039812 | 148 | 0.003477 | 0.51459
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012912 | 48 | 0.003477 | 0.16689
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012912 | 48 | 0.003477 | 0.16689
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.040423 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.26679 | 6.6 | 0.0034711 | 0.022909
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.040423 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3865 | 34.3 | 0.0034711 | 0.11906
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020461 | 0 | 0.003467 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020979 | 0 | 0.003467 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020461 | 0 | 0.003467 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.02072 | 0 | 0.003467 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020306 | 0 | 0.003467 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.006475 | 0 | 0.003467 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.011914 | 0 | 0.003467 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.007252 | 0 | 0.003467 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.011292 | 0 | 0.003467 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.019166 | 0 | 0.003467 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.000259 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.08029 | 310 | 0.003467 | 1.0748
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.000259 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.10697 | 413 | 0.003467 | 1.4319
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.009534 | 42 | 0.003435 | 0.14427
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.009988 | 44 | 0.003435 | 0.15114
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.009988 | 44 | 0.003435 | 0.15114
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.010669 | 47 | 0.003435 | 0.16144
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.040367 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6466 | 214.2 | 0.0034151 | 0.73151
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.000146 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.019272 | 132 | 0.003354 | 0.44272
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.000146 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.019564 | 134 | 0.003354 | 0.44943
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.000146 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.047158 | 323 | 0.003354 | 1.0833
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.000141 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.021503 | 152.5 | 0.003349 | 0.51072
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.000141 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.02108 | 149.5 | 0.003349 | 0.50067
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.000141 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.032797 | 232.6 | 0.003349 | 0.77897
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.040276 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.336 | 58 | 0.0033241 | 0.1928
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00445 | 50 | 0.003297 | 0.16485
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00445 | 50 | 0.003297 | 0.16485
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00445 | 50 | 0.003297 | 0.16485
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00445 | 50 | 0.003297 | 0.16485
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.04023 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0431 | 100.5 | 0.0032781 | 0.32945
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 6.4e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.010112 | 158 | 0.003272 | 0.51697
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 6.4e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.01024 | 160 | 0.003272 | 0.52352
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 6.4e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0112 | 175 | 0.003272 | 0.57259
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 5.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.023815 | 433 | 0.003263 | 1.4129
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 5.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.03212 | 584 | 0.003263 | 1.9056
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 5.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.032725 | 595 | 0.003263 | 1.9415
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003208 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003208 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.000256 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.34125 | 0 | 0.002952 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.000256 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.33997 | 0 | 0.002952 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.021204 | 76 | 0.002929 | 0.2226
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.021204 | 76 | 0.002929 | 0.2226
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.029295 | 105 | 0.002929 | 0.30754
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.020646 | 74 | 0.002929 | 0.21674
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.020646 | 74 | 0.002929 | 0.21674
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.028458 | 102 | 0.002929 | 0.29876
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.000293 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.16672 | 569 | 0.002915 | 1.6586
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.000293 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.17023 | 581 | 0.002915 | 1.6936
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.0003 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.0198 | 66 | 0.002908 | 0.19193
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.03981 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9317 | 149 | 0.0028581 | 0.42586
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9712 | 150 | 0.0028561 | 0.42841
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7578 | 220 | 0.0028561 | 0.62834
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9616 | 200 | 0.0028561 | 0.57122
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8526 | 121.9 | 0.0028561 | 0.34816
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.039802 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7861 | 0 | 0.0028501 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.039802 | west | 8 | N | N | Nwest | Nwest | 1 | 2.9215 | 0 | 0.0028501 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.039802 | west | 8 | N | N | Nwest | Nwest | 1 | 2.8021 | 0 | 0.0028501 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02666 | 0 | 0.002778 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.030702 | 0 | 0.002778 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01935 | 0 | 0.002778 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04343 | 0 | 0.002778 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03698 | 0 | 0.002778 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03784 | 0 | 0.002778 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0215 | 0 | 0.002778 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.00774 | 0 | 0.002778 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04042 | 0 | 0.002778 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0301 | 0 | 0.002778 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02709 | 0 | 0.002778 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03096 | 0 | 0.002778 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027864 | 0 | 0.002778 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04343 | 0 | 0.002778 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04171 | 0 | 0.002778 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04429 | 0 | 0.002778 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03268 | 0 | 0.002778 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0344 | 0 | 0.002778 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0344 | 0 | 0.002778 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07353 | 0 | 0.002778 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.000462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.032802 | 0 | 0.002746 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.000462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.00462 | 0 | 0.002746 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7776 | 70 | 0.0027281 | 0.19097
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7776 | 70 | 0.0027281 | 0.19097
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6823 | 92.8 | 0.0027281 | 0.25317
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1744 | 80 | 0.0027281 | 0.21825
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1744 | 80 | 0.0027281 | 0.21825
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5632 | 115 | 0.0027281 | 0.31373
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.261 | 208.2 | 0.0027261 | 0.56757
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.6382 | 142.1 | 0.0027261 | 0.38738
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2534 | 132.4 | 0.0027261 | 0.36093
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.3962 | 136 | 0.0027261 | 0.37075
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8327 | 147 | 0.0027261 | 0.40073
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.3324 | 210 | 0.0027261 | 0.57248
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.054168 | 0 | 0.00272 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.054168 | 0 | 0.00272 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.058072 | 0 | 0.00272 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.053436 | 0 | 0.00272 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.039613 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3865 | 35 | 0.0026611 | 0.093138
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.039613 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1884 | 30 | 0.0026611 | 0.079833
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.000574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.026461 | 0 | 0.002634 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.000582 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.37888 | 651 | 0.002626 | 1.7095
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.000582 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.32825 | 564 | 0.002626 | 1.481
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.000582 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.3492 | 600 | 0.002626 | 1.5756
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.000583 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.095029 | 0 | 0.002625 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.000583 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.095029 | 0 | 0.002625 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.000583 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14283 | 0 | 0.002625 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.000587 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.019371 | 0 | 0.002621 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.000599 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.096439 | 161 | 0.002609 | 0.42004
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.000599 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.099434 | 166 | 0.002609 | 0.43309
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.000599 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.14855 | 248 | 0.002609 | 0.64702
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.000599 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.32705 | 546 | 0.002609 | 1.4245
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.000599 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -0.38516 | 0 | 0.002609 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.000599 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.007787 | 13 | 0.002609 | 0.033917
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6091 | 66 | 0.0025801 | 0.17029
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.5696 | 65 | 0.0025801 | 0.16771
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6486 | 67 | 0.0025801 | 0.17287
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6486 | 67 | 0.0025801 | 0.17287
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6486 | 67 | 0.0025801 | 0.17287
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.039532 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0025801 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.039532 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0025801 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.045029 | 0 | 0.002572 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.042421 | 0 | 0.002572 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.033708 | 0 | 0.002572 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.097435 | 0 | 0.002572 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.097626 | 0 | 0.002572 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.096863 | 0 | 0.002572 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.061056 | 0 | 0.002572 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.15518 | 0 | 0.002572 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02544 | 0 | 0.002572 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.020352 | 0 | 0.002572 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01908 | 0 | 0.002572 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.063791 | 0 | 0.002572 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.059084 | 0 | 0.002572 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.065317 | 0 | 0.002572 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.064872 | 0 | 0.002572 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.000656 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.0328 | 50 | 0.002552 | 0.1276
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.000668 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00254 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.062244 | 0 | 0.002524 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059918 | 0 | 0.002524 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059508 | 0 | 0.002524 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.037278 | 0 | 0.002524 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0083448 | 0 | 0.002524 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044915 | 0 | 0.002517 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.04146 | 0 | 0.002517 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044915 | 0 | 0.002517 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044915 | 0 | 0.002517 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.032292 | 46 | 0.002506 | 0.11527
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.032292 | 46 | 0.002506 | 0.11527
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.032292 | 46 | 0.002506 | 0.11527
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.03861 | 55 | 0.002506 | 0.13783
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.03861 | 55 | 0.002506 | 0.13783
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.037908 | 54 | 0.002506 | 0.13532
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.000703 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.054834 | 0 | 0.002505 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.000703 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.05624 | 0 | 0.002505 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11506 | 0 | 0.002503 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11076 | 0 | 0.002503 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11104 | 0 | 0.002503 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11069 | 0 | 0.002503 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.18965 | 0 | 0.002503 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.000709 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024815 | 0 | 0.002499 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.000711 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.008532 | 12 | 0.002497 | 0.029964
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.000711 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.002497 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.000712 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10609 | 0 | 0.002496 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.000712 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.046351 | 0 | 0.002496 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.000712 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.11748 | 165 | 0.002496 | 0.41184
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.000712 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.12033 | 169 | 0.002496 | 0.42182
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.000713 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12834 | 0 | 0.002495 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.000713 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11308 | 0 | 0.002495 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.000713 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11194 | 0 | 0.002495 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.000713 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.16256 | 228 | 0.002495 | 0.56885
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.045632 | 0 | 0.002495 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.045062 | 0 | 0.002495 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.058894 | 0 | 0.002495 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052477 | 0 | 0.002495 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.011551 | 0 | 0.002495 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.000713 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.15187 | 213 | 0.002495 | 0.53143
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.050907 | 0 | 0.002491 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.051624 | 0 | 0.002491 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027963 | 0 | 0.002491 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02151 | 0 | 0.002491 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.030408 | 42 | 0.002484 | 0.10433
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.030408 | 42 | 0.002484 | 0.10433
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.027512 | 38 | 0.002484 | 0.094391
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.027512 | 38 | 0.002484 | 0.094391
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.000724 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.098464 | 0 | 0.002484 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.000726 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1256 | 0 | 0.002482 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.000726 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.09801 | 0 | 0.002482 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.076648 | 104 | 0.002471 | 0.25698
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.076648 | 104 | 0.002471 | 0.25698
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039798 | 54 | 0.002471 | 0.13343
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039061 | 53 | 0.002471 | 0.13096
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039798 | 54 | 0.002471 | 0.13343
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.042009 | 57 | 0.002471 | 0.14085
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039798 | 54 | 0.002471 | 0.13343
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039798 | 54 | 0.002471 | 0.13343
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.042746 | 58 | 0.002471 | 0.14332
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.042746 | 58 | 0.002471 | 0.14332
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.000739 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.54317 | 735 | 0.002469 | 1.8147
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.025228 | 0 | 0.002466 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.025747 | 0 | 0.002466 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024263 | 0 | 0.002466 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.034058 | 0 | 0.002466 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.013133 | 0 | 0.002466 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015137 | 0 | 0.002466 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.014766 | 0 | 0.002466 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02597 | 0 | 0.002466 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.013356 | 0 | 0.002466 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.063367 | 0 | 0.002466 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10982 | 0 | 0.002466 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.000747 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.008964 | 12 | 0.002461 | 0.029532
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.000749 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.003745 | 0 | 0.002459 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.000749 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015729 | 0 | 0.002459 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.00075 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.55725 | 743 | 0.002458 | 1.8263
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.00075 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.009 | 12 | 0.002458 | 0.029496
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04875 | 0 | 0.002458 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0495 | 0 | 0.002458 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0525 | 0 | 0.002458 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04725 | 0 | 0.002458 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0465 | 0 | 0.002458 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078 | 0 | 0.002458 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04425 | 0 | 0.002458 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.000752 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11806 | 0 | 0.002456 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.000753 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.12952 | 172 | 0.002455 | 0.42226
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.000753 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.12952 | 172 | 0.002455 | 0.42226
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.000753 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.12952 | 172 | 0.002455 | 0.42226
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12373 | 0 | 0.002448 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12266 | 0 | 0.002448 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12076 | 0 | 0.002448 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20459 | 0 | 0.002448 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.000764 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.30407 | 398 | 0.002444 | 0.9727
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.043064 | 56 | 0.002439 | 0.13658
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.045371 | 59 | 0.002439 | 0.1439
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.043064 | 56 | 0.002439 | 0.13658
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.043064 | 56 | 0.002439 | 0.13658
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.045371 | 59 | 0.002439 | 0.1439
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.043064 | 56 | 0.002439 | 0.13658
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14048 | 0 | 0.002396 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12667 | 0 | 0.002396 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12505 | 0 | 0.002396 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12505 | 0 | 0.002396 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.000812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13154 | 0 | 0.002396 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.039207 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8811 | 150 | 0.0022551 | 0.33826
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.039207 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9009 | 125 | 0.0022551 | 0.28189
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.039207 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9009 | 125 | 0.0022551 | 0.28189
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3968 | 112.5 | 0.0021311 | 0.23975
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8429 | 149.5 | 0.0021311 | 0.3186
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2694 | 186 | 0.0021311 | 0.39638
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3833 | 214.5 | 0.0021311 | 0.45712
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.0384 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.18432 | 0 | 0.0014481 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037927 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0342 | 80 | 0.00097509 | 0.078007
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037927 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0342 | 80 | 0.00097509 | 0.078007
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.037805 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8354 | 75 | 0.00085309 | 0.063982
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037805 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0244 | 80 | 0.00085309 | 0.068247
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.037805 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5122 | 40 | 0.00085309 | 0.034124
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037778 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0222 | 80 | 0.00082609 | 0.066087
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.037775 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.022 | 80 | 0.00082309 | 0.065847
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.037759 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6639 | 150 | 0.00080709 | 0.12106
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.037759 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6639 | 150 | 0.00080709 | 0.12106
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.03714 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9712 | 80 | 0.00018809 | 0.015047
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.03702 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.832 | 76.5 | 6.8088e-05 | 0.0052087
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.036931 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1022 | 84 | -2.0912e-05 | -0.0017566
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3098 | 209 | -0.0019769 | -0.41317
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4243 | 126.5 | -0.0019769 | -0.25008
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7088 | 249 | -0.0019769 | -0.49225
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8901 | 197 | -0.0019769 | -0.38945
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.034511 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8044 | 400 | -0.0024409 | -0.97636
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.034412 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1212 | 236 | -0.0025399 | -0.59942
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.033614 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0033379 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.030836 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6254 | 150 | -0.0061159 | -0.91739
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.026734 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4111 | 165 | -0.010218 | -1.686
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.012995 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.023957 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.002418 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.88499 | 366 | -0.034534 | -12.6394
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.001407 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.08442 | 60 | -0.035545 | -2.1327
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0893 | 100 | -0.036059 | -3.6059
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.036952 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.036952 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -5.3e-05 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.061321 | 0 | -0.037005 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -5.3e-05 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.061374 | 0 | -0.037005 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.000319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.069319 | 217.3 | -0.037271 | -8.099
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.000319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.065395 | 205 | -0.037271 | -7.6405
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.000319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.086896 | 272.4 | -0.037271 | -10.1526
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.00103 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.037982 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.001147 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038099 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.001147 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038099 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.001191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.17865 | 150 | -0.038143 | -5.7214
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.001191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.09528 | 80 | -0.038143 | -3.0514
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.001205 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.30728 | 255 | -0.038157 | -9.73
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.001205 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.17955 | 149 | -0.038157 | -5.6854
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.001205 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.18437 | 153 | -0.038157 | -5.838
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.18782 | 0 | -0.03817 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.19001 | 0 | -0.03817 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.19001 | 0 | -0.03817 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.46284 | 0 | -0.03817 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.001225 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038177 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.001225 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.96408 | 787 | -0.038177 | -30.0452
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.001293 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.062064 | 48 | -0.038245 | -1.8358
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.001293 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.059478 | 46 | -0.038245 | -1.7593
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.001293 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.13576 | 105 | -0.038245 | -4.0157
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.001299 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.041568 | 0 | -0.038251 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.001301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.022117 | 17 | -0.038253 | -0.6503
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.001302 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.60283 | 463 | -0.038254 | -17.7116
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.001549 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.023235 | 0 | -0.038501 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.001549 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.023235 | 0 | -0.038501 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3483 | 855 | -0.038529 | -32.9422
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3483 | 855 | -0.038529 | -32.9422
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.24018 | 152.3 | -0.038529 | -5.868
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.24128 | 153 | -0.038529 | -5.8949
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.001689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3968 | 827 | -0.038641 | -31.956
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.001689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3833 | 819 | -0.038641 | -31.6469
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.12026 | 70 | -0.03867 | -2.7069
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11854 | 69 | -0.03867 | -2.6682
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11854 | 69 | -0.03867 | -2.6682
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11682 | 68 | -0.03867 | -2.6296
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.001761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.29585 | 168 | -0.038713 | -6.5038
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.001761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.15849 | 90 | -0.038713 | -3.4842
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.41395 | 224 | -0.0388 | -8.6912
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.41765 | 226 | -0.0388 | -8.7688
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.39178 | 212 | -0.0388 | -8.2256
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.38993 | 211 | -0.0388 | -8.1868
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.001974 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.214 | 615 | -0.038926 | -23.9394
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.001974 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.1587 | 587 | -0.038926 | -22.8495
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.002042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.30773 | 150.7 | -0.038994 | -5.8764
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.002042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.30834 | 151 | -0.038994 | -5.8881
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.002042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.36225 | 177.4 | -0.038994 | -6.9175
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.002066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.313 | 151.5 | -0.039018 | -5.9112
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.002066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.31465 | 152.3 | -0.039018 | -5.9424
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.002066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.36672 | 177.5 | -0.039018 | -6.9257
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.002095 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.45336 | 216.4 | -0.039047 | -8.4498
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.002095 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.45273 | 216.1 | -0.039047 | -8.438
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.002275 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.4459 | 196 | -0.039227 | -7.6885
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.002275 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.25252 | 111 | -0.039227 | -4.3542
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.002319 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.51946 | 224 | -0.039271 | -8.7967
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.002467 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.12335 | 50 | -0.039419 | -1.9709
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.002468 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.44918 | 182 | -0.03942 | -7.1744
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.002468 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.1945 | 484 | -0.03942 | -19.0792
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.002473 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.039425 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.37207 | 0 | -0.039466 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.32682 | 0 | -0.039466 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.36453 | 0 | -0.039466 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.0031 | 0 | -0.039466 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.002564 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.0127 | 785 | -0.039516 | -31.02
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.002564 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.0384 | 795 | -0.039516 | -31.4152
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.002564 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9999 | 780 | -0.039516 | -30.8224
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.002575 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.0171 | 395 | -0.039527 | -15.6131
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.002575 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1201 | 435 | -0.039527 | -17.1942
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.002643 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1497 | 435 | -0.039595 | -17.2238
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.002645 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.31211 | 118 | -0.039597 | -4.6724
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.002645 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.30417 | 115 | -0.039597 | -4.5536
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.002645 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.4706 | 556 | -0.039597 | -22.0159
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.002856 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039808 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.002856 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039808 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.002928 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1361 | 388 | -0.03988 | -15.4734
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.002928 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.5079 | 515 | -0.03988 | -20.5382
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47189 | 161 | -0.039883 | -6.4211
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.48068 | 164 | -0.039883 | -6.5408
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.48068 | 164 | -0.039883 | -6.5408
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.2134 | 414 | -0.039883 | -16.5115
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47482 | 162 | -0.039883 | -6.461
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47189 | 161 | -0.039883 | -6.4211
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47775 | 163 | -0.039883 | -6.5009
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.1988 | 409 | -0.039883 | -16.3121
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.003092 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.12368 | 40 | -0.040044 | -1.6018
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.003102 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.06204 | 20 | -0.040054 | -0.80108
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.003102 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.07755 | 25 | -0.040054 | -1.0013
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.003102 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.12718 | 41 | -0.040054 | -1.6422
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.003125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.24688 | 79 | -0.040077 | -3.1661
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.003125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.33125 | 106 | -0.040077 | -4.2482
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.003125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.45625 | 146 | -0.040077 | -5.8512
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.003125 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.2375 | 76 | -0.040077 | -3.0458
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.003308 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.8459 | 558 | -0.04026 | -22.465
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.003308 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9153 | 579 | -0.04026 | -23.3105
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.003308 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.6729 | 808 | -0.04026 | -32.53
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.003377 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.040329 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.55312 | 160 | -0.040409 | -6.4654
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.53929 | 156 | -0.040409 | -6.3038
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.67757 | 196 | -0.040409 | -7.9201
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.53929 | 156 | -0.040409 | -6.3038
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.54275 | 157 | -0.040409 | -6.3442
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.68449 | 198 | -0.040409 | -8.001
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.003489 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.26167 | 0 | -0.040441 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.003489 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.27772 | 0 | -0.040441 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.003489 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.30843 | 0 | -0.040441 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.003509 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.2983 | 370 | -0.040461 | -14.9705
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.49126 | 0 | -0.040461 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.49477 | 0 | -0.040461 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.0843 | 0 | -0.040461 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.50179 | 0 | -0.040461 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.5053 | 0 | -0.040461 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.0878 | 0 | -0.040461 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.003825 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.040777 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.003994 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.67898 | 170 | -0.040946 | -6.9608
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.003994 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.0769 | 520 | -0.040946 | -21.2919
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.004316 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.17264 | 0 | -0.041268 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.004316 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.17264 | 0 | -0.041268 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.004651 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.004651 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.004651 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.004719 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.96268 | 204 | -0.041671 | -8.5009
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.004719 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.94852 | 201 | -0.041671 | -8.3759
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.004719 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.142 | 242 | -0.041671 | -10.0844
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.005928 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.35568 | 60 | -0.04288 | -2.5728
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.005928 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.37346 | 63 | -0.04288 | -2.7014
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.007026 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.5129 | 73 | -0.043978 | -3.2104
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.007026 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.83609 | 119 | -0.043978 | -5.2334
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.007026 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.4403 | 205 | -0.043978 | -9.0155
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.007026 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.71665 | 102 | -0.043978 | -4.4857
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.007026 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.6745 | 96 | -0.043978 | -4.2219
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.011125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.20025 | 18 | -0.048077 | -0.86538
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.011125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.20025 | 18 | -0.048077 | -0.86538
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.011125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.42275 | 38 | -0.048077 | -1.8269
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.015651 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.8781 | 120 | -0.052603 | -6.3123
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.019569 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.7357 | 242 | -0.056521 | -13.6781
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.021935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3173 | 288 | -0.058887 | -16.9594
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.021935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2244 | 147 | -0.058887 | -8.6564
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.021935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2244 | 147 | -0.058887 | -8.6564
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.023127 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27752 | 0 | -0.060079 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.023127 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27752 | 0 | -0.060079 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.025743 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.8961 | 112.5 | -0.062695 | -7.0532
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.94982 | 20 | -0.084443 | -1.6889
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.94982 | 20 | -0.084443 | -1.6889
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.94982 | 20 | -0.084443 | -1.6889
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.80735 | 17 | -0.084443 | -1.4355

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1426 FISHRDSS - 1427 FISHERRD C: 1422 BOWMAN5 - 1425 FISHRDSS | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.94982 | 20 | -0.084443 | -1.6889 | 20 | 1.6889
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.94982 | 20 | -0.084443 | -1.6889 | 40 | 3.3777
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.94982 | 20 | -0.084443 | -1.6889 | 60 | 5.0666
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.047491 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.80735 | 17 | -0.084443 | -1.4355 | 77 | 6.5021 | Weighted Shift Factors
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.025743 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.8961 | 0 | -0.062695 | 0 | 77 | 6.5021 | North | -0.003208
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.023127 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27752 | 0 | -0.060079 | 0 | 77 | 6.5021 | West | 0.036952
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.023127 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27752 | 0 | -0.060079 | 0 | 77 | 6.5021 |  | -0.04016
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.021935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3173 | 288 | -0.058887 | -16.9594 | 365 | 23.4615
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.021935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2244 | 147 | -0.058887 | -8.6564 | 512 | 32.1179 | Line Rating | 287
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.021935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2244 | 147 | -0.058887 | -8.6564 |  |  | Conc Gen | 512
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.019569 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.7357 | 242 | -0.056521 | -13.6781 |  |  | Weighted Imp. | 32.1179
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.015651 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.8781 | 0 | -0.052603 | 0 |  |  | PTDF | 0.06273
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.011125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.20025 | 18 | -0.048077 | -0.86538
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.011125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.20025 | 18 | -0.048077 | -0.86538 |  |  | Concentration | -1.562
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.011125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.42275 | 38 | -0.048077 | -1.8269
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.007026 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.5129 | 73 | -0.043978 | -3.2104
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.007026 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.83609 | 119 | -0.043978 | -5.2334
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.007026 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.4403 | 205 | -0.043978 | -9.0155
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.007026 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.71665 | 102 | -0.043978 | -4.4857
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.007026 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.6745 | 96 | -0.043978 | -4.2219
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.005928 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.35568 | 60 | -0.04288 | -2.5728
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.005928 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.37346 | 63 | -0.04288 | -2.7014
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.004719 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.96268 | 204 | -0.041671 | -8.5009
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.004719 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.94852 | 201 | -0.041671 | -8.3759
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.004719 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.142 | 242 | -0.041671 | -10.0844
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.004651 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.004651 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.004651 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.004316 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.17264 | 0 | -0.041268 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.004316 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.17264 | 0 | -0.041268 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.003994 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.67898 | 170 | -0.040946 | -6.9608
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.003994 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.0769 | 520 | -0.040946 | -21.2919
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.003825 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.040777 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.003509 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.2983 | 370 | -0.040461 | -14.9705
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.49126 | 0 | -0.040461 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.49477 | 0 | -0.040461 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.0843 | 0 | -0.040461 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.50179 | 0 | -0.040461 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.5053 | 0 | -0.040461 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.003509 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.0878 | 0 | -0.040461 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.003489 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.26167 | 0 | -0.040441 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.003489 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.27772 | 0 | -0.040441 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.003489 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.30843 | 0 | -0.040441 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.55312 | 160 | -0.040409 | -6.4654
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.53929 | 156 | -0.040409 | -6.3038
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.67757 | 196 | -0.040409 | -7.9201
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.53929 | 156 | -0.040409 | -6.3038
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.54275 | 157 | -0.040409 | -6.3442
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.003457 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.68449 | 198 | -0.040409 | -8.001
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.003377 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.040329 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.003308 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.8459 | 0 | -0.04026 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.003308 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9153 | 0 | -0.04026 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.003308 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.6729 | 0 | -0.04026 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.003125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.24688 | 79 | -0.040077 | -3.1661
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.003125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.33125 | 106 | -0.040077 | -4.2482
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.003125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.45625 | 146 | -0.040077 | -5.8512
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.003125 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.2375 | 76 | -0.040077 | -3.0458
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.003102 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.06204 | 20 | -0.040054 | -0.80108
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.003102 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.07755 | 25 | -0.040054 | -1.0013
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.003102 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.12718 | 41 | -0.040054 | -1.6422
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.003092 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.12368 | 40 | -0.040044 | -1.6018
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47189 | 161 | -0.039883 | -6.4211
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.48068 | 164 | -0.039883 | -6.5408
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.48068 | 164 | -0.039883 | -6.5408
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.2134 | 414 | -0.039883 | -16.5115
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47482 | 162 | -0.039883 | -6.461
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47189 | 161 | -0.039883 | -6.4211
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.47775 | 163 | -0.039883 | -6.5009
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.002931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.1988 | 409 | -0.039883 | -16.3121
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.002928 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1361 | 388 | -0.03988 | -15.4734
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.002928 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.5079 | 515 | -0.03988 | -20.5382
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.002856 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039808 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.002856 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039808 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.002645 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.31211 | 118 | -0.039597 | -4.6724
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.002645 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.30417 | 115 | -0.039597 | -4.5536
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.002645 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.4706 | 556 | -0.039597 | -22.0159
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.002643 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1497 | 435 | -0.039595 | -17.2238
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.002575 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.0171 | 395 | -0.039527 | -15.6131
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.002575 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1201 | 435 | -0.039527 | -17.1942
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.002564 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.0127 | 0 | -0.039516 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.002564 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.0384 | 0 | -0.039516 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.002564 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9999 | 0 | -0.039516 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.37207 | 0 | -0.039466 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.32682 | 0 | -0.039466 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.36453 | 0 | -0.039466 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.002514 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.0031 | 0 | -0.039466 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.002473 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.039425 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.002468 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.44918 | 182 | -0.03942 | -7.1744
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.002468 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.1945 | 484 | -0.03942 | -19.0792
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.002467 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.12335 | 0 | -0.039419 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.002319 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.51946 | 224 | -0.039271 | -8.7967
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.002275 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.4459 | 196 | -0.039227 | -7.6885
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.002275 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.25252 | 111 | -0.039227 | -4.3542
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.002095 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.45336 | 216.4 | -0.039047 | -8.4498
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.002095 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.45273 | 216.1 | -0.039047 | -8.438
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.002066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.313 | 151.5 | -0.039018 | -5.9112
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.002066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.31465 | 152.3 | -0.039018 | -5.9424
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.002066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.36672 | 177.5 | -0.039018 | -6.9257
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.002042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.30773 | 150.7 | -0.038994 | -5.8764
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.002042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.30834 | 151 | -0.038994 | -5.8881
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.002042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.36225 | 177.4 | -0.038994 | -6.9175
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.001974 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.214 | 0 | -0.038926 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.001974 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.1587 | 0 | -0.038926 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.41395 | 224 | -0.0388 | -8.6912
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.41765 | 226 | -0.0388 | -8.7688
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.39178 | 212 | -0.0388 | -8.2256
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.001848 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.38993 | 211 | -0.0388 | -8.1868
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.001761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.29585 | 168 | -0.038713 | -6.5038
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.001761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.15849 | 90 | -0.038713 | -3.4842
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.12026 | 70 | -0.03867 | -2.7069
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11854 | 69 | -0.03867 | -2.6682
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11854 | 69 | -0.03867 | -2.6682
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.001718 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11682 | 68 | -0.03867 | -2.6296
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.001689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3968 | 0 | -0.038641 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.001689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3833 | 0 | -0.038641 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3483 | 0 | -0.038529 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3483 | 0 | -0.038529 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.24018 | 0 | -0.038529 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.001577 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.24128 | 0 | -0.038529 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.001549 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.023235 | 0 | -0.038501 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.001549 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.023235 | 0 | -0.038501 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.001302 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.60283 | 0 | -0.038254 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.001301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.022117 | 17 | -0.038253 | -0.6503
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.001301 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.001299 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.041568 | 0 | -0.038251 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.001293 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.062064 | 48 | -0.038245 | -1.8358
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.001293 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.059478 | 46 | -0.038245 | -1.7593
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.001293 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.13576 | 105 | -0.038245 | -4.0157
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.001225 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038177 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.001225 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.96408 | 787 | -0.038177 | -30.0452
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.18782 | 0 | -0.03817 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.19001 | 0 | -0.03817 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.19001 | 0 | -0.03817 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.001218 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.46284 | 0 | -0.03817 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.001205 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.30728 | 255 | -0.038157 | -9.73
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.001205 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.17955 | 149 | -0.038157 | -5.6854
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.001205 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.18437 | 153 | -0.038157 | -5.838
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.001191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.17865 | 150 | -0.038143 | -5.7214
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.001191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.09528 | 80 | -0.038143 | -3.0514
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.001147 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038099 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.001147 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038099 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.00103 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.037982 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.000319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.069319 | 217.3 | -0.037271 | -8.099
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.000319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.065395 | 205 | -0.037271 | -7.6405
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.000319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.086896 | 272.4 | -0.037271 | -10.1526
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -5.3e-05 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.061321 | 0 | -0.037005 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -5.3e-05 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.061374 | 0 | -0.037005 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.036952 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.036952 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0893 | 0 | -0.036059 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.001407 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.08442 | 0 | -0.035545 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.002418 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.88499 | 366 | -0.034534 | -12.6394
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.012995 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.023957 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.026734 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4111 | 0 | -0.010218 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.030836 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6254 | 0 | -0.0061159 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.033614 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0033379 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.034412 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1212 | 0 | -0.0025399 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.034511 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8044 | 0 | -0.0024409 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3098 | 0 | -0.0019769 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4243 | 0 | -0.0019769 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7088 | 0 | -0.0019769 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.034975 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8901 | 0 | -0.0019769 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.036931 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1022 | 0 | -2.0912e-05 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.03702 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.832 | 0 | 6.8088e-05 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.03714 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9712 | 0 | 0.00018809 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.037759 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6639 | 0 | 0.00080709 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.037759 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6639 | 0 | 0.00080709 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.037775 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.022 | 0 | 0.00082309 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037778 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0222 | 0 | 0.00082609 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.037805 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8354 | 0 | 0.00085309 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037805 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0244 | 0 | 0.00085309 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.037805 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5122 | 0 | 0.00085309 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037927 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0342 | 0 | 0.00097509 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037927 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0342 | 0 | 0.00097509 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.0384 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.18432 | 0 | 0.0014481 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3968 | 0 | 0.0021311 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8429 | 0 | 0.0021311 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2694 | 0 | 0.0021311 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.039083 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3833 | 0 | 0.0021311 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.039207 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9009 | 0 | 0.0022551 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.039207 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9009 | 0 | 0.0022551 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.039207 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8811 | 0 | 0.0022551 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14048 | 0 | 0.002396 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12667 | 0 | 0.002396 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12505 | 0 | 0.002396 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000812 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12505 | 0 | 0.002396 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.000812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13154 | 0 | 0.002396 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.043064 | 56 | 0.002439 | 0.13658
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.045371 | 59 | 0.002439 | 0.1439
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.043064 | 56 | 0.002439 | 0.13658
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.043064 | 56 | 0.002439 | 0.13658
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.045371 | 59 | 0.002439 | 0.1439
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.000769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.043064 | 56 | 0.002439 | 0.13658
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.000764 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.30407 | 398 | 0.002444 | 0.9727
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12373 | 0 | 0.002448 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12266 | 0 | 0.002448 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12076 | 0 | 0.002448 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.00076 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20459 | 0 | 0.002448 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.000753 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.12952 | 172 | 0.002455 | 0.42226
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.000753 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.12952 | 172 | 0.002455 | 0.42226
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.000753 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.12952 | 172 | 0.002455 | 0.42226
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.000752 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11806 | 0 | 0.002456 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04875 | 0 | 0.002458 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0495 | 0 | 0.002458 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0525 | 0 | 0.002458 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04725 | 0 | 0.002458 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0465 | 0 | 0.002458 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078 | 0 | 0.002458 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.00075 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04425 | 0 | 0.002458 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.00075 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.009 | 0 | 0.002458 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.00075 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.55725 | 743 | 0.002458 | 1.8263
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.000749 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.003745 | 0 | 0.002459 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.000749 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015729 | 0 | 0.002459 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.000747 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.008964 | 12 | 0.002461 | 0.029532
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.025228 | 0 | 0.002466 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.025747 | 0 | 0.002466 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024263 | 0 | 0.002466 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.034058 | 0 | 0.002466 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.013133 | 0 | 0.002466 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015137 | 0 | 0.002466 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.014766 | 0 | 0.002466 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02597 | 0 | 0.002466 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.013356 | 0 | 0.002466 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.063367 | 0 | 0.002466 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.000742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10982 | 0 | 0.002466 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.000739 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.54317 | 735 | 0.002469 | 1.8147
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.076648 | 104 | 0.002471 | 0.25698
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.076648 | 104 | 0.002471 | 0.25698
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039798 | 54 | 0.002471 | 0.13343
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039061 | 53 | 0.002471 | 0.13096
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039798 | 54 | 0.002471 | 0.13343
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.042009 | 57 | 0.002471 | 0.14085
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039798 | 54 | 0.002471 | 0.13343
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.039798 | 54 | 0.002471 | 0.13343
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.042746 | 58 | 0.002471 | 0.14332
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.000737 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.042746 | 58 | 0.002471 | 0.14332
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.000726 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1256 | 0 | 0.002482 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.000726 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.09801 | 0 | 0.002482 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.000724 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.098464 | 0 | 0.002484 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.030408 | 42 | 0.002484 | 0.10433
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.030408 | 42 | 0.002484 | 0.10433
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.027512 | 38 | 0.002484 | 0.094391
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.000724 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.027512 | 38 | 0.002484 | 0.094391
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.050907 | 0 | 0.002491 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.051624 | 0 | 0.002491 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027963 | 0 | 0.002491 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.000717 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02151 | 0 | 0.002491 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.000713 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.15187 | 213 | 0.002495 | 0.53143
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.011551 | 0 | 0.002495 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.045632 | 0 | 0.002495 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.045062 | 0 | 0.002495 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.058894 | 0 | 0.002495 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.000713 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052477 | 0 | 0.002495 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.000713 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.16256 | 228 | 0.002495 | 0.56885
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.000713 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12834 | 0 | 0.002495 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.000713 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11308 | 0 | 0.002495 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.000713 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11194 | 0 | 0.002495 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.000712 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.12033 | 169 | 0.002496 | 0.42182
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.000712 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.11748 | 165 | 0.002496 | 0.41184
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.000712 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10609 | 0 | 0.002496 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.000712 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.046351 | 0 | 0.002496 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.000711 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.008532 | 12 | 0.002497 | 0.029964
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.000711 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.002497 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.000709 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024815 | 0 | 0.002499 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11506 | 0 | 0.002503 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11076 | 0 | 0.002503 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11104 | 0 | 0.002503 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.11069 | 0 | 0.002503 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.000705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.18965 | 0 | 0.002503 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.000703 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.054834 | 0 | 0.002505 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.000703 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.05624 | 0 | 0.002505 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.032292 | 46 | 0.002506 | 0.11527
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.032292 | 46 | 0.002506 | 0.11527
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.032292 | 46 | 0.002506 | 0.11527
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.03861 | 55 | 0.002506 | 0.13783
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.03861 | 55 | 0.002506 | 0.13783
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.000702 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.037908 | 54 | 0.002506 | 0.13532
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044915 | 0 | 0.002517 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.04146 | 0 | 0.002517 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044915 | 0 | 0.002517 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.000691 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044915 | 0 | 0.002517 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.062244 | 0 | 0.002524 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059918 | 0 | 0.002524 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059508 | 0 | 0.002524 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.037278 | 0 | 0.002524 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.000684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0083448 | 0 | 0.002524 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.000668 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00254 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.000656 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.0328 | 50 | 0.002552 | 0.1276
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.063791 | 0 | 0.002572 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.059084 | 0 | 0.002572 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.065317 | 0 | 0.002572 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.064872 | 0 | 0.002572 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.020352 | 0 | 0.002572 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01908 | 0 | 0.002572 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.045029 | 0 | 0.002572 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.042421 | 0 | 0.002572 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.033708 | 0 | 0.002572 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.097435 | 0 | 0.002572 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.097626 | 0 | 0.002572 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.096863 | 0 | 0.002572 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.061056 | 0 | 0.002572 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.000636 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.15518 | 0 | 0.002572 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.000636 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02544 | 0 | 0.002572 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6091 | 66 | 0.0025801 | 0.17029
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.5696 | 65 | 0.0025801 | 0.16771
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6486 | 67 | 0.0025801 | 0.17287
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6486 | 67 | 0.0025801 | 0.17287
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.039532 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6486 | 67 | 0.0025801 | 0.17287
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.039532 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0025801 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.039532 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0025801 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.000599 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.096439 | 161 | 0.002609 | 0.42004
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.000599 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.099434 | 166 | 0.002609 | 0.43309
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.000599 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.14855 | 248 | 0.002609 | 0.64702
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.000599 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.32705 | 546 | 0.002609 | 1.4245
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.000599 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -0.38516 | 0 | 0.002609 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.000599 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.007787 | 13 | 0.002609 | 0.033917
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.000587 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.019371 | 0 | 0.002621 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.000583 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.095029 | 0 | 0.002625 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.000583 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.095029 | 0 | 0.002625 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.000583 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14283 | 0 | 0.002625 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.000582 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.37888 | 0 | 0.002626 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.000582 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.32825 | 0 | 0.002626 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.000582 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.3492 | 0 | 0.002626 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.000574 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.026461 | 0 | 0.002634 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.039613 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3865 | 0 | 0.0026611 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.039613 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1884 | 0 | 0.0026611 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.054168 | 0 | 0.00272 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.054168 | 0 | 0.00272 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.058072 | 0 | 0.00272 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.000488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.053436 | 0 | 0.00272 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.261 | 208.2 | 0.0027261 | 0.56757
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.6382 | 142.1 | 0.0027261 | 0.38738
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2534 | 132.4 | 0.0027261 | 0.36093
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.3962 | 136 | 0.0027261 | 0.37075
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8327 | 147 | 0.0027261 | 0.40073
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.039678 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.3324 | 210 | 0.0027261 | 0.57248
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7776 | 70 | 0.0027281 | 0.19097
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7776 | 70 | 0.0027281 | 0.19097
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6823 | 92.8 | 0.0027281 | 0.25317
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1744 | 80 | 0.0027281 | 0.21825
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1744 | 80 | 0.0027281 | 0.21825
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.03968 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5632 | 115 | 0.0027281 | 0.31373
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.000462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.032802 | 0 | 0.002746 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.000462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.00462 | 0 | 0.002746 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02666 | 0 | 0.002778 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.030702 | 0 | 0.002778 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01935 | 0 | 0.002778 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04343 | 0 | 0.002778 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03698 | 0 | 0.002778 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03784 | 0 | 0.002778 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0215 | 0 | 0.002778 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.00774 | 0 | 0.002778 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04042 | 0 | 0.002778 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0301 | 0 | 0.002778 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02709 | 0 | 0.002778 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03096 | 0 | 0.002778 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027864 | 0 | 0.002778 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04343 | 0 | 0.002778 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04171 | 0 | 0.002778 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04429 | 0 | 0.002778 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03268 | 0 | 0.002778 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0344 | 0 | 0.002778 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0344 | 0 | 0.002778 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.00043 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07353 | 0 | 0.002778 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.039802 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7861 | 0 | 0.0028501 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.039802 | west | 8 | N | N | Nwest | Nwest | 1 | 2.9215 | 0 | 0.0028501 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.039802 | west | 8 | N | N | Nwest | Nwest | 1 | 2.8021 | 0 | 0.0028501 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9712 | 0 | 0.0028561 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7578 | 0 | 0.0028561 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9616 | 0 | 0.0028561 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.039808 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8526 | 0 | 0.0028561 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.03981 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9317 | 0 | 0.0028581 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.0003 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.0198 | 66 | 0.002908 | 0.19193
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.000293 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.16672 | 0 | 0.002915 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.000293 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.17023 | 0 | 0.002915 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.021204 | 76 | 0.002929 | 0.2226
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.021204 | 76 | 0.002929 | 0.2226
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.029295 | 105 | 0.002929 | 0.30754
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.020646 | 74 | 0.002929 | 0.21674
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.020646 | 74 | 0.002929 | 0.21674
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.000279 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.028458 | 102 | 0.002929 | 0.29876
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.000256 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.34125 | 0 | 0.002952 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.000256 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.33997 | 0 | 0.002952 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003208 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003208 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003208 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 5.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.03212 | 0 | 0.003263 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 5.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.032725 | 0 | 0.003263 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 5.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.023815 | 0 | 0.003263 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 6.4e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.010112 | 158 | 0.003272 | 0.51697
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 6.4e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.01024 | 160 | 0.003272 | 0.52352
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 6.4e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0112 | 175 | 0.003272 | 0.57259
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.04023 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0431 | 0 | 0.0032781 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00445 | 50 | 0.003297 | 0.16485
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00445 | 50 | 0.003297 | 0.16485
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00445 | 50 | 0.003297 | 0.16485
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00445 | 50 | 0.003297 | 0.16485
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.040276 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.336 | 0 | 0.0033241 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.000141 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.021503 | 152.5 | 0.003349 | 0.51072
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.000141 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.02108 | 149.5 | 0.003349 | 0.50067
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.000141 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.032797 | 232.6 | 0.003349 | 0.77897
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.000146 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.019272 | 132 | 0.003354 | 0.44272
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.000146 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.019564 | 134 | 0.003354 | 0.44943
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.000146 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.047158 | 323 | 0.003354 | 1.0833
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.040367 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6466 | 0 | 0.0034151 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.009534 | 42 | 0.003435 | 0.14427
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.009988 | 44 | 0.003435 | 0.15114
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.009988 | 44 | 0.003435 | 0.15114
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.000227 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.010669 | 47 | 0.003435 | 0.16144
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.000259 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.08029 | 310 | 0.003467 | 1.0748
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.000259 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.10697 | 413 | 0.003467 | 1.4319
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020461 | 0 | 0.003467 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020979 | 0 | 0.003467 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020461 | 0 | 0.003467 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.02072 | 0 | 0.003467 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020306 | 0 | 0.003467 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.006475 | 0 | 0.003467 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.011914 | 0 | 0.003467 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.007252 | 0 | 0.003467 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.011292 | 0 | 0.003467 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.000259 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.019166 | 0 | 0.003467 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.040423 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.26679 | 0 | 0.0034711 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.040423 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3865 | 0 | 0.0034711 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.013181 | 49 | 0.003477 | 0.17037
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012374 | 46 | 0.003477 | 0.15994
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012374 | 46 | 0.003477 | 0.15994
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012643 | 47 | 0.003477 | 0.16342
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.000269 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.041426 | 154 | 0.003477 | 0.53545
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.000269 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.039812 | 148 | 0.003477 | 0.51459
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012912 | 48 | 0.003477 | 0.16689
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.000269 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012912 | 48 | 0.003477 | 0.16689
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.000274 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013152 | 0 | 0.003482 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.000298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002384 | 0 | 0.003506 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.000298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002384 | 0 | 0.003506 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00924 | 0 | 0.003538 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00231 | 0 | 0.003538 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01287 | 0 | 0.003538 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00495 | 0 | 0.003538 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00231 | 0 | 0.003538 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00495 | 0 | 0.003538 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01287 | 0 | 0.003538 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.00033 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01287 | 0 | 0.003538 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.000341 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.002728 | 0 | 0.003549 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00519 | 0 | 0.003554 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.007958 | 0 | 0.003554 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.000367 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.026791 | 0 | 0.003575 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.000382 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.055008 | 144 | 0.00359 | 0.51696
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.000382 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.071816 | 188 | 0.00359 | 0.67491
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.018794 | 47.7 | 0.003602 | 0.17181
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.014696 | 37.3 | 0.003602 | 0.13435
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.018124 | 46 | 0.003602 | 0.16569
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.000394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.018912 | 48 | 0.003602 | 0.17289
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000416 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.004992 | 0 | 0.003624 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.00042 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001008 | 0 | 0.003628 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.00042 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001008 | 0 | 0.003628 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.000422 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.009284 | 22 | 0.00363 | 0.079859
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.000422 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.004642 | 11 | 0.00363 | 0.03993
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.000422 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.004642 | 11 | 0.00363 | 0.03993
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10031 | 223.9 | 0.003656 | 0.81857
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1008 | 225 | 0.003656 | 0.82259
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10062 | 224.6 | 0.003656 | 0.82113
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.000448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10156 | 226.7 | 0.003656 | 0.82881
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.07663 | 0 | 0.003693 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.074205 | 0 | 0.003693 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.0485 | 0 | 0.003693 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.070325 | 0 | 0.003693 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.071295 | 0 | 0.003693 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.000485 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.061595 | 0 | 0.003693 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.000485 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00582 | 0 | 0.003693 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.069012 | 142 | 0.003694 | 0.52454
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.07047 | 145 | 0.003694 | 0.53563
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.073386 | 151 | 0.003694 | 0.55779
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.000486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14094 | 290 | 0.003694 | 1.0713
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.000488 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0011712 | 0 | 0.003696 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.000488 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0011712 | 0 | 0.003696 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.000488 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0013664 | 0 | 0.003696 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 0 | 0.003706 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 0 | 0.003706 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 0 | 0.003706 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007968 | 0 | 0.003706 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 0 | 0.003706 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 0 | 0.003706 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01245 | 0 | 0.003706 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.000498 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.00747 | 0 | 0.003706 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.000514 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.32331 | 0 | 0.003722 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.000515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17304 | 336 | 0.003723 | 1.2509
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.000515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0927 | 180 | 0.003723 | 0.67013
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.000516 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.076523 | 0 | 0.003724 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.000516 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.076678 | 0 | 0.003724 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.000516 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.078948 | 0 | 0.003724 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.000516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.09288 | 180 | 0.003724 | 0.67031
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.000521 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.17401 | 334 | 0.003729 | 1.2455
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.000521 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.17714 | 340 | 0.003729 | 1.2679
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.000521 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.09378 | 180 | 0.003729 | 0.67121
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.000521 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.09378 | 180 | 0.003729 | 0.67121
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.000525 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013125 | 0 | 0.003733 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.000525 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013125 | 0 | 0.003733 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.077175 | 147 | 0.003733 | 0.54875
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.07245 | 138 | 0.003733 | 0.51515
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0735 | 140 | 0.003733 | 0.52262
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.077175 | 147 | 0.003733 | 0.54875
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.09555 | 182 | 0.003733 | 0.6794
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.000525 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10395 | 198 | 0.003733 | 0.73913
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.000525 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01995 | 0 | 0.003733 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.000529 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.020102 | 0 | 0.003737 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.000544 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.015776 | 0 | 0.003752 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.000546 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.003276 | 0 | 0.003754 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.000552 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002208 | 0 | 0.00376 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.052546 | 0 | 0.003767 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.022919 | 0 | 0.003767 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.021242 | 0 | 0.003767 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.010621 | 0 | 0.003767 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.052546 | 0 | 0.003767 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.020124 | 0 | 0.003767 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.024037 | 0 | 0.003767 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.012298 | 0 | 0.003767 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.082732 | 0 | 0.003767 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02795 | 0 | 0.003767 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.030745 | 0 | 0.003767 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.000559 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02795 | 0 | 0.003767 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.000571 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.021698 | 38 | 0.003779 | 0.1436
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.000571 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.01102 | 19.3 | 0.003779 | 0.072934
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.000571 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.008565 | 15 | 0.003779 | 0.056685
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.000571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.026837 | 47 | 0.003779 | 0.17761
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.000571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003779 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.000601 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.086544 | 144 | 0.003809 | 0.54849
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.000601 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.086544 | 144 | 0.003809 | 0.54849
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.000601 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10277 | 171 | 0.003809 | 0.65133
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.000602 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12461 | 207 | 0.00381 | 0.78866
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.000602 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13045 | 216.7 | 0.00381 | 0.82562
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.000602 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14568 | 242 | 0.00381 | 0.92201
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.000636 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.34726 | 0 | 0.003844 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.000636 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.477 | 0 | 0.003844 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.000652 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.095518 | 146.5 | 0.00386 | 0.56549
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.000652 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.096431 | 147.9 | 0.00386 | 0.57089
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.000652 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1128 | 173 | 0.00386 | 0.66777
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10214 | 155 | 0.003867 | 0.59938
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.000659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.11203 | 170 | 0.003867 | 0.65739
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10214 | 155 | 0.003867 | 0.59938
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.040827 | west | 8 | N | N | Nwest | Nwest | 1 | 1.0533 | 0 | 0.0038751 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.000674 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003882 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.000674 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003882 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.000674 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.003882 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.00069 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003898 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000712 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02492 | 0 | 0.00392 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000712 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.024208 | 0 | 0.00392 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000712 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02492 | 0 | 0.00392 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.000717 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003925 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.000726 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.30782 | 0 | 0.003934 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.000726 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.30855 | 0 | 0.003934 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.30406 | 412 | 0.003946 | 1.6257
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.2952 | 400 | 0.003946 | 1.5784
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.15424 | 209 | 0.003946 | 0.82471
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.000738 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.15941 | 216 | 0.003946 | 0.85233
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.033948 | 46 | 0.003946 | 0.18151
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.034686 | 47 | 0.003946 | 0.18546
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.033948 | 46 | 0.003946 | 0.18151
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.000738 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.033948 | 46 | 0.003946 | 0.18151
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.000743 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.29423 | 0 | 0.003951 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.000762 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.31013 | 407 | 0.00397 | 1.6158
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7009 | 66 | 0.0039711 | 0.26209
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.8237 | 69 | 0.0039711 | 0.27401
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.8237 | 69 | 0.0039711 | 0.27401
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7418 | 67 | 0.0039711 | 0.26606
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7418 | 67 | 0.0039711 | 0.26606
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.040923 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.66 | 65 | 0.0039711 | 0.25812
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000831 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.048198 | 58 | 0.004039 | 0.23426
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000831 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.073959 | 89 | 0.004039 | 0.35947
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.036564 | 44 | 0.004039 | 0.17771
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.036564 | 44 | 0.004039 | 0.17771
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035733 | 43 | 0.004039 | 0.17368
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000831 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.037395 | 45 | 0.004039 | 0.18175
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1018 | 0 | 0.004101 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.19825 | 0 | 0.004101 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.16431 | 0 | 0.004101 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.20003 | 0 | 0.004101 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10269 | 0 | 0.004101 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.041071 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9285 | 0 | 0.0041191 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000957 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011484 | 0 | 0.004165 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000957 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010527 | 0 | 0.004165 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000957 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011484 | 0 | 0.004165 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.041224 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9469 | 0 | 0.0042721 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.001248 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004456 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.001583 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1583 | 100 | 0.004791 | 0.4791
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.001583 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1583 | 100 | 0.004791 | 0.4791
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.001583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004791 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.041786 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4018 | 0 | 0.0048341 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.001631 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.029358 | 0 | 0.004839 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.001631 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.029358 | 0 | 0.004839 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.041867 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5361 | 0 | 0.0049151 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.041867 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5361 | 0 | 0.0049151 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.001935 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.05418 | 0 | 0.005143 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.001935 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.056115 | 0 | 0.005143 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.002037 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.85961 | 422 | 0.005245 | 2.2134
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.002104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037872 | 0 | 0.005312 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.002104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037872 | 0 | 0.005312 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.002104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03156 | 0 | 0.005312 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.002169 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.052056 | 24 | 0.005377 | 0.12905
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.002169 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.052056 | 24 | 0.005377 | 0.12905
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.002169 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.049887 | 23 | 0.005377 | 0.12367
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.042446 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6741 | 0 | 0.0054941 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002464 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.020698 | 8.4 | 0.005672 | 0.047645
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.002576 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.035291 | 0 | 0.005784 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.042962 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0576 | 0 | 0.0060101 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.042962 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1554 | 0 | 0.0060101 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.043039 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2609 | 0 | 0.0060871 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.043039 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6254 | 0 | 0.0060871 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.043039 | west | 7 | N | N | Nwest | Nwest | 1 | 1.076 | 0 | 0.0060871 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.043039 | west | 7 | N | N | Nwest | Nwest | 1 | 1.9669 | 0 | 0.0060871 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.043039 | west | 7 | N | N | Nwest | Nwest | 1 | 1.9669 | 0 | 0.0060871 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.044407 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7302 | 0 | 0.0074551 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.045449 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8174 | 0 | 0.0084971 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.045449 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5903 | 0 | 0.0084971 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.046247 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8389 | 0 | 0.0092951 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.008085 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011293 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8207 | 0 | 0.0116 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2193 | 0 | 0.0116 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5545 | 0 | 0.0116 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.7777 | 0 | 0.0116 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.098 | 0 | 0.0116 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.048552 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9084 | 0 | 0.0116 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.008804 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.052824 | 0 | 0.012012 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.049112 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8934 | 0 | 0.01216 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.049112 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.4431 | 0 | 0.01216 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.049112 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3589 | 0 | 0.01216 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.050411 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5617 | 0 | 0.013459 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.011896 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.39257 | 0 | 0.015104 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.011896 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2974 | 0 | 0.015104 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.011896 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015104 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.074485 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4691 | 0 | 0.037533 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.25405 | west | 4 | Y | N | Ywest | Nwest | 1 | 165.0582 | 0 | 0.2171 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
20
25
30
35
40
45
50
55
60
65
70
75
80
85
90
95
100
105
110
| 115 | 0
| Max | 287
| Min | 287
| Avg | 287