## test results
CRE test for: |  | COMCHESS - COMANCHE 138 kV 1441 -1650 | [5 empty] | PASS
Line Rating: |  | 215.35
Direction |  | North | → | West |  | N-W
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | COMCHESS - COMANCHE 138 kV 1441 -1650
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.0078945
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.0020663
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.052161
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.0020519
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | COMCHESS - COMANCHE 138 kV 1441 -1650
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.0088487
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.0024441
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.052595
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0021193
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | COMCHESS - COMANCHE 138 kV 1441 -1650
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.010339
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.06049
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.0057752
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.050529
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.0041182
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.05428
PTDF tests
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.06049 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.06049 | -0.010339
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.025212
[6 empty] | Concentration |  | -0.41679 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.11455
[6 empty] | Concentration |  | -1.8937 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 21.5211
| Percent of line rating => | [6 empty] | 9.994% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -13.4695
[7 empty] | B1(N-S) | -0.09913 | 0.040127 | 0.13926 | -0.09913
[7 empty] | B2 (N-W) | 0 | 0.81477 | 0.81477 | 0
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.058815 | 0.018975 | 0.077789 | -0.058815
[7 empty] | B4 (S-W) | 0.095169 | 0.77577 | 0.6806 | 0.095169
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.035446 | -0.020024 | -0.05547 | 0.035446
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.061804 | -0.79294 | -0.73113 | -0.061804
[7 empty] | test | 0 | 0.81477 | 0.81477 | 0
[7 empty] | B1 | -12.17%
Deployment Error Percent | [6 empty] | B2 | 0%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -7.219%
[7 empty] | B4 | 11.68%
[7 empty] | B5 | 4.35%
[7 empty] | B6 | -7.585%
[7 empty] | Max Abs Error | 12.17% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-W
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:COMCHESS - COMANCHE 138 kV 1441 -1650 C: COMCHESS - COMCHPKW 345kV 1440 - 1900 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:COMCHESS - COMANCHE 138 kV 1441 -1650 C: COMCHESS - COMCHPKW 345kV 1440 - 1900
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.015749 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -4.016
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.015749 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -2.3466
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.023857 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.35785
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.023857 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.35785
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.015749 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -2.4096
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.022159 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -3.3239
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.022159 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -1.7727
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.061956 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -4.5228
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.061956 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -7.3728
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.061956 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -12.701
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.061956 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -6.3195
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.061956 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -5.9478
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.016726 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.20071
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.016726 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.20071
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.018189 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -3.0558
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.018189 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -1.637
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.029876 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.53777
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.029876 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.53777
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.029876 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -1.1353
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.016092 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -4.6345
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.016092 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -2.3655
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.016092 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -2.3655
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.006928 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -0.7794
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.005732 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.22928
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.005683 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -0.44896
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.005683 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -0.6024
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.005683 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -0.82972
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.005683 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -0.43191
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.004322 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -0.25932
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.004322 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -0.27229
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.005707 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.11414
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.005707 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.14267
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.005707 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.23399
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.004245 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -1.9654
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 3.6126
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 3.5578
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.6673
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.6673
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.6673
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.054736 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 6.2399
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.054736 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 28.189
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 3.4865
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 3.645
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 3.645
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 3.5393
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 3.5393
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 3.4337
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.053758 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 3.7631
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.053758 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 3.9458
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.053758 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 3.7846
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 8.0484
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 11.8043
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.051067 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 5.0556
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.051067 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 3.1151
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.051134 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 7.2099
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.051067 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 1.2767
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.051067 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 2.3338
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.051067 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 2.3338
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.051134 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 6.1361
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.054935 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 1.4173
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.054124 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 5.4395
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.053461 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 6.4153
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.05389 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 3.1256
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.053741 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 11.5113
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.04978 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 7.467
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.05879 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.38801
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.05879 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 2.0165
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.04978 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 5.0278
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.053308 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 6.397
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.014701 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 5.3806
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.003939 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 0.95324
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.036011 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 14.4044
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.035976 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 8.4903
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.03087 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 5.0935
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.004834 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 0.98614
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.004834 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 0.97163
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.004834 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 1.1698
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.22466
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.22466
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.22466
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.19096
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.017709 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -2.1251
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.10967 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -6.5802
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.005544 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -0.4158
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.005544 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -0.4413
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.005544 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -0.49009
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -0.88304
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.86096
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -1.0817
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.86096
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -0.86648
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -1.0928
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.005545 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -0.94265
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.005545 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -2.8834
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.005501 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -2.0354
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.005538 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -3.0902
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.005538 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -3.2065
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.005538 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -4.4747
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.005829 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -0.65285
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.005829 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -0.5829
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.005829 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -2.2034
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.007938 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -1.7249
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.007938 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -1.6273
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.007938 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -2.1623
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.009648 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -7.429
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -2.085
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -2.0552
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -2.0552
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -2.0254
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.008154 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -9.4342
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.008154 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -9.4423
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -1.699
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -1.7142
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.006621 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -1.4328
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.006621 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -1.4308
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -1.608
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -1.6004
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.006362 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -2.513
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.006435 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -2.7992
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.006362 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -2.7675
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.005245 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -0.72381
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.006255 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -0.73809
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.006255 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -0.71932
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.006255 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -3.4778
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.00586 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -2.2737
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.00586 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -3.0179
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.005989 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -4.7014
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.005989 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -4.7613
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.005989 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -4.6714
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.006025 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -1.0965
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.006025 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -2.9161
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.007634 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -1.71
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.006016 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -0.3008
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.006016 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.25267
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.006013 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -3.698
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.006013 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -3.5296
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.007945 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -4.2665
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.007945 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -6.2527
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.008107 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -0.60803
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.008107 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -1.7998
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.001823 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -1.0373
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.002621 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.54779
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.002621 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.56614
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.002698 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 1.0981
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.12057
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.12319
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.12057
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.12057
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.002611 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 1.1071
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.002611 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 1.1097
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002845 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.16501
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002845 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.25321
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.12518
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.12518
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.12233
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.12802
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.002629 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 1.0831
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.002629 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 1.0516
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.002352 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 1.2842
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.002352 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 1.764
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.002473 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.15085
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.002473 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.23494
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.002473 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.37342
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.00246 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.3813
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.00246 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.4182
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.00246 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.3813
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.001359 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.029898
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.001359 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.014949
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.001359 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.014949
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.062678
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.049012
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.060444
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.063072
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.002627 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.031524
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.002627 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.028897
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.005342 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.12821
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.005342 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.12821
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.005342 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.12287
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.002371 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 0.93892
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.000713 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -0.95043
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.000713 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -0.94686
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.001776 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.067488
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.001776 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.034277
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.001776 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.02664
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.001776 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.083472
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.058099 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 4.3574
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.044901 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 6.7351
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.070499 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 11.9496
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.070025 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 10.5038
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.051577 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 3.2494
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.026129 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 16.976
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.005565 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.2226
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.005565 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.2226
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.017317 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 7.3078
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.001088 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.14362
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.001088 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.14579
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.001088 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 0.35142
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.054826
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.05552
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 0.060725
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.000428 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 0.24995
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.000428 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 0.25466
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.00043 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 0.18619
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.42048
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.42255
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.4218
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.42574
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.002334 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.018672
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.002334 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.018672
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.024742 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.44536
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.024742 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.44536
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.024742 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.37113
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.022374 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.30652
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.013922 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.2506
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.013922 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.2506
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.006224 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.21784
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.006224 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.21162
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.006224 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.21784
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.017285 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.48398
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.017285 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.50126
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.05466 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.9131
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.05466 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.6398
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.03615
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.03615
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.03615
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.03615
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.002777 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.016662
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.002074 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0049776
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.002074 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0049776
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.002074 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.0058072
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.002234 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.008936
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.001796 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0043104
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.001796 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0043104
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.29914
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.28083
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.2849
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.29914
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.37037
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.40293
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.000759 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.11575
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.000759 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.11347
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.000759 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 0.17654
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.27761
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.28347
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.2952
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 0.56695
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.024952 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.82342
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.024952 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.6238
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.002627 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.031524
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.001251 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.091323
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.071495
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.073305
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.031416
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.007854
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.071495
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.0724
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.070952
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.022625
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.04163
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.001705 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 1.0724
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.001304 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.18778
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.001304 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.24515
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.001634 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.019608
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.01871 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.11226
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.001634 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 0.54902
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.001651 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 0.55143
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.001651 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 0.56134
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.001669 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.063422
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.001659 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.041475
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.001659 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.041475
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.001662 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.063156
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.001714 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.049706
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.001635 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.24247
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.001635 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.24296
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.001635 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.25016
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.24458
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.23684
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.1548
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.22446
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.22756
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.1966
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.001956 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.28655
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.001956 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.28929
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.001956 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.33839
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.38171
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.39959
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.44625
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.26554
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.26554
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.31532
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.00201 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 0.6231
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.00201 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 0.83013
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.0756
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.0792
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.0792
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.0846
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.099029
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.092966
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.092966
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.094987
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.002021 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.31123
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.002021 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.29911
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.097008
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.097008
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 3.7937
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 3.7937
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 5.0294
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 4.3357
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 4.3357
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 6.2325
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 11.2849
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 7.7021
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 7.1763
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 7.3715
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 7.9677
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 11.3824
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 10.1288
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 6.1306
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 12.0673
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 9.5472
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 10.7312
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 6.5407
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.054453 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 8.1135
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.052217 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 9.3991
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.052217 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 9.3991
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.052318 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 11.7715
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.051457 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 6.4321
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.051457 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 6.4321
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -0.77014
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -0.77564
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -1.6998
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -0.78664
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -0.79214
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -1.7053
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.008224 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -1.6119
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.008224 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -0.91286
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.005415 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.93638
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.95382
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.95382
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -2.4078
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -0.94219
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.93638
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -0.94801
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -2.3787
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.005937 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.005937 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -0.88933
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -0.78117
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -0.8713
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -2.3976
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.006027 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -0.90827
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.006027 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -0.91008
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.006027 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -1.0692
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.006042 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -0.91536
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.006042 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -0.9202
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.006042 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -1.0725
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.001823 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -1.0592
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -4.3391
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -4.3391
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.004365 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.13968
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.004393 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.21086
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.004393 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.20208
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.052476
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.22302
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.004373 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.074341
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.096206
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.10933
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.004393 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -0.46126
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.049922 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 4.1934
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.058117 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 4.6494
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.058148 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 8.7222
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.058148 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 8.7222
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.14118
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.133
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.10568
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -0.30548
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -0.30608
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -0.30369
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.19142
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -0.48654
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.07976
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.1999
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.18515
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.20468
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.20329
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.001993 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.063776
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.001993 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.05979
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.1665
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.1665
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -0.1785
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -0.16425
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -0.77292
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -0.77648
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.002292 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.31171
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.001829 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.060357
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.096222
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.096222
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.087058
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.087058
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.001409 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.10004
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.001409 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.01409
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.001814 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.29568
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.001814 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.29568
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.001814 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -0.44443
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.14164
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.13074
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.14164
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.14164
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.002252 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.33555
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.002252 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.14661
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.19638
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.18904
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.18775
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.11761
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.026328
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.00238 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -1.7683
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.002344 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -1.7228
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.00239 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.41108
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.00239 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.41108
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.00239 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.41108
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.44824
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.002299 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -0.39773
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.002299 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.31037
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.39332
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.38994
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.3839
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -0.65039
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.14426
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.14245
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.18618
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.16589
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -0.36377
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -0.35018
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -0.35107
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -0.34995
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -0.5996
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.002378 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.01189
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.002378 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.049938
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -0.61187
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.61901
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.61901
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -1.5078
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.002427 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -0.96595
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.10198
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.10198
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.10198
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.12194
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.12194
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.11972
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.005407 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -4.4716
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.005407 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -4.4283
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.001786 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.082335
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.060952
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.060952
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.08421
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.059348
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.059348
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.081804
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.002255 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -0.4059
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.002255 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -0.35764
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.002255 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -0.35403
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.002241 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.078435
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.002102 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -0.96482
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.15463
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.15701
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.16653
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.14988
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.1475
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.24742
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.14036
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.4042
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.39901
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.39901
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002591 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.41974
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.002388 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.37492
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.16103
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.1633
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.088452
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.06804
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.17316
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.1776
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.036515
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.002251 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -0.37141
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.00225 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -0.38025
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.002253 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -0.47989
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.002254 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -0.51391
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.00225 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.027
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.00225 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.0405
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.002063 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.10315
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.24305
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.24305
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.1262
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.12386
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.1262
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.13321
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.1262
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.1262
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.13555
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.13555
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.002369 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.028428
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.13681
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.14414
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.13681
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.13681
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.14414
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.13681
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.000876 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.057816
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.001868 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -0.30075
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.001868 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -0.31009
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.001868 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -0.46326
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.001868 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -1.0199
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.001868 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -1.2011
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.001812 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -1.1796
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.001812 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -1.022
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.001812 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -1.0872
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.001868 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.024284
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.002379 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.028548
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.080002
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.081649
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.076943
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.108
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.041648
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.048001
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.046825
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.082355
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.042354
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.20095
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.34824
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.080724
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.092963
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.05859
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.1315
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.11197
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.11458
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.0651
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.023436
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.12239
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.09114
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.082026
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.093744
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.08437
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.1315
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.12629
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.13411
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.098952
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.10416
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.10416
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -0.22264
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.04993
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.059776 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 4.5729
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.058099 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 4.6479
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.058099 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 2.324
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.057967 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 4.6374
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.05811 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 4.6488
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.058985 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 4.7188
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.059268 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 4.9785
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.057967 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 4.6374
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.42898
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.063757 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 7.6508
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.063757 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 14.8554
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.063757 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 10.8514
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.83539
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.69239
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.84291
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.43274
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.3763
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.039048 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 2.3429
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.036384 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.063415 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.056913 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.27318
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 1.8971
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 5.4383
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 6.8295
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 6.0201
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 5.3118
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 4.0724
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.068941 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 10.3412
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 8.0942
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 10.7562
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 13.3823
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 15.4328
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.001776 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.017258 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.004033 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.02534
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.039458
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.06697
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.16441
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.071709
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.066462
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.033231
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.16441
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.062964
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.075207
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.038478
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.043758
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.01683
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.007854
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.01683
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.043758
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.043758
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.25885
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.08745
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.096195
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.08745
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.001548 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.018576
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.001175 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.017625
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.001175 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.027025
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.000953 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.045744
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.001154 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.009232
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.001636 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.29448
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.001634 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.29412
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.001651 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.29718
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.001651 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.29718
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.004032 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.4032
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.004032 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.4032
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.0396
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.0396
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.0396
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.025344
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.0396
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.0396
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.0396
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.02376
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.004032 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.004032 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 2.016
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.004032 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 2.016
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.004032 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.002111 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.024952 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.00327 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.002115 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:COMCHESS - COMANCHE 138 kV 1441 -1650 C: COMCHESS - COMCHPKW 345kV 1440 - 1900 | [7 empty] | 21.5211
Number of Bus | Name of Bus | ID | Max MW | L:COMCHESS - COMANCHE 138 kV 1441 -1650 C: COMCHESS - COMCHPKW 345kV 1440 - 1900 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.015749 | north | Y | -0.0078545 | -0.017815 | -0.06791 | -0.013697 | 0.0078545 | North | N | 0.0078545 | 0
239 | BOSQUESW | 1 | 149 | -0.015749 | north | Y | -0.0078545 | -0.017815 | -0.06791 | -0.013697 | 0.0078545 | North | N | 0.0078545 | 0
244 | WHITNYDM | 1 | 15 | -0.023857 | north | N | -0.015962 | -0.025923 | -0.076018 | -0.021805 | 0.015962 | North | N | 0.015962 | 0
245 | WHITNYDM | 2 | 15 | -0.023857 | north | N | -0.015962 | -0.025923 | -0.076018 | -0.021805 | 0.015962 | North | N | 0.015962 | 0
247 | BOSQUESW | 2 | 153 | -0.015749 | north | Y | -0.0078545 | -0.017815 | -0.06791 | -0.013697 | 0.0078545 | North | N | 0.0078545 | 0
251 | BOSQUESW | 2 | 150 | -0.022159 | north | Y | -0.014264 | -0.024225 | -0.07432 | -0.020107 | 0.014264 | North | N | 0.014264 | 0
253 | BOSQUESW | 2 | 80 | -0.022159 | north | Y | -0.014264 | -0.024225 | -0.07432 | -0.020107 | 0.014264 | North | N | 0.014264 | 0
332 | RWMILLER | 1 | 73 | -0.061956 | north | Y | -0.054061 | -0.064022 | -0.11412 | -0.059904 | 0.054061 | North | N | 0.054061 | 0
333 | RWMILLER | 2 | 119 | -0.061956 | north | Y | -0.054061 | -0.064022 | -0.11412 | -0.059904 | 0.054061 | North | N | 0.054061 | 0
334 | RWMILLER | 3 | 205 | -0.061956 | north | Y | -0.054061 | -0.064022 | -0.11412 | -0.059904 | 0.054061 | North | N | 0.054061 | 0
335 | RWMILLER | 4 | 102 | -0.061956 | north | Y | -0.054061 | -0.064022 | -0.11412 | -0.059904 | 0.054061 | North | N | 0.054061 | 0
336 | RWMILLER | 5 | 96 | -0.061956 | north | Y | -0.054061 | -0.064022 | -0.11412 | -0.059904 | 0.054061 | North | N | 0.054061 | 0
344 | MRSSHPRD | 1 | 12 | -0.016726 | north | N | -0.0088315 | -0.018792 | -0.068887 | -0.014674 | 0.0088315 | North | N | 0.0088315 | 0
345 | MRSSHPRD | 2 | 12 | -0.016726 | north | N | -0.0088315 | -0.018792 | -0.068887 | -0.014674 | 0.0088315 | North | N | 0.0088315 | 0
366 | JNSNCNTY | 1 | 168 | -0.018189 | north | Y | -0.010294 | -0.020255 | -0.07035 | -0.016137 | 0.010294 | North | N | 0.010294 | 0
367 | JNSNCNTY | 2 | 90 | -0.018189 | north | Y | -0.010294 | -0.020255 | -0.07035 | -0.016137 | 0.010294 | North | N | 0.010294 | 0
503 | NTHTEXAS | 1 | 18 | -0.029876 | north | Y | -0.021981 | -0.031942 | -0.082037 | -0.027824 | 0.021981 | North | N | 0.021981 | 0
504 | NTHTEXAS | 2 | 18 | -0.029876 | north | Y | -0.021981 | -0.031942 | -0.082037 | -0.027824 | 0.021981 | North | N | 0.021981 | 0
505 | NTHTEXAS | 3 | 38 | -0.029876 | north | Y | -0.021981 | -0.031942 | -0.082037 | -0.027824 | 0.021981 | North | N | 0.021981 | 0
580 | JCKCNTY8 | 1 | 288 | -0.016092 | north | Y | -0.0081975 | -0.018158 | -0.068253 | -0.01404 | 0.0081975 | North | N | 0.0081975 | 0
581 | JCKCNTY8 | 2 | 147 | -0.016092 | north | Y | -0.0081975 | -0.018158 | -0.068253 | -0.01404 | 0.0081975 | North | N | 0.0081975 | 0
582 | JCKCNTY8 | 3 | 147 | -0.016092 | north | Y | -0.0081975 | -0.018158 | -0.068253 | -0.01404 | 0.0081975 | North | N | 0.0081975 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.006928 | north | Y | 0.00096651 | -0.0089943 | -0.059089 | -0.0048761 | 0.00096651 | North | N | 0.00096651 | 0
837 | NEWMAN_G | 1 | 40 | -0.005732 | north | Y | 0.0021625 | -0.0077983 | -0.057893 | -0.0036801 | 0.0021625 | North | N | 0.0021625 | 0
842 | OLINGER_ | 1 | 79 | -0.005683 | north | Y | 0.0022115 | -0.0077493 | -0.057844 | -0.0036311 | 0.0022115 | North | N | 0.0022115 | 0
843 | OLINGER_ | 1 | 106 | -0.005683 | north | Y | 0.0022115 | -0.0077493 | -0.057844 | -0.0036311 | 0.0022115 | North | N | 0.0022115 | 0
844 | OLINGER_ | 1 | 146 | -0.005683 | north | Y | 0.0022115 | -0.0077493 | -0.057844 | -0.0036311 | 0.0022115 | North | N | 0.0022115 | 0
845 | OLINGER_ | 1 | 76 | -0.005683 | north | Y | 0.0022115 | -0.0077493 | -0.057844 | -0.0036311 | 0.0022115 | North | N | 0.0022115 | 0
923 | SPENCER_ | 1 | 60 | -0.004322 | north | Y | 0.0035725 | -0.0063883 | -0.056483 | -0.0022701 | 0.0022701 | houston | Y | 0.0035725 | 0.078145
924 | SPENCER_ | 1 | 63 | -0.004322 | north | Y | 0.0035725 | -0.0063883 | -0.056483 | -0.0022701 | 0.0022701 | houston | Y | 0.0035725 | 0.082052
948 | STEAM1 | 1 | 20 | -0.005707 | north | Y | 0.0021875 | -0.0077733 | -0.057868 | -0.0036551 | 0.0021875 | North | N | 0.0021875 | 0
949 | STEAM2 | 1 | 25 | -0.005707 | north | Y | 0.0021875 | -0.0077733 | -0.057868 | -0.0036551 | 0.0021875 | North | N | 0.0021875 | 0
950 | STEAM3 | 1 | 41 | -0.005707 | north | Y | 0.0021875 | -0.0077733 | -0.057868 | -0.0036551 | 0.0021875 | North | N | 0.0021875 | 0
990 | GIBN_CRE | 1 | 463 | -0.004245 | north | Y | 0.0036495 | -0.0063113 | -0.056406 | -0.0021931 | 0.0021931 | houston | Y | 0.0036495 | 0.67432
1002 | PBCTAGE_ | A | 66 | 0.054736 | west | Y | 0.062631 | 0.05267 | 0.0025749 | 0.056788 | 0.0025749 | west | N | 0.0025749 | 0
1003 | PBCTBGE_ | B | 65 | 0.054736 | west | Y | 0.062631 | 0.05267 | 0.0025749 | 0.056788 | 0.0025749 | west | N | 0.0025749 | 0
1004 | PBCTCGE_ | C | 67 | 0.054736 | west | Y | 0.062631 | 0.05267 | 0.0025749 | 0.056788 | 0.0025749 | west | N | 0.0025749 | 0
1005 | PBCTDGE_ | D | 67 | 0.054736 | west | Y | 0.062631 | 0.05267 | 0.0025749 | 0.056788 | 0.0025749 | west | N | 0.0025749 | 0
1006 | PBCTEGE_ | E | 67 | 0.054736 | west | Y | 0.062631 | 0.05267 | 0.0025749 | 0.056788 | 0.0025749 | west | N | 0.0025749 | 0
1007 | PB5GEN_6 | MB | 114 | 0.054736 | west | Y | 0.062631 | 0.05267 | 0.0025749 | 0.056788 | 0.0025749 | west | N | 0.0025749 | 0
1008 | PB6GEN_7 | MB | 515 | 0.054736 | west | Y | 0.062631 | 0.05267 | 0.0025749 | 0.056788 | 0.0025749 | west | N | 0.0025749 | 0
1039 | MRGNAG_1 | A | 66 | 0.052826 | west | Y | 0.060721 | 0.05076 | 0.00066495 | 0.054878 | 0.00066495 | west | N | 0.00066495 | 0
1040 | MRGNBG_2 | B | 69 | 0.052826 | west | Y | 0.060721 | 0.05076 | 0.00066495 | 0.054878 | 0.00066495 | west | N | 0.00066495 | 0
1041 | MRGNCG_3 | C | 69 | 0.052826 | west | Y | 0.060721 | 0.05076 | 0.00066495 | 0.054878 | 0.00066495 | west | N | 0.00066495 | 0
1042 | MRGNDG_4 | D | 67 | 0.052826 | west | Y | 0.060721 | 0.05076 | 0.00066495 | 0.054878 | 0.00066495 | west | N | 0.00066495 | 0
1043 | MRGNEG_5 | E | 67 | 0.052826 | west | Y | 0.060721 | 0.05076 | 0.00066495 | 0.054878 | 0.00066495 | west | N | 0.00066495 | 0
1044 | MRGNFG_6 | F | 65 | 0.052826 | west | Y | 0.060721 | 0.05076 | 0.00066495 | 0.054878 | 0.00066495 | west | N | 0.00066495 | 0
1045 | CALENG1G | 1 | 70 | 0.053758 | west | N | 0.061653 | 0.051692 | 0.0015969 | 0.05581 | 0.0015969 | west | N | 0.0015969 | 0
1046 | CALENG2G | 2 | 73.4 | 0.053758 | west | N | 0.061653 | 0.051692 | 0.0015969 | 0.05581 | 0.0015969 | west | N | 0.0015969 | 0
1047 | CALENG3G | 3 | 70.4 | 0.053758 | west | N | 0.061653 | 0.051692 | 0.0015969 | 0.05581 | 0.0015969 | west | N | 0.0015969 | 0
1058 | LONGSHOR | 1 | 150 | 0.053656 | west | Y | 0.061551 | 0.05159 | 0.0014949 | 0.055708 | 0.0014949 | west | N | 0.0014949 | 0
1058 | LONGSHOR | 2 | 220 | 0.053656 | west | Y | 0.061551 | 0.05159 | 0.0014949 | 0.055708 | 0.0014949 | west | N | 0.0014949 | 0
1061 | CIELOGEN | 1 | 99 | 0.051067 | west | Y | 0.058962 | 0.049001 | -0.0010941 | 0.053119 | 0.0010941 | west | N | 0.0010941 | 0
1062 | CIELOGEN | 1 | 61 | 0.051067 | west | Y | 0.058962 | 0.049001 | -0.0010941 | 0.053119 | 0.0010941 | west | N | 0.0010941 | 0
1068 | SCURRYCW | 1 | 141 | 0.051134 | west | Y | 0.059029 | 0.049068 | -0.0010271 | 0.053186 | 0.0010271 | west | N | 0.0010271 | 0
1069 | KINDERMG | 1 | 25 | 0.051067 | west | N | 0.058962 | 0.049001 | -0.0010941 | 0.053119 | 0.0010941 | west | N | 0.0010941 | 0
1070 | KINDERMG | 1 | 45.7 | 0.051067 | west | N | 0.058962 | 0.049001 | -0.0010941 | 0.053119 | 0.0010941 | west | N | 0.0010941 | 0
1071 | KINDERMG | 1 | 45.7 | 0.051067 | west | N | 0.058962 | 0.049001 | -0.0010941 | 0.053119 | 0.0010941 | west | N | 0.0010941 | 0
1073 | SCURRYCW | 2 | 120 | 0.051134 | west | Y | 0.059029 | 0.049068 | -0.0010271 | 0.053186 | 0.0010271 | west | N | 0.0010271 | 0
1320 | BSP 1 | 1 | 25.8 | 0.054935 | west | N | 0.06283 | 0.052869 | 0.0027739 | 0.056987 | 0.0027739 | west | N | 0.0027739 | 0
1326 | STANTONW | 1 | 100.5 | 0.054124 | west | Y | 0.062019 | 0.052058 | 0.0019629 | 0.056176 | 0.0019629 | west | N | 0.0019629 | 0
1327 | WILDHRSE | 1 | 120 | 0.053461 | west | Y | 0.061356 | 0.051395 | 0.0012999 | 0.055513 | 0.0012999 | west | N | 0.0012999 | 0
1328 | OCOTILLO | 1 | 58 | 0.05389 | west | Y | 0.061785 | 0.051824 | 0.0017289 | 0.055942 | 0.0017289 | west | N | 0.0017289 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.053741 | west | Y | 0.061636 | 0.051675 | 0.0015799 | 0.055793 | 0.0015799 | west | N | 0.0015799 | 0
1343 | TRENTIPP | 1 | 150 | 0.04978 | west | Y | 0.057675 | 0.047714 | -0.0023811 | 0.051832 | 0.0023811 | west | N | 0.0023811 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.05879 | west | Y | 0.066685 | 0.056724 | 0.0066289 | 0.060842 | 0.0066289 | west | N | 0.0066289 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.05879 | west | Y | 0.066685 | 0.056724 | 0.0066289 | 0.060842 | 0.0066289 | west | N | 0.0066289 | 0
1354 | AEPWIND_ | 1 | 101 | 0.04978 | west | Y | 0.057675 | 0.047714 | -0.0023811 | 0.051832 | 0.0023811 | west | N | 0.0023811 | 0
1360 | GUNSIGHT | 1 | 120 | 0.053308 | west | Y | 0.061203 | 0.051242 | 0.0011469 | 0.05536 | 0.0011469 | west | N | 0.0011469 | 0
1432 | GRHAMSES | 2 | 366 | 0.014701 | north | Y | 0.022596 | 0.012635 | -0.03746 | 0.016753 | 0.012635 | south | Y | 0.022596 | 3.6456
1433 | GRHAMSES | 1 | 242 | 0.003939 | north | Y | 0.011834 | 0.0018727 | -0.048222 | 0.0059909 | 0.0018727 | south | Y | 0.011834 | 2.4105
1437 | MESQUITW | 1 | 400 | 0.036011 | west | Y | 0.043906 | 0.033945 | -0.01615 | 0.038063 | 0.01615 | west | N | 0.01615 | 0
1438 | MESQUITW | 1 | 236 | 0.035976 | west | Y | 0.043871 | 0.03391 | -0.016185 | 0.038028 | 0.016185 | west | N | 0.016185 | 0
1442 | COKFIELD | 1 | 165 | 0.03087 | west | Y | 0.038765 | 0.028804 | -0.021291 | 0.032922 | 0.021291 | west | N | 0.021291 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.004834 | north | Y | 0.012729 | 0.0027677 | -0.047327 | 0.0068859 | 0.0027677 | south | Y | 0.012729 | 2.032
1454 | WCPWRCO_ | 2 | 201 | 0.004834 | north | Y | 0.012729 | 0.0027677 | -0.047327 | 0.0068859 | 0.0027677 | south | Y | 0.012729 | 2.0021
1455 | WCPWRCO_ | 3 | 242 | 0.004834 | north | Y | 0.012729 | 0.0027677 | -0.047327 | 0.0068859 | 0.0027677 | south | Y | 0.012729 | 2.4105
1479 | WFCOGEN_ | 1 | 20 | 0.011233 | west | Y | 0.019128 | 0.0091667 | -0.040928 | 0.013285 | 0.0091667 | south | Y | 0.040928 | 0.63523
1479 | WFCOGEN_ | 2 | 20 | 0.011233 | west | Y | 0.019128 | 0.0091667 | -0.040928 | 0.013285 | 0.0091667 | south | Y | 0.040928 | 0.63523
1482 | WFCOGEN_ | 1 | 20 | 0.011233 | west | Y | 0.019128 | 0.0091667 | -0.040928 | 0.013285 | 0.0091667 | south | Y | 0.040928 | 0.63523
1482 | WFCOGEN_ | 2 | 17 | 0.011233 | west | Y | 0.019128 | 0.0091667 | -0.040928 | 0.013285 | 0.0091667 | south | Y | 0.040928 | 0.53994
1600 | BARTNWND | 1 | 120 | -0.017709 | north | Y | -0.0098145 | -0.019775 | -0.06987 | -0.015657 | 0.0098145 | North | N | 0.0098145 | 0
1643 | SLSTR1PP | 1 | 60 | -0.10967 | north | Y | -0.10178 | -0.11174 | -0.16183 | -0.10762 | 0.10178 | North | N | 0.10178 | 0
1675 | PEC_1G | 1 | 75 | -0.005544 | north | N | 0.0023505 | -0.0076103 | -0.057705 | -0.0034921 | 0.0023505 | North | N | 0.0023505 | 0
1676 | PEC_2G | 2 | 79.6 | -0.005544 | north | N | 0.0023505 | -0.0076103 | -0.057705 | -0.0034921 | 0.0023505 | North | N | 0.0023505 | 0
1677 | PEC_3G | 3 | 88.4 | -0.005544 | north | N | 0.0023505 | -0.0076103 | -0.057705 | -0.0034921 | 0.0023505 | North | N | 0.0023505 | 0
1678 | LAMARPWR | 1 | 160 | -0.005519 | north | Y | 0.0023755 | -0.0075853 | -0.05768 | -0.0034671 | 0.0023755 | North | N | 0.0023755 | 0
1679 | LAMARPWR | 2 | 156 | -0.005519 | north | Y | 0.0023755 | -0.0075853 | -0.05768 | -0.0034671 | 0.0023755 | North | N | 0.0023755 | 0
1680 | LAMARPWR | 3 | 196 | -0.005519 | north | Y | 0.0023755 | -0.0075853 | -0.05768 | -0.0034671 | 0.0023755 | North | N | 0.0023755 | 0
1681 | LAMARPWR | 4 | 156 | -0.005519 | north | Y | 0.0023755 | -0.0075853 | -0.05768 | -0.0034671 | 0.0023755 | North | N | 0.0023755 | 0
1682 | LAMARPWR | 5 | 157 | -0.005519 | north | Y | 0.0023755 | -0.0075853 | -0.05768 | -0.0034671 | 0.0023755 | North | N | 0.0023755 | 0
1683 | LAMARPWR | 6 | 198 | -0.005519 | north | Y | 0.0023755 | -0.0075853 | -0.05768 | -0.0034671 | 0.0023755 | North | N | 0.0023755 | 0
1687 | VALLEY_1 | 1 | 170 | -0.005545 | north | Y | 0.0023495 | -0.0076113 | -0.057706 | -0.0034931 | 0.0023495 | North | N | 0.0023495 | 0
1688 | VALLEY_2 | 2 | 520 | -0.005545 | north | Y | 0.0023495 | -0.0076113 | -0.057706 | -0.0034931 | 0.0023495 | North | N | 0.0023495 | 0
1689 | VALLEY_3 | 3 | 370 | -0.005501 | north | Y | 0.0023935 | -0.0075673 | -0.057662 | -0.0034491 | 0.0023935 | North | N | 0.0023935 | 0
1701 | MOSES_1G | 1 | 558 | -0.005538 | north | Y | 0.0023565 | -0.0076043 | -0.057699 | -0.0034861 | 0.0023565 | North | N | 0.0023565 | 0
1702 | MOSES_2G | 2 | 579 | -0.005538 | north | Y | 0.0023565 | -0.0076043 | -0.057699 | -0.0034861 | 0.0023565 | North | N | 0.0023565 | 0
1703 | MOSES_3G | 3 | 808 | -0.005538 | north | Y | 0.0023565 | -0.0076043 | -0.057699 | -0.0034861 | 0.0023565 | North | N | 0.0023565 | 0
1861 | EAGLEMNT | MB | 112 | -0.005829 | north | Y | 0.0020655 | -0.0078953 | -0.05799 | -0.0037771 | 0.0020655 | North | N | 0.0020655 | 0
1862 | EAGLEMNT | MB | 100 | -0.005829 | north | Y | 0.0020655 | -0.0078953 | -0.05799 | -0.0037771 | 0.0020655 | North | N | 0.0020655 | 0
1863 | EAGLEMNT | MB | 378 | -0.005829 | north | Y | 0.0020655 | -0.0078953 | -0.05799 | -0.0037771 | 0.0020655 | North | N | 0.0020655 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.007938 | north | Y | -4.3486e-05 | -0.010004 | -0.060099 | -0.0058861 | 4.3486e-05 | North | N | 4.3486e-05 | 0
1878 | WLFHOLW_ | 2 | 205 | -0.007938 | north | Y | -4.3486e-05 | -0.010004 | -0.060099 | -0.0058861 | 4.3486e-05 | North | N | 4.3486e-05 | 0
1879 | WLFHOLW_ | 3 | 272.4 | -0.007938 | north | Y | -4.3486e-05 | -0.010004 | -0.060099 | -0.0058861 | 4.3486e-05 | North | N | 4.3486e-05 | 0
1889 | DECRDOVA | MB | 770 | -0.009648 | north | Y | -0.0017535 | -0.011714 | -0.061809 | -0.0075961 | 0.0017535 | North | N | 0.0017535 | 0
1892 | DECRDOVA | A | 70 | -0.029786 | north | Y | -0.021891 | -0.031852 | -0.081947 | -0.027734 | 0.021891 | North | N | 0.021891 | 0
1893 | DECRDOVA | B | 69 | -0.029786 | north | Y | -0.021891 | -0.031852 | -0.081947 | -0.027734 | 0.021891 | North | N | 0.021891 | 0
1894 | DECRDOVA | C | 69 | -0.029786 | north | Y | -0.021891 | -0.031852 | -0.081947 | -0.027734 | 0.021891 | North | N | 0.021891 | 0
1895 | DECRDOVA | D | 68 | -0.029786 | north | Y | -0.021891 | -0.031852 | -0.081947 | -0.027734 | 0.021891 | North | N | 0.021891 | 0
1898 | COMCHEPK | 1 | 1157 | -0.008154 | north | N | -0.00025949 | -0.01022 | -0.060315 | -0.0061021 | 0.00025949 | North | N | 0.00025949 | 0
1899 | COMCHEPK | 2 | 1158 | -0.008154 | north | N | -0.00025949 | -0.01022 | -0.060315 | -0.0061021 | 0.00025949 | North | N | 0.00025949 | 0
1937 | MDLTHELP | 5 | 224 | -0.007585 | north | Y | 0.00030951 | -0.0096513 | -0.059746 | -0.0055331 | 0.00030951 | North | N | 0.00030951 | 0
1938 | MDLTHELP | 6 | 226 | -0.007585 | north | Y | 0.00030951 | -0.0096513 | -0.059746 | -0.0055331 | 0.00030951 | North | N | 0.00030951 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.006621 | north | Y | 0.0012735 | -0.0086873 | -0.058782 | -0.0045691 | 0.0012735 | North | N | 0.0012735 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.006621 | north | Y | 0.0012735 | -0.0086873 | -0.058782 | -0.0045691 | 0.0012735 | North | N | 0.0012735 | 0
1943 | MDLTHELP | 3 | 212 | -0.007585 | north | Y | 0.00030951 | -0.0096513 | -0.059746 | -0.0055331 | 0.00030951 | North | N | 0.00030951 | 0
1944 | MDLTHELP | 4 | 211 | -0.007585 | north | Y | 0.00030951 | -0.0096513 | -0.059746 | -0.0055331 | 0.00030951 | North | N | 0.00030951 | 0
1947 | HANDLEY_ | 3 | 395 | -0.006362 | north | Y | 0.0015325 | -0.0084283 | -0.058523 | -0.0043101 | 0.0015325 | North | N | 0.0015325 | 0
1948 | HANDLEY_ | 4 | 435 | -0.006435 | north | Y | 0.0014595 | -0.0085013 | -0.058596 | -0.0043831 | 0.0014595 | North | N | 0.0014595 | 0
1949 | HANDLEY_ | 5 | 435 | -0.006362 | north | Y | 0.0015325 | -0.0084283 | -0.058523 | -0.0043101 | 0.0015325 | North | N | 0.0015325 | 0
2371 | COLLIN_1 | MB | 138 | -0.005245 | north | Y | 0.0026495 | -0.0073113 | -0.057406 | -0.0031931 | 0.0026495 | North | N | 0.0026495 | 0
2413 | MTCK6_G | 6 | 118 | -0.006255 | north | Y | 0.0016395 | -0.0083213 | -0.058416 | -0.0042031 | 0.0016395 | North | N | 0.0016395 | 0
2414 | MTCK7_G | 7 | 115 | -0.006255 | north | Y | 0.0016395 | -0.0083213 | -0.058416 | -0.0042031 | 0.0016395 | North | N | 0.0016395 | 0
2417 | MTCK8_G | 8 | 556 | -0.006255 | north | Y | 0.0016395 | -0.0083213 | -0.058416 | -0.0042031 | 0.0016395 | North | N | 0.0016395 | 0
2451 | LKHB1_G | 1 | 388 | -0.00586 | north | Y | 0.0020345 | -0.0079263 | -0.058021 | -0.0038081 | 0.0020345 | North | N | 0.0020345 | 0
2452 | LKHB2_G | 2 | 515 | -0.00586 | north | Y | 0.0020345 | -0.0079263 | -0.058021 | -0.0038081 | 0.0020345 | North | N | 0.0020345 | 0
3097 | MARTLAKE | 1 | 785 | -0.005989 | north | Y | 0.0019055 | -0.0080553 | -0.05815 | -0.0039371 | 0.0019055 | North | N | 0.0019055 | 0
3098 | MARTLAKE | 2 | 795 | -0.005989 | north | Y | 0.0019055 | -0.0080553 | -0.05815 | -0.0039371 | 0.0019055 | North | N | 0.0019055 | 0
3099 | MARTLAKE | 3 | 780 | -0.005989 | north | Y | 0.0019055 | -0.0080553 | -0.05815 | -0.0039371 | 0.0019055 | North | N | 0.0019055 | 0
3107 | STRYKER_ | 1 | 182 | -0.006025 | north | Y | 0.0018695 | -0.0080913 | -0.058186 | -0.0039731 | 0.0018695 | North | N | 0.0018695 | 0
3108 | STRYKER_ | 2 | 484 | -0.006025 | north | Y | 0.0018695 | -0.0080913 | -0.058186 | -0.0039731 | 0.0018695 | North | N | 0.0018695 | 0
3126 | TRINIDAD | 1 | 224 | -0.007634 | north | Y | 0.00026051 | -0.0097003 | -0.059795 | -0.0055821 | 0.00026051 | North | N | 0.00026051 | 0
3309 | ASPN_G | 1 | 50 | -0.006016 | north | Y | 0.0018785 | -0.0080823 | -0.058177 | -0.0039641 | 0.0018785 | North | N | 0.0018785 | 0
3348 | CHAMPION | MB | 42 | -0.006016 | north | N | 0.0018785 | -0.0080823 | -0.058177 | -0.0039641 | 0.0018785 | North | N | 0.0018785 | 0
3381 | BBRN_1G | 1 | 615 | -0.006013 | north | Y | 0.0018815 | -0.0080793 | -0.058174 | -0.0039611 | 0.0018815 | North | N | 0.0018815 | 0
3382 | BBRN_2G | 2 | 587 | -0.006013 | north | Y | 0.0018815 | -0.0080793 | -0.058174 | -0.0039611 | 0.0018815 | North | N | 0.0018815 | 0
3403 | THOUSE_1 | MB | 537 | -0.007945 | north | Y | -5.0486e-05 | -0.010011 | -0.060106 | -0.0058931 | 5.0486e-05 | North | N | 5.0486e-05 | 0
3404 | THOUSE_2 | 2 | 787 | -0.007945 | north | Y | -5.0486e-05 | -0.010011 | -0.060106 | -0.0058931 | 5.0486e-05 | North | N | 5.0486e-05 | 0
3416 | LAKE_CRK | MB | 75 | -0.008107 | north | Y | -0.00021249 | -0.010173 | -0.060268 | -0.0060551 | 0.00021249 | North | N | 0.00021249 | 0
3417 | LAKE_CRK | MB | 222 | -0.008107 | north | Y | -0.00021249 | -0.010173 | -0.060268 | -0.0060551 | 0.00021249 | North | N | 0.00021249 | 0
3432 | SANDOW_4 | 4 | 569 | -0.001823 | south | Y | 0.0060715 | -0.0038893 | -0.053984 | 0.00022891 | 0.00022891 | houston | Y | 0.0038893 | 2.0827
5026 | BRAUNIG_ | 1 | 209 | 0.002621 | south | Y | 0.010516 | 0.00055473 | -0.04954 | 0.0046729 | 0.00055473 | south | N | 0.00055473 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.002621 | south | Y | 0.010516 | 0.00055473 | -0.04954 | 0.0046729 | 0.00055473 | south | N | 0.00055473 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.002698 | south | Y | 0.010593 | 0.00063173 | -0.049463 | 0.0047499 | 0.00063173 | south | N | 0.00063173 | 0
5031 | BRA_VHBC | 1 | 46 | 0.002621 | south | Y | 0.010516 | 0.00055473 | -0.04954 | 0.0046729 | 0.00055473 | south | N | 0.00055473 | 0
5032 | BRA_VHBC | 2 | 47 | 0.002621 | south | Y | 0.010516 | 0.00055473 | -0.04954 | 0.0046729 | 0.00055473 | south | N | 0.00055473 | 0
5033 | BRA_VHBC | 3 | 46 | 0.002621 | south | Y | 0.010516 | 0.00055473 | -0.04954 | 0.0046729 | 0.00055473 | south | N | 0.00055473 | 0
5034 | BRA_VHBC | 4 | 46 | 0.002621 | south | Y | 0.010516 | 0.00055473 | -0.04954 | 0.0046729 | 0.00055473 | south | N | 0.00055473 | 0
5111 | CALAVER_ | 1 | 424 | 0.002611 | south | Y | 0.010506 | 0.00054473 | -0.04955 | 0.0046629 | 0.00054473 | south | N | 0.00054473 | 0
5112 | CALAVER_ | 2 | 425 | 0.002611 | south | Y | 0.010506 | 0.00054473 | -0.04955 | 0.0046629 | 0.00054473 | south | N | 0.00054473 | 0
5264 | LEON_LCP | 3 | 58 | 0.002845 | south | Y | 0.01074 | 0.00077873 | -0.049316 | 0.0048969 | 0.00077873 | south | N | 0.00077873 | 0
5265 | LEON_LCP | 4 | 89 | 0.002845 | south | Y | 0.01074 | 0.00077873 | -0.049316 | 0.0048969 | 0.00077873 | south | N | 0.00077873 | 0
5266 | LEON_LCP | 1 | 44 | 0.002845 | south | Y | 0.01074 | 0.00077873 | -0.049316 | 0.0048969 | 0.00077873 | south | N | 0.00077873 | 0
5267 | LEON_LCP | 2 | 44 | 0.002845 | south | Y | 0.01074 | 0.00077873 | -0.049316 | 0.0048969 | 0.00077873 | south | N | 0.00077873 | 0
5268 | LEON_LCP | 3 | 43 | 0.002845 | south | Y | 0.01074 | 0.00077873 | -0.049316 | 0.0048969 | 0.00077873 | south | N | 0.00077873 | 0
5269 | LEON_LCP | 4 | 45 | 0.002845 | south | Y | 0.01074 | 0.00077873 | -0.049316 | 0.0048969 | 0.00077873 | south | N | 0.00077873 | 0
5396 | CALAVER_ | 1 | 412 | 0.002629 | south | Y | 0.010524 | 0.00056273 | -0.049532 | 0.0046809 | 0.00056273 | south | N | 0.00056273 | 0
5397 | CALAVER_ | 2 | 400 | 0.002629 | south | Y | 0.010524 | 0.00056273 | -0.049532 | 0.0046809 | 0.00056273 | south | N | 0.00056273 | 0
5401 | CALAVER_ | 1 | 546 | 0.002352 | south | Y | 0.010247 | 0.00028573 | -0.049809 | 0.0044039 | 0.00028573 | south | N | 0.00028573 | 0
5402 | CALAVER_ | 2 | 750 | 0.002352 | south | Y | 0.010247 | 0.00028573 | -0.049809 | 0.0044039 | 0.00028573 | south | N | 0.00028573 | 0
5436 | TUTTL_WB | MB | 61 | 0.002473 | south | Y | 0.010368 | 0.00040673 | -0.049688 | 0.0045249 | 0.00040673 | south | N | 0.00040673 | 0
5438 | TUTTL_WB | MB | 95 | 0.002473 | south | Y | 0.010368 | 0.00040673 | -0.049688 | 0.0045249 | 0.00040673 | south | N | 0.00040673 | 0
5439 | TUTTL_WB | MB | 151 | 0.002473 | south | Y | 0.010368 | 0.00040673 | -0.049688 | 0.0045249 | 0.00040673 | south | N | 0.00040673 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.00246 | south | Y | 0.010355 | 0.00039373 | -0.049701 | 0.0045119 | 0.00039373 | south | N | 0.00039373 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.00246 | south | Y | 0.010355 | 0.00039373 | -0.049701 | 0.0045119 | 0.00039373 | south | N | 0.00039373 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.00246 | south | Y | 0.010355 | 0.00039373 | -0.049701 | 0.0045119 | 0.00039373 | south | N | 0.00039373 | 0
5503 | RAYBURNG | 1 | 22 | 0.001359 | south | Y | 0.0092535 | -0.00070727 | -0.050802 | 0.0034109 | 0.00070727 | south | N | 0.00070727 | 0
5505 | RAYBURNG | 1 | 11 | 0.001359 | south | Y | 0.0092535 | -0.00070727 | -0.050802 | 0.0034109 | 0.00070727 | south | N | 0.00070727 | 0
5506 | RAYBURNG | 1 | 11 | 0.001359 | south | Y | 0.0092535 | -0.00070727 | -0.050802 | 0.0034109 | 0.00070727 | south | N | 0.00070727 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.001314 | south | Y | 0.0092085 | -0.00075227 | -0.050847 | 0.0033659 | 0.00075227 | south | N | 0.00075227 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.001314 | south | Y | 0.0092085 | -0.00075227 | -0.050847 | 0.0033659 | 0.00075227 | south | N | 0.00075227 | 0
5511 | RAYBURNC | 1 | 46 | 0.001314 | south | Y | 0.0092085 | -0.00075227 | -0.050847 | 0.0033659 | 0.00075227 | south | N | 0.00075227 | 0
5512 | RAYBURNC | 1 | 48 | 0.001314 | south | Y | 0.0092085 | -0.00075227 | -0.050847 | 0.0033659 | 0.00075227 | south | N | 0.00075227 | 0
5728 | FALCONHY | 2 | 12 | 0.002627 | south | N | 0.010522 | 0.00056073 | -0.049534 | 0.0046789 | 0.00056073 | south | N | 0.00056073 | 0
5729 | FALCONHY | 3 | 11 | 0.002627 | south | N | 0.010522 | 0.00056073 | -0.049534 | 0.0046789 | 0.00056073 | south | N | 0.00056073 | 0
5890 | PEARSALL | 1 | 24 | 0.005342 | south | Y | 0.013237 | 0.0032757 | -0.046819 | 0.0073939 | 0.0032757 | south | N | 0.0032757 | 0
5891 | PEARSALL | 1 | 24 | 0.005342 | south | Y | 0.013237 | 0.0032757 | -0.046819 | 0.0073939 | 0.0032757 | south | N | 0.0032757 | 0
5892 | PEARSALL | 1 | 23 | 0.005342 | south | Y | 0.013237 | 0.0032757 | -0.046819 | 0.0073939 | 0.0032757 | south | N | 0.0032757 | 0
5903 | SANMIGUE | 1 | 396 | 0.002371 | south | Y | 0.010266 | 0.00030473 | -0.04979 | 0.0044229 | 0.00030473 | south | N | 0.00030473 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.000713 | houston | N | 0.0071815 | -0.0027793 | -0.052874 | 0.0013389 | 0.0013389 | houston | N | 0.0013389 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.000713 | houston | N | 0.0071815 | -0.0027793 | -0.052874 | 0.0013389 | 0.0013389 | houston | N | 0.0013389 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.0078945 | 0
5932 | SI_RAY9 | 9 | 38 | 0.001776 | south | Y | 0.0096705 | -0.00029027 | -0.050385 | 0.0038279 | 0.00029027 | south | N | 0.00029027 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.001776 | south | Y | 0.0096705 | -0.00029027 | -0.050385 | 0.0038279 | 0.00029027 | south | N | 0.00029027 | 0
5934 | SI_RAY5 | 5 | 15 | 0.001776 | south | Y | 0.0096705 | -0.00029027 | -0.050385 | 0.0038279 | 0.00029027 | south | N | 0.00029027 | 0
5935 | SI_RAY10 | 10 | 47 | 0.001776 | south | Y | 0.0096705 | -0.00029027 | -0.050385 | 0.0038279 | 0.00029027 | south | N | 0.00029027 | 0
6016 | SWMESA | 1 | 75 | 0.058099 | west | Y | 0.065994 | 0.056033 | 0.0059379 | 0.060151 | 0.0059379 | west | N | 0.0059379 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.052161 | 0
6144 | MCADOO1A | 1 | 150 | 0.044901 | west | Y | 0.052796 | 0.042835 | -0.0072601 | 0.046953 | 0.0072601 | west | N | 0.0072601 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.070499 | west | Y | 0.078394 | 0.068433 | 0.018338 | 0.072551 | 0.018338 | west | N | 0.018338 | 0
6476 | LANGFORD | 1 | 150 | 0.070025 | west | Y | 0.07792 | 0.067959 | 0.017864 | 0.072077 | 0.017864 | west | N | 0.017864 | 0
6637 | SNYDERW1 | 1 | 63 | 0.051577 | west | Y | 0.059472 | 0.049511 | -0.00058405 | 0.053629 | 0.00058405 | west | N | 0.00058405 | 0
6752 | OKLA0A | 1 | 649.7 | 0.026129 | west | Y | 0.034024 | 0.024063 | -0.026032 | 0.028181 | 0.024063 | south | Y | 0.026032 | 1.2795
6948 | DENISNDM | 1 | 40 | -0.005565 | north | N | 0.0023295 | -0.0076313 | -0.057726 | -0.0035131 | 0.0023295 | North | N | 0.0023295 | 0
6948 | DENISNDM | 2 | 40 | -0.005565 | north | N | 0.0023295 | -0.0076313 | -0.057726 | -0.0035131 | 0.0023295 | North | N | 0.0023295 | 0
7000 | L_FERGUS | 1 | 422 | 0.017317 | south | Y | 0.025212 | 0.015251 | -0.034844 | 0.019369 | 0.015251 | south | N | 0.015251 | 0
7004 | L_SIMGID | 1 | 132 | 0.001088 | south | Y | 0.0089825 | -0.00097827 | -0.051073 | 0.0031399 | 0.00097827 | south | N | 0.00097827 | 0
7005 | L_SIMGID | 2 | 134 | 0.001088 | south | Y | 0.0089825 | -0.00097827 | -0.051073 | 0.0031399 | 0.00097827 | south | N | 0.00097827 | 0
7006 | L_SIMGID | 3 | 323 | 0.001088 | south | Y | 0.0089825 | -0.00097827 | -0.051073 | 0.0031399 | 0.00097827 | south | N | 0.00097827 | 0
7007 | L_LOSTPI | 1 | 158 | 0.000347 | south | Y | 0.0082415 | -0.0017193 | -0.051814 | 0.0023989 | 0.0017193 | south | N | 0.0017193 | 0
7008 | L_LOSTPI | 2 | 160 | 0.000347 | south | Y | 0.0082415 | -0.0017193 | -0.051814 | 0.0023989 | 0.0017193 | south | N | 0.0017193 | 0
7009 | L_LOSTPI | 3 | 175 | 0.000347 | south | Y | 0.0082415 | -0.0017193 | -0.051814 | 0.0023989 | 0.0017193 | south | N | 0.0017193 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.000428 | south | Y | 0.0083225 | -0.0016383 | -0.051733 | 0.0024799 | 0.0016383 | south | N | 0.0016383 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.000428 | south | Y | 0.0083225 | -0.0016383 | -0.051733 | 0.0024799 | 0.0016383 | south | N | 0.0016383 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.00043 | south | Y | 0.0083245 | -0.0016363 | -0.051731 | 0.0024819 | 0.0016363 | south | N | 0.0016363 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.001878 | south | Y | 0.0097725 | -0.00018827 | -0.050283 | 0.0039299 | 0.00018827 | south | N | 0.00018827 | 0
7015 | L_HAYSEN | 2 | 225 | 0.001878 | south | Y | 0.0097725 | -0.00018827 | -0.050283 | 0.0039299 | 0.00018827 | south | N | 0.00018827 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.001878 | south | Y | 0.0097725 | -0.00018827 | -0.050283 | 0.0039299 | 0.00018827 | south | N | 0.00018827 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.001878 | south | Y | 0.0097725 | -0.00018827 | -0.050283 | 0.0039299 | 0.00018827 | south | N | 0.00018827 | 0
7020 | L_AUSTPL | 1 | 8 | 0.002334 | south | N | 0.010229 | 0.00026773 | -0.049827 | 0.0043859 | 0.00026773 | south | N | 0.00026773 | 0
7020 | L_AUSTPL | 2 | 8 | 0.002334 | south | N | 0.010229 | 0.00026773 | -0.049827 | 0.0043859 | 0.00026773 | south | N | 0.00026773 | 0
7022 | L_BUCHAN | 1 | 18 | 0.024742 | south | N | 0.032637 | 0.022676 | -0.027419 | 0.026794 | 0.022676 | south | N | 0.022676 | 0
7023 | L_BUCHAN | 2 | 18 | 0.024742 | south | N | 0.032637 | 0.022676 | -0.027419 | 0.026794 | 0.022676 | south | N | 0.022676 | 0
7024 | L_BUCHAN | 3 | 15 | 0.024742 | south | N | 0.032637 | 0.022676 | -0.027419 | 0.026794 | 0.022676 | south | N | 0.022676 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.022374 | south | N | 0.030269 | 0.020308 | -0.029787 | 0.024426 | 0.020308 | south | N | 0.020308 | 0
7028 | L_MARBFA | 1 | 18 | 0.013922 | south | N | 0.021817 | 0.011856 | -0.038239 | 0.015974 | 0.011856 | south | N | 0.011856 | 0
7029 | L_MARBFA | 2 | 18 | 0.013922 | south | N | 0.021817 | 0.011856 | -0.038239 | 0.015974 | 0.011856 | south | N | 0.011856 | 0
7031 | L_MARSFO | 1 | 35 | 0.006224 | south | N | 0.014119 | 0.0041577 | -0.045937 | 0.0082759 | 0.0041577 | south | N | 0.0041577 | 0
7032 | L_MARSFO | 2 | 34 | 0.006224 | south | N | 0.014119 | 0.0041577 | -0.045937 | 0.0082759 | 0.0041577 | south | N | 0.0041577 | 0
7033 | L_MARSFO | 3 | 35 | 0.006224 | south | N | 0.014119 | 0.0041577 | -0.045937 | 0.0082759 | 0.0041577 | south | N | 0.0041577 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.017285 | south | N | 0.02518 | 0.015219 | -0.034876 | 0.019337 | 0.015219 | south | N | 0.015219 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.017285 | south | N | 0.02518 | 0.015219 | -0.034876 | 0.019337 | 0.015219 | south | N | 0.015219 | 0
7038 | L_DELAWA | 1 | 35 | 0.05466 | west | Y | 0.062555 | 0.052594 | 0.0024989 | 0.056712 | 0.0024989 | west | N | 0.0024989 | 0
7038 | L_DELAWA | 2 | 30 | 0.05466 | west | Y | 0.062555 | 0.052594 | 0.0024989 | 0.056712 | 0.0024989 | west | N | 0.0024989 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.000723 | south | Y | 0.0086175 | -0.0013433 | -0.051438 | 0.0027749 | 0.0013433 | south | N | 0.0013433 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.000723 | south | Y | 0.0086175 | -0.0013433 | -0.051438 | 0.0027749 | 0.0013433 | south | N | 0.0013433 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.000723 | south | Y | 0.0086175 | -0.0013433 | -0.051438 | 0.0027749 | 0.0013433 | south | N | 0.0013433 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.000723 | south | Y | 0.0086175 | -0.0013433 | -0.051438 | 0.0027749 | 0.0013433 | south | N | 0.0013433 | 0
7487 | L_CANYHY | 1 | 6 | 0.002777 | south | N | 0.010672 | 0.00071073 | -0.049384 | 0.0048289 | 0.00071073 | south | N | 0.00071073 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.002074 | south | N | 0.0099685 | 7.7341e-06 | -0.050087 | 0.0041259 | 7.7341e-06 | south | N | 7.7341e-06 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.002074 | south | N | 0.0099685 | 7.7341e-06 | -0.050087 | 0.0041259 | 7.7341e-06 | south | N | 7.7341e-06 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.002074 | south | N | 0.0099685 | 7.7341e-06 | -0.050087 | 0.0041259 | 7.7341e-06 | south | N | 7.7341e-06 | 0
7609 | L_SCHUMA | 1 | 4 | 0.002234 | south | N | 0.010129 | 0.00016773 | -0.049927 | 0.0042859 | 0.00016773 | south | N | 0.00016773 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.001796 | south | N | 0.0096905 | -0.00027027 | -0.050365 | 0.0038479 | 0.00027027 | south | N | 0.00027027 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.001796 | south | N | 0.0096905 | -0.00027027 | -0.050365 | 0.0038479 | 0.00027027 | south | N | 0.00027027 | 0
7800 | L_GUADGE | 1 | 147 | 0.002035 | south | Y | 0.0099295 | -3.1266e-05 | -0.050126 | 0.0040869 | 3.1266e-05 | south | N | 3.1266e-05 | 0
7801 | L_GUADGE | 2 | 138 | 0.002035 | south | Y | 0.0099295 | -3.1266e-05 | -0.050126 | 0.0040869 | 3.1266e-05 | south | N | 3.1266e-05 | 0
7802 | L_GUADGE | 3 | 140 | 0.002035 | south | Y | 0.0099295 | -3.1266e-05 | -0.050126 | 0.0040869 | 3.1266e-05 | south | N | 3.1266e-05 | 0
7803 | L_GUADGE | 4 | 147 | 0.002035 | south | Y | 0.0099295 | -3.1266e-05 | -0.050126 | 0.0040869 | 3.1266e-05 | south | N | 3.1266e-05 | 0
7804 | L_GUADGE | 5 | 182 | 0.002035 | south | Y | 0.0099295 | -3.1266e-05 | -0.050126 | 0.0040869 | 3.1266e-05 | south | N | 3.1266e-05 | 0
7805 | L_GUADGE | 6 | 198 | 0.002035 | south | Y | 0.0099295 | -3.1266e-05 | -0.050126 | 0.0040869 | 3.1266e-05 | south | N | 3.1266e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.000759 | south | Y | 0.0086535 | -0.0013073 | -0.051402 | 0.0028109 | 0.0013073 | south | N | 0.0013073 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.000759 | south | Y | 0.0086535 | -0.0013073 | -0.051402 | 0.0028109 | 0.0013073 | south | N | 0.0013073 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.000759 | south | Y | 0.0086535 | -0.0013073 | -0.051402 | 0.0028109 | 0.0013073 | south | N | 0.0013073 | 0
7810 | L_RIONOG | 1 | 142 | 0.001955 | south | Y | 0.0098495 | -0.00011127 | -0.050206 | 0.0040069 | 0.00011127 | south | N | 0.00011127 | 0
7811 | L_RIONOG | 2 | 145 | 0.001955 | south | Y | 0.0098495 | -0.00011127 | -0.050206 | 0.0040069 | 0.00011127 | south | N | 0.00011127 | 0
7812 | L_RIONOG | 3 | 151 | 0.001955 | south | Y | 0.0098495 | -0.00011127 | -0.050206 | 0.0040069 | 0.00011127 | south | N | 0.00011127 | 0
7813 | L_RIONOG | 4 | 290 | 0.001955 | south | Y | 0.0098495 | -0.00011127 | -0.050206 | 0.0040069 | 0.00011127 | south | N | 0.00011127 | 0
8032 | AMISTADH | 1 | 33 | 0.024952 | south | N | 0.032847 | 0.022886 | -0.027209 | 0.027004 | 0.022886 | south | N | 0.022886 | 0
8033 | AMISTADH | 2 | 25 | 0.024952 | south | N | 0.032847 | 0.022886 | -0.027209 | 0.027004 | 0.022886 | south | N | 0.022886 | 0
8048 | FALCONHY | 1 | 12 | 0.002627 | south | N | 0.010522 | 0.00056073 | -0.049534 | 0.0046789 | 0.00056073 | south | N | 0.00056073 | 0
8066 | DUP1V#1 | 1 | 73 | 0.001251 | south | N | 0.0091455 | -0.00081527 | -0.05091 | 0.0033029 | 0.00081527 | south | N | 0.00081527 | 0
8134 | FOR69CG0 | 1 | 79 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
8138 | FOR69CG0 | 2 | 81 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.0020663 | 0
8147 | UCAR #2 | 10 | 28 | 0.001122 | south | N | 0.0090165 | -0.00094427 | -0.051039 | 0.0031739 | 0.00094427 | south | N | 0.00094427 | 0
8148 | UCAR #1 | 2 | 7 | 0.001122 | south | N | 0.0090165 | -0.00094427 | -0.051039 | 0.0031739 | 0.00094427 | south | N | 0.00094427 | 0
8153 | FOR69CG0 | 3 | 79 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
8154 | FOR69CG0 | 4 | 80 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
8156 | FOR69CG0 | 6 | 25 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
8157 | FOR69CG0 | 7 | 46 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
8161 | COLETOU1 | 1 | 629 | 0.001705 | south | Y | 0.0095995 | -0.00036127 | -0.050456 | 0.0037569 | 0.00036127 | south | N | 0.00036127 | 0
8173 | VICEC51A | 5 | 144 | 0.001304 | south | Y | 0.0091985 | -0.00076227 | -0.050857 | 0.0033559 | 0.00076227 | south | N | 0.00076227 | 0
8174 | VICEC61A | 6 | 188 | 0.001304 | south | Y | 0.0091985 | -0.00076227 | -0.050857 | 0.0033559 | 0.00076227 | south | N | 0.00076227 | 0
8189 | CUERO 2 | 1 | 12 | 0.001634 | south | N | 0.0095285 | -0.00043227 | -0.050527 | 0.0036859 | 0.00043227 | south | N | 0.00043227 | 0
8262 | ELPS | 1 | 6 | 0.01871 | south | N | 0.026605 | 0.016644 | -0.033451 | 0.020762 | 0.016644 | south | N | 0.016644 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.0020663 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.0020663 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.0020663 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.0020663 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.0020663 | 0
8442 | NBEC71A | 1 | 336 | 0.001634 | south | Y | 0.0095285 | -0.00043227 | -0.050527 | 0.0036859 | 0.00043227 | south | N | 0.00043227 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.0020663 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | 0.0078945 | -0.0020663 | -0.052161 | 0.0020519 | 0.0020519 | houston | Y | 0.0020663 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.001651 | south | Y | 0.0095455 | -0.00041527 | -0.05051 | 0.0037029 | 0.00041527 | south | N | 0.00041527 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.001651 | south | Y | 0.0095455 | -0.00041527 | -0.05051 | 0.0037029 | 0.00041527 | south | N | 0.00041527 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.001669 | south | N | 0.0095635 | -0.00039727 | -0.050492 | 0.0037209 | 0.00039727 | south | N | 0.00039727 | 0
8506 | VAL #1 | 1 | 25 | 0.001659 | south | N | 0.0095535 | -0.00040727 | -0.050502 | 0.0037109 | 0.00040727 | south | N | 0.00040727 | 0
8507 | VAL #2 | 2 | 25 | 0.001659 | south | N | 0.0095535 | -0.00040727 | -0.050502 | 0.0037109 | 0.00040727 | south | N | 0.00040727 | 0
8511 | OXY_CC0A | 1 | 38 | 0.001662 | south | N | 0.0095565 | -0.00040427 | -0.050499 | 0.0037139 | 0.00040427 | south | N | 0.00040427 | 0
8517 | CELANEBI | 1 | 29 | 0.001714 | south | N | 0.0096085 | -0.00035227 | -0.050447 | 0.0037659 | 0.00035227 | south | N | 0.00035227 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.001635 | south | N | 0.0095295 | -0.00043127 | -0.050526 | 0.0036869 | 0.00043127 | south | N | 0.00043127 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.001635 | south | N | 0.0095295 | -0.00043127 | -0.050526 | 0.0036869 | 0.00043127 | south | N | 0.00043127 | 0
8562 | CNOPST1 | 3 | 153 | 0.001635 | south | N | 0.0095295 | -0.00043127 | -0.050526 | 0.0036869 | 0.00043127 | south | N | 0.00043127 | 0
8926 | LGE_GT10 | 1 | 158 | 0.001548 | south | N | 0.0094425 | -0.00051827 | -0.050613 | 0.0035999 | 0.00051827 | south | N | 0.00051827 | 0
8927 | LGE_GT20 | 2 | 153 | 0.001548 | south | N | 0.0094425 | -0.00051827 | -0.050613 | 0.0035999 | 0.00051827 | south | N | 0.00051827 | 0
8928 | LGE_STG0 | 3 | 100 | 0.001548 | south | N | 0.0094425 | -0.00051827 | -0.050613 | 0.0035999 | 0.00051827 | south | N | 0.00051827 | 0
8930 | ICPGN10A | 1 | 145 | 0.001548 | south | N | 0.0094425 | -0.00051827 | -0.050613 | 0.0035999 | 0.00051827 | south | N | 0.00051827 | 0
8931 | ICPGN20A | 2 | 147 | 0.001548 | south | N | 0.0094425 | -0.00051827 | -0.050613 | 0.0035999 | 0.00051827 | south | N | 0.00051827 | 0
8932 | ICPGN30A | 3 | 127 | 0.001548 | south | N | 0.0094425 | -0.00051827 | -0.050613 | 0.0035999 | 0.00051827 | south | N | 0.00051827 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.001956 | south | Y | 0.0098505 | -0.00011027 | -0.050205 | 0.0040079 | 0.00011027 | south | N | 0.00011027 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.001956 | south | Y | 0.0098505 | -0.00011027 | -0.050205 | 0.0040079 | 0.00011027 | south | N | 0.00011027 | 0
8935 | FGNTS201 | 3 | 173 | 0.001956 | south | Y | 0.0098505 | -0.00011027 | -0.050205 | 0.0040079 | 0.00011027 | south | N | 0.00011027 | 0
8936 | MVGN#1 | 1 | 207 | 0.001844 | south | Y | 0.0097385 | -0.00022227 | -0.050317 | 0.0038959 | 0.00022227 | south | N | 0.00022227 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.001844 | south | Y | 0.0097385 | -0.00022227 | -0.050317 | 0.0038959 | 0.00022227 | south | N | 0.00022227 | 0
8938 | MVGN#3 | 3 | 242 | 0.001844 | south | Y | 0.0097385 | -0.00022227 | -0.050317 | 0.0038959 | 0.00022227 | south | N | 0.00022227 | 0
8981 | HECN1 | 1 | 144 | 0.001844 | south | Y | 0.0097385 | -0.00022227 | -0.050317 | 0.0038959 | 0.00022227 | south | N | 0.00022227 | 0
8982 | HECN2 | 2 | 144 | 0.001844 | south | Y | 0.0097385 | -0.00022227 | -0.050317 | 0.0038959 | 0.00022227 | south | N | 0.00022227 | 0
8983 | HECN3 | 3 | 171 | 0.001844 | south | Y | 0.0097385 | -0.00022227 | -0.050317 | 0.0038959 | 0.00022227 | south | N | 0.00022227 | 0
9000 | DECKR_G1 | 1 | 310 | 0.00201 | south | Y | 0.0099045 | -5.6266e-05 | -0.050151 | 0.0040619 | 5.6266e-05 | south | N | 5.6266e-05 | 0
9001 | DECKR_G2 | 2 | 413 | 0.00201 | south | Y | 0.0099045 | -5.6266e-05 | -0.050151 | 0.0040619 | 5.6266e-05 | south | N | 5.6266e-05 | 0
9002 | DECKR_G3 | 3 | 42 | 0.0018 | south | Y | 0.0096945 | -0.00026627 | -0.050361 | 0.0038519 | 0.00026627 | south | N | 0.00026627 | 0
9003 | DECKR_G4 | 4 | 44 | 0.0018 | south | Y | 0.0096945 | -0.00026627 | -0.050361 | 0.0038519 | 0.00026627 | south | N | 0.00026627 | 0
9004 | DECKR_G5 | 5 | 44 | 0.0018 | south | Y | 0.0096945 | -0.00026627 | -0.050361 | 0.0038519 | 0.00026627 | south | N | 0.00026627 | 0
9005 | DECKR_G6 | 6 | 47 | 0.0018 | south | Y | 0.0096945 | -0.00026627 | -0.050361 | 0.0038519 | 0.00026627 | south | N | 0.00026627 | 0
9016 | SANDH_G1 | 1 | 49 | 0.002021 | south | Y | 0.0099155 | -4.5266e-05 | -0.05014 | 0.0040729 | 4.5266e-05 | south | N | 4.5266e-05 | 0
9017 | SANDH_G2 | 2 | 46 | 0.002021 | south | Y | 0.0099155 | -4.5266e-05 | -0.05014 | 0.0040729 | 4.5266e-05 | south | N | 4.5266e-05 | 0
9018 | SANDH_G3 | 3 | 46 | 0.002021 | south | Y | 0.0099155 | -4.5266e-05 | -0.05014 | 0.0040729 | 4.5266e-05 | south | N | 4.5266e-05 | 0
9019 | SANDH_G4 | 4 | 47 | 0.002021 | south | Y | 0.0099155 | -4.5266e-05 | -0.05014 | 0.0040729 | 4.5266e-05 | south | N | 4.5266e-05 | 0
9020 | SANDHG5A | 5A | 154 | 0.002021 | south | Y | 0.0099155 | -4.5266e-05 | -0.05014 | 0.0040729 | 4.5266e-05 | south | N | 4.5266e-05 | 0
9021 | SANDHG5C | 5C | 148 | 0.002021 | south | Y | 0.0099155 | -4.5266e-05 | -0.05014 | 0.0040729 | 4.5266e-05 | south | N | 4.5266e-05 | 0
9022 | SANDH_G6 | 6 | 48 | 0.002021 | south | Y | 0.0099155 | -4.5266e-05 | -0.05014 | 0.0040729 | 4.5266e-05 | south | N | 4.5266e-05 | 0
9023 | SANDH_G7 | 7 | 48 | 0.002021 | south | Y | 0.0099155 | -4.5266e-05 | -0.05014 | 0.0040729 | 4.5266e-05 | south | N | 4.5266e-05 | 0
11001 | NAV1CT | 1 | 70 | 0.054196 | west | Y | 0.062091 | 0.05213 | 0.0020349 | 0.056248 | 0.0020349 | west | N | 0.0020349 | 0
11009 | NAV2CT | 1 | 70 | 0.054196 | west | Y | 0.062091 | 0.05213 | 0.0020349 | 0.056248 | 0.0020349 | west | N | 0.0020349 | 0
11011 | NAV3ST | 1 | 92.8 | 0.054196 | west | Y | 0.062091 | 0.05213 | 0.0020349 | 0.056248 | 0.0020349 | west | N | 0.0020349 | 0
11012 | NAV4CT | 1 | 80 | 0.054196 | west | Y | 0.062091 | 0.05213 | 0.0020349 | 0.056248 | 0.0020349 | west | N | 0.0020349 | 0
11013 | NAV5CT | 1 | 80 | 0.054196 | west | Y | 0.062091 | 0.05213 | 0.0020349 | 0.056248 | 0.0020349 | west | N | 0.0020349 | 0
11014 | NAV6ST | 1 | 115 | 0.054196 | west | Y | 0.062091 | 0.05213 | 0.0020349 | 0.056248 | 0.0020349 | west | N | 0.0020349 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.054202 | west | Y | 0.062097 | 0.052136 | 0.0020409 | 0.056254 | 0.0020409 | west | N | 0.0020409 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.054202 | west | Y | 0.062097 | 0.052136 | 0.0020409 | 0.056254 | 0.0020409 | west | N | 0.0020409 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.054202 | west | Y | 0.062097 | 0.052136 | 0.0020409 | 0.056254 | 0.0020409 | west | N | 0.0020409 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.054202 | west | Y | 0.062097 | 0.052136 | 0.0020409 | 0.056254 | 0.0020409 | west | N | 0.0020409 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.054202 | west | Y | 0.062097 | 0.052136 | 0.0020409 | 0.056254 | 0.0020409 | west | N | 0.0020409 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.054202 | west | Y | 0.062097 | 0.052136 | 0.0020409 | 0.056254 | 0.0020409 | west | N | 0.0020409 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.048463 | west | Y | 0.056358 | 0.046397 | -0.0036981 | 0.050515 | 0.0036981 | west | N | 0.0036981 | 0
11057 | CHAMPION | 1 | 126.5 | 0.048463 | west | Y | 0.056358 | 0.046397 | -0.0036981 | 0.050515 | 0.0036981 | west | N | 0.0036981 | 0
11058 | PYRON_1G | 1 | 249 | 0.048463 | west | Y | 0.056358 | 0.046397 | -0.0036981 | 0.050515 | 0.0036981 | west | N | 0.0036981 | 0
11059 | INADALE_ | 1 | 197 | 0.048463 | west | Y | 0.056358 | 0.046397 | -0.0036981 | 0.050515 | 0.0036981 | west | N | 0.0036981 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.053656 | west | Y | 0.061551 | 0.05159 | 0.0014949 | 0.055708 | 0.0014949 | west | N | 0.0014949 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.053656 | west | Y | 0.061551 | 0.05159 | 0.0014949 | 0.055708 | 0.0014949 | west | N | 0.0014949 | 0
11147 | NOTREES_ | 1 | 149 | 0.054453 | west | Y | 0.062348 | 0.052387 | 0.0022919 | 0.056505 | 0.0022919 | west | N | 0.0022919 | 0
11309 | BULLCREK | 1 | 180 | 0.052217 | west | Y | 0.060112 | 0.050151 | 5.5949e-05 | 0.054269 | 5.5949e-05 | west | N | 5.5949e-05 | 0
11310 | BULLCREK | 1 | 180 | 0.052217 | west | Y | 0.060112 | 0.050151 | 5.5949e-05 | 0.054269 | 5.5949e-05 | west | N | 5.5949e-05 | 0
11320 | COYOTE_1 | 1 | 225 | 0.052318 | west | Y | 0.060213 | 0.050252 | 0.00015695 | 0.05437 | 0.00015695 | west | N | 0.00015695 | 0
11415 | LORAINE_ | 1 | 125 | 0.051457 | west | Y | 0.059352 | 0.049391 | -0.00070405 | 0.053509 | 0.00070405 | west | N | 0.00070405 | 0
11416 | LORAINE_ | 1 | 125 | 0.051457 | west | Y | 0.059352 | 0.049391 | -0.00070405 | 0.053509 | 0.00070405 | west | N | 0.00070405 | 0
11691 | KMICHICT | 1 | 140 | -0.005501 | north | N | 0.0023935 | -0.0075673 | -0.057662 | -0.0034491 | 0.0023935 | North | N | 0.0023935 | 0
11692 | KMICHICT | 2 | 141 | -0.005501 | north | N | 0.0023935 | -0.0075673 | -0.057662 | -0.0034491 | 0.0023935 | North | N | 0.0023935 | 0
11693 | KMICHIST | 3 | 309 | -0.005501 | north | N | 0.0023935 | -0.0075673 | -0.057662 | -0.0034491 | 0.0023935 | North | N | 0.0023935 | 0
11694 | KMICHICT | 4 | 143 | -0.005501 | north | N | 0.0023935 | -0.0075673 | -0.057662 | -0.0034491 | 0.0023935 | North | N | 0.0023935 | 0
11695 | KMICHICT | 5 | 144 | -0.005501 | north | N | 0.0023935 | -0.0075673 | -0.057662 | -0.0034491 | 0.0023935 | North | N | 0.0023935 | 0
11696 | KMICHIST | 6 | 310 | -0.005501 | north | N | 0.0023935 | -0.0075673 | -0.057662 | -0.0034491 | 0.0023935 | North | N | 0.0023935 | 0
12322 | ENNSTRAC | 1 | 196 | -0.008224 | north | Y | -0.00032949 | -0.01029 | -0.060385 | -0.0061721 | 0.00032949 | North | N | 0.00032949 | 0
12323 | ENNSTRAC | 2 | 111 | -0.008224 | north | Y | -0.00032949 | -0.01029 | -0.060385 | -0.0061721 | 0.00032949 | North | N | 0.00032949 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.005415 | north | N | 0.0024795 | -0.0074813 | -0.057576 | -0.0033631 | 0.0024795 | North | N | 0.0024795 | 0
12411 | FPLEFR1A | 1 | 161 | -0.005816 | north | Y | 0.0020785 | -0.0078823 | -0.057977 | -0.0037641 | 0.0020785 | North | N | 0.0020785 | 0
12412 | FPLEFR1B | 2 | 164 | -0.005816 | north | Y | 0.0020785 | -0.0078823 | -0.057977 | -0.0037641 | 0.0020785 | North | N | 0.0020785 | 0
12413 | FPLEFR1C | 3 | 164 | -0.005816 | north | Y | 0.0020785 | -0.0078823 | -0.057977 | -0.0037641 | 0.0020785 | North | N | 0.0020785 | 0
12414 | FPLEFR1S | 4 | 414 | -0.005816 | north | Y | 0.0020785 | -0.0078823 | -0.057977 | -0.0037641 | 0.0020785 | North | N | 0.0020785 | 0
12421 | FPLEFR2A | 1 | 162 | -0.005816 | north | Y | 0.0020785 | -0.0078823 | -0.057977 | -0.0037641 | 0.0020785 | North | N | 0.0020785 | 0
12422 | FPLEFR2B | 2 | 161 | -0.005816 | north | Y | 0.0020785 | -0.0078823 | -0.057977 | -0.0037641 | 0.0020785 | North | N | 0.0020785 | 0
12423 | FPLEFR2C | 3 | 163 | -0.005816 | north | Y | 0.0020785 | -0.0078823 | -0.057977 | -0.0037641 | 0.0020785 | North | N | 0.0020785 | 0
12424 | FPLEFR2S | 4 | 409 | -0.005816 | north | Y | 0.0020785 | -0.0078823 | -0.057977 | -0.0037641 | 0.0020785 | North | N | 0.0020785 | 0
12440 | PARKD_1S | 1 | 0 | -0.005937 | north | N | 0.0019575 | -0.0080033 | -0.058098 | -0.0038851 | 0.0019575 | North | N | 0.0019575 | 0
12449 | PARKD_2S | 1 | 0 | -0.005937 | north | N | 0.0019575 | -0.0080033 | -0.058098 | -0.0038851 | 0.0019575 | North | N | 0.0019575 | 0
13116 | TGATEWAY | 1 | 148 | -0.006009 | north | N | 0.0018855 | -0.0080753 | -0.05817 | -0.0039571 | 0.0018855 | North | N | 0.0018855 | 0
13117 | TGATEWAY | 2 | 130 | -0.006009 | north | N | 0.0018855 | -0.0080753 | -0.05817 | -0.0039571 | 0.0018855 | North | N | 0.0018855 | 0
13118 | TGATEWAY | 3 | 145 | -0.006009 | north | N | 0.0018855 | -0.0080753 | -0.05817 | -0.0039571 | 0.0018855 | North | N | 0.0018855 | 0
13119 | TGATEWAY | 4 | 399 | -0.006009 | north | N | 0.0018855 | -0.0080753 | -0.05817 | -0.0039571 | 0.0018855 | North | N | 0.0018855 | 0
13131 | CALFREST | 1 | 150.7 | -0.006027 | north | Y | 0.0018675 | -0.0080933 | -0.058188 | -0.0039751 | 0.0018675 | North | N | 0.0018675 | 0
13132 | CALFREST | 2 | 151 | -0.006027 | north | Y | 0.0018675 | -0.0080933 | -0.058188 | -0.0039751 | 0.0018675 | North | N | 0.0018675 | 0
13133 | CALFREST | 3 | 177.4 | -0.006027 | north | Y | 0.0018675 | -0.0080933 | -0.058188 | -0.0039751 | 0.0018675 | North | N | 0.0018675 | 0
13134 | CALFREST | 4 | 151.5 | -0.006042 | north | Y | 0.0018525 | -0.0081083 | -0.058203 | -0.0039901 | 0.0018525 | North | N | 0.0018525 | 0
13135 | CALFREST | 5 | 152.3 | -0.006042 | north | Y | 0.0018525 | -0.0081083 | -0.058203 | -0.0039901 | 0.0018525 | North | N | 0.0018525 | 0
13136 | CALFREST | 6 | 177.5 | -0.006042 | north | Y | 0.0018525 | -0.0081083 | -0.058203 | -0.0039901 | 0.0018525 | North | N | 0.0018525 | 0
13432 | SANDOW_5 | 5 | 581 | -0.001823 | south | Y | 0.0060715 | -0.0038893 | -0.053984 | 0.00022891 | 0.00022891 | houston | Y | 0.0038893 | 2.1267
13691 | OAKGROVE | 1 | 855 | -0.005075 | north | Y | 0.0028195 | -0.0071413 | -0.057236 | -0.0030231 | 0.0028195 | North | N | 0.0028195 | 0
13692 | OAKGROVE | 2 | 855 | -0.005075 | north | Y | 0.0028195 | -0.0071413 | -0.057236 | -0.0030231 | 0.0028195 | North | N | 0.0028195 | 0
32798 | BRYN_TAM | 1 | 32 | -0.004365 | north | N | 0.0035295 | -0.0064313 | -0.056526 | -0.0023131 | 0.0023131 | houston | Y | 0.0035295 | 0
32883 | BRYN_DNS | 1 | 48 | -0.004393 | north | Y | 0.0035015 | -0.0064593 | -0.056554 | -0.0023411 | 0.0023411 | houston | Y | 0.0035015 | 0.0557
32884 | BRYN_DNS | 1 | 46 | -0.004393 | north | Y | 0.0035015 | -0.0064593 | -0.056554 | -0.0023411 | 0.0023411 | houston | Y | 0.0035015 | 0.053379
32886 | BRYN_ATK | MB | 12 | -0.004373 | north | Y | 0.0035215 | -0.0064393 | -0.056534 | -0.0023211 | 0.0023211 | houston | Y | 0.0035215 | 0
32887 | BRYN_ATK | MB | 51 | -0.004373 | north | Y | 0.0035215 | -0.0064393 | -0.056534 | -0.0023211 | 0.0023211 | houston | Y | 0.0035215 | 0
32888 | BRYN_ATK | 1 | 17 | -0.004373 | north | Y | 0.0035215 | -0.0064393 | -0.056534 | -0.0023211 | 0.0023211 | houston | Y | 0.0035215 | 0.020407
32890 | BRYN_ATK | MB | 22 | -0.004373 | north | Y | 0.0035215 | -0.0064393 | -0.056534 | -0.0023211 | 0.0023211 | houston | Y | 0.0035215 | 0
32891 | BRYN_ATK | MB | 25 | -0.004373 | north | Y | 0.0035215 | -0.0064393 | -0.056534 | -0.0023211 | 0.0023211 | houston | Y | 0.0035215 | 0
32892 | BRYN_DNS | 1 | 105 | -0.004393 | north | Y | 0.0035015 | -0.0064593 | -0.056554 | -0.0023411 | 0.0023411 | houston | Y | 0.0035015 | 0.12184
36998 | RDCNYNG1 | 1 | 84 | 0.049922 | west | Y | 0.057817 | 0.047856 | -0.0022391 | 0.051974 | 0.0022391 | west | N | 0.0022391 | 0
38332 | WDWRDU2 | 1 | 80 | 0.058117 | west | Y | 0.066012 | 0.056051 | 0.0059559 | 0.060169 | 0.0059559 | west | N | 0.0059559 | 0
38437 | TNSRBNMS | 1 | 150 | 0.058148 | west | Y | 0.066043 | 0.056082 | 0.0059869 | 0.0602 | 0.0059869 | west | N | 0.0059869 | 0
38438 | TNSRBNMS | 1 | 150 | 0.058148 | west | Y | 0.066043 | 0.056082 | 0.0059869 | 0.0602 | 0.0059869 | west | N | 0.0059869 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.001994 | houston | N | 0.0059005 | -0.0040603 | -0.054155 | 5.7905e-05 | 5.7905e-05 | houston | N | 5.7905e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.001994 | houston | N | 0.0059005 | -0.0040603 | -0.054155 | 5.7905e-05 | 5.7905e-05 | houston | N | 5.7905e-05 | 0
38600 | TNBP_CGN | 5 | 53 | -0.001994 | houston | N | 0.0059005 | -0.0040603 | -0.054155 | 5.7905e-05 | 5.7905e-05 | houston | N | 5.7905e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.001994 | houston | N | 0.0059005 | -0.0040603 | -0.054155 | 5.7905e-05 | 5.7905e-05 | houston | N | 5.7905e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.001994 | houston | N | 0.0059005 | -0.0040603 | -0.054155 | 5.7905e-05 | 5.7905e-05 | houston | N | 5.7905e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.001994 | houston | N | 0.0059005 | -0.0040603 | -0.054155 | 5.7905e-05 | 5.7905e-05 | houston | N | 5.7905e-05 | 0
38614 | TNBPAMCG | 4 | 96 | -0.001994 | houston | N | 0.0059005 | -0.0040603 | -0.054155 | 5.7905e-05 | 5.7905e-05 | houston | N | 5.7905e-05 | 0
38615 | TNBPAMCG | 1 | 244 | -0.001994 | houston | N | 0.0059005 | -0.0040603 | -0.054155 | 5.7905e-05 | 5.7905e-05 | houston | N | 5.7905e-05 | 0
38690 | TNBP_CGN | 3 | 40 | -0.001994 | houston | N | 0.0059005 | -0.0040603 | -0.054155 | 5.7905e-05 | 5.7905e-05 | houston | N | 5.7905e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.001993 | houston | N | 0.0059015 | -0.0040593 | -0.054154 | 5.8905e-05 | 5.8905e-05 | houston | N | 5.8905e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.001993 | houston | N | 0.0059015 | -0.0040593 | -0.054154 | 5.8905e-05 | 5.8905e-05 | houston | N | 5.8905e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.001993 | houston | N | 0.0059015 | -0.0040593 | -0.054154 | 5.8905e-05 | 5.8905e-05 | houston | N | 5.8905e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.001993 | houston | N | 0.0059015 | -0.0040593 | -0.054154 | 5.8905e-05 | 5.8905e-05 | houston | N | 5.8905e-05 | 0
39470 | TNDOWCGN | 1 | 32 | -0.001993 | houston | N | 0.0059015 | -0.0040593 | -0.054154 | 5.8905e-05 | 5.8905e-05 | houston | N | 5.8905e-05 | 0
39480 | TNDOWCGN | 1 | 30 | -0.001993 | houston | N | 0.0059015 | -0.0040593 | -0.054154 | 5.8905e-05 | 5.8905e-05 | houston | N | 5.8905e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.0015 | houston | N | 0.0063945 | -0.0035663 | -0.053661 | 0.00055191 | 0.00055191 | houston | N | 0.00055191 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.0015 | houston | N | 0.0063945 | -0.0035663 | -0.053661 | 0.00055191 | 0.00055191 | houston | N | 0.00055191 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.0015 | houston | N | 0.0063945 | -0.0035663 | -0.053661 | 0.00055191 | 0.00055191 | houston | N | 0.00055191 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.0015 | houston | N | 0.0063945 | -0.0035663 | -0.053661 | 0.00055191 | 0.00055191 | houston | N | 0.00055191 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.005075 | north | Y | 0.0028195 | -0.0071413 | -0.057236 | -0.0030231 | 0.0028195 | North | N | 0.0028195 | 0
39970 | TNTNPONE | 1 | 153 | -0.005075 | north | Y | 0.0028195 | -0.0071413 | -0.057236 | -0.0030231 | 0.0028195 | North | N | 0.0028195 | 0
48500 | APD_GT1_ | 1 | 136 | -0.002292 | houston | N | 0.0056025 | -0.0043583 | -0.054453 | -0.00024009 | 0.00024009 | houston | N | 0.00024009 | 0
48510 | AK_GT1__ | 1 | 33 | -0.001829 | houston | N | 0.0060655 | -0.0038953 | -0.05399 | 0.00022291 | 0.00022291 | houston | N | 0.00022291 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.002291 | houston | Y | 0.0056035 | -0.0043573 | -0.054452 | -0.00023909 | 0.00023909 | houston | N | 0.00023909 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.002291 | houston | Y | 0.0056035 | -0.0043573 | -0.054452 | -0.00023909 | 0.00023909 | houston | N | 0.00023909 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.002291 | houston | Y | 0.0056035 | -0.0043573 | -0.054452 | -0.00023909 | 0.00023909 | houston | N | 0.00023909 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.002291 | houston | Y | 0.0056035 | -0.0043573 | -0.054452 | -0.00023909 | 0.00023909 | houston | N | 0.00023909 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.001409 | houston | N | 0.0064855 | -0.0034753 | -0.05357 | 0.00064291 | 0.00064291 | houston | N | 0.00064291 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.001409 | houston | N | 0.0064855 | -0.0034753 | -0.05357 | 0.00064291 | 0.00064291 | houston | N | 0.00064291 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.001814 | houston | N | 0.0060805 | -0.0038803 | -0.053975 | 0.00023791 | 0.00023791 | houston | N | 0.00023791 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.001814 | houston | N | 0.0060805 | -0.0038803 | -0.053975 | 0.00023791 | 0.00023791 | houston | N | 0.00023791 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.001814 | houston | N | 0.0060805 | -0.0038803 | -0.053975 | 0.00023791 | 0.00023791 | houston | N | 0.00023791 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.002179 | houston | N | 0.0057155 | -0.0042453 | -0.05434 | -0.00012709 | 0.00012709 | houston | N | 0.00012709 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.002179 | houston | N | 0.0057155 | -0.0042453 | -0.05434 | -0.00012709 | 0.00012709 | houston | N | 0.00012709 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.002179 | houston | N | 0.0057155 | -0.0042453 | -0.05434 | -0.00012709 | 0.00012709 | houston | N | 0.00012709 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.002179 | houston | N | 0.0057155 | -0.0042453 | -0.05434 | -0.00012709 | 0.00012709 | houston | N | 0.00012709 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.002252 | houston | N | 0.0056425 | -0.0043183 | -0.054413 | -0.00020009 | 0.00020009 | houston | N | 0.00020009 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.002252 | houston | N | 0.0056425 | -0.0043183 | -0.054413 | -0.00020009 | 0.00020009 | houston | N | 0.00020009 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.002158 | houston | N | 0.0057365 | -0.0042243 | -0.054319 | -0.00010609 | 0.00010609 | houston | N | 0.00010609 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.002158 | houston | N | 0.0057365 | -0.0042243 | -0.054319 | -0.00010609 | 0.00010609 | houston | N | 0.00010609 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.002158 | houston | N | 0.0057365 | -0.0042243 | -0.054319 | -0.00010609 | 0.00010609 | houston | N | 0.00010609 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.002158 | houston | N | 0.0057365 | -0.0042243 | -0.054319 | -0.00010609 | 0.00010609 | houston | N | 0.00010609 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.002158 | houston | N | 0.0057365 | -0.0042243 | -0.054319 | -0.00010609 | 0.00010609 | houston | N | 0.00010609 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.00238 | houston | Y | 0.0055145 | -0.0044463 | -0.054541 | -0.00032809 | 0.00032809 | houston | N | 0.00032809 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.002344 | houston | Y | 0.0055505 | -0.0044103 | -0.054505 | -0.00029209 | 0.00029209 | houston | N | 0.00029209 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.00239 | houston | Y | 0.0055045 | -0.0044563 | -0.054551 | -0.00033809 | 0.00033809 | houston | N | 0.00033809 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.00239 | houston | Y | 0.0055045 | -0.0044563 | -0.054551 | -0.00033809 | 0.00033809 | houston | N | 0.00033809 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.00239 | houston | Y | 0.0055045 | -0.0044563 | -0.054551 | -0.00033809 | 0.00033809 | houston | N | 0.00033809 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.002591 | houston | N | 0.0053035 | -0.0046573 | -0.054752 | -0.00053909 | 0.00053909 | houston | N | 0.00053909 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.002299 | houston | N | 0.0055955 | -0.0043653 | -0.05446 | -0.00024709 | 0.00024709 | houston | N | 0.00024709 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.002299 | houston | N | 0.0055955 | -0.0043653 | -0.05446 | -0.00024709 | 0.00024709 | houston | N | 0.00024709 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.002416 | houston | N | 0.0054785 | -0.0044823 | -0.054577 | -0.00036409 | 0.00036409 | houston | N | 0.00036409 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.002416 | houston | N | 0.0054785 | -0.0044823 | -0.054577 | -0.00036409 | 0.00036409 | houston | N | 0.00036409 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.002416 | houston | N | 0.0054785 | -0.0044823 | -0.054577 | -0.00036409 | 0.00036409 | houston | N | 0.00036409 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.002416 | houston | N | 0.0054785 | -0.0044823 | -0.054577 | -0.00036409 | 0.00036409 | houston | N | 0.00036409 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.002254 | houston | N | 0.0056405 | -0.0043203 | -0.054415 | -0.00020209 | 0.00020209 | houston | N | 0.00020209 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.002254 | houston | N | 0.0056405 | -0.0043203 | -0.054415 | -0.00020209 | 0.00020209 | houston | N | 0.00020209 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.002254 | houston | N | 0.0056405 | -0.0043203 | -0.054415 | -0.00020209 | 0.00020209 | houston | N | 0.00020209 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.002254 | houston | N | 0.0056405 | -0.0043203 | -0.054415 | -0.00020209 | 0.00020209 | houston | N | 0.00020209 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.002229 | houston | N | 0.0056655 | -0.0042953 | -0.05439 | -0.00017709 | 0.00017709 | houston | N | 0.00017709 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.002229 | houston | N | 0.0056655 | -0.0042953 | -0.05439 | -0.00017709 | 0.00017709 | houston | N | 0.00017709 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.002229 | houston | N | 0.0056655 | -0.0042953 | -0.05439 | -0.00017709 | 0.00017709 | houston | N | 0.00017709 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.002229 | houston | N | 0.0056655 | -0.0042953 | -0.05439 | -0.00017709 | 0.00017709 | houston | N | 0.00017709 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.002229 | houston | N | 0.0056655 | -0.0042953 | -0.05439 | -0.00017709 | 0.00017709 | houston | N | 0.00017709 | 0
48651 | EP_1_2 | 1 | 5 | -0.002378 | houston | N | 0.0055165 | -0.0044443 | -0.054539 | -0.00032609 | 0.00032609 | houston | N | 0.00032609 | 0
48651 | EP_1_2 | 2 | 21 | -0.002378 | houston | N | 0.0055165 | -0.0044443 | -0.054539 | -0.00032609 | 0.00032609 | houston | N | 0.00032609 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.003968 | north | N | 0.0039265 | -0.0060343 | -0.056129 | -0.0019161 | 0.0019161 | houston | Y | 0.0039265 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.003968 | north | N | 0.0039265 | -0.0060343 | -0.056129 | -0.0019161 | 0.0019161 | houston | Y | 0.0039265 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.003968 | north | N | 0.0039265 | -0.0060343 | -0.056129 | -0.0019161 | 0.0019161 | houston | Y | 0.0039265 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.003968 | north | N | 0.0039265 | -0.0060343 | -0.056129 | -0.0019161 | 0.0019161 | houston | Y | 0.0039265 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.002427 | houston | Y | 0.0054675 | -0.0044933 | -0.054588 | -0.00037509 | 0.00037509 | houston | N | 0.00037509 | 0
48691 | GBY_7374 | A | 46 | -0.002217 | houston | Y | 0.0056775 | -0.0042833 | -0.054378 | -0.00016509 | 0.00016509 | houston | N | 0.00016509 | 0
48691 | GBY_7374 | B | 46 | -0.002217 | houston | Y | 0.0056775 | -0.0042833 | -0.054378 | -0.00016509 | 0.00016509 | houston | N | 0.00016509 | 0
48692 | GBY_8182 | C | 46 | -0.002217 | houston | Y | 0.0056775 | -0.0042833 | -0.054378 | -0.00016509 | 0.00016509 | houston | N | 0.00016509 | 0
48692 | GBY_8182 | D | 55 | -0.002217 | houston | Y | 0.0056775 | -0.0042833 | -0.054378 | -0.00016509 | 0.00016509 | houston | N | 0.00016509 | 0
48693 | GBY_8384 | E | 55 | -0.002217 | houston | Y | 0.0056775 | -0.0042833 | -0.054378 | -0.00016509 | 0.00016509 | houston | N | 0.00016509 | 0
48693 | GBY_8384 | F | 54 | -0.002217 | houston | Y | 0.0056775 | -0.0042833 | -0.054378 | -0.00016509 | 0.00016509 | houston | N | 0.00016509 | 0
48721 | LEG_1___ | 1 | 827 | -0.005407 | north | Y | 0.0024875 | -0.0074733 | -0.057568 | -0.0033551 | 0.0024875 | North | N | 0.0024875 | 0
48722 | LEG_2___ | 2 | 819 | -0.005407 | north | Y | 0.0024875 | -0.0074733 | -0.057568 | -0.0033551 | 0.0024875 | North | N | 0.0024875 | 0
48730 | MNS_GT | 1 | 46.1 | -0.001786 | houston | N | 0.0061085 | -0.0038523 | -0.053947 | 0.00026591 | 0.00026591 | houston | N | 0.00026591 | 0
48731 | CBE_GT1 | 1 | 76 | -0.000802 | houston | Y | 0.0070925 | -0.0028683 | -0.052963 | 0.0012499 | 0.0012499 | houston | N | 0.0012499 | 0
48732 | CBE_GT2 | 1 | 76 | -0.000802 | houston | Y | 0.0070925 | -0.0028683 | -0.052963 | 0.0012499 | 0.0012499 | houston | N | 0.0012499 | 0
48733 | CBE_ST12 | 1 | 105 | -0.000802 | houston | Y | 0.0070925 | -0.0028683 | -0.052963 | 0.0012499 | 0.0012499 | houston | N | 0.0012499 | 0
48734 | CBE_GT3 | 1 | 74 | -0.000802 | houston | Y | 0.0070925 | -0.0028683 | -0.052963 | 0.0012499 | 0.0012499 | houston | N | 0.0012499 | 0
48735 | CBE_GT4 | 1 | 74 | -0.000802 | houston | Y | 0.0070925 | -0.0028683 | -0.052963 | 0.0012499 | 0.0012499 | houston | N | 0.0012499 | 0
48736 | CBE_ST34 | 1 | 102 | -0.000802 | houston | Y | 0.0070925 | -0.0028683 | -0.052963 | 0.0012499 | 0.0012499 | houston | N | 0.0012499 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.002255 | houston | N | 0.0056395 | -0.0043213 | -0.054416 | -0.00020309 | 0.00020309 | houston | N | 0.00020309 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.002255 | houston | N | 0.0056395 | -0.0043213 | -0.054416 | -0.00020309 | 0.00020309 | houston | N | 0.00020309 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.002255 | houston | N | 0.0056395 | -0.0043213 | -0.054416 | -0.00020309 | 0.00020309 | houston | N | 0.00020309 | 0
48761 | PR_GT1__ | 1 | 35 | -0.002241 | houston | N | 0.0056535 | -0.0043073 | -0.054402 | -0.00018909 | 0.00018909 | houston | N | 0.00018909 | 0
48772 | PHR_GN2_ | MB | 459 | -0.002102 | houston | Y | 0.0057925 | -0.0041683 | -0.054263 | -5.0095e-05 | 5.0095e-05 | houston | N | 5.0095e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.002379 | houston | N | 0.0055155 | -0.0044453 | -0.05454 | -0.00032709 | 0.00032709 | houston | N | 0.00032709 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.002379 | houston | N | 0.0055155 | -0.0044453 | -0.05454 | -0.00032709 | 0.00032709 | houston | N | 0.00032709 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.002379 | houston | N | 0.0055155 | -0.0044453 | -0.05454 | -0.00032709 | 0.00032709 | houston | N | 0.00032709 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.002379 | houston | N | 0.0055155 | -0.0044453 | -0.05454 | -0.00032709 | 0.00032709 | houston | N | 0.00032709 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.002379 | houston | N | 0.0055155 | -0.0044453 | -0.05454 | -0.00032709 | 0.00032709 | houston | N | 0.00032709 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.002379 | houston | N | 0.0055155 | -0.0044453 | -0.05454 | -0.00032709 | 0.00032709 | houston | N | 0.00032709 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.002379 | houston | N | 0.0055155 | -0.0044453 | -0.05454 | -0.00032709 | 0.00032709 | houston | N | 0.00032709 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.002591 | houston | N | 0.0053035 | -0.0046573 | -0.054752 | -0.00053909 | 0.00053909 | houston | N | 0.00053909 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.002591 | houston | N | 0.0053035 | -0.0046573 | -0.054752 | -0.00053909 | 0.00053909 | houston | N | 0.00053909 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.002591 | houston | N | 0.0053035 | -0.0046573 | -0.054752 | -0.00053909 | 0.00053909 | houston | N | 0.00053909 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.002591 | houston | N | 0.0053035 | -0.0046573 | -0.054752 | -0.00053909 | 0.00053909 | houston | N | 0.00053909 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.002388 | houston | N | 0.0055065 | -0.0044543 | -0.054549 | -0.00033609 | 0.00033609 | houston | N | 0.00033609 | 0
48820 | SHELLG1_ | 1 | 71 | -0.002268 | houston | N | 0.0056265 | -0.0043343 | -0.054429 | -0.00021609 | 0.00021609 | houston | N | 0.00021609 | 0
48821 | SHELLG2 | 2 | 72 | -0.002268 | houston | N | 0.0056265 | -0.0043343 | -0.054429 | -0.00021609 | 0.00021609 | houston | N | 0.00021609 | 0
48822 | SHELLG3_ | 1 | 39 | -0.002268 | houston | N | 0.0056265 | -0.0043343 | -0.054429 | -0.00021609 | 0.00021609 | houston | N | 0.00021609 | 0
48822 | SHELLG3_ | 2 | 30 | -0.002268 | houston | N | 0.0056265 | -0.0043343 | -0.054429 | -0.00021609 | 0.00021609 | houston | N | 0.00021609 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.00222 | houston | N | 0.0056745 | -0.0042863 | -0.054381 | -0.00016809 | 0.00016809 | houston | N | 0.00016809 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.00222 | houston | N | 0.0056745 | -0.0042863 | -0.054381 | -0.00016809 | 0.00016809 | houston | N | 0.00016809 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.002254 | houston | N | 0.0056405 | -0.0043203 | -0.054415 | -0.00020209 | 0.00020209 | houston | N | 0.00020209 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.002251 | houston | Y | 0.0056435 | -0.0043173 | -0.054412 | -0.00019909 | 0.00019909 | houston | N | 0.00019909 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.00225 | houston | Y | 0.0056445 | -0.0043163 | -0.054411 | -0.00019809 | 0.00019809 | houston | N | 0.00019809 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.002253 | houston | Y | 0.0056415 | -0.0043193 | -0.054414 | -0.00020109 | 0.00020109 | houston | N | 0.00020109 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.002254 | houston | Y | 0.0056405 | -0.0043203 | -0.054415 | -0.00020209 | 0.00020209 | houston | N | 0.00020209 | 0
48855 | SRB_GT21 | B2 | 12 | -0.00225 | houston | Y | 0.0056445 | -0.0043163 | -0.054411 | -0.00019809 | 0.00019809 | houston | N | 0.00019809 | 0
48855 | SRB_GT21 | MB | 18 | -0.00225 | houston | Y | 0.0056445 | -0.0043163 | -0.054411 | -0.00019809 | 0.00019809 | houston | N | 0.00019809 | 0
48865 | TECO_GT1 | 1 | 50 | -0.002063 | houston | Y | 0.0058315 | -0.0041293 | -0.054224 | -1.1095e-05 | 1.1095e-05 | houston | N | 1.1095e-05 | 0
48873 | THW_ST3_ | 3 | 104 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48874 | THW_ST4_ | 4 | 104 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48875 | THW_3132 | A | 54 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48875 | THW_3132 | B | 53 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48877 | THW_3334 | C | 54 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48877 | THW_3334 | D | 57 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48879 | THW_4142 | E | 54 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48879 | THW_4142 | F | 54 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48881 | THW_4344 | G | 58 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48881 | THW_4344 | H | 58 | -0.002337 | houston | Y | 0.0055575 | -0.0044033 | -0.054498 | -0.00028509 | 0.00028509 | houston | N | 0.00028509 | 0
48883 | THW_GT1_ | B2 | 12 | -0.002369 | houston | Y | 0.0055255 | -0.0044353 | -0.05453 | -0.00031709 | 0.00031709 | houston | N | 0.00031709 | 0
48885 | THW_5152 | A | 56 | -0.002443 | houston | Y | 0.0054515 | -0.0045093 | -0.054604 | -0.00039109 | 0.00039109 | houston | N | 0.00039109 | 0
48885 | THW_5152 | B | 59 | -0.002443 | houston | Y | 0.0054515 | -0.0045093 | -0.054604 | -0.00039109 | 0.00039109 | houston | N | 0.00039109 | 0
48886 | THW_5354 | C | 56 | -0.002443 | houston | Y | 0.0054515 | -0.0045093 | -0.054604 | -0.00039109 | 0.00039109 | houston | N | 0.00039109 | 0
48886 | THW_5354 | D | 56 | -0.002443 | houston | Y | 0.0054515 | -0.0045093 | -0.054604 | -0.00039109 | 0.00039109 | houston | N | 0.00039109 | 0
48887 | THW_5556 | E | 59 | -0.002443 | houston | Y | 0.0054515 | -0.0045093 | -0.054604 | -0.00039109 | 0.00039109 | houston | N | 0.00039109 | 0
48887 | THW_5556 | F | 56 | -0.002443 | houston | Y | 0.0054515 | -0.0045093 | -0.054604 | -0.00039109 | 0.00039109 | houston | N | 0.00039109 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.000876 | houston | Y | 0.0070185 | -0.0029423 | -0.053037 | 0.0011759 | 0.0011759 | houston | N | 0.0011759 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.001868 | houston | Y | 0.0060265 | -0.0039343 | -0.054029 | 0.00018391 | 0.00018391 | houston | N | 0.00018391 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.001868 | houston | Y | 0.0060265 | -0.0039343 | -0.054029 | 0.00018391 | 0.00018391 | houston | N | 0.00018391 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.001868 | houston | Y | 0.0060265 | -0.0039343 | -0.054029 | 0.00018391 | 0.00018391 | houston | N | 0.00018391 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.001868 | houston | Y | 0.0060265 | -0.0039343 | -0.054029 | 0.00018391 | 0.00018391 | houston | N | 0.00018391 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.001868 | houston | N | 0.0060265 | -0.0039343 | -0.054029 | 0.00018391 | 0.00018391 | houston | N | 0.00018391 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.001812 | houston | Y | 0.0060825 | -0.0038783 | -0.053973 | 0.00023991 | 0.00023991 | houston | N | 0.00023991 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.001812 | houston | Y | 0.0060825 | -0.0038783 | -0.053973 | 0.00023991 | 0.00023991 | houston | N | 0.00023991 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.001812 | houston | Y | 0.0060825 | -0.0038783 | -0.053973 | 0.00023991 | 0.00023991 | houston | N | 0.00023991 | 0
48929 | WAPGT21_ | B1 | 13 | -0.001868 | houston | Y | 0.0060265 | -0.0039343 | -0.054029 | 0.00018391 | 0.00018391 | houston | N | 0.00018391 | 0
48940 | WARVUE_G | G1 | 12 | -0.002379 | houston | Y | 0.0055155 | -0.0044453 | -0.05454 | -0.00032709 | 0.00032709 | houston | N | 0.00032709 | 0
49803 | EXN_15GT | 1 | 34 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49826 | EXN938GT | 5 | 45.9 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49828 | EXN941GT | 10 | 17.7 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49829 | EXN942GT | 11 | 20.4 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49830 | EXN943GT | 12 | 19.9 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49831 | EXN944GT | 13 | 35 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49832 | EXN945GT | 9 | 18 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49837 | EXN_GT | 4 | 85.4 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49838 | EXN_14GT | 14 | 148 | -0.002353 | houston | N | 0.0055415 | -0.0044193 | -0.054514 | -0.00030109 | 0.00030109 | houston | N | 0.00030109 | 0
49851 | DOW17000 | 37 | 62 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49858 | DOW38100 | 31 | 71.4 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49859 | DOW38200 | 33 | 45 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49860 | DOW38300 | 32 | 101 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49862 | DOW39100 | 36 | 86 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49863 | DOW39200 | 35 | 88 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49865 | DOW41000 | 41 | 50 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49866 | DOW42000 | 42 | 18 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49869 | DOW49000 | 45 | 94 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49870 | DOW61000 | 61 | 70 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49871 | DOW62000 | 62 | 63 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49872 | DOW63000 | 63 | 72 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49873 | DOW64000 | 64 | 64.8 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49876 | DOW65000 | 65 | 101 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49877 | DOW66000 | 66 | 97 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49878 | DOW67000 | 67 | 103 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49882 | DOW81000 | 81 | 76 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49884 | DOW82000 | 82 | 80 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49885 | DOW83000 | 83 | 80 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
49886 | DOW84000 | 84 | 171 | -0.001302 | houston | N | 0.0065925 | -0.0033683 | -0.053463 | 0.00074991 | 0.00074991 | houston | N | 0.00074991 | 0
58909 | PEARSALL | 1 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58909 | PEARSALL | 2 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58909 | PEARSALL | 3 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58909 | PEARSALL | 4 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58909 | PEARSALL | 5 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58909 | PEARSALL | 6 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58919 | PEARSALL | 1 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58919 | PEARSALL | 2 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58919 | PEARSALL | 3 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58919 | PEARSALL | 4 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58919 | PEARSALL | 5 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58919 | PEARSALL | 6 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58929 | PEARSALL | 1 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58929 | PEARSALL | 2 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58929 | PEARSALL | 3 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58929 | PEARSALL | 4 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58929 | PEARSALL | 5 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58929 | PEARSALL | 6 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58949 | PEARSALL | 1 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58949 | PEARSALL | 2 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58949 | PEARSALL | 3 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58949 | PEARSALL | 4 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58949 | PEARSALL | 5 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
58949 | PEARSALL | 6 | 8.4 | 0.005944 | south | Y | 0.013839 | 0.0038777 | -0.046217 | 0.0079959 | 0.0038777 | south | N | 0.0038777 | 0
60000 | DSKY2 | 1 | 76.5 | 0.059776 | west | Y | 0.067671 | 0.05771 | 0.0076149 | 0.061828 | 0.0076149 | west | N | 0.0076149 | 0
60003 | KING_NE1 | 1 | 80 | 0.058099 | west | Y | 0.065994 | 0.056033 | 0.0059379 | 0.060151 | 0.0059379 | west | N | 0.0059379 | 0
60005 | KING_SE1 | 1 | 40 | 0.058099 | west | Y | 0.065994 | 0.056033 | 0.0059379 | 0.060151 | 0.0059379 | west | N | 0.0059379 | 0
60007 | KING_SW1 | 1 | 80 | 0.057967 | west | Y | 0.065862 | 0.055901 | 0.0058059 | 0.060019 | 0.0058059 | west | N | 0.0058059 | 0
60016 | WOODWRD1 | 1 | 80 | 0.05811 | west | Y | 0.066005 | 0.056044 | 0.0059489 | 0.060162 | 0.0059489 | west | N | 0.0059489 | 0
60017 | ORNNWP1 | 1 | 80 | 0.058985 | west | Y | 0.06688 | 0.056919 | 0.0068239 | 0.061037 | 0.0068239 | west | N | 0.0068239 | 0
60018 | DSKY1 | 1 | 84 | 0.059268 | west | Y | 0.067163 | 0.057202 | 0.0071069 | 0.06132 | 0.0071069 | west | N | 0.0071069 | 0
60019 | KING_NW1 | 1 | 80 | 0.057967 | west | Y | 0.065862 | 0.055901 | 0.0058059 | 0.060019 | 0.0058059 | west | N | 0.0058059 | 0
60057 | CALLAHAN | 1 | 114 | 0.003763 | south | Y | 0.011658 | 0.0016967 | -0.048398 | 0.0058149 | 0.0016967 | south | N | 0.0016967 | 0
60058 | BUFF_GAP | 1 | 120 | 0.063757 | west | Y | 0.071652 | 0.061691 | 0.011596 | 0.065809 | 0.011596 | west | N | 0.011596 | 0
60060 | CIRELLO | 1 | 233 | 0.063757 | west | Y | 0.071652 | 0.061691 | 0.011596 | 0.065809 | 0.011596 | west | N | 0.011596 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.063757 | west | Y | 0.071652 | 0.061691 | 0.011596 | 0.065809 | 0.011596 | west | N | 0.011596 | 0
60066 | H_HOLLOW | 1 | 222 | 0.003763 | south | Y | 0.011658 | 0.0016967 | -0.048398 | 0.0058149 | 0.0016967 | south | N | 0.0016967 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.003763 | south | Y | 0.011658 | 0.0016967 | -0.048398 | 0.0058149 | 0.0016967 | south | N | 0.0016967 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.003763 | south | Y | 0.011658 | 0.0016967 | -0.048398 | 0.0058149 | 0.0016967 | south | N | 0.0016967 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.003763 | south | Y | 0.011658 | 0.0016967 | -0.048398 | 0.0058149 | 0.0016967 | south | N | 0.0016967 | 0
60074 | HORSH5 | 1 | 100 | 0.003763 | south | Y | 0.011658 | 0.0016967 | -0.048398 | 0.0058149 | 0.0016967 | south | N | 0.0016967 | 0
60081 | WHRLWIND | 1 | 60 | 0.039048 | west | Y | 0.046943 | 0.036982 | -0.013113 | 0.0411 | 0.013113 | west | N | 0.013113 | 0
60201 | RIO DRCS | F | 0 | 0.036384 | south | N | 0.044279 | 0.034318 | -0.015777 | 0.038436 | 0.015777 | west | Y | 0.034318 | 0
60202 | FRIEND_R | F | 0 | 0.063415 | west | N | 0.07131 | 0.061349 | 0.011254 | 0.065467 | 0.011254 | west | N | 0.011254 | 0
60203 | PRES0A | BT | 4.8 | 0.056913 | west | N | 0.064808 | 0.054847 | 0.0047519 | 0.058965 | 0.0047519 | west | N | 0.0047519 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.050589 | west | Y | 0.058484 | 0.048523 | -0.0015721 | 0.052641 | 0.0015721 | west | N | 0.0015721 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.050589 | west | Y | 0.058484 | 0.048523 | -0.0015721 | 0.052641 | 0.0015721 | west | N | 0.0015721 | 0
71057 | L_SWEETW | W1 | 135 | 0.050589 | west | Y | 0.058484 | 0.048523 | -0.0015721 | 0.052641 | 0.0015721 | west | N | 0.0015721 | 0
71059 | L_SWEETW | W1 | 119 | 0.050589 | west | Y | 0.058484 | 0.048523 | -0.0015721 | 0.052641 | 0.0015721 | west | N | 0.0015721 | 0
71060 | L_SWEETW | W1 | 105 | 0.050589 | west | Y | 0.058484 | 0.048523 | -0.0015721 | 0.052641 | 0.0015721 | west | N | 0.0015721 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.050589 | west | Y | 0.058484 | 0.048523 | -0.0015721 | 0.052641 | 0.0015721 | west | N | 0.0015721 | 0
76031 | L_GASCCR | W1 | 150 | 0.068941 | west | Y | 0.076836 | 0.066875 | 0.01678 | 0.070993 | 0.01678 | west | N | 0.01678 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.071948 | west | Y | 0.079843 | 0.069882 | 0.019787 | 0.074 | 0.019787 | west | N | 0.019787 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.071948 | west | Y | 0.079843 | 0.069882 | 0.019787 | 0.074 | 0.019787 | west | N | 0.019787 | 0
76096 | L_CAPRSI | W1 | 186 | 0.071948 | west | Y | 0.079843 | 0.069882 | 0.019787 | 0.074 | 0.019787 | west | N | 0.019787 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.071948 | west | Y | 0.079843 | 0.069882 | 0.019787 | 0.074 | 0.019787 | west | N | 0.019787 | 0
80003 | MILHWYS | F | 0 | 0.001776 | south | N | 0.0096705 | -0.00029027 | -0.050385 | 0.0038279 | 0.00029027 | south | N | 0.00029027 | 0
80010 | EPLVT1 | F | 0 | 0.017258 | south | N | 0.025153 | 0.015192 | -0.034903 | 0.01931 | 0.015192 | south | N | 0.015192 | 0
80012 | LAR | F | 0 | 0.004033 | south | N | 0.011928 | 0.0019667 | -0.048128 | 0.0060849 | 0.0019667 | south | N | 0.0019667 | 0
80051 | FORPVCM0 | 8 | 28 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
80053 | FOR69CG0 | 10 | 74 | 0.000905 | south | N | 0.0087995 | -0.0011613 | -0.051256 | 0.0029569 | 0.0011613 | south | N | 0.0011613 | 0
80080 | GWINDT11 | 1 | 94 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80080 | GWINDT11 | 2 | 41 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80080 | GWINDT11 | 3 | 38 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80080 | GWINDT11 | 4 | 19 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80081 | GWINDT21 | 1 | 94 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80081 | GWINDT21 | 2 | 36 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80081 | GWINDT21 | 3 | 43 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80081 | GWINDT21 | 4 | 22 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80137 | CSDR89 | 8 | 39 | 0.001122 | south | N | 0.0090165 | -0.00094427 | -0.051039 | 0.0031739 | 0.00094427 | south | N | 0.00094427 | 0
80137 | CSDR89 | 9 | 15 | 0.001122 | south | N | 0.0090165 | -0.00094427 | -0.051039 | 0.0031739 | 0.00094427 | south | N | 0.00094427 | 0
80138 | CSDR7 | 7 | 7 | 0.001122 | south | N | 0.0090165 | -0.00094427 | -0.051039 | 0.0031739 | 0.00094427 | south | N | 0.00094427 | 0
80139 | CSDR56 | 5 | 15 | 0.001122 | south | N | 0.0090165 | -0.00094427 | -0.051039 | 0.0031739 | 0.00094427 | south | N | 0.00094427 | 0
80139 | CSDR56 | 6 | 39 | 0.001122 | south | N | 0.0090165 | -0.00094427 | -0.051039 | 0.0031739 | 0.00094427 | south | N | 0.00094427 | 0
80140 | CSDR11 | 11 | 39 | 0.001122 | south | N | 0.0090165 | -0.00094427 | -0.051039 | 0.0031739 | 0.00094427 | south | N | 0.00094427 | 0
80180 | PNSCALT1 | 1 | 148 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80180 | PNSCALT1 | 2 | 50 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80181 | PNSCALT2 | 1 | 55 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80181 | PNSCALT2 | 2 | 50 | 0.001749 | south | Y | 0.0096435 | -0.00031727 | -0.050412 | 0.0038009 | 0.00031727 | south | N | 0.00031727 | 0
80223 | REYSHR G | 1 | 12 | 0.001548 | south | N | 0.0094425 | -0.00051827 | -0.050613 | 0.0035999 | 0.00051827 | south | N | 0.00051827 | 0
80224 | VISTRONG | 1 | 15 | 0.001175 | south | N | 0.0090695 | -0.00089127 | -0.050986 | 0.0032269 | 0.00089127 | south | N | 0.00089127 | 0
80225 | VISTRONG | 2 | 23 | 0.001175 | south | N | 0.0090695 | -0.00089127 | -0.050986 | 0.0032269 | 0.00089127 | south | N | 0.00089127 | 0
80226 | ALCOA G | 1 | 48 | 0.000953 | south | N | 0.0088475 | -0.0011133 | -0.051208 | 0.0030049 | 0.0011133 | south | N | 0.0011133 | 0
80227 | AIRCO G | 1 | 8 | 0.001154 | south | N | 0.0090485 | -0.00091227 | -0.051007 | 0.0032059 | 0.00091227 | south | N | 0.00091227 | 0
80261 | NBEC81A | 1 | 180 | 0.001636 | south | Y | 0.0095305 | -0.00043027 | -0.050525 | 0.0036879 | 0.00043027 | south | N | 0.00043027 | 0
80262 | NBEC91A | 1 | 180 | 0.001634 | south | Y | 0.0095285 | -0.00043227 | -0.050527 | 0.0036859 | 0.00043227 | south | N | 0.00043227 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.001651 | south | Y | 0.0095455 | -0.00041527 | -0.05051 | 0.0037029 | 0.00041527 | south | N | 0.00041527 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.001651 | south | Y | 0.0095455 | -0.00041527 | -0.05051 | 0.0037029 | 0.00041527 | south | N | 0.00041527 | 0
80265 | LARECU40 | 4 | 100 | 0.004032 | south | Y | 0.011927 | 0.0019657 | -0.048129 | 0.0060839 | 0.0019657 | south | N | 0.0019657 | 0
80266 | LARECU50 | 5 | 100 | 0.004032 | south | Y | 0.011927 | 0.0019657 | -0.048129 | 0.0060839 | 0.0019657 | south | N | 0.0019657 | 0
80291 | PAPALOTE | 1 | 25 | 0.001584 | south | Y | 0.0094785 | -0.00048227 | -0.050577 | 0.0036359 | 0.00048227 | south | N | 0.00048227 | 0
80291 | PAPALOTE | 2 | 25 | 0.001584 | south | Y | 0.0094785 | -0.00048227 | -0.050577 | 0.0036359 | 0.00048227 | south | N | 0.00048227 | 0
80291 | PAPALOTE | 3 | 25 | 0.001584 | south | Y | 0.0094785 | -0.00048227 | -0.050577 | 0.0036359 | 0.00048227 | south | N | 0.00048227 | 0
80291 | PAPALOTE | 4 | 16 | 0.001584 | south | Y | 0.0094785 | -0.00048227 | -0.050577 | 0.0036359 | 0.00048227 | south | N | 0.00048227 | 0
80294 | PAPALOTE | 5 | 25 | 0.001584 | south | Y | 0.0094785 | -0.00048227 | -0.050577 | 0.0036359 | 0.00048227 | south | N | 0.00048227 | 0
80294 | PAPALOTE | 6 | 25 | 0.001584 | south | Y | 0.0094785 | -0.00048227 | -0.050577 | 0.0036359 | 0.00048227 | south | N | 0.00048227 | 0
80294 | PAPALOTE | 7 | 25 | 0.001584 | south | Y | 0.0094785 | -0.00048227 | -0.050577 | 0.0036359 | 0.00048227 | south | N | 0.00048227 | 0
80294 | PAPALOTE | 8 | 15 | 0.001584 | south | Y | 0.0094785 | -0.00048227 | -0.050577 | 0.0036359 | 0.00048227 | south | N | 0.00048227 | 0
86104 | CID-138 | EQ | 0 | 0.004032 | south | N | 0.011927 | 0.0019657 | -0.048129 | 0.0060839 | 0.0019657 | south | N | 0.0019657 | 0
86105 | CID-230 | EQ | 500 | 0.004032 | south | N | 0.011927 | 0.0019657 | -0.048129 | 0.0060839 | 0.0019657 | south | N | 0.0019657 | 0
86106 | CUF-230 | EQ | 500 | 0.004032 | south | N | 0.011927 | 0.0019657 | -0.048129 | 0.0060839 | 0.0019657 | south | N | 0.0019657 | 0
86107 | CUF-138 | EQ | 0 | 0.004032 | south | N | 0.011927 | 0.0019657 | -0.048129 | 0.0060839 | 0.0019657 | south | N | 0.0019657 | 0
88198 | BEEVILLE | F | 0 | 0.002111 | south | N | 0.010006 | 4.4734e-05 | -0.05005 | 0.0041629 | 4.4734e-05 | south | N | 4.4734e-05 | 0
88253 | HAMILTON | F | 0 | 0.024952 | south | N | 0.032847 | 0.022886 | -0.027209 | 0.027004 | 0.022886 | south | N | 0.022886 | 0
88299 | ZAPATA | F | 0 | 0.00327 | south | N | 0.011165 | 0.0012037 | -0.048891 | 0.0053219 | 0.0012037 | south | N | 0.0012037 | 0
88508 | FALFURRI | F | 0 | 0.002115 | south | N | 0.01001 | 4.8734e-05 | -0.050046 | 0.0041669 | 4.8734e-05 | south | N | 4.8734e-05 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:COMCHESS - COMANCHE 138 kV 1441 -1650 C: COMCHESS - COMCHPKW 345kV 1440 - 1900 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.024952 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.82342 | 0 | 0.032847 | 0 | 0 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.024952 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.6238 | 0 | 0.032847 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.024952 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.032847 | 0 | 0 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.024742 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.44536 | 0 | 0.032637 | 0 | 0 | 0 | Weighted Shift Factors
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.024742 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.44536 | 0 | 0.032637 | 0 | 0 | 0 | North | -0.0078945
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.024742 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37113 | 0 | 0.032637 | 0 | 0 | 0 | West | 0.052595
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.022374 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.30652 | 0 | 0.030269 | 0 | 0 | 0 |  | -0.06049
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.01871 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11226 | 0 | 0.026605 | 0 | 0 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.017317 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.3078 | 422 | 0.025212 | 10.6393 | 422 | 10.6393 | Line Rating | 215.35
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.017285 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.48398 | 0 | 0.02518 | 0 | 422 | 10.6393 | Conc Gen | 422
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.017285 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.50126 | 0 | 0.02518 | 0 | 422 | 10.6393 | Weighted Imp. | 10.6393
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.017258 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.025153 | 0 | 422 | 10.6393 | PTDF | 0.025212
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.013922 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2506 | 0 | 0.021817 | 0 | 422 | 10.6393
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.013922 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2506 | 0 | 0.021817 | 0 | 422 | 10.6393 | Concentration | -0.41679
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0942 | 112.5 | 0.019353 | 2.1772
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7562 | 149.5 | 0.019353 | 2.8933
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3823 | 186 | 0.019353 | 3.5997
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4328 | 214.5 | 0.019353 | 4.1512
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.070499 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9496 | 169.5 | 0.017904 | 3.0347
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.070025 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5038 | 150 | 0.01743 | 2.6145
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.068941 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.3412 | 150 | 0.016346 | 2.4519
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.006224 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21784 | 0 | 0.014119 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.006224 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21162 | 0 | 0.014119 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.006224 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21784 | 0 | 0.014119 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.005342 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.12821 | 24 | 0.013237 | 0.31768
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.005342 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.12821 | 24 | 0.013237 | 0.31768
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.005342 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.12287 | 23 | 0.013237 | 0.30444
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.004033 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011928 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.004032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.4032 | 100 | 0.011927 | 1.1927
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.004032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.4032 | 100 | 0.011927 | 1.1927
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.004032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011927 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.004032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011927 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.004032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011927 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.004032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011927 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.42898 | 114 | 0.011658 | 1.329
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.83539 | 222 | 0.011658 | 2.588
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.69239 | 184 | 0.011658 | 2.145
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.84291 | 224 | 0.011658 | 2.6113
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.43274 | 115 | 0.011658 | 1.3406
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.00327 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011165 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.063757 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6508 | 120 | 0.011162 | 1.3394
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.063757 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8554 | 233 | 0.011162 | 2.6007
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.063757 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8514 | 170.2 | 0.011162 | 1.8998
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.063415 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.01082 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.002845 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.16501 | 58 | 0.01074 | 0.62289
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.002845 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.25321 | 89 | 0.01074 | 0.95582
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12518 | 44 | 0.01074 | 0.47254
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12518 | 44 | 0.01074 | 0.47254
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12233 | 43 | 0.01074 | 0.4618
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12802 | 45 | 0.01074 | 0.48328
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002777 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.016662 | 0 | 0.010672 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.002698 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0981 | 407 | 0.010593 | 4.3112
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.002629 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0831 | 412 | 0.010524 | 4.3357
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.002629 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0516 | 400 | 0.010524 | 4.2094
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.002627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031524 | 0 | 0.010522 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.002627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.028897 | 0 | 0.010522 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.002627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031524 | 0 | 0.010522 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.002621 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.54779 | 209 | 0.010516 | 2.1977
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.002621 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56614 | 216 | 0.010516 | 2.2714
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12057 | 46 | 0.010516 | 0.48371
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12319 | 47 | 0.010516 | 0.49423
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12057 | 46 | 0.010516 | 0.48371
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12057 | 46 | 0.010516 | 0.48371
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.002611 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1071 | 424 | 0.010506 | 4.4543
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.002611 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1097 | 425 | 0.010506 | 4.4648
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.002473 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.010368 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.002473 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.010368 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.002473 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.010368 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.00246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.3813 | 155 | 0.010355 | 1.6049
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.00246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4182 | 170 | 0.010355 | 1.7603
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.00246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.3813 | 155 | 0.010355 | 1.6049
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.002371 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.93892 | 396 | 0.010266 | 4.0651
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.002352 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2842 | 546 | 0.010247 | 5.5946
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.002352 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.764 | 750 | 0.010247 | 7.6849
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.002334 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018672 | 0 | 0.010229 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.002334 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018672 | 0 | 0.010229 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002234 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.008936 | 0 | 0.010129 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.002115 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.01001 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.002111 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.010006 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.002074 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0049776 | 0 | 0.0099685 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.002074 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0049776 | 0 | 0.0099685 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.002074 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0058072 | 0 | 0.0099685 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29914 | 147 | 0.0099295 | 1.4596
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.28083 | 138 | 0.0099295 | 1.3703
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2849 | 140 | 0.0099295 | 1.3901
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29914 | 147 | 0.0099295 | 1.4596
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.37037 | 182 | 0.0099295 | 1.8072
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.40293 | 198 | 0.0099295 | 1.966
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.099029 | 49 | 0.0099155 | 0.48586
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.092966 | 46 | 0.0099155 | 0.45611
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.092966 | 46 | 0.0099155 | 0.45611
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.094987 | 47 | 0.0099155 | 0.46603
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.002021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31123 | 154 | 0.0099155 | 1.527
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.002021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29911 | 148 | 0.0099155 | 1.4675
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.097008 | 48 | 0.0099155 | 0.47594
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.097008 | 48 | 0.0099155 | 0.47594
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.00201 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.6231 | 310 | 0.0099045 | 3.0704
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.00201 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.83013 | 413 | 0.0099045 | 4.0906
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.001956 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.28655 | 146.5 | 0.0098505 | 1.4431
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.001956 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.28929 | 147.9 | 0.0098505 | 1.4569
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.001956 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33839 | 173 | 0.0098505 | 1.7041
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.27761 | 142 | 0.0098495 | 1.3986
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.28347 | 145 | 0.0098495 | 1.4282
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2952 | 151 | 0.0098495 | 1.4873
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.56695 | 290 | 0.0098495 | 2.8564
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42048 | 223.9 | 0.0097725 | 2.1881
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42255 | 225 | 0.0097725 | 2.1988
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4218 | 224.6 | 0.0097725 | 2.1949
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42574 | 226.7 | 0.0097725 | 2.2154
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.26554 | 144 | 0.0097385 | 1.4023
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.26554 | 144 | 0.0097385 | 1.4023
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31532 | 171 | 0.0097385 | 1.6653
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38171 | 207 | 0.0097385 | 2.0159
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39959 | 216.7 | 0.0097385 | 2.1103
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44625 | 242 | 0.0097385 | 2.3567
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0756 | 42 | 0.0096945 | 0.40717
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0792 | 44 | 0.0096945 | 0.42656
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0792 | 44 | 0.0096945 | 0.42656
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0846 | 47 | 0.0096945 | 0.45564
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.001796 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0043104 | 0 | 0.0096905 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.001796 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0043104 | 0 | 0.0096905 | 0
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.001776 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0096705 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.001776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.067488 | 38 | 0.0096705 | 0.36748
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.001776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.034277 | 19.3 | 0.0096705 | 0.18664
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.001776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.02664 | 15 | 0.0096705 | 0.14506
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.001776 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.083472 | 47 | 0.0096705 | 0.45451
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.16441 | 94 | 0.0096435 | 0.90649
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.071709 | 41 | 0.0096435 | 0.39538
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.066462 | 38 | 0.0096435 | 0.36645
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.033231 | 19 | 0.0096435 | 0.18323
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.16441 | 94 | 0.0096435 | 0.90649
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.062964 | 36 | 0.0096435 | 0.34717
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.075207 | 43 | 0.0096435 | 0.41467
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.038478 | 22 | 0.0096435 | 0.21216
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.25885 | 148 | 0.0096435 | 1.4272
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08745 | 50 | 0.0096435 | 0.48218
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.096195 | 55 | 0.0096435 | 0.53039
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08745 | 50 | 0.0096435 | 0.48218
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.001714 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049706 | 0 | 0.0096085 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.001705 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.0724 | 629 | 0.0095995 | 6.0381
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.001669 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.063422 | 0 | 0.0095635 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.001662 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.063156 | 0 | 0.0095565 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.001659 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.041475 | 0 | 0.0095535 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.001659 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.041475 | 0 | 0.0095535 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.001651 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.55143 | 334 | 0.0095455 | 3.1882
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.001651 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56134 | 340 | 0.0095455 | 3.2455
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.001651 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29718 | 180 | 0.0095455 | 1.7182
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.001651 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29718 | 180 | 0.0095455 | 1.7182
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.001636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29448 | 180 | 0.0095305 | 1.7155
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.001635 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.24247 | 0 | 0.0095295 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.001635 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.24296 | 0 | 0.0095295 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.001635 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.25016 | 0 | 0.0095295 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.001634 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54902 | 336 | 0.0095285 | 3.2016
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.001634 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29412 | 180 | 0.0095285 | 1.7151
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.001634 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.019608 | 0 | 0.0095285 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 25 | 0.0094785 | 0.23696
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 25 | 0.0094785 | 0.23696
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 25 | 0.0094785 | 0.23696
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.025344 | 16 | 0.0094785 | 0.15166
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 25 | 0.0094785 | 0.23696
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 25 | 0.0094785 | 0.23696
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 25 | 0.0094785 | 0.23696
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02376 | 15 | 0.0094785 | 0.14218
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.24458 | 0 | 0.0094425 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.23684 | 0 | 0.0094425 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1548 | 0 | 0.0094425 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.22446 | 0 | 0.0094425 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.22756 | 0 | 0.0094425 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1966 | 0 | 0.0094425 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.001548 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.018576 | 0 | 0.0094425 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.001359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.029898 | 22 | 0.0092535 | 0.20358
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.001359 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.014949 | 11 | 0.0092535 | 0.10179
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.001359 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.014949 | 11 | 0.0092535 | 0.10179
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.062678 | 47.7 | 0.0092085 | 0.43925
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.049012 | 37.3 | 0.0092085 | 0.34348
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060444 | 46 | 0.0092085 | 0.42359
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.063072 | 48 | 0.0092085 | 0.44201
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.001304 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18778 | 144 | 0.0091985 | 1.3246
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.001304 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.24515 | 188 | 0.0091985 | 1.7293
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.001251 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.091323 | 0 | 0.0091455 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.001175 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.017625 | 0 | 0.0090695 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.001175 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.027025 | 0 | 0.0090695 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.001154 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.009232 | 0 | 0.0090485 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.031416 | 0 | 0.0090165 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.007854 | 0 | 0.0090165 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.043758 | 0 | 0.0090165 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01683 | 0 | 0.0090165 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.007854 | 0 | 0.0090165 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01683 | 0 | 0.0090165 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.043758 | 0 | 0.0090165 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.043758 | 0 | 0.0090165 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.001088 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.14362 | 132 | 0.0089825 | 1.1857
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.001088 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.14579 | 134 | 0.0089825 | 1.2037
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.001088 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.35142 | 323 | 0.0089825 | 2.9014
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.000953 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.045744 | 0 | 0.0088475 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.071495 | 0 | 0.0087995 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.073305 | 0 | 0.0087995 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.071495 | 0 | 0.0087995 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0724 | 0 | 0.0087995 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.070952 | 0 | 0.0087995 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.022625 | 0 | 0.0087995 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.04163 | 0 | 0.0087995 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.02534 | 0 | 0.0087995 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.039458 | 0 | 0.0087995 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06697 | 0 | 0.0087995 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.000759 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.11575 | 152.5 | 0.0086535 | 1.3197
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.000759 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.11347 | 149.5 | 0.0086535 | 1.2937
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.000759 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17654 | 232.6 | 0.0086535 | 2.0128
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.03615 | 50 | 0.0086175 | 0.43088
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.03615 | 50 | 0.0086175 | 0.43088
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.03615 | 50 | 0.0086175 | 0.43088
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.03615 | 50 | 0.0086175 | 0.43088
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.00043 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.18619 | 433 | 0.0083245 | 3.6045
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.000428 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.24995 | 584 | 0.0083225 | 4.8603
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.000428 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.25466 | 595 | 0.0083225 | 4.9519
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.054826 | 158 | 0.0082415 | 1.3022
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.05552 | 160 | 0.0082415 | 1.3186
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060725 | 175 | 0.0082415 | 1.4423
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0078945 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0078945 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.000713 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.95043 | 0 | 0.0071815 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.000713 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.94686 | 0 | 0.0071815 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.059776 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5729 | 76.5 | 0.007181 | 0.54935
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.060952 | 76 | 0.0070925 | 0.53903
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.060952 | 76 | 0.0070925 | 0.53903
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.08421 | 105 | 0.0070925 | 0.74471
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.059348 | 74 | 0.0070925 | 0.52485
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.059348 | 74 | 0.0070925 | 0.52485
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.081804 | 102 | 0.0070925 | 0.72344
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.000876 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.057816 | 66 | 0.0070185 | 0.46322
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.059268 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9785 | 84 | 0.006673 | 0.56053
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.080724 | 0 | 0.0065925 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.092963 | 0 | 0.0065925 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.05859 | 0 | 0.0065925 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1315 | 0 | 0.0065925 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11197 | 0 | 0.0065925 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11458 | 0 | 0.0065925 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0651 | 0 | 0.0065925 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.023436 | 0 | 0.0065925 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12239 | 0 | 0.0065925 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09114 | 0 | 0.0065925 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.082026 | 0 | 0.0065925 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.093744 | 0 | 0.0065925 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.08437 | 0 | 0.0065925 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1315 | 0 | 0.0065925 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12629 | 0 | 0.0065925 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13411 | 0 | 0.0065925 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.098952 | 0 | 0.0065925 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10416 | 0 | 0.0065925 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10416 | 0 | 0.0065925 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22264 | 0 | 0.0065925 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.001409 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10004 | 0 | 0.0064855 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.001409 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01409 | 0 | 0.0064855 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1665 | 0 | 0.0063945 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1665 | 0 | 0.0063945 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1785 | 0 | 0.0063945 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16425 | 0 | 0.0063945 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058985 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7188 | 80 | 0.00639 | 0.5112
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.05879 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.38801 | 6.6 | 0.006195 | 0.040887
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.05879 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0165 | 34.3 | 0.006195 | 0.21249
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.001786 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.082335 | 0 | 0.0061085 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.001812 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.1796 | 651 | 0.0060825 | 3.9597
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.001812 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.022 | 564 | 0.0060825 | 3.4305
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.001812 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.0872 | 600 | 0.0060825 | 3.6495
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.001814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.29568 | 0 | 0.0060805 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.001814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.29568 | 0 | 0.0060805 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.001814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.44443 | 0 | 0.0060805 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.001823 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.0373 | 569 | 0.0060715 | 3.4547
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.001823 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.0592 | 581 | 0.0060715 | 3.5275
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.001829 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.060357 | 0 | 0.0060655 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.001868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.30075 | 161 | 0.0060265 | 0.97027
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.001868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.31009 | 166 | 0.0060265 | 1.0004
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.001868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.46326 | 248 | 0.0060265 | 1.4946
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.001868 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.0199 | 546 | 0.0060265 | 3.2905
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.001868 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -1.2011 | 0 | 0.0060265 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.001868 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.024284 | 13 | 0.0060265 | 0.078345
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.001993 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.063776 | 0 | 0.0059015 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.001993 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.05979 | 0 | 0.0059015 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1999 | 0 | 0.0059015 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.18515 | 0 | 0.0059015 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.20468 | 0 | 0.0059015 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.20329 | 0 | 0.0059015 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14118 | 0 | 0.0059005 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.133 | 0 | 0.0059005 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10568 | 0 | 0.0059005 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30548 | 0 | 0.0059005 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30608 | 0 | 0.0059005 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30369 | 0 | 0.0059005 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19142 | 0 | 0.0059005 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.48654 | 0 | 0.0059005 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07976 | 0 | 0.0059005 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.002063 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.10315 | 50 | 0.0058315 | 0.29158
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.002102 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0057925 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19638 | 0 | 0.0057365 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18904 | 0 | 0.0057365 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18775 | 0 | 0.0057365 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11761 | 0 | 0.0057365 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.026328 | 0 | 0.0057365 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14164 | 0 | 0.0057155 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13074 | 0 | 0.0057155 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14164 | 0 | 0.0057155 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14164 | 0 | 0.0057155 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10198 | 46 | 0.0056775 | 0.26117
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10198 | 46 | 0.0056775 | 0.26117
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10198 | 46 | 0.0056775 | 0.26117
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12194 | 55 | 0.0056775 | 0.31226
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12194 | 55 | 0.0056775 | 0.31226
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11972 | 54 | 0.0056775 | 0.30659
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.17316 | 0 | 0.0056745 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1776 | 0 | 0.0056745 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.36377 | 0 | 0.0056655 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35018 | 0 | 0.0056655 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35107 | 0 | 0.0056655 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.34995 | 0 | 0.0056655 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.5996 | 0 | 0.0056655 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.002241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078435 | 0 | 0.0056535 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.00225 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.38025 | 169 | 0.0056445 | 0.95392
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00225 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.027 | 12 | 0.0056445 | 0.067734
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.00225 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0056445 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.002251 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.37141 | 165 | 0.0056435 | 0.93118
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.002252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33555 | 0 | 0.0056425 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.002252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14661 | 0 | 0.0056425 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.002253 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.47989 | 213 | 0.0056415 | 1.2016
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.002254 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.51391 | 228 | 0.0056405 | 1.286
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14426 | 0 | 0.0056405 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14245 | 0 | 0.0056405 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18618 | 0 | 0.0056405 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16589 | 0 | 0.0056405 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.036515 | 0 | 0.0056405 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.002255 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4059 | 0 | 0.0056395 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.002255 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35764 | 0 | 0.0056395 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.002255 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35403 | 0 | 0.0056395 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16103 | 0 | 0.0056265 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1633 | 0 | 0.0056265 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.088452 | 0 | 0.0056265 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.06804 | 0 | 0.0056265 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.096222 | 42 | 0.0056035 | 0.23535
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.096222 | 42 | 0.0056035 | 0.23535
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.087058 | 38 | 0.0056035 | 0.21293
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.087058 | 38 | 0.0056035 | 0.21293
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.002292 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.31171 | 0 | 0.0056025 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.002299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39773 | 0 | 0.0055955 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.002299 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.31037 | 0 | 0.0055955 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.24305 | 104 | 0.0055575 | 0.57798
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.24305 | 104 | 0.0055575 | 0.57798
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1262 | 54 | 0.0055575 | 0.30011
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.12386 | 53 | 0.0055575 | 0.29455
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1262 | 54 | 0.0055575 | 0.30011
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13321 | 57 | 0.0055575 | 0.31678
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1262 | 54 | 0.0055575 | 0.30011
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1262 | 54 | 0.0055575 | 0.30011
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13555 | 58 | 0.0055575 | 0.32234
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13555 | 58 | 0.0055575 | 0.32234
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.058148 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7222 | 150 | 0.005553 | 0.83295
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.058148 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7222 | 150 | 0.005553 | 0.83295
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.002344 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.7228 | 735 | 0.0055505 | 4.0796
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.080002 | 0 | 0.0055415 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.081649 | 0 | 0.0055415 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.076943 | 0 | 0.0055415 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.108 | 0 | 0.0055415 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.041648 | 0 | 0.0055415 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.048001 | 0 | 0.0055415 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.046825 | 0 | 0.0055415 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.082355 | 0 | 0.0055415 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.042354 | 0 | 0.0055415 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20095 | 0 | 0.0055415 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34824 | 0 | 0.0055415 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002369 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.028428 | 12 | 0.0055255 | 0.066306
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.058117 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6494 | 80 | 0.005522 | 0.44176
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.002378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01189 | 0 | 0.0055165 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.002378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.049938 | 0 | 0.0055165 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.002379 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.028548 | 12 | 0.0055155 | 0.066186
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15463 | 0 | 0.0055155 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15701 | 0 | 0.0055155 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16653 | 0 | 0.0055155 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14988 | 0 | 0.0055155 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1475 | 0 | 0.0055155 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24742 | 0 | 0.0055155 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14036 | 0 | 0.0055155 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.05811 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6488 | 80 | 0.005515 | 0.4412
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.00238 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.7683 | 743 | 0.0055145 | 4.0973
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.002388 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.37492 | 0 | 0.0055065 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.00239 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.41108 | 172 | 0.0055045 | 0.94678
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.00239 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.41108 | 172 | 0.0055045 | 0.94678
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.00239 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.41108 | 172 | 0.0055045 | 0.94678
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.058099 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3574 | 75 | 0.005504 | 0.4128
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058099 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6479 | 80 | 0.005504 | 0.44032
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.058099 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.324 | 40 | 0.005504 | 0.22016
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39332 | 0 | 0.0054785 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38994 | 0 | 0.0054785 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3839 | 0 | 0.0054785 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65039 | 0 | 0.0054785 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.002427 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.96595 | 398 | 0.0054675 | 2.1761
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13681 | 56 | 0.0054515 | 0.30528
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14414 | 59 | 0.0054515 | 0.32164
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13681 | 56 | 0.0054515 | 0.30528
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13681 | 56 | 0.0054515 | 0.30528
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14414 | 59 | 0.0054515 | 0.32164
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13681 | 56 | 0.0054515 | 0.30528
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057967 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6374 | 80 | 0.005372 | 0.42976
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057967 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6374 | 80 | 0.005372 | 0.42976
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.44824 | 0 | 0.0053035 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4042 | 0 | 0.0053035 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39901 | 0 | 0.0053035 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39901 | 0 | 0.0053035 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.002591 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41974 | 0 | 0.0053035 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.056913 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.27318 | 0 | 0.004318 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.054935 | west | 8 | N | N | Nwest | Nwest | 1 | 1.4173 | 0 | 0.00234 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6126 | 66 | 0.002141 | 0.14131
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5578 | 65 | 0.002141 | 0.13917
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6673 | 67 | 0.002141 | 0.14345
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6673 | 67 | 0.002141 | 0.14345
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6673 | 67 | 0.002141 | 0.14345
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.054736 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.002141 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.054736 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.002141 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.05466 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9131 | 35 | 0.002065 | 0.072275
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.05466 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.6398 | 30 | 0.002065 | 0.06195
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.054453 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1135 | 149 | 0.001858 | 0.27684
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.2849 | 208.2 | 0.001607 | 0.33458
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.7021 | 142.1 | 0.001607 | 0.22836
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.1763 | 132.4 | 0.001607 | 0.21277
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3715 | 136 | 0.001607 | 0.21855
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.9677 | 147 | 0.001607 | 0.23623
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.3824 | 210 | 0.001607 | 0.33747
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7937 | 70 | 0.001601 | 0.11207
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7937 | 70 | 0.001601 | 0.11207
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.0294 | 92.8 | 0.001601 | 0.14857
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3357 | 80 | 0.001601 | 0.12808
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3357 | 80 | 0.001601 | 0.12808
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.2325 | 115 | 0.001601 | 0.18412
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.054124 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4395 | 100.5 | 0.001529 | 0.15367
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.05389 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1256 | 58 | 0.001295 | 0.075111
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.053758 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7631 | 0 | 0.001163 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.053758 | west | 8 | N | N | Nwest | Nwest | 1 | 3.9458 | 0 | 0.001163 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.053758 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7846 | 0 | 0.001163 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.053741 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.5113 | 214.2 | 0.001146 | 0.24548
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0484 | 150 | 0.001061 | 0.15915
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8043 | 220 | 0.001061 | 0.23342
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7312 | 200 | 0.001061 | 0.2122
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5407 | 121.9 | 0.001061 | 0.12934
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.053461 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4153 | 120 | 0.00086601 | 0.10392
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.053308 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.397 | 120 | 0.00071301 | 0.085562
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4865 | 66 | 0.00023101 | 0.015247
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.645 | 69 | 0.00023101 | 0.01594
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.645 | 69 | 0.00023101 | 0.01594
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5393 | 67 | 0.00023101 | 0.015478
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5393 | 67 | 0.00023101 | 0.015478
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4337 | 65 | 0.00023101 | 0.015016
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.052318 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7715 | 225 | -0.00027699 | -0.062322
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.052217 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3991 | 180 | -0.00037799 | -0.068038
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.052217 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3991 | 180 | -0.00037799 | -0.068038
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.051577 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2494 | 63 | -0.001018 | -0.064133
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.051457 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4321 | 125 | -0.001138 | -0.14225
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.051457 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4321 | 125 | -0.001138 | -0.14225
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.051134 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2099 | 141 | -0.001461 | -0.206
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.051134 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1361 | 120 | -0.001461 | -0.17532
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.051067 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0556 | 99 | -0.001528 | -0.15127
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.051067 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1151 | 61 | -0.001528 | -0.093207
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.051067 | west | 7 | N | N | Nwest | Nwest | 1 | 1.2767 | 0 | -0.001528 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.051067 | west | 7 | N | N | Nwest | Nwest | 1 | 2.3338 | 0 | -0.001528 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.051067 | west | 7 | N | N | Nwest | Nwest | 1 | 2.3338 | 0 | -0.001528 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8971 | 37.5 | -0.002006 | -0.075224
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4383 | 107.5 | -0.002006 | -0.21564
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8295 | 135 | -0.002006 | -0.27081
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0201 | 119 | -0.002006 | -0.23871
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3118 | 105 | -0.002006 | -0.21063
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0724 | 80.5 | -0.002006 | -0.16148
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.049922 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1934 | 84 | -0.002673 | -0.22453
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.04978 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.467 | 150 | -0.002815 | -0.42225
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.04978 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0278 | 101 | -0.002815 | -0.28431
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.1288 | 209 | -0.004132 | -0.86359
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1306 | 126.5 | -0.004132 | -0.5227
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.0673 | 249 | -0.004132 | -1.0289
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5472 | 197 | -0.004132 | -0.814
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.044901 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7351 | 150 | -0.007694 | -1.1541
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.039048 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3429 | 60 | -0.013547 | -0.81282
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.036384 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.016211 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.036011 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.4044 | 400 | -0.016584 | -6.6336
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.035976 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.4903 | 236 | -0.016619 | -3.9221
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.03087 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0935 | 165 | -0.021725 | -3.5846
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.026129 | west | 4 | Y | N | Ywest | Nwest | 1 | 16.976 | 649.7 | -0.026466 | -17.195
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.014701 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.3806 | 366 | -0.037894 | -13.8692
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.22466 | 20 | -0.041362 | -0.82724
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.22466 | 20 | -0.041362 | -0.82724
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.22466 | 20 | -0.041362 | -0.82724
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.19096 | 17 | -0.041362 | -0.70315
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.004834 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.98614 | 204 | -0.047761 | -9.7432
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.004834 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.97163 | 201 | -0.047761 | -9.6
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.004834 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1698 | 242 | -0.047761 | -11.5582
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.003939 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.95324 | 242 | -0.048656 | -11.7747
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.3763 | 100 | -0.048832 | -4.8832
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.052595 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.052595 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.61187 | 0 | -0.056563 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.61901 | 0 | -0.056563 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.61901 | 0 | -0.056563 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.5078 | 0 | -0.056563 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.004245 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9654 | 463 | -0.05684 | -26.3169
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.004322 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.25932 | 60 | -0.056917 | -3.415
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.004322 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.27229 | 63 | -0.056917 | -3.5858
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.004365 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.13968 | 0 | -0.05696 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056968 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056968 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.004373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.074341 | 17 | -0.056968 | -0.96846
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056968 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056968 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.004393 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.21086 | 48 | -0.056988 | -2.7354
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.004393 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.20208 | 46 | -0.056988 | -2.6214
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.004393 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.46126 | 105 | -0.056988 | -5.9837
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.3391 | 855 | -0.05767 | -49.3078
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.3391 | 855 | -0.05767 | -49.3078
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.77292 | 152.3 | -0.05767 | -8.7831
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.77648 | 153 | -0.05767 | -8.8235
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.005245 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.05784 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.005407 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.4716 | 827 | -0.058002 | -47.9676
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.005407 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.4283 | 819 | -0.058002 | -47.5036
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.005415 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.05801 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.005501 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.0354 | 370 | -0.058096 | -21.4955
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.77014 | 0 | -0.058096 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.77564 | 0 | -0.058096 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.6998 | 0 | -0.058096 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.78664 | 0 | -0.058096 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.79214 | 0 | -0.058096 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.7053 | 0 | -0.058096 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.88304 | 160 | -0.058114 | -9.2982
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.86096 | 156 | -0.058114 | -9.0658
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0817 | 196 | -0.058114 | -11.3903
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.86096 | 156 | -0.058114 | -9.0658
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.86648 | 157 | -0.058114 | -9.1239
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0928 | 198 | -0.058114 | -11.5066
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.005538 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.0902 | 558 | -0.058133 | -32.4382
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.005538 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.2065 | 579 | -0.058133 | -33.659
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.005538 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.4747 | 808 | -0.058133 | -46.9715
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.005544 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.4158 | 0 | -0.058139 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.005544 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.4413 | 0 | -0.058139 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.005544 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.49009 | 0 | -0.058139 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.005545 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.94265 | 170 | -0.05814 | -9.8838
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.005545 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.8834 | 520 | -0.05814 | -30.2328
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.005565 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.2226 | 0 | -0.05816 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.005565 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.2226 | 0 | -0.05816 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.005683 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.44896 | 79 | -0.058278 | -4.604
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.005683 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.6024 | 106 | -0.058278 | -6.1775
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.005683 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.82972 | 146 | -0.058278 | -8.5086
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.005683 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.43191 | 76 | -0.058278 | -4.4291
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.005707 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.11414 | 20 | -0.058302 | -1.166
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.005707 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.14267 | 25 | -0.058302 | -1.4575
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.005707 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.23399 | 41 | -0.058302 | -2.3904
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.005732 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.22928 | 40 | -0.058327 | -2.3331
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.93638 | 161 | -0.058411 | -9.4042
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.95382 | 164 | -0.058411 | -9.5794
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.95382 | 164 | -0.058411 | -9.5794
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4078 | 414 | -0.058411 | -24.1821
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.94219 | 162 | -0.058411 | -9.4626
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.93638 | 161 | -0.058411 | -9.4042
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.94801 | 163 | -0.058411 | -9.521
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3787 | 409 | -0.058411 | -23.8901
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.005829 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058424 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.005829 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058424 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.005829 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058424 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.00586 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.2737 | 388 | -0.058455 | -22.6805
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.00586 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.0179 | 515 | -0.058455 | -30.1043
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.005937 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.058532 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.005937 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.058532 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.005989 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.7014 | 785 | -0.058584 | -45.9884
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.005989 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.7613 | 795 | -0.058584 | -46.5743
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.005989 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.6714 | 780 | -0.058584 | -45.6955
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.88933 | 0 | -0.058604 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.78117 | 0 | -0.058604 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.8713 | 0 | -0.058604 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.3976 | 0 | -0.058604 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.006013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.698 | 615 | -0.058608 | -36.0439
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.006013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.5296 | 587 | -0.058608 | -34.4029
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.006016 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.3008 | 50 | -0.058611 | -2.9305
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.006016 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.058611 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.006025 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.0965 | 182 | -0.05862 | -10.6688
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.006025 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.9161 | 484 | -0.05862 | -28.3721
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.006027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.90827 | 150.7 | -0.058622 | -8.8343
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.006027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.91008 | 151 | -0.058622 | -8.8519
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.006027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0692 | 177.4 | -0.058622 | -10.3995
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.006042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.91536 | 151.5 | -0.058637 | -8.8835
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.006042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.9202 | 152.3 | -0.058637 | -8.9304
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.006042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0725 | 177.5 | -0.058637 | -10.4081
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.006255 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.73809 | 118 | -0.05885 | -6.9443
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.006255 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.71932 | 115 | -0.05885 | -6.7677
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.006255 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.4778 | 556 | -0.05885 | -32.7206
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.006362 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.513 | 395 | -0.058957 | -23.288
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.006362 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.7675 | 435 | -0.058957 | -25.6463
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.006435 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.7992 | 435 | -0.05903 | -25.678
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.006621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.4328 | 216.4 | -0.059216 | -12.8143
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.006621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.4308 | 216.1 | -0.059216 | -12.7966
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.006928 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.7794 | 112.5 | -0.059523 | -6.6963
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.699 | 224 | -0.06018 | -13.4803
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.7142 | 226 | -0.06018 | -13.6007
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.608 | 212 | -0.06018 | -12.7582
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.6004 | 211 | -0.06018 | -12.698
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.007634 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.71 | 224 | -0.060229 | -13.4913
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.007938 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.7249 | 217.3 | -0.060533 | -13.1538
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.007938 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.6273 | 205 | -0.060533 | -12.4093
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.007938 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.1623 | 272.4 | -0.060533 | -16.4892
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.007945 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.06054 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.007945 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -6.2527 | 787 | -0.06054 | -47.645
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.008107 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.060702 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.008107 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.060702 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.008154 | north | 3 | N | N | Nnorth | Nnorth | 1 | -9.4342 | 0 | -0.060749 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.008154 | north | 3 | N | N | Nnorth | Nnorth | 1 | -9.4423 | 0 | -0.060749 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.008224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.6119 | 196 | -0.060819 | -11.9205
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.008224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.91286 | 111 | -0.060819 | -6.7509
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.009648 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.062243 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.015749 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.016 | 255 | -0.068344 | -17.4277
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.015749 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.3466 | 149 | -0.068344 | -10.1833
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.015749 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.4096 | 153 | -0.068344 | -10.4566
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.016092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.6345 | 288 | -0.068687 | -19.7819
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.016092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3655 | 147 | -0.068687 | -10.097
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.016092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3655 | 147 | -0.068687 | -10.097
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.016726 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.20071 | 0 | -0.069321 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.016726 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.20071 | 0 | -0.069321 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.017709 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.1251 | 120 | -0.070304 | -8.4365
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.018189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0558 | 168 | -0.070784 | -11.8917
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.018189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.637 | 90 | -0.070784 | -6.3706
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.022159 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3239 | 150 | -0.074754 | -11.2131
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.022159 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.7727 | 80 | -0.074754 | -5.9803
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.023857 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.35785 | 0 | -0.076452 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.023857 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.35785 | 0 | -0.076452 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.085 | 70 | -0.082381 | -5.7667
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.0552 | 69 | -0.082381 | -5.6843
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.0552 | 69 | -0.082381 | -5.6843
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.0254 | 68 | -0.082381 | -5.6019
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.029876 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.53777 | 18 | -0.082471 | -1.4845
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.029876 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.53777 | 18 | -0.082471 | -1.4845
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.029876 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1353 | 38 | -0.082471 | -3.1339
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.061956 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -4.5228 | 73 | -0.11455 | -8.3622
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.061956 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -7.3728 | 119 | -0.11455 | -13.6316
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.061956 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.701 | 205 | -0.11455 | -23.483
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.061956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -6.3195 | 102 | -0.11455 | -11.6842
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.061956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.9478 | 96 | -0.11455 | -10.9969
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.10967 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -6.5802 | 60 | -0.16226 | -9.7359

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:COMCHESS - COMANCHE 138 kV 1441 -1650 C: COMCHESS - COMCHPKW 345kV 1440 - 1900 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.10967 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -6.5802 | 0 | -0.16226 | 0 | 0 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.061956 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -4.5228 | 73 | -0.11455 | -8.3622 | 73 | 8.3622
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.061956 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -7.3728 | 119 | -0.11455 | -13.6316 | 192 | 21.9938
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.061956 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.701 | 205 | -0.11455 | -23.483 | 397 | 45.4767 | Weighted Shift Factors
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.061956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -6.3195 | 102 | -0.11455 | -11.6842 |  |  | North | -0.0078945
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.061956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -5.9478 | 96 | -0.11455 | -10.9969 |  |  | West | 0.052595
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.029876 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.53777 | 18 | -0.082471 | -1.4845 |  |  |  | -0.06049
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.029876 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.53777 | 18 | -0.082471 | -1.4845
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.029876 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1353 | 38 | -0.082471 | -3.1339 |  |  | Line Rating | 215.35
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.085 | 70 | -0.082381 | -5.7667 |  |  | Conc Gen | 397
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.0552 | 69 | -0.082381 | -5.6843 |  |  | Weighted Imp. | 45.4767
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.0552 | 69 | -0.082381 | -5.6843 |  |  | PTDF | 0.11455
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.029786 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.0254 | 68 | -0.082381 | -5.6019
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.023857 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.35785 | 0 | -0.076452 | 0 |  |  | Concentration | -1.8937
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.023857 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.35785 | 0 | -0.076452 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.022159 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3239 | 150 | -0.074754 | -11.2131
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.022159 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.7727 | 80 | -0.074754 | -5.9803
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.018189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0558 | 168 | -0.070784 | -11.8917
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.018189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.637 | 90 | -0.070784 | -6.3706
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.017709 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.1251 | 0 | -0.070304 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.016726 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.20071 | 0 | -0.069321 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.016726 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.20071 | 0 | -0.069321 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.016092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.6345 | 288 | -0.068687 | -19.7819
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.016092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3655 | 147 | -0.068687 | -10.097
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.016092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3655 | 147 | -0.068687 | -10.097
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.015749 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.016 | 255 | -0.068344 | -17.4277
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.015749 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.3466 | 149 | -0.068344 | -10.1833
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.015749 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.4096 | 153 | -0.068344 | -10.4566
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.009648 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.062243 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.008224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.6119 | 196 | -0.060819 | -11.9205
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.008224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.91286 | 111 | -0.060819 | -6.7509
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.008154 | north | 3 | N | N | Nnorth | Nnorth | 1 | -9.4342 | 0 | -0.060749 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.008154 | north | 3 | N | N | Nnorth | Nnorth | 1 | -9.4423 | 0 | -0.060749 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.008107 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.060702 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.008107 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.060702 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.007945 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.06054 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.007945 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -6.2527 | 787 | -0.06054 | -47.645
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.007938 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.7249 | 217.3 | -0.060533 | -13.1538
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.007938 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.6273 | 205 | -0.060533 | -12.4093
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.007938 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.1623 | 272.4 | -0.060533 | -16.4892
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.007634 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.71 | 224 | -0.060229 | -13.4913
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.699 | 224 | -0.06018 | -13.4803
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.7142 | 226 | -0.06018 | -13.6007
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.608 | 212 | -0.06018 | -12.7582
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.007585 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.6004 | 211 | -0.06018 | -12.698
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.006928 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.7794 | 0 | -0.059523 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.006621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.4328 | 216.4 | -0.059216 | -12.8143
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.006621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.4308 | 216.1 | -0.059216 | -12.7966
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.006435 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.7992 | 435 | -0.05903 | -25.678
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.006362 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.513 | 395 | -0.058957 | -23.288
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.006362 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.7675 | 435 | -0.058957 | -25.6463
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.006255 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.73809 | 118 | -0.05885 | -6.9443
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.006255 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.71932 | 115 | -0.05885 | -6.7677
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.006255 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.4778 | 556 | -0.05885 | -32.7206
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.006042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.91536 | 151.5 | -0.058637 | -8.8835
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.006042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.9202 | 152.3 | -0.058637 | -8.9304
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.006042 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0725 | 177.5 | -0.058637 | -10.4081
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.006027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.90827 | 150.7 | -0.058622 | -8.8343
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.006027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.91008 | 151 | -0.058622 | -8.8519
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.006027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0692 | 177.4 | -0.058622 | -10.3995
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.006025 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.0965 | 182 | -0.05862 | -10.6688
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.006025 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.9161 | 484 | -0.05862 | -28.3721
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.006016 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.058611 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.006016 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.3008 | 0 | -0.058611 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.006013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.698 | 0 | -0.058608 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.006013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.5296 | 0 | -0.058608 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.88933 | 0 | -0.058604 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.78117 | 0 | -0.058604 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.8713 | 0 | -0.058604 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.006009 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.3976 | 0 | -0.058604 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.005989 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.7014 | 0 | -0.058584 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.005989 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.7613 | 0 | -0.058584 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.005989 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.6714 | 0 | -0.058584 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.005937 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.058532 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.005937 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.058532 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.00586 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.2737 | 388 | -0.058455 | -22.6805
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.00586 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.0179 | 515 | -0.058455 | -30.1043
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.005829 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058424 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.005829 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058424 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.005829 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.058424 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.93638 | 161 | -0.058411 | -9.4042
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.95382 | 164 | -0.058411 | -9.5794
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.95382 | 164 | -0.058411 | -9.5794
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4078 | 414 | -0.058411 | -24.1821
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.94219 | 162 | -0.058411 | -9.4626
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.93638 | 161 | -0.058411 | -9.4042
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.94801 | 163 | -0.058411 | -9.521
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.005816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3787 | 409 | -0.058411 | -23.8901
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.005732 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.22928 | 40 | -0.058327 | -2.3331
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.005707 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.11414 | 20 | -0.058302 | -1.166
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.005707 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.14267 | 25 | -0.058302 | -1.4575
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.005707 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.23399 | 41 | -0.058302 | -2.3904
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.005683 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.44896 | 79 | -0.058278 | -4.604
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.005683 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.6024 | 106 | -0.058278 | -6.1775
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.005683 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.82972 | 146 | -0.058278 | -8.5086
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.005683 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.43191 | 76 | -0.058278 | -4.4291
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.005565 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.2226 | 0 | -0.05816 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.005565 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.2226 | 0 | -0.05816 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.005545 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.94265 | 170 | -0.05814 | -9.8838
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.005545 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.8834 | 520 | -0.05814 | -30.2328
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.005544 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.4158 | 0 | -0.058139 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.005544 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.4413 | 0 | -0.058139 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.005544 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.49009 | 0 | -0.058139 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.005538 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.0902 | 0 | -0.058133 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.005538 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.2065 | 0 | -0.058133 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.005538 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.4747 | 0 | -0.058133 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.88304 | 160 | -0.058114 | -9.2982
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.86096 | 156 | -0.058114 | -9.0658
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0817 | 196 | -0.058114 | -11.3903
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.86096 | 156 | -0.058114 | -9.0658
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.86648 | 157 | -0.058114 | -9.1239
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.005519 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0928 | 198 | -0.058114 | -11.5066
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.005501 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.0354 | 370 | -0.058096 | -21.4955
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.77014 | 0 | -0.058096 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.77564 | 0 | -0.058096 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.6998 | 0 | -0.058096 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.78664 | 0 | -0.058096 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.79214 | 0 | -0.058096 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.005501 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.7053 | 0 | -0.058096 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.005415 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.05801 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.005407 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.4716 | 0 | -0.058002 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.005407 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.4283 | 0 | -0.058002 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.005245 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.05784 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.3391 | 0 | -0.05767 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.3391 | 0 | -0.05767 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.77292 | 0 | -0.05767 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.005075 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.77648 | 0 | -0.05767 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.004393 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.21086 | 48 | -0.056988 | -2.7354
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.004393 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.20208 | 46 | -0.056988 | -2.6214
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.004393 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.46126 | 105 | -0.056988 | -5.9837
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056968 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056968 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.004373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.074341 | 17 | -0.056968 | -0.96846
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056968 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.004373 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.056968 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.004365 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.13968 | 0 | -0.05696 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.004322 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.25932 | 60 | -0.056917 | -3.415
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.004322 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.27229 | 63 | -0.056917 | -3.5858
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.004245 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9654 | 0 | -0.05684 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.61187 | 0 | -0.056563 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.61901 | 0 | -0.056563 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.61901 | 0 | -0.056563 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.003968 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.5078 | 0 | -0.056563 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.052595 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.052595 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.3763 | 0 | -0.048832 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.003939 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.95324 | 242 | -0.048656 | -11.7747
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.004834 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.98614 | 204 | -0.047761 | -9.7432
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.004834 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.97163 | 201 | -0.047761 | -9.6
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.004834 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1698 | 242 | -0.047761 | -11.5582
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.22466 | 20 | -0.041362 | -0.82724
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.22466 | 20 | -0.041362 | -0.82724
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.22466 | 20 | -0.041362 | -0.82724
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.011233 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.19096 | 17 | -0.041362 | -0.70315
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.014701 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.3806 | 366 | -0.037894 | -13.8692
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.026129 | west | 4 | Y | N | Ywest | Nwest | 1 | 16.976 | 0 | -0.026466 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.03087 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0935 | 0 | -0.021725 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.035976 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.4903 | 0 | -0.016619 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.036011 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.4044 | 0 | -0.016584 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.036384 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.016211 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.039048 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3429 | 0 | -0.013547 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.044901 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7351 | 0 | -0.007694 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.1288 | 0 | -0.004132 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1306 | 0 | -0.004132 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.0673 | 0 | -0.004132 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.048463 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5472 | 0 | -0.004132 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.04978 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.467 | 0 | -0.002815 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.04978 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0278 | 0 | -0.002815 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.049922 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1934 | 0 | -0.002673 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8971 | 0 | -0.002006 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4383 | 0 | -0.002006 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8295 | 0 | -0.002006 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0201 | 0 | -0.002006 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3118 | 0 | -0.002006 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.050589 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0724 | 0 | -0.002006 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.051067 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0556 | 0 | -0.001528 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.051067 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1151 | 0 | -0.001528 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.051067 | west | 7 | N | N | Nwest | Nwest | 1 | 1.2767 | 0 | -0.001528 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.051067 | west | 7 | N | N | Nwest | Nwest | 1 | 2.3338 | 0 | -0.001528 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.051067 | west | 7 | N | N | Nwest | Nwest | 1 | 2.3338 | 0 | -0.001528 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.051134 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2099 | 0 | -0.001461 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.051134 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1361 | 0 | -0.001461 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.051457 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4321 | 0 | -0.001138 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.051457 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4321 | 0 | -0.001138 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.051577 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2494 | 0 | -0.001018 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.052217 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3991 | 0 | -0.00037799 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.052217 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3991 | 0 | -0.00037799 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.052318 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7715 | 0 | -0.00027699 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4865 | 66 | 0.00023101 | 0.015247
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.645 | 69 | 0.00023101 | 0.01594
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.645 | 69 | 0.00023101 | 0.01594
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5393 | 67 | 0.00023101 | 0.015478
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5393 | 67 | 0.00023101 | 0.015478
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.052826 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4337 | 65 | 0.00023101 | 0.015016
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.053308 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.397 | 0 | 0.00071301 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.053461 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4153 | 0 | 0.00086601 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0484 | 0 | 0.001061 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8043 | 0 | 0.001061 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7312 | 0 | 0.001061 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.053656 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5407 | 0 | 0.001061 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.053741 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.5113 | 0 | 0.001146 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.053758 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7631 | 0 | 0.001163 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.053758 | west | 8 | N | N | Nwest | Nwest | 1 | 3.9458 | 0 | 0.001163 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.053758 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7846 | 0 | 0.001163 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.05389 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1256 | 0 | 0.001295 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.054124 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4395 | 0 | 0.001529 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7937 | 70 | 0.001601 | 0.11207
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7937 | 70 | 0.001601 | 0.11207
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.0294 | 92.8 | 0.001601 | 0.14857
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3357 | 80 | 0.001601 | 0.12808
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3357 | 80 | 0.001601 | 0.12808
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.054196 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.2325 | 115 | 0.001601 | 0.18412
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.2849 | 208.2 | 0.001607 | 0.33458
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.7021 | 142.1 | 0.001607 | 0.22836
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.1763 | 132.4 | 0.001607 | 0.21277
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3715 | 136 | 0.001607 | 0.21855
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.9677 | 147 | 0.001607 | 0.23623
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.054202 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.3824 | 210 | 0.001607 | 0.33747
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.054453 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1135 | 0 | 0.001858 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.05466 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9131 | 0 | 0.002065 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.05466 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.6398 | 0 | 0.002065 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6126 | 66 | 0.002141 | 0.14131
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5578 | 65 | 0.002141 | 0.13917
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6673 | 67 | 0.002141 | 0.14345
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6673 | 67 | 0.002141 | 0.14345
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.054736 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6673 | 67 | 0.002141 | 0.14345
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.054736 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.002141 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.054736 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.002141 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.054935 | west | 8 | N | N | Nwest | Nwest | 1 | 1.4173 | 0 | 0.00234 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.056913 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.27318 | 0 | 0.004318 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.44824 | 0 | 0.0053035 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4042 | 0 | 0.0053035 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39901 | 0 | 0.0053035 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39901 | 0 | 0.0053035 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.002591 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41974 | 0 | 0.0053035 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057967 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6374 | 0 | 0.005372 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057967 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6374 | 0 | 0.005372 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13681 | 56 | 0.0054515 | 0.30528
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14414 | 59 | 0.0054515 | 0.32164
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13681 | 56 | 0.0054515 | 0.30528
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13681 | 56 | 0.0054515 | 0.30528
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14414 | 59 | 0.0054515 | 0.32164
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.002443 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13681 | 56 | 0.0054515 | 0.30528
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.002427 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.96595 | 398 | 0.0054675 | 2.1761
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39332 | 0 | 0.0054785 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38994 | 0 | 0.0054785 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3839 | 0 | 0.0054785 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.002416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65039 | 0 | 0.0054785 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.058099 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3574 | 0 | 0.005504 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058099 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6479 | 0 | 0.005504 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.058099 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.324 | 0 | 0.005504 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.00239 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.41108 | 172 | 0.0055045 | 0.94678
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.00239 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.41108 | 172 | 0.0055045 | 0.94678
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.00239 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.41108 | 172 | 0.0055045 | 0.94678
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.002388 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.37492 | 0 | 0.0055065 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.00238 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.7683 | 743 | 0.0055145 | 4.0973
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.05811 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6488 | 0 | 0.005515 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15463 | 0 | 0.0055155 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15701 | 0 | 0.0055155 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16653 | 0 | 0.0055155 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14988 | 0 | 0.0055155 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1475 | 0 | 0.0055155 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24742 | 0 | 0.0055155 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.002379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14036 | 0 | 0.0055155 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.002379 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.028548 | 0 | 0.0055155 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.002378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01189 | 0 | 0.0055165 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.002378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.049938 | 0 | 0.0055165 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.058117 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6494 | 0 | 0.005522 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002369 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.028428 | 12 | 0.0055255 | 0.066306
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.080002 | 0 | 0.0055415 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.081649 | 0 | 0.0055415 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.076943 | 0 | 0.0055415 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.108 | 0 | 0.0055415 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.041648 | 0 | 0.0055415 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.048001 | 0 | 0.0055415 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.046825 | 0 | 0.0055415 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.082355 | 0 | 0.0055415 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.042354 | 0 | 0.0055415 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20095 | 0 | 0.0055415 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.002353 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34824 | 0 | 0.0055415 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.002344 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.7228 | 735 | 0.0055505 | 4.0796
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.058148 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7222 | 0 | 0.005553 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.058148 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7222 | 0 | 0.005553 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.24305 | 104 | 0.0055575 | 0.57798
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.24305 | 104 | 0.0055575 | 0.57798
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1262 | 54 | 0.0055575 | 0.30011
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.12386 | 53 | 0.0055575 | 0.29455
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1262 | 54 | 0.0055575 | 0.30011
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13321 | 57 | 0.0055575 | 0.31678
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1262 | 54 | 0.0055575 | 0.30011
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.1262 | 54 | 0.0055575 | 0.30011
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13555 | 58 | 0.0055575 | 0.32234
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.002337 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.13555 | 58 | 0.0055575 | 0.32234
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.002299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39773 | 0 | 0.0055955 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.002299 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.31037 | 0 | 0.0055955 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.002292 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.31171 | 0 | 0.0056025 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.096222 | 42 | 0.0056035 | 0.23535
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.096222 | 42 | 0.0056035 | 0.23535
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.087058 | 38 | 0.0056035 | 0.21293
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.002291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.087058 | 38 | 0.0056035 | 0.21293
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16103 | 0 | 0.0056265 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1633 | 0 | 0.0056265 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.088452 | 0 | 0.0056265 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.002268 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.06804 | 0 | 0.0056265 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.002255 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4059 | 0 | 0.0056395 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.002255 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35764 | 0 | 0.0056395 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.002255 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35403 | 0 | 0.0056395 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.036515 | 0 | 0.0056405 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14426 | 0 | 0.0056405 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14245 | 0 | 0.0056405 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18618 | 0 | 0.0056405 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.002254 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16589 | 0 | 0.0056405 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.002254 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.51391 | 228 | 0.0056405 | 1.286
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.002253 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.47989 | 213 | 0.0056415 | 1.2016
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.002252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33555 | 0 | 0.0056425 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.002252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14661 | 0 | 0.0056425 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.002251 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.37141 | 165 | 0.0056435 | 0.93118
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00225 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.027 | 12 | 0.0056445 | 0.067734
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.00225 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0056445 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.00225 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.38025 | 169 | 0.0056445 | 0.95392
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.002241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078435 | 0 | 0.0056535 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.36377 | 0 | 0.0056655 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35018 | 0 | 0.0056655 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35107 | 0 | 0.0056655 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.34995 | 0 | 0.0056655 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.002229 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.5996 | 0 | 0.0056655 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.17316 | 0 | 0.0056745 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.00222 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1776 | 0 | 0.0056745 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10198 | 46 | 0.0056775 | 0.26117
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10198 | 46 | 0.0056775 | 0.26117
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10198 | 46 | 0.0056775 | 0.26117
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12194 | 55 | 0.0056775 | 0.31226
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12194 | 55 | 0.0056775 | 0.31226
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.002217 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11972 | 54 | 0.0056775 | 0.30659
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14164 | 0 | 0.0057155 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13074 | 0 | 0.0057155 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14164 | 0 | 0.0057155 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.002179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14164 | 0 | 0.0057155 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19638 | 0 | 0.0057365 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18904 | 0 | 0.0057365 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18775 | 0 | 0.0057365 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11761 | 0 | 0.0057365 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.002158 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.026328 | 0 | 0.0057365 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.002102 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0057925 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.002063 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.10315 | 50 | 0.0058315 | 0.29158
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14118 | 0 | 0.0059005 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.133 | 0 | 0.0059005 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10568 | 0 | 0.0059005 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30548 | 0 | 0.0059005 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30608 | 0 | 0.0059005 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30369 | 0 | 0.0059005 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19142 | 0 | 0.0059005 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.001994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.48654 | 0 | 0.0059005 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.001994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07976 | 0 | 0.0059005 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1999 | 0 | 0.0059015 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.18515 | 0 | 0.0059015 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.20468 | 0 | 0.0059015 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.001993 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.20329 | 0 | 0.0059015 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.001993 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.063776 | 0 | 0.0059015 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.001993 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.05979 | 0 | 0.0059015 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.001868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.30075 | 161 | 0.0060265 | 0.97027
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.001868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.31009 | 166 | 0.0060265 | 1.0004
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.001868 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.46326 | 248 | 0.0060265 | 1.4946
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.001868 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.0199 | 546 | 0.0060265 | 3.2905
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.001868 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -1.2011 | 0 | 0.0060265 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.001868 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.024284 | 13 | 0.0060265 | 0.078345
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.001829 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.060357 | 0 | 0.0060655 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.001823 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.0373 | 0 | 0.0060715 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.001823 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.0592 | 0 | 0.0060715 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.001814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.29568 | 0 | 0.0060805 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.001814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.29568 | 0 | 0.0060805 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.001814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.44443 | 0 | 0.0060805 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.001812 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.1796 | 0 | 0.0060825 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.001812 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.022 | 0 | 0.0060825 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.001812 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.0872 | 0 | 0.0060825 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.001786 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.082335 | 0 | 0.0061085 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.05879 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.38801 | 0 | 0.006195 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.05879 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0165 | 0 | 0.006195 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.058985 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7188 | 0 | 0.00639 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1665 | 0 | 0.0063945 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1665 | 0 | 0.0063945 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1785 | 0 | 0.0063945 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.0015 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16425 | 0 | 0.0063945 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.001409 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10004 | 0 | 0.0064855 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.001409 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01409 | 0 | 0.0064855 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.080724 | 0 | 0.0065925 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.092963 | 0 | 0.0065925 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.05859 | 0 | 0.0065925 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1315 | 0 | 0.0065925 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11197 | 0 | 0.0065925 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11458 | 0 | 0.0065925 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0651 | 0 | 0.0065925 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.023436 | 0 | 0.0065925 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12239 | 0 | 0.0065925 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09114 | 0 | 0.0065925 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.082026 | 0 | 0.0065925 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.093744 | 0 | 0.0065925 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.08437 | 0 | 0.0065925 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1315 | 0 | 0.0065925 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12629 | 0 | 0.0065925 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13411 | 0 | 0.0065925 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.098952 | 0 | 0.0065925 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10416 | 0 | 0.0065925 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10416 | 0 | 0.0065925 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.001302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22264 | 0 | 0.0065925 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.059268 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9785 | 0 | 0.006673 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.000876 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.057816 | 66 | 0.0070185 | 0.46322
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.060952 | 76 | 0.0070925 | 0.53903
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.060952 | 76 | 0.0070925 | 0.53903
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.08421 | 105 | 0.0070925 | 0.74471
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.059348 | 74 | 0.0070925 | 0.52485
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.059348 | 74 | 0.0070925 | 0.52485
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.000802 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.081804 | 102 | 0.0070925 | 0.72344
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.059776 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5729 | 0 | 0.007181 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.000713 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.95043 | 0 | 0.0071815 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.000713 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.94686 | 0 | 0.0071815 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0078945 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0078945 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0078945 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.054826 | 158 | 0.0082415 | 1.3022
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.05552 | 160 | 0.0082415 | 1.3186
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060725 | 175 | 0.0082415 | 1.4423
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.000428 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.24995 | 0 | 0.0083225 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.000428 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.25466 | 0 | 0.0083225 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.00043 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.18619 | 0 | 0.0083245 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.03615 | 50 | 0.0086175 | 0.43088
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.03615 | 50 | 0.0086175 | 0.43088
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.03615 | 50 | 0.0086175 | 0.43088
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.000723 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.03615 | 50 | 0.0086175 | 0.43088
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.000759 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.11575 | 152.5 | 0.0086535 | 1.3197
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.000759 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.11347 | 149.5 | 0.0086535 | 1.2937
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.000759 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17654 | 232.6 | 0.0086535 | 2.0128
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.071495 | 0 | 0.0087995 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.073305 | 0 | 0.0087995 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.071495 | 0 | 0.0087995 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0724 | 0 | 0.0087995 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.070952 | 0 | 0.0087995 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.022625 | 0 | 0.0087995 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.04163 | 0 | 0.0087995 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.02534 | 0 | 0.0087995 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.039458 | 0 | 0.0087995 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.000905 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06697 | 0 | 0.0087995 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.000953 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.045744 | 0 | 0.0088475 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.001088 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.14362 | 132 | 0.0089825 | 1.1857
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.001088 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.14579 | 134 | 0.0089825 | 1.2037
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.001088 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.35142 | 323 | 0.0089825 | 2.9014
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.031416 | 0 | 0.0090165 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.007854 | 0 | 0.0090165 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.043758 | 0 | 0.0090165 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01683 | 0 | 0.0090165 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.007854 | 0 | 0.0090165 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.01683 | 0 | 0.0090165 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.043758 | 0 | 0.0090165 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.001122 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.043758 | 0 | 0.0090165 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.001154 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.009232 | 0 | 0.0090485 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.001175 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.017625 | 0 | 0.0090695 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.001175 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.027025 | 0 | 0.0090695 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.001251 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.091323 | 0 | 0.0091455 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.001304 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18778 | 144 | 0.0091985 | 1.3246
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.001304 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.24515 | 188 | 0.0091985 | 1.7293
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.062678 | 47.7 | 0.0092085 | 0.43925
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.049012 | 37.3 | 0.0092085 | 0.34348
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060444 | 46 | 0.0092085 | 0.42359
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.001314 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.063072 | 48 | 0.0092085 | 0.44201
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.001359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.029898 | 22 | 0.0092535 | 0.20358
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.001359 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.014949 | 11 | 0.0092535 | 0.10179
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.001359 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.014949 | 11 | 0.0092535 | 0.10179
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.24458 | 0 | 0.0094425 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.23684 | 0 | 0.0094425 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1548 | 0 | 0.0094425 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.22446 | 0 | 0.0094425 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.22756 | 0 | 0.0094425 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.001548 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.1966 | 0 | 0.0094425 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.001548 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.018576 | 0 | 0.0094425 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 0 | 0.0094785 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 0 | 0.0094785 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 0 | 0.0094785 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.025344 | 0 | 0.0094785 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 0 | 0.0094785 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 0 | 0.0094785 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.0396 | 0 | 0.0094785 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.001584 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.02376 | 0 | 0.0094785 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.001634 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.019608 | 0 | 0.0095285 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.001634 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54902 | 336 | 0.0095285 | 3.2016
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.001634 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29412 | 180 | 0.0095285 | 1.7151
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.001635 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.24247 | 0 | 0.0095295 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.001635 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.24296 | 0 | 0.0095295 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.001635 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.25016 | 0 | 0.0095295 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.001636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29448 | 180 | 0.0095305 | 1.7155
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.001651 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.55143 | 334 | 0.0095455 | 3.1882
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.001651 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56134 | 340 | 0.0095455 | 3.2455
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.001651 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29718 | 180 | 0.0095455 | 1.7182
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.001651 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29718 | 180 | 0.0095455 | 1.7182
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.001659 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.041475 | 0 | 0.0095535 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.001659 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.041475 | 0 | 0.0095535 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.001662 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.063156 | 0 | 0.0095565 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.001669 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.063422 | 0 | 0.0095635 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.001705 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.0724 | 0 | 0.0095995 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.001714 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049706 | 0 | 0.0096085 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.16441 | 0 | 0.0096435 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.071709 | 0 | 0.0096435 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.066462 | 0 | 0.0096435 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.033231 | 0 | 0.0096435 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.16441 | 0 | 0.0096435 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.062964 | 0 | 0.0096435 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.075207 | 0 | 0.0096435 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.038478 | 0 | 0.0096435 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.25885 | 0 | 0.0096435 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08745 | 0 | 0.0096435 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.096195 | 0 | 0.0096435 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.001749 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08745 | 0 | 0.0096435 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.001776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.067488 | 38 | 0.0096705 | 0.36748
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.001776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.034277 | 19.3 | 0.0096705 | 0.18664
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.001776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.02664 | 15 | 0.0096705 | 0.14506
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.001776 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.083472 | 47 | 0.0096705 | 0.45451
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.001776 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0096705 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.001796 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0043104 | 0 | 0.0096905 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.001796 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0043104 | 0 | 0.0096905 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0756 | 42 | 0.0096945 | 0.40717
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0792 | 44 | 0.0096945 | 0.42656
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0792 | 44 | 0.0096945 | 0.42656
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.0018 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0846 | 47 | 0.0096945 | 0.45564
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38171 | 207 | 0.0097385 | 2.0159
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39959 | 216.7 | 0.0097385 | 2.1103
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44625 | 242 | 0.0097385 | 2.3567
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.26554 | 144 | 0.0097385 | 1.4023
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.26554 | 144 | 0.0097385 | 1.4023
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.001844 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31532 | 171 | 0.0097385 | 1.6653
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42048 | 223.9 | 0.0097725 | 2.1881
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42255 | 225 | 0.0097725 | 2.1988
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4218 | 224.6 | 0.0097725 | 2.1949
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.001878 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42574 | 226.7 | 0.0097725 | 2.2154
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.27761 | 142 | 0.0098495 | 1.3986
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.28347 | 145 | 0.0098495 | 1.4282
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2952 | 151 | 0.0098495 | 1.4873
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.001955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.56695 | 290 | 0.0098495 | 2.8564
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.001956 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.28655 | 146.5 | 0.0098505 | 1.4431
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.001956 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.28929 | 147.9 | 0.0098505 | 1.4569
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.001956 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33839 | 173 | 0.0098505 | 1.7041
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.00201 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.6231 | 310 | 0.0099045 | 3.0704
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.00201 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.83013 | 413 | 0.0099045 | 4.0906
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.099029 | 49 | 0.0099155 | 0.48586
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.092966 | 46 | 0.0099155 | 0.45611
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.092966 | 46 | 0.0099155 | 0.45611
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.094987 | 47 | 0.0099155 | 0.46603
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.002021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31123 | 154 | 0.0099155 | 1.527
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.002021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29911 | 148 | 0.0099155 | 1.4675
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.097008 | 48 | 0.0099155 | 0.47594
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.002021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.097008 | 48 | 0.0099155 | 0.47594
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29914 | 147 | 0.0099295 | 1.4596
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.28083 | 138 | 0.0099295 | 1.3703
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2849 | 140 | 0.0099295 | 1.3901
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29914 | 147 | 0.0099295 | 1.4596
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.37037 | 182 | 0.0099295 | 1.8072
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.002035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.40293 | 198 | 0.0099295 | 1.966
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.002074 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0049776 | 0 | 0.0099685 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.002074 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0049776 | 0 | 0.0099685 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.002074 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0058072 | 0 | 0.0099685 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.002111 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.010006 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.002115 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.01001 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002234 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.008936 | 0 | 0.010129 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.002334 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018672 | 0 | 0.010229 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.002334 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018672 | 0 | 0.010229 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.002352 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2842 | 0 | 0.010247 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.002352 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.764 | 0 | 0.010247 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.002371 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.93892 | 0 | 0.010266 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.00246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.3813 | 155 | 0.010355 | 1.6049
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.00246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4182 | 170 | 0.010355 | 1.7603
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.00246 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.3813 | 155 | 0.010355 | 1.6049
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.002473 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.010368 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.002473 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.010368 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.002473 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.010368 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.002611 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1071 | 0 | 0.010506 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.002611 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1097 | 0 | 0.010506 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.002621 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.54779 | 209 | 0.010516 | 2.1977
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.002621 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56614 | 216 | 0.010516 | 2.2714
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12057 | 46 | 0.010516 | 0.48371
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12319 | 47 | 0.010516 | 0.49423
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12057 | 46 | 0.010516 | 0.48371
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.002621 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12057 | 46 | 0.010516 | 0.48371
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.002627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031524 | 0 | 0.010522 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.002627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.028897 | 0 | 0.010522 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.002627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031524 | 0 | 0.010522 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.002629 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0831 | 412 | 0.010524 | 4.3357
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.002629 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0516 | 400 | 0.010524 | 4.2094
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.002698 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0981 | 407 | 0.010593 | 4.3112
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002777 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.016662 | 0 | 0.010672 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.002845 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.16501 | 58 | 0.01074 | 0.62289
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.002845 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.25321 | 89 | 0.01074 | 0.95582
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12518 | 44 | 0.01074 | 0.47254
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12518 | 44 | 0.01074 | 0.47254
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12233 | 43 | 0.01074 | 0.4618
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.002845 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12802 | 45 | 0.01074 | 0.48328
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.063415 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.01082 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.063757 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6508 | 0 | 0.011162 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.063757 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8554 | 0 | 0.011162 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.063757 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8514 | 0 | 0.011162 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.00327 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011165 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.42898 | 0 | 0.011658 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.83539 | 0 | 0.011658 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.69239 | 0 | 0.011658 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.84291 | 0 | 0.011658 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.003763 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.43274 | 0 | 0.011658 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.004032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.4032 | 100 | 0.011927 | 1.1927
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.004032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.4032 | 100 | 0.011927 | 1.1927
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.004032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011927 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.004032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011927 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.004032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011927 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.004032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011927 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.004033 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011928 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.005342 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.12821 | 24 | 0.013237 | 0.31768
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.005342 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.12821 | 24 | 0.013237 | 0.31768
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.005342 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.12287 | 23 | 0.013237 | 0.30444
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.005944 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.04993 | 8.4 | 0.013839 | 0.11624
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.006224 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21784 | 0 | 0.014119 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.006224 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21162 | 0 | 0.014119 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.006224 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21784 | 0 | 0.014119 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.068941 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.3412 | 0 | 0.016346 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.070025 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5038 | 0 | 0.01743 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.070499 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9496 | 0 | 0.017904 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0942 | 0 | 0.019353 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7562 | 0 | 0.019353 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3823 | 0 | 0.019353 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.071948 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4328 | 0 | 0.019353 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.013922 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2506 | 0 | 0.021817 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.013922 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2506 | 0 | 0.021817 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.017258 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.025153 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.017285 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.48398 | 0 | 0.02518 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.017285 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.50126 | 0 | 0.02518 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.017317 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.3078 | 422 | 0.025212 | 10.6393
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.01871 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11226 | 0 | 0.026605 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.022374 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.30652 | 0 | 0.030269 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.024742 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.44536 | 0 | 0.032637 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.024742 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.44536 | 0 | 0.032637 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.024742 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37113 | 0 | 0.032637 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.024952 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.82342 | 0 | 0.032847 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.024952 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.6238 | 0 | 0.032847 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.024952 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.032847 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 233
| 25 | 233
| 30 | 233
| 35 | 233
| 40 | 233
| 45 | 233
| 50 | 233
| 55 | 233
| 60 | 232
| 65 | 227
| 70 | 222
| 75 | 217
| 80 | 212
| 85 | 207
| 90 | 202
| 95 | 196
| 100 | 191
| 105 | 185
| 110 | 179
| 115 | 173
| Max | 233
| Min | 173
| Avg | 215.35