## test results
CRE test for: |  | 1422 BOWMAN5 - 1425 FISHRDSS | [5 empty] | FAIL
Line Rating: |  | 1079.45
Direction |  | North | → | West |  | N-W
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1422 BOWMAN5 - 1425 FISHRDSS
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.015087
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.0039774
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.18789
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0089938
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1422 BOWMAN5 - 1425 FISHRDSS
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.015533
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.0037049
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.16184
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.0090789
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 1422 BOWMAN5 - 1425 FISHRDSS
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.011382
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.17693
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.0060079
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.16582
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.0050164
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.19697
PTDF tests
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.17693 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.17693 | 0.011382
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.19986
[6 empty] | Concentration |  | 1.1296 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.014425
[6 empty] | Concentration |  | 0.081527 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 67.5032
| Percent of line rating => | [6 empty] | 6.253% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 4.605
[7 empty] | B1(N-S) | -0.012286 | 0.040127 | 0.052413 | -0.012286
[7 empty] | B2 (N-W) | 0 | 0.81477 | 0.81477 | 0
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.0086915 | 0.018975 | 0.027666 | -0.0086915
[7 empty] | B4 (S-W) | 0.01216 | 0.77577 | 0.76361 | 0.01216
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.0030763 | -0.020024 | -0.0231 | 0.0030763
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.11409 | -0.79294 | -0.90703 | 0.11409
[7 empty] | test | 0 | 0.81477 | 0.81477 | 0
[7 empty] | B1 | -1.508%
Deployment Error Percent | [6 empty] | B2 | 0%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -1.067%
[7 empty] | B4 | 1.492%
[7 empty] | B5 | 0.3776%
[7 empty] | B6 | 14%
[7 empty] | Max Abs Error | 14% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-W
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:1422 BOWMAN5 - 1425 FISHRDSS C: 1430 GRHAMES - 1435 LONGCREK C: 1439 LONCREK2 - 1442 COKFIELD | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:1422 BOWMAN5 - 1425 FISHRDSS C: 1430 GRHAMES - 1435 LONGCREK C: 1439 LONCREK2 - 1442 COKFIELD
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.010119 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 2.5803
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.010119 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.5077
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.008977 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.13465
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.008977 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.13465
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.010119 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.5482
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.009156 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 1.3734
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.009156 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.73248
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.004576 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -0.33405
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.004576 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -0.54454
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.004576 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -0.93808
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.004576 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -0.46675
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.004576 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -0.4393
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.029517 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.3542
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.029517 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.3542
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.010416 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 1.7499
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.010416 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 0.93744
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.000117 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.002106
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.000117 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.002106
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.000117 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.004446
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.005328 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -1.5345
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.005328 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -0.78322
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.005328 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -0.78322
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.005011 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -0.56374
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.018072 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.72288
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.01815 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 1.4339
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.01815 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 1.9239
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.01815 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 2.6499
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.01815 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 1.3794
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.020617 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.237
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.020617 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.2989
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.018075 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.3615
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.018075 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.45188
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.018075 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.74108
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.011782 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 5.4551
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -10.7906
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -10.6271
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -10.9541
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -10.9541
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -10.9541
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.16349 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -18.6383
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.16349 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -84.1994
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -11.1073
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -11.6121
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -11.6121
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -11.2756
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -11.2756
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -10.939
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.16544 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -11.5806
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.16544 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -12.1431
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.16544 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -11.6468
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -24.8367
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -36.4272
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.17279 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -17.1066
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.17279 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -10.5404
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.17262 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -24.3394
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.17279 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -4.3198
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.17279 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -7.8967
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.17279 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -7.8967
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.17262 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -20.7144
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.16715 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -4.3126
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.16584 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -16.6669
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.16808 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -20.1698
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.16601 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -9.6287
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.16633 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -35.6281
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.1816 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -27.2392
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.16513 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -1.0899
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.16513 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -5.6639
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.1816 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -18.3411
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.16843 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -20.2117
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.04277 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 15.6538
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.023281 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -5.634
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.21245 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -84.9796
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.21235 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -50.1141
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.04277 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 7.0571
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.048632 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 9.9209
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.048632 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 9.775
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.048632 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 11.7689
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -1.3587
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -1.3587
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -1.3587
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -1.1549
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.013707 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -1.6448
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.031383 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -1.883
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.018276 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 1.3707
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.018276 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 1.4548
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.018276 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 1.6156
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 2.9395
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.866
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 3.6009
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.866
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 2.8844
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 3.6377
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.018032 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 3.0654
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.018032 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 9.3766
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.018402 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 6.8087
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.018383 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 10.2577
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.018383 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 10.6438
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.018383 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 14.8535
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.019219 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 2.1525
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.019219 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 1.9219
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.019219 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 7.2648
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.011221 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 2.4383
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.011221 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 2.3003
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.011221 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 3.0566
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.014078 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 10.8401
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 0.63896
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.62983
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.62983
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.6207
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.010276 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 11.8893
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.010276 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 11.8996
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 3.4335
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 3.4641
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.016178 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 3.5009
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.016178 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 3.4961
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 3.2495
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 3.2342
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.017821 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 7.0393
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.017809 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 7.7469
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.017821 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 7.7521
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.019058 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 2.63
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017291 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 2.0403
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017291 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 1.9885
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017291 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 9.6138
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.017736 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 6.8816
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.017736 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 9.134
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.016582 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 13.0169
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.016582 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 13.1827
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.016582 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 12.934
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.016275 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 2.9621
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.016275 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 7.8771
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.015576 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 3.489
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.016302 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.8151
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.016315 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.68523
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.014787 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 9.094
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.014787 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 8.68
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.011343 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 6.0912
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.011343 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 8.9269
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.010831 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.81232
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.010831 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 2.4045
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.007336 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 4.1742
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003053 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.63808
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003053 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.65945
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.002952 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 1.2015
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.14044
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.14349
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.14044
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.14044
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.003104 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 1.3161
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.003104 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 1.3192
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002662 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.1544
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002662 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.23692
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.11713
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.11713
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.11447
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.11979
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.003054 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 1.2582
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.003054 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 1.2216
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.003485 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 1.9028
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.003485 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 2.6138
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.00332 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.20252
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.00332 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.3154
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.00332 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.50132
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.003384 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.52452
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.003384 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.57528
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.003384 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.52452
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.004405 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.09691
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.004405 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.048455
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.004405 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.048455
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.2156
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.1686
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.20792
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.21696
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.00215 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.0258
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.00215 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.02365
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.002958 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.070992
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.002958 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.070992
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.002958 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.068034
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.003037 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 1.2027
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.00729 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 9.7176
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.00729 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 9.6811
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.003774 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.14341
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.003774 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.072838
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.003774 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.05661
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.003774 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.17738
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.15535 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -11.651
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.18868 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -28.3012
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.18266 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -30.9612
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.12248 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -18.3723
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.17161 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -10.8112
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.55475 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -360.423
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.017812 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.71248
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.017812 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.71248
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.002537 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -1.0706
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.005508 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.72706
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.005508 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.73807
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.005508 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 1.7791
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.005862 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.9262
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.005862 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.93792
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.005862 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 1.0258
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.005915 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 3.4544
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.005915 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 3.5194
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.005914 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 2.5608
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.95381
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.9585
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.9568
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.96574
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.004849 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.038792
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.004849 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.038792
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.002926 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.052668
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.002926 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.052668
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.002926 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.04389
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.004838 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.066281
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.000816 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.014688
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.000816 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.014688
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.003085 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.10798
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.003085 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.10489
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.003085 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.10798
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.002115 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.05922
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.002115 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.061335
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.16371 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -5.7299
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.16371 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -4.9113
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.28815
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.28815
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.28815
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.28815
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.003837 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.023022
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.004096 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0098304
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.004096 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0098304
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.004096 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.011469
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.00383 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.01532
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.00438 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.010512
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.00438 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.010512
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.57977
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.54427
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.55216
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.57977
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.71781
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.78091
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.005534 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.84393
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.005534 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.82733
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.005534 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 1.2872
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.58291
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.59523
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.61986
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 1.1905
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.043841 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -1.4468
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.043841 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.096
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.00215 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.0258
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.004636 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.33843
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.40258
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.41278
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.1342
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.033551
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.40258
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.40768
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.39953
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.1274
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.23442
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.00401 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 2.5223
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.00457 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.65808
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.00457 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.85916
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.004406 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.052872
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.030846 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.18508
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.00401 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 1.3474
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003985 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 1.331
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003985 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 1.3549
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.003953 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.15021
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.00397 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.09925
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.00397 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.09925
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.003968 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.15078
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.003887 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.11272
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.004009 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.59453
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.004009 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.59574
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.004009 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.61338
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.65396
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.63327
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.4139
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.60015
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.60843
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.52565
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.50279
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.50759
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.59374
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.75472
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.79009
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.88233
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.52502
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.52502
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.62347
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.005015 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 1.5547
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.005015 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 2.0712
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.21634
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.22664
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.22664
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.2421
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.24392
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.22899
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.22899
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.23397
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004978 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.76661
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004978 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.73674
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.23894
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.23894
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -11.5224
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -11.5224
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -15.2754
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -13.1685
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -13.1685
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -18.9297
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -34.2687
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -23.3889
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -21.7924
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -22.3849
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -24.1955
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -34.565
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -28.9902
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -17.5467
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -34.5385
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -27.3257
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -33.1156
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -20.184
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.16428 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -24.4774
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.16999 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -30.5978
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.16999 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -30.5978
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.16977 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -38.1974
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.17129 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -21.411
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.17129 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -21.411
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 2.5763
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 2.5947
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 5.6862
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 2.6315
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 2.6499
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 5.7046
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.015651 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 3.0676
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.015651 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 1.7373
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.018851 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.8421
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.8951
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.8951
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 7.3083
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 2.8598
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.8421
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 2.8774
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 7.2201
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017631 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017631 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 2.4327
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 2.1368
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 2.3834
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 6.5584
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.01503 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 2.265
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.01503 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 2.2695
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.01503 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 2.6663
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.015079 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 2.2845
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.015079 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 2.2965
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.015079 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 2.6765
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.007336 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 4.2622
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 11.0902
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 11.0902
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.011756 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.37619
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.011727 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.5629
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.011727 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.53944
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.14116
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.59991
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011763 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.19997
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.25879
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.29407
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.011727 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 1.2313
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.17574 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -14.7623
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.15521 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -12.4169
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.15513 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -23.2703
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.15513 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -23.2703
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.63161
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.59503
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.47281
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 1.3667
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 1.3694
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 1.3587
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 0.85642
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 2.1767
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.35684
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 0.89468
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 0.82867
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 0.91608
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 0.90984
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.00892 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.28544
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.00892 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.2676
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.91997
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.91997
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 0.98627
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 0.90754
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 1.9755
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 1.9846
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.009299 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 1.2647
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.008711 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.28746
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.39052
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.39052
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.35332
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.35332
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.008174 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.58035
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.008174 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.08174
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008694 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.4171
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008694 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.4171
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008694 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 2.13
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.5952
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.54942
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.5952
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.5952
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.009248 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 1.378
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.009248 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.60204
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 0.83083
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.79979
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.79431
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.49758
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.11139
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.009411 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 6.9924
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.009365 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 6.8833
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.009424 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.6209
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.009424 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.6209
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.009424 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.6209
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 1.6746
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.009308 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 1.6103
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.009308 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 1.2566
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 1.5396
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 1.5264
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 1.5027
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 2.5458
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.59206
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.58466
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.76413
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.68087
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 1.5045
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 1.4483
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 1.452
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 1.4474
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 2.4799
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.00941 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.04705
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.00941 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.19761
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 1.7616
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.7821
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.7821
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 4.3411
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.009471 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 3.7695
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.42343
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.42343
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.42343
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.50628
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.50628
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.49707
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.013448 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 11.1215
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.013448 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 11.0139
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.008656 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.39904
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.56164
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.56164
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 0.77595
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.54686
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.54686
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 0.75378
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 1.6655
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 1.4675
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 1.4527
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.009234 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.32319
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.009059 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 4.1581
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.61172
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.62113
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.65877
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.59289
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.58348
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 0.97874
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.55525
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 1.5101
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.4907
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.4907
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00968 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 1.5682
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.009421 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 1.4791
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.6581
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.66737
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.36149
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.27807
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.009208 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.71822
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.009208 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.73664
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.14987
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.009248 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 1.5259
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.009247 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 1.5627
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.009251 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 1.9705
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.009252 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 2.1095
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.009246 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.11095
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.009246 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.16643
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.00901 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.4505
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.97313
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.97313
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.50528
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.49592
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.50528
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.53335
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.50528
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.50528
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.54271
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.54271
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.009398 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.11278
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.53155
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.56003
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.53155
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.53155
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.56003
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.53155
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.007479 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.49361
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008762 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 1.4107
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008762 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 1.4545
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008762 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 2.173
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008762 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 4.7841
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008762 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 5.634
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008691 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 5.6578
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008691 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 4.9017
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008691 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 5.2146
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008762 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.11391
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.00941 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.11292
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.31882
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.32538
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.30663
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.4304
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.16597
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.19129
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.1866
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.3282
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.16879
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.8008
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 1.3878
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.49848
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.57406
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.3618
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.81204
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.69144
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.70752
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.402
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.14472
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 0.75576
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.5628
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.50652
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.57888
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.52099
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.81204
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 0.77988
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 0.82812
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.61104
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.6432
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.6432
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 1.3748
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.035255
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.15161 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -11.5983
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.15535 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -12.4278
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.15535 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -6.2139
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -12.4732
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.15523 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -12.4182
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.15225 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -12.1803
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.15128 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -12.7077
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -12.4732
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.27337
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.19359 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -23.231
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.19359 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -45.1069
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.19359 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -32.9494
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.53236
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.44123
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.53715
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.27577
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.2398
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.23467 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -14.0799
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.047963 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.13587 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.15816 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.75917
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -7.3037
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -20.9373
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -26.2934
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -23.1772
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -20.4504
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -15.6787
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.16073 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -24.1089
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -17.9695
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -23.8795
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -29.7096
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -34.2619
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.003774 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.027824 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.00049 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.14269
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.22219
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.3771
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.35955
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.15682
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.14535
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.072675
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.35955
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.1377
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.16448
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.08415
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.18693
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.071895
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.033551
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.071895
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.18693
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.18693
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.5661
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.19125
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.21038
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.19125
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.004139 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.049668
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.004727 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.070905
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.004727 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.10872
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.005032 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.24154
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.004748 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.037984
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.004006 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.72108
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.00401 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.7218
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003985 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.7173
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003985 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.7173
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000487 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.0487
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000487 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.0487
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.1021
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.1021
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.1021
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.065344
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.1021
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.1021
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.1021
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.06126
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000487 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000487 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -0.2435
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000487 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -0.2435
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000487 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.003269 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.043841 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.000923 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.00316 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:1422 BOWMAN5 - 1425 FISHRDSS C: 1430 GRHAMES - 1435 LONGCREK C: 1439 LONCREK2 - 1442 COKFIELD | [7 empty] | 67.5032
Number of Bus | Name of Bus | ID | Max MW | L:1422 BOWMAN5 - 1425 FISHRDSS C: 1430 GRHAMES - 1435 LONGCREK C: 1439 LONCREK2 - 1442 COKFIELD | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.010119 | north | Y | -0.0049678 | 0.0061416 | 0.19801 | 0.0011252 | 0.0011252 | houston | Y | 0.0049678 | 0.97986
239 | BOSQUESW | 1 | 149 | 0.010119 | north | Y | -0.0049678 | 0.0061416 | 0.19801 | 0.0011252 | 0.0011252 | houston | Y | 0.0049678 | 0.57254
244 | WHITNYDM | 1 | 15 | 0.008977 | north | N | -0.0061098 | 0.0049996 | 0.19686 | -1.682e-05 | 1.682e-05 | houston | Y | 0.0061098 | 0
245 | WHITNYDM | 2 | 15 | 0.008977 | north | N | -0.0061098 | 0.0049996 | 0.19686 | -1.682e-05 | 1.682e-05 | houston | Y | 0.0061098 | 0
247 | BOSQUESW | 2 | 153 | 0.010119 | north | Y | -0.0049678 | 0.0061416 | 0.19801 | 0.0011252 | 0.0011252 | houston | Y | 0.0049678 | 0.58791
251 | BOSQUESW | 2 | 150 | 0.009156 | north | Y | -0.0059308 | 0.0051786 | 0.19704 | 0.00016218 | 0.00016218 | houston | Y | 0.0059308 | 0.86529
253 | BOSQUESW | 2 | 80 | 0.009156 | north | Y | -0.0059308 | 0.0051786 | 0.19704 | 0.00016218 | 0.00016218 | houston | Y | 0.0059308 | 0.46149
332 | RWMILLER | 1 | 73 | -0.004576 | north | Y | -0.019663 | -0.0085534 | 0.18331 | -0.01357 | 0.0085534 | south | Y | 0.019663 | 0.81098
333 | RWMILLER | 2 | 119 | -0.004576 | north | Y | -0.019663 | -0.0085534 | 0.18331 | -0.01357 | 0.0085534 | south | Y | 0.019663 | 1.322
334 | RWMILLER | 3 | 205 | -0.004576 | north | Y | -0.019663 | -0.0085534 | 0.18331 | -0.01357 | 0.0085534 | south | Y | 0.019663 | 2.2774
335 | RWMILLER | 4 | 102 | -0.004576 | north | Y | -0.019663 | -0.0085534 | 0.18331 | -0.01357 | 0.0085534 | south | Y | 0.019663 | 1.1332
336 | RWMILLER | 5 | 96 | -0.004576 | north | Y | -0.019663 | -0.0085534 | 0.18331 | -0.01357 | 0.0085534 | south | Y | 0.019663 | 1.0665
344 | MRSSHPRD | 1 | 12 | -0.029517 | north | N | -0.044604 | -0.033494 | 0.15837 | -0.038511 | 0.033494 | south | Y | 0.044604 | 0
345 | MRSSHPRD | 2 | 12 | -0.029517 | north | N | -0.044604 | -0.033494 | 0.15837 | -0.038511 | 0.033494 | south | Y | 0.044604 | 0
366 | JNSNCNTY | 1 | 168 | 0.010416 | north | Y | -0.0046708 | 0.0064386 | 0.1983 | 0.0014222 | 0.0014222 | houston | Y | 0.0046708 | 0.54576
367 | JNSNCNTY | 2 | 90 | 0.010416 | north | Y | -0.0046708 | 0.0064386 | 0.1983 | 0.0014222 | 0.0014222 | houston | Y | 0.0046708 | 0.29237
503 | NTHTEXAS | 1 | 18 | -0.000117 | north | Y | -0.015204 | -0.0040944 | 0.18777 | -0.0091108 | 0.0040944 | south | Y | 0.015204 | 0.19997
504 | NTHTEXAS | 2 | 18 | -0.000117 | north | Y | -0.015204 | -0.0040944 | 0.18777 | -0.0091108 | 0.0040944 | south | Y | 0.015204 | 0.19997
505 | NTHTEXAS | 3 | 38 | -0.000117 | north | Y | -0.015204 | -0.0040944 | 0.18777 | -0.0091108 | 0.0040944 | south | Y | 0.015204 | 0.42215
580 | JCKCNTY8 | 1 | 288 | -0.005328 | north | Y | -0.020415 | -0.0093054 | 0.18256 | -0.014322 | 0.0093054 | south | Y | 0.020415 | 3.1995
581 | JCKCNTY8 | 2 | 147 | -0.005328 | north | Y | -0.020415 | -0.0093054 | 0.18256 | -0.014322 | 0.0093054 | south | Y | 0.020415 | 1.6331
582 | JCKCNTY8 | 3 | 147 | -0.005328 | north | Y | -0.020415 | -0.0093054 | 0.18256 | -0.014322 | 0.0093054 | south | Y | 0.020415 | 1.6331
728 | WOLFRIDG | 1 | 112.5 | -0.005011 | north | Y | -0.020098 | -0.0089884 | 0.18288 | -0.014005 | 0.0089884 | south | Y | 0.020098 | 1.2498
837 | NEWMAN_G | 1 | 40 | 0.018072 | north | Y | 0.0029852 | 0.014095 | 0.20596 | 0.0090782 | 0.0029852 | North | N | 0.0029852 | 0
842 | OLINGER_ | 1 | 79 | 0.01815 | north | Y | 0.0030632 | 0.014173 | 0.20604 | 0.0091562 | 0.0030632 | North | N | 0.0030632 | 0
843 | OLINGER_ | 1 | 106 | 0.01815 | north | Y | 0.0030632 | 0.014173 | 0.20604 | 0.0091562 | 0.0030632 | North | N | 0.0030632 | 0
844 | OLINGER_ | 1 | 146 | 0.01815 | north | Y | 0.0030632 | 0.014173 | 0.20604 | 0.0091562 | 0.0030632 | North | N | 0.0030632 | 0
845 | OLINGER_ | 1 | 76 | 0.01815 | north | Y | 0.0030632 | 0.014173 | 0.20604 | 0.0091562 | 0.0030632 | North | N | 0.0030632 | 0
923 | SPENCER_ | 1 | 60 | 0.020617 | north | Y | 0.0055302 | 0.01664 | 0.2085 | 0.011623 | 0.0055302 | North | N | 0.0055302 | 0
924 | SPENCER_ | 1 | 63 | 0.020617 | north | Y | 0.0055302 | 0.01664 | 0.2085 | 0.011623 | 0.0055302 | North | N | 0.0055302 | 0
948 | STEAM1 | 1 | 20 | 0.018075 | north | Y | 0.0029882 | 0.014098 | 0.20596 | 0.0090812 | 0.0029882 | North | N | 0.0029882 | 0
949 | STEAM2 | 1 | 25 | 0.018075 | north | Y | 0.0029882 | 0.014098 | 0.20596 | 0.0090812 | 0.0029882 | North | N | 0.0029882 | 0
950 | STEAM3 | 1 | 41 | 0.018075 | north | Y | 0.0029882 | 0.014098 | 0.20596 | 0.0090812 | 0.0029882 | North | N | 0.0029882 | 0
990 | GIBN_CRE | 1 | 463 | 0.011782 | north | Y | -0.0033048 | 0.0078046 | 0.19967 | 0.0027882 | 0.0027882 | houston | Y | 0.0033048 | 0.23917
1002 | PBCTAGE_ | A | 66 | -0.16349 | west | Y | -0.17858 | -0.16747 | 0.024394 | -0.17249 | 0.024394 | west | N | 0.024394 | 0
1003 | PBCTBGE_ | B | 65 | -0.16349 | west | Y | -0.17858 | -0.16747 | 0.024394 | -0.17249 | 0.024394 | west | N | 0.024394 | 0
1004 | PBCTCGE_ | C | 67 | -0.16349 | west | Y | -0.17858 | -0.16747 | 0.024394 | -0.17249 | 0.024394 | west | N | 0.024394 | 0
1005 | PBCTDGE_ | D | 67 | -0.16349 | west | Y | -0.17858 | -0.16747 | 0.024394 | -0.17249 | 0.024394 | west | N | 0.024394 | 0
1006 | PBCTEGE_ | E | 67 | -0.16349 | west | Y | -0.17858 | -0.16747 | 0.024394 | -0.17249 | 0.024394 | west | N | 0.024394 | 0
1007 | PB5GEN_6 | MB | 114 | -0.16349 | west | Y | -0.17858 | -0.16747 | 0.024394 | -0.17249 | 0.024394 | west | N | 0.024394 | 0
1008 | PB6GEN_7 | MB | 515 | -0.16349 | west | Y | -0.17858 | -0.16747 | 0.024394 | -0.17249 | 0.024394 | west | N | 0.024394 | 0
1039 | MRGNAG_1 | A | 66 | -0.16829 | west | Y | -0.18338 | -0.17227 | 0.019596 | -0.17729 | 0.019596 | west | N | 0.019596 | 0
1040 | MRGNBG_2 | B | 69 | -0.16829 | west | Y | -0.18338 | -0.17227 | 0.019596 | -0.17729 | 0.019596 | west | N | 0.019596 | 0
1041 | MRGNCG_3 | C | 69 | -0.16829 | west | Y | -0.18338 | -0.17227 | 0.019596 | -0.17729 | 0.019596 | west | N | 0.019596 | 0
1042 | MRGNDG_4 | D | 67 | -0.16829 | west | Y | -0.18338 | -0.17227 | 0.019596 | -0.17729 | 0.019596 | west | N | 0.019596 | 0
1043 | MRGNEG_5 | E | 67 | -0.16829 | west | Y | -0.18338 | -0.17227 | 0.019596 | -0.17729 | 0.019596 | west | N | 0.019596 | 0
1044 | MRGNFG_6 | F | 65 | -0.16829 | west | Y | -0.18338 | -0.17227 | 0.019596 | -0.17729 | 0.019596 | west | N | 0.019596 | 0
1045 | CALENG1G | 1 | 70 | -0.16544 | west | N | -0.18052 | -0.16941 | 0.022451 | -0.17443 | 0.022451 | west | N | 0.022451 | 0
1046 | CALENG2G | 2 | 73.4 | -0.16544 | west | N | -0.18052 | -0.16941 | 0.022451 | -0.17443 | 0.022451 | west | N | 0.022451 | 0
1047 | CALENG3G | 3 | 70.4 | -0.16544 | west | N | -0.18052 | -0.16941 | 0.022451 | -0.17443 | 0.022451 | west | N | 0.022451 | 0
1058 | LONGSHOR | 1 | 150 | -0.16558 | west | Y | -0.18066 | -0.16956 | 0.02231 | -0.17457 | 0.02231 | west | N | 0.02231 | 0
1058 | LONGSHOR | 2 | 220 | -0.16558 | west | Y | -0.18066 | -0.16956 | 0.02231 | -0.17457 | 0.02231 | west | N | 0.02231 | 0
1061 | CIELOGEN | 1 | 99 | -0.17279 | west | Y | -0.18788 | -0.17677 | 0.015094 | -0.18179 | 0.015094 | west | N | 0.015094 | 0
1062 | CIELOGEN | 1 | 61 | -0.17279 | west | Y | -0.18788 | -0.17677 | 0.015094 | -0.18179 | 0.015094 | west | N | 0.015094 | 0
1068 | SCURRYCW | 1 | 141 | -0.17262 | west | Y | -0.18771 | -0.1766 | 0.015268 | -0.18161 | 0.015268 | west | N | 0.015268 | 0
1069 | KINDERMG | 1 | 25 | -0.17279 | west | N | -0.18788 | -0.17677 | 0.015094 | -0.18179 | 0.015094 | west | N | 0.015094 | 0
1070 | KINDERMG | 1 | 45.7 | -0.17279 | west | N | -0.18788 | -0.17677 | 0.015094 | -0.18179 | 0.015094 | west | N | 0.015094 | 0
1071 | KINDERMG | 1 | 45.7 | -0.17279 | west | N | -0.18788 | -0.17677 | 0.015094 | -0.18179 | 0.015094 | west | N | 0.015094 | 0
1073 | SCURRYCW | 2 | 120 | -0.17262 | west | Y | -0.18771 | -0.1766 | 0.015268 | -0.18161 | 0.015268 | west | N | 0.015268 | 0
1320 | BSP 1 | 1 | 25.8 | -0.16715 | west | N | -0.18224 | -0.17113 | 0.020734 | -0.17615 | 0.020734 | west | N | 0.020734 | 0
1326 | STANTONW | 1 | 100.5 | -0.16584 | west | Y | -0.18093 | -0.16982 | 0.022048 | -0.17483 | 0.022048 | west | N | 0.022048 | 0
1327 | WILDHRSE | 1 | 120 | -0.16808 | west | Y | -0.18317 | -0.17206 | 0.019806 | -0.17708 | 0.019806 | west | N | 0.019806 | 0
1328 | OCOTILLO | 1 | 58 | -0.16601 | west | Y | -0.1811 | -0.16999 | 0.021876 | -0.17501 | 0.021876 | west | N | 0.021876 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.16633 | west | Y | -0.18142 | -0.17031 | 0.021557 | -0.17532 | 0.021557 | west | N | 0.021557 | 0
1343 | TRENTIPP | 1 | 150 | -0.1816 | west | Y | -0.19668 | -0.18557 | 0.0062927 | -0.19059 | 0.0062927 | west | N | 0.0062927 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.16513 | west | Y | -0.18022 | -0.16911 | 0.022759 | -0.17412 | 0.022759 | west | N | 0.022759 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.16513 | west | Y | -0.18022 | -0.16911 | 0.022759 | -0.17412 | 0.022759 | west | N | 0.022759 | 0
1354 | AEPWIND_ | 1 | 101 | -0.1816 | west | Y | -0.19668 | -0.18557 | 0.0062927 | -0.19059 | 0.0062927 | west | N | 0.0062927 | 0
1360 | GUNSIGHT | 1 | 120 | -0.16843 | west | Y | -0.18352 | -0.17241 | 0.019457 | -0.17742 | 0.019457 | west | N | 0.019457 | 0
1432 | GRHAMSES | 2 | 366 | 0.04277 | north | Y | 0.027683 | 0.038793 | 0.23066 | 0.033776 | 0.027683 | North | N | 0.027683 | 0
1433 | GRHAMSES | 1 | 242 | -0.023281 | north | Y | -0.038368 | -0.027258 | 0.16461 | -0.032275 | 0.027258 | south | Y | 0.038368 | 2.6885
1437 | MESQUITW | 1 | 400 | -0.21245 | west | Y | -0.22754 | -0.21643 | -0.024561 | -0.22144 | 0.024561 | west | N | 0.024561 | 0
1438 | MESQUITW | 1 | 236 | -0.21235 | west | Y | -0.22743 | -0.21633 | -0.02446 | -0.22134 | 0.02446 | west | N | 0.02446 | 0
1442 | COKFIELD | 1 | 165 | 0.04277 | west | Y | 0.027683 | 0.038793 | 0.23066 | 0.033776 | 0.027683 | North | Y | 0.23066 | 33.4908
1453 | WCPWRCO_ | 1 | 204 | 0.048632 | north | Y | 0.033545 | 0.044655 | 0.23652 | 0.039638 | 0.033545 | North | N | 0.033545 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.048632 | north | Y | 0.033545 | 0.044655 | 0.23652 | 0.039638 | 0.033545 | North | N | 0.033545 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.048632 | north | Y | 0.033545 | 0.044655 | 0.23652 | 0.039638 | 0.033545 | North | N | 0.033545 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.067936 | west | Y | -0.083023 | -0.071913 | 0.11995 | -0.07693 | 0.071913 | south | Y | 0.11995 | 0.96076
1479 | WFCOGEN_ | 2 | 20 | -0.067936 | west | Y | -0.083023 | -0.071913 | 0.11995 | -0.07693 | 0.071913 | south | Y | 0.11995 | 0.96076
1482 | WFCOGEN_ | 1 | 20 | -0.067936 | west | Y | -0.083023 | -0.071913 | 0.11995 | -0.07693 | 0.071913 | south | Y | 0.11995 | 0.96076
1482 | WFCOGEN_ | 2 | 17 | -0.067936 | west | Y | -0.083023 | -0.071913 | 0.11995 | -0.07693 | 0.071913 | south | Y | 0.11995 | 0.81665
1600 | BARTNWND | 1 | 120 | -0.013707 | north | Y | -0.028794 | -0.017684 | 0.17418 | -0.022701 | 0.017684 | south | Y | 0.028794 | 1.3331
1643 | SLSTR1PP | 1 | 60 | -0.031383 | north | Y | -0.04647 | -0.03536 | 0.1565 | -0.040377 | 0.03536 | south | Y | 0.04647 | 0.66656
1675 | PEC_1G | 1 | 75 | 0.018276 | north | N | 0.0031892 | 0.014299 | 0.20616 | 0.0092822 | 0.0031892 | North | N | 0.0031892 | 0
1676 | PEC_2G | 2 | 79.6 | 0.018276 | north | N | 0.0031892 | 0.014299 | 0.20616 | 0.0092822 | 0.0031892 | North | N | 0.0031892 | 0
1677 | PEC_3G | 3 | 88.4 | 0.018276 | north | N | 0.0031892 | 0.014299 | 0.20616 | 0.0092822 | 0.0031892 | North | N | 0.0031892 | 0
1678 | LAMARPWR | 1 | 160 | 0.018372 | north | Y | 0.0032852 | 0.014395 | 0.20626 | 0.0093782 | 0.0032852 | North | N | 0.0032852 | 0
1679 | LAMARPWR | 2 | 156 | 0.018372 | north | Y | 0.0032852 | 0.014395 | 0.20626 | 0.0093782 | 0.0032852 | North | N | 0.0032852 | 0
1680 | LAMARPWR | 3 | 196 | 0.018372 | north | Y | 0.0032852 | 0.014395 | 0.20626 | 0.0093782 | 0.0032852 | North | N | 0.0032852 | 0
1681 | LAMARPWR | 4 | 156 | 0.018372 | north | Y | 0.0032852 | 0.014395 | 0.20626 | 0.0093782 | 0.0032852 | North | N | 0.0032852 | 0
1682 | LAMARPWR | 5 | 157 | 0.018372 | north | Y | 0.0032852 | 0.014395 | 0.20626 | 0.0093782 | 0.0032852 | North | N | 0.0032852 | 0
1683 | LAMARPWR | 6 | 198 | 0.018372 | north | Y | 0.0032852 | 0.014395 | 0.20626 | 0.0093782 | 0.0032852 | North | N | 0.0032852 | 0
1687 | VALLEY_1 | 1 | 170 | 0.018032 | north | Y | 0.0029452 | 0.014055 | 0.20592 | 0.0090382 | 0.0029452 | North | N | 0.0029452 | 0
1688 | VALLEY_2 | 2 | 520 | 0.018032 | north | Y | 0.0029452 | 0.014055 | 0.20592 | 0.0090382 | 0.0029452 | North | N | 0.0029452 | 0
1689 | VALLEY_3 | 3 | 370 | 0.018402 | north | Y | 0.0033152 | 0.014425 | 0.20629 | 0.0094082 | 0.0033152 | North | N | 0.0033152 | 0
1701 | MOSES_1G | 1 | 558 | 0.018383 | north | Y | 0.0032962 | 0.014406 | 0.20627 | 0.0093892 | 0.0032962 | North | N | 0.0032962 | 0
1702 | MOSES_2G | 2 | 579 | 0.018383 | north | Y | 0.0032962 | 0.014406 | 0.20627 | 0.0093892 | 0.0032962 | North | N | 0.0032962 | 0
1703 | MOSES_3G | 3 | 808 | 0.018383 | north | Y | 0.0032962 | 0.014406 | 0.20627 | 0.0093892 | 0.0032962 | North | N | 0.0032962 | 0
1861 | EAGLEMNT | MB | 112 | 0.019219 | north | Y | 0.0041322 | 0.015242 | 0.20711 | 0.010225 | 0.0041322 | North | N | 0.0041322 | 0
1862 | EAGLEMNT | MB | 100 | 0.019219 | north | Y | 0.0041322 | 0.015242 | 0.20711 | 0.010225 | 0.0041322 | North | N | 0.0041322 | 0
1863 | EAGLEMNT | MB | 378 | 0.019219 | north | Y | 0.0041322 | 0.015242 | 0.20711 | 0.010225 | 0.0041322 | North | N | 0.0041322 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.011221 | north | Y | -0.0038658 | 0.0072436 | 0.19911 | 0.0022272 | 0.0022272 | houston | Y | 0.0038658 | 0.35606
1878 | WLFHOLW_ | 2 | 205 | 0.011221 | north | Y | -0.0038658 | 0.0072436 | 0.19911 | 0.0022272 | 0.0022272 | houston | Y | 0.0038658 | 0.33591
1879 | WLFHOLW_ | 3 | 272.4 | 0.011221 | north | Y | -0.0038658 | 0.0072436 | 0.19911 | 0.0022272 | 0.0022272 | houston | Y | 0.0038658 | 0.44635
1889 | DECRDOVA | MB | 770 | 0.014078 | north | Y | -0.0010088 | 0.010101 | 0.20197 | 0.0050842 | 0.0010088 | North | N | 0.0010088 | 0
1892 | DECRDOVA | A | 70 | 0.009128 | north | Y | -0.0059588 | 0.0051506 | 0.19702 | 0.00013418 | 0.00013418 | houston | Y | 0.0059588 | 0.40772
1893 | DECRDOVA | B | 69 | 0.009128 | north | Y | -0.0059588 | 0.0051506 | 0.19702 | 0.00013418 | 0.00013418 | houston | Y | 0.0059588 | 0.4019
1894 | DECRDOVA | C | 69 | 0.009128 | north | Y | -0.0059588 | 0.0051506 | 0.19702 | 0.00013418 | 0.00013418 | houston | Y | 0.0059588 | 0.4019
1895 | DECRDOVA | D | 68 | 0.009128 | north | Y | -0.0059588 | 0.0051506 | 0.19702 | 0.00013418 | 0.00013418 | houston | Y | 0.0059588 | 0.39607
1898 | COMCHEPK | 1 | 1157 | 0.010276 | north | N | -0.0048108 | 0.0062986 | 0.19816 | 0.0012822 | 0.0012822 | houston | Y | 0.0048108 | 0
1899 | COMCHEPK | 2 | 1158 | 0.010276 | north | N | -0.0048108 | 0.0062986 | 0.19816 | 0.0012822 | 0.0012822 | houston | Y | 0.0048108 | 0
1937 | MDLTHELP | 5 | 224 | 0.015328 | north | Y | 0.00024125 | 0.011351 | 0.20322 | 0.0063342 | 0.00024125 | North | N | 0.00024125 | 0
1938 | MDLTHELP | 6 | 226 | 0.015328 | north | Y | 0.00024125 | 0.011351 | 0.20322 | 0.0063342 | 0.00024125 | North | N | 0.00024125 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.016178 | north | Y | 0.0010912 | 0.012201 | 0.20407 | 0.0071842 | 0.0010912 | North | N | 0.0010912 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.016178 | north | Y | 0.0010912 | 0.012201 | 0.20407 | 0.0071842 | 0.0010912 | North | N | 0.0010912 | 0
1943 | MDLTHELP | 3 | 212 | 0.015328 | north | Y | 0.00024125 | 0.011351 | 0.20322 | 0.0063342 | 0.00024125 | North | N | 0.00024125 | 0
1944 | MDLTHELP | 4 | 211 | 0.015328 | north | Y | 0.00024125 | 0.011351 | 0.20322 | 0.0063342 | 0.00024125 | North | N | 0.00024125 | 0
1947 | HANDLEY_ | 3 | 395 | 0.017821 | north | Y | 0.0027342 | 0.013844 | 0.20571 | 0.0088272 | 0.0027342 | North | N | 0.0027342 | 0
1948 | HANDLEY_ | 4 | 435 | 0.017809 | north | Y | 0.0027222 | 0.013832 | 0.2057 | 0.0088152 | 0.0027222 | North | N | 0.0027222 | 0
1949 | HANDLEY_ | 5 | 435 | 0.017821 | north | Y | 0.0027342 | 0.013844 | 0.20571 | 0.0088272 | 0.0027342 | North | N | 0.0027342 | 0
2371 | COLLIN_1 | MB | 138 | 0.019058 | north | Y | 0.0039712 | 0.015081 | 0.20695 | 0.010064 | 0.0039712 | North | N | 0.0039712 | 0
2413 | MTCK6_G | 6 | 118 | 0.017291 | north | Y | 0.0022042 | 0.013314 | 0.20518 | 0.0082972 | 0.0022042 | North | N | 0.0022042 | 0
2414 | MTCK7_G | 7 | 115 | 0.017291 | north | Y | 0.0022042 | 0.013314 | 0.20518 | 0.0082972 | 0.0022042 | North | N | 0.0022042 | 0
2417 | MTCK8_G | 8 | 556 | 0.017291 | north | Y | 0.0022042 | 0.013314 | 0.20518 | 0.0082972 | 0.0022042 | North | N | 0.0022042 | 0
2451 | LKHB1_G | 1 | 388 | 0.017736 | north | Y | 0.0026492 | 0.013759 | 0.20562 | 0.0087422 | 0.0026492 | North | N | 0.0026492 | 0
2452 | LKHB2_G | 2 | 515 | 0.017736 | north | Y | 0.0026492 | 0.013759 | 0.20562 | 0.0087422 | 0.0026492 | North | N | 0.0026492 | 0
3097 | MARTLAKE | 1 | 785 | 0.016582 | north | Y | 0.0014952 | 0.012605 | 0.20447 | 0.0075882 | 0.0014952 | North | N | 0.0014952 | 0
3098 | MARTLAKE | 2 | 795 | 0.016582 | north | Y | 0.0014952 | 0.012605 | 0.20447 | 0.0075882 | 0.0014952 | North | N | 0.0014952 | 0
3099 | MARTLAKE | 3 | 780 | 0.016582 | north | Y | 0.0014952 | 0.012605 | 0.20447 | 0.0075882 | 0.0014952 | North | N | 0.0014952 | 0
3107 | STRYKER_ | 1 | 182 | 0.016275 | north | Y | 0.0011882 | 0.012298 | 0.20416 | 0.0072812 | 0.0011882 | North | N | 0.0011882 | 0
3108 | STRYKER_ | 2 | 484 | 0.016275 | north | Y | 0.0011882 | 0.012298 | 0.20416 | 0.0072812 | 0.0011882 | North | N | 0.0011882 | 0
3126 | TRINIDAD | 1 | 224 | 0.015576 | north | Y | 0.00048925 | 0.011599 | 0.20346 | 0.0065822 | 0.00048925 | North | N | 0.00048925 | 0
3309 | ASPN_G | 1 | 50 | 0.016302 | north | Y | 0.0012152 | 0.012325 | 0.20419 | 0.0073082 | 0.0012152 | North | N | 0.0012152 | 0
3348 | CHAMPION | MB | 42 | 0.016315 | north | N | 0.0012282 | 0.012338 | 0.2042 | 0.0073212 | 0.0012282 | North | N | 0.0012282 | 0
3381 | BBRN_1G | 1 | 615 | 0.014787 | north | Y | -0.00029975 | 0.01081 | 0.20267 | 0.0057932 | 0.00029975 | North | N | 0.00029975 | 0
3382 | BBRN_2G | 2 | 587 | 0.014787 | north | Y | -0.00029975 | 0.01081 | 0.20267 | 0.0057932 | 0.00029975 | North | N | 0.00029975 | 0
3403 | THOUSE_1 | MB | 537 | 0.011343 | north | Y | -0.0037438 | 0.0073656 | 0.19923 | 0.0023492 | 0.0023492 | houston | Y | 0.0037438 | 0
3404 | THOUSE_2 | 2 | 787 | 0.011343 | north | Y | -0.0037438 | 0.0073656 | 0.19923 | 0.0023492 | 0.0023492 | houston | Y | 0.0037438 | 1.0975
3416 | LAKE_CRK | MB | 75 | 0.010831 | north | Y | -0.0042558 | 0.0068536 | 0.19872 | 0.0018372 | 0.0018372 | houston | Y | 0.0042558 | 0
3417 | LAKE_CRK | MB | 222 | 0.010831 | north | Y | -0.0042558 | 0.0068536 | 0.19872 | 0.0018372 | 0.0018372 | houston | Y | 0.0042558 | 0
3432 | SANDOW_4 | 4 | 569 | 0.007336 | south | Y | -0.0077508 | 0.0033586 | 0.19522 | -0.0016578 | 0.0016578 | houston | Y | 0.0033586 | 0.96773
5026 | BRAUNIG_ | 1 | 209 | 0.003053 | south | Y | -0.012034 | -0.00092442 | 0.19094 | -0.0059408 | 0.00092442 | south | N | 0.00092442 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.003053 | south | Y | -0.012034 | -0.00092442 | 0.19094 | -0.0059408 | 0.00092442 | south | N | 0.00092442 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.002952 | south | Y | -0.012135 | -0.0010254 | 0.19084 | -0.0060418 | 0.0010254 | south | N | 0.0010254 | 0
5031 | BRA_VHBC | 1 | 46 | 0.003053 | south | Y | -0.012034 | -0.00092442 | 0.19094 | -0.0059408 | 0.00092442 | south | N | 0.00092442 | 0
5032 | BRA_VHBC | 2 | 47 | 0.003053 | south | Y | -0.012034 | -0.00092442 | 0.19094 | -0.0059408 | 0.00092442 | south | N | 0.00092442 | 0
5033 | BRA_VHBC | 3 | 46 | 0.003053 | south | Y | -0.012034 | -0.00092442 | 0.19094 | -0.0059408 | 0.00092442 | south | N | 0.00092442 | 0
5034 | BRA_VHBC | 4 | 46 | 0.003053 | south | Y | -0.012034 | -0.00092442 | 0.19094 | -0.0059408 | 0.00092442 | south | N | 0.00092442 | 0
5111 | CALAVER_ | 1 | 424 | 0.003104 | south | Y | -0.011983 | -0.00087342 | 0.19099 | -0.0058898 | 0.00087342 | south | N | 0.00087342 | 0
5112 | CALAVER_ | 2 | 425 | 0.003104 | south | Y | -0.011983 | -0.00087342 | 0.19099 | -0.0058898 | 0.00087342 | south | N | 0.00087342 | 0
5264 | LEON_LCP | 3 | 58 | 0.002662 | south | Y | -0.012425 | -0.0013154 | 0.19055 | -0.0063318 | 0.0013154 | south | N | 0.0013154 | 0
5265 | LEON_LCP | 4 | 89 | 0.002662 | south | Y | -0.012425 | -0.0013154 | 0.19055 | -0.0063318 | 0.0013154 | south | N | 0.0013154 | 0
5266 | LEON_LCP | 1 | 44 | 0.002662 | south | Y | -0.012425 | -0.0013154 | 0.19055 | -0.0063318 | 0.0013154 | south | N | 0.0013154 | 0
5267 | LEON_LCP | 2 | 44 | 0.002662 | south | Y | -0.012425 | -0.0013154 | 0.19055 | -0.0063318 | 0.0013154 | south | N | 0.0013154 | 0
5268 | LEON_LCP | 3 | 43 | 0.002662 | south | Y | -0.012425 | -0.0013154 | 0.19055 | -0.0063318 | 0.0013154 | south | N | 0.0013154 | 0
5269 | LEON_LCP | 4 | 45 | 0.002662 | south | Y | -0.012425 | -0.0013154 | 0.19055 | -0.0063318 | 0.0013154 | south | N | 0.0013154 | 0
5396 | CALAVER_ | 1 | 412 | 0.003054 | south | Y | -0.012033 | -0.00092342 | 0.19094 | -0.0059398 | 0.00092342 | south | N | 0.00092342 | 0
5397 | CALAVER_ | 2 | 400 | 0.003054 | south | Y | -0.012033 | -0.00092342 | 0.19094 | -0.0059398 | 0.00092342 | south | N | 0.00092342 | 0
5401 | CALAVER_ | 1 | 546 | 0.003485 | south | Y | -0.011602 | -0.00049242 | 0.19137 | -0.0055088 | 0.00049242 | south | N | 0.00049242 | 0
5402 | CALAVER_ | 2 | 750 | 0.003485 | south | Y | -0.011602 | -0.00049242 | 0.19137 | -0.0055088 | 0.00049242 | south | N | 0.00049242 | 0
5436 | TUTTL_WB | MB | 61 | 0.00332 | south | Y | -0.011767 | -0.00065742 | 0.19121 | -0.0056738 | 0.00065742 | south | N | 0.00065742 | 0
5438 | TUTTL_WB | MB | 95 | 0.00332 | south | Y | -0.011767 | -0.00065742 | 0.19121 | -0.0056738 | 0.00065742 | south | N | 0.00065742 | 0
5439 | TUTTL_WB | MB | 151 | 0.00332 | south | Y | -0.011767 | -0.00065742 | 0.19121 | -0.0056738 | 0.00065742 | south | N | 0.00065742 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.003384 | south | Y | -0.011703 | -0.00059342 | 0.19127 | -0.0056098 | 0.00059342 | south | N | 0.00059342 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.003384 | south | Y | -0.011703 | -0.00059342 | 0.19127 | -0.0056098 | 0.00059342 | south | N | 0.00059342 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.003384 | south | Y | -0.011703 | -0.00059342 | 0.19127 | -0.0056098 | 0.00059342 | south | N | 0.00059342 | 0
5503 | RAYBURNG | 1 | 22 | 0.004405 | south | Y | -0.010682 | 0.00042758 | 0.19229 | -0.0045888 | 0.00042758 | south | N | 0.00042758 | 0
5505 | RAYBURNG | 1 | 11 | 0.004405 | south | Y | -0.010682 | 0.00042758 | 0.19229 | -0.0045888 | 0.00042758 | south | N | 0.00042758 | 0
5506 | RAYBURNG | 1 | 11 | 0.004405 | south | Y | -0.010682 | 0.00042758 | 0.19229 | -0.0045888 | 0.00042758 | south | N | 0.00042758 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.00452 | south | Y | -0.010567 | 0.00054258 | 0.19241 | -0.0044738 | 0.00054258 | south | N | 0.00054258 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.00452 | south | Y | -0.010567 | 0.00054258 | 0.19241 | -0.0044738 | 0.00054258 | south | N | 0.00054258 | 0
5511 | RAYBURNC | 1 | 46 | 0.00452 | south | Y | -0.010567 | 0.00054258 | 0.19241 | -0.0044738 | 0.00054258 | south | N | 0.00054258 | 0
5512 | RAYBURNC | 1 | 48 | 0.00452 | south | Y | -0.010567 | 0.00054258 | 0.19241 | -0.0044738 | 0.00054258 | south | N | 0.00054258 | 0
5728 | FALCONHY | 2 | 12 | 0.00215 | south | N | -0.012937 | -0.0018274 | 0.19004 | -0.0068438 | 0.0018274 | south | N | 0.0018274 | 0
5729 | FALCONHY | 3 | 11 | 0.00215 | south | N | -0.012937 | -0.0018274 | 0.19004 | -0.0068438 | 0.0018274 | south | N | 0.0018274 | 0
5890 | PEARSALL | 1 | 24 | -0.002958 | south | Y | -0.018045 | -0.0069354 | 0.18493 | -0.011952 | 0.0069354 | south | N | 0.0069354 | 0
5891 | PEARSALL | 1 | 24 | -0.002958 | south | Y | -0.018045 | -0.0069354 | 0.18493 | -0.011952 | 0.0069354 | south | N | 0.0069354 | 0
5892 | PEARSALL | 1 | 23 | -0.002958 | south | Y | -0.018045 | -0.0069354 | 0.18493 | -0.011952 | 0.0069354 | south | N | 0.0069354 | 0
5903 | SANMIGUE | 1 | 396 | 0.003037 | south | Y | -0.01205 | -0.00094042 | 0.19092 | -0.0059568 | 0.00094042 | south | N | 0.00094042 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.00729 | houston | N | -0.0077968 | 0.0033126 | 0.19518 | -0.0017038 | 0.0017038 | houston | N | 0.0017038 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.00729 | houston | N | -0.0077968 | 0.0033126 | 0.19518 | -0.0017038 | 0.0017038 | houston | N | 0.0017038 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | Y | 0.015087 | 0
5932 | SI_RAY9 | 9 | 38 | 0.003774 | south | Y | -0.011313 | -0.00020342 | 0.19166 | -0.0052198 | 0.00020342 | south | N | 0.00020342 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.003774 | south | Y | -0.011313 | -0.00020342 | 0.19166 | -0.0052198 | 0.00020342 | south | N | 0.00020342 | 0
5934 | SI_RAY5 | 5 | 15 | 0.003774 | south | Y | -0.011313 | -0.00020342 | 0.19166 | -0.0052198 | 0.00020342 | south | N | 0.00020342 | 0
5935 | SI_RAY10 | 10 | 47 | 0.003774 | south | Y | -0.011313 | -0.00020342 | 0.19166 | -0.0052198 | 0.00020342 | south | N | 0.00020342 | 0
6016 | SWMESA | 1 | 75 | -0.15535 | west | Y | -0.17043 | -0.15932 | 0.032541 | -0.16434 | 0.032541 | west | N | 0.032541 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | Y | 0.18789 | 0
6144 | MCADOO1A | 1 | 150 | -0.18868 | west | Y | -0.20376 | -0.19265 | -0.00078734 | -0.19767 | 0.00078734 | west | N | 0.00078734 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.18266 | west | Y | -0.19775 | -0.18664 | 0.0052257 | -0.19166 | 0.0052257 | west | N | 0.0052257 | 0
6476 | LANGFORD | 1 | 150 | -0.12248 | west | Y | -0.13757 | -0.12646 | 0.065406 | -0.13148 | 0.065406 | west | N | 0.065406 | 0
6637 | SNYDERW1 | 1 | 63 | -0.17161 | west | Y | -0.18669 | -0.17558 | 0.016282 | -0.1806 | 0.016282 | west | N | 0.016282 | 0
6752 | OKLA0A | 1 | 649.7 | -0.55475 | west | Y | -0.56984 | -0.55873 | -0.36687 | -0.56375 | 0.36687 | west | N | 0.36687 | 0
6948 | DENISNDM | 1 | 40 | 0.017812 | north | N | 0.0027252 | 0.013835 | 0.2057 | 0.0088182 | 0.0027252 | North | N | 0.0027252 | 0
6948 | DENISNDM | 2 | 40 | 0.017812 | north | N | 0.0027252 | 0.013835 | 0.2057 | 0.0088182 | 0.0027252 | North | N | 0.0027252 | 0
7000 | L_FERGUS | 1 | 422 | -0.002537 | south | Y | -0.017624 | -0.0065144 | 0.18535 | -0.011531 | 0.0065144 | south | N | 0.0065144 | 0
7004 | L_SIMGID | 1 | 132 | 0.005508 | south | Y | -0.0095788 | 0.0015306 | 0.1934 | -0.0034858 | 0.0015306 | south | N | 0.0015306 | 0
7005 | L_SIMGID | 2 | 134 | 0.005508 | south | Y | -0.0095788 | 0.0015306 | 0.1934 | -0.0034858 | 0.0015306 | south | N | 0.0015306 | 0
7006 | L_SIMGID | 3 | 323 | 0.005508 | south | Y | -0.0095788 | 0.0015306 | 0.1934 | -0.0034858 | 0.0015306 | south | N | 0.0015306 | 0
7007 | L_LOSTPI | 1 | 158 | 0.005862 | south | Y | -0.0092248 | 0.0018846 | 0.19375 | -0.0031318 | 0.0018846 | south | N | 0.0018846 | 0
7008 | L_LOSTPI | 2 | 160 | 0.005862 | south | Y | -0.0092248 | 0.0018846 | 0.19375 | -0.0031318 | 0.0018846 | south | N | 0.0018846 | 0
7009 | L_LOSTPI | 3 | 175 | 0.005862 | south | Y | -0.0092248 | 0.0018846 | 0.19375 | -0.0031318 | 0.0018846 | south | N | 0.0018846 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.005915 | south | Y | -0.0091718 | 0.0019376 | 0.1938 | -0.0030788 | 0.0019376 | south | N | 0.0019376 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.005915 | south | Y | -0.0091718 | 0.0019376 | 0.1938 | -0.0030788 | 0.0019376 | south | N | 0.0019376 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.005914 | south | Y | -0.0091728 | 0.0019366 | 0.1938 | -0.0030798 | 0.0019366 | south | N | 0.0019366 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.00426 | south | Y | -0.010827 | 0.00028258 | 0.19215 | -0.0047338 | 0.00028258 | south | N | 0.00028258 | 0
7015 | L_HAYSEN | 2 | 225 | 0.00426 | south | Y | -0.010827 | 0.00028258 | 0.19215 | -0.0047338 | 0.00028258 | south | N | 0.00028258 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.00426 | south | Y | -0.010827 | 0.00028258 | 0.19215 | -0.0047338 | 0.00028258 | south | N | 0.00028258 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.00426 | south | Y | -0.010827 | 0.00028258 | 0.19215 | -0.0047338 | 0.00028258 | south | N | 0.00028258 | 0
7020 | L_AUSTPL | 1 | 8 | 0.004849 | south | N | -0.010238 | 0.00087158 | 0.19274 | -0.0041448 | 0.00087158 | south | N | 0.00087158 | 0
7020 | L_AUSTPL | 2 | 8 | 0.004849 | south | N | -0.010238 | 0.00087158 | 0.19274 | -0.0041448 | 0.00087158 | south | N | 0.00087158 | 0
7022 | L_BUCHAN | 1 | 18 | -0.002926 | south | N | -0.018013 | -0.0069034 | 0.18496 | -0.01192 | 0.0069034 | south | N | 0.0069034 | 0
7023 | L_BUCHAN | 2 | 18 | -0.002926 | south | N | -0.018013 | -0.0069034 | 0.18496 | -0.01192 | 0.0069034 | south | N | 0.0069034 | 0
7024 | L_BUCHAN | 3 | 15 | -0.002926 | south | N | -0.018013 | -0.0069034 | 0.18496 | -0.01192 | 0.0069034 | south | N | 0.0069034 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.004838 | south | N | -0.019925 | -0.0088154 | 0.18305 | -0.013832 | 0.0088154 | south | N | 0.0088154 | 0
7028 | L_MARBFA | 1 | 18 | -0.000816 | south | N | -0.015903 | -0.0047934 | 0.18707 | -0.0098098 | 0.0047934 | south | N | 0.0047934 | 0
7029 | L_MARBFA | 2 | 18 | -0.000816 | south | N | -0.015903 | -0.0047934 | 0.18707 | -0.0098098 | 0.0047934 | south | N | 0.0047934 | 0
7031 | L_MARSFO | 1 | 35 | 0.003085 | south | N | -0.012002 | -0.00089242 | 0.19097 | -0.0059088 | 0.00089242 | south | N | 0.00089242 | 0
7032 | L_MARSFO | 2 | 34 | 0.003085 | south | N | -0.012002 | -0.00089242 | 0.19097 | -0.0059088 | 0.00089242 | south | N | 0.00089242 | 0
7033 | L_MARSFO | 3 | 35 | 0.003085 | south | N | -0.012002 | -0.00089242 | 0.19097 | -0.0059088 | 0.00089242 | south | N | 0.00089242 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.002115 | south | N | -0.017202 | -0.0060924 | 0.18577 | -0.011109 | 0.0060924 | south | N | 0.0060924 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.002115 | south | N | -0.017202 | -0.0060924 | 0.18577 | -0.011109 | 0.0060924 | south | N | 0.0060924 | 0
7038 | L_DELAWA | 1 | 35 | -0.16371 | west | Y | -0.1788 | -0.16769 | 0.024177 | -0.1727 | 0.024177 | west | N | 0.024177 | 0
7038 | L_DELAWA | 2 | 30 | -0.16371 | west | Y | -0.1788 | -0.16769 | 0.024177 | -0.1727 | 0.024177 | west | N | 0.024177 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.005763 | south | Y | -0.0093238 | 0.0017856 | 0.19365 | -0.0032308 | 0.0017856 | south | N | 0.0017856 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.005763 | south | Y | -0.0093238 | 0.0017856 | 0.19365 | -0.0032308 | 0.0017856 | south | N | 0.0017856 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.005763 | south | Y | -0.0093238 | 0.0017856 | 0.19365 | -0.0032308 | 0.0017856 | south | N | 0.0017856 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.005763 | south | Y | -0.0093238 | 0.0017856 | 0.19365 | -0.0032308 | 0.0017856 | south | N | 0.0017856 | 0
7487 | L_CANYHY | 1 | 6 | 0.003837 | south | N | -0.01125 | -0.00014042 | 0.19172 | -0.0051568 | 0.00014042 | south | N | 0.00014042 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.004096 | south | N | -0.010991 | 0.00011858 | 0.19198 | -0.0048978 | 0.00011858 | south | N | 0.00011858 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.004096 | south | N | -0.010991 | 0.00011858 | 0.19198 | -0.0048978 | 0.00011858 | south | N | 0.00011858 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.004096 | south | N | -0.010991 | 0.00011858 | 0.19198 | -0.0048978 | 0.00011858 | south | N | 0.00011858 | 0
7609 | L_SCHUMA | 1 | 4 | 0.00383 | south | N | -0.011257 | -0.00014742 | 0.19172 | -0.0051638 | 0.00014742 | south | N | 0.00014742 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.00438 | south | N | -0.010707 | 0.00040258 | 0.19227 | -0.0046138 | 0.00040258 | south | N | 0.00040258 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.00438 | south | N | -0.010707 | 0.00040258 | 0.19227 | -0.0046138 | 0.00040258 | south | N | 0.00040258 | 0
7800 | L_GUADGE | 1 | 147 | 0.003944 | south | Y | -0.011143 | -3.3424e-05 | 0.19183 | -0.0050498 | 3.3424e-05 | south | N | 3.3424e-05 | 0
7801 | L_GUADGE | 2 | 138 | 0.003944 | south | Y | -0.011143 | -3.3424e-05 | 0.19183 | -0.0050498 | 3.3424e-05 | south | N | 3.3424e-05 | 0
7802 | L_GUADGE | 3 | 140 | 0.003944 | south | Y | -0.011143 | -3.3424e-05 | 0.19183 | -0.0050498 | 3.3424e-05 | south | N | 3.3424e-05 | 0
7803 | L_GUADGE | 4 | 147 | 0.003944 | south | Y | -0.011143 | -3.3424e-05 | 0.19183 | -0.0050498 | 3.3424e-05 | south | N | 3.3424e-05 | 0
7804 | L_GUADGE | 5 | 182 | 0.003944 | south | Y | -0.011143 | -3.3424e-05 | 0.19183 | -0.0050498 | 3.3424e-05 | south | N | 3.3424e-05 | 0
7805 | L_GUADGE | 6 | 198 | 0.003944 | south | Y | -0.011143 | -3.3424e-05 | 0.19183 | -0.0050498 | 3.3424e-05 | south | N | 3.3424e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.005534 | south | Y | -0.0095528 | 0.0015566 | 0.19342 | -0.0034598 | 0.0015566 | south | N | 0.0015566 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.005534 | south | Y | -0.0095528 | 0.0015566 | 0.19342 | -0.0034598 | 0.0015566 | south | N | 0.0015566 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.005534 | south | Y | -0.0095528 | 0.0015566 | 0.19342 | -0.0034598 | 0.0015566 | south | N | 0.0015566 | 0
7810 | L_RIONOG | 1 | 142 | 0.004105 | south | Y | -0.010982 | 0.00012758 | 0.19199 | -0.0048888 | 0.00012758 | south | N | 0.00012758 | 0
7811 | L_RIONOG | 2 | 145 | 0.004105 | south | Y | -0.010982 | 0.00012758 | 0.19199 | -0.0048888 | 0.00012758 | south | N | 0.00012758 | 0
7812 | L_RIONOG | 3 | 151 | 0.004105 | south | Y | -0.010982 | 0.00012758 | 0.19199 | -0.0048888 | 0.00012758 | south | N | 0.00012758 | 0
7813 | L_RIONOG | 4 | 290 | 0.004105 | south | Y | -0.010982 | 0.00012758 | 0.19199 | -0.0048888 | 0.00012758 | south | N | 0.00012758 | 0
8032 | AMISTADH | 1 | 33 | -0.043841 | south | N | -0.058928 | -0.047818 | 0.14405 | -0.052835 | 0.047818 | south | N | 0.047818 | 0
8033 | AMISTADH | 2 | 25 | -0.043841 | south | N | -0.058928 | -0.047818 | 0.14405 | -0.052835 | 0.047818 | south | N | 0.047818 | 0
8048 | FALCONHY | 1 | 12 | 0.00215 | south | N | -0.012937 | -0.0018274 | 0.19004 | -0.0068438 | 0.0018274 | south | N | 0.0018274 | 0
8066 | DUP1V#1 | 1 | 73 | 0.004636 | south | N | -0.010451 | 0.00065858 | 0.19252 | -0.0043578 | 0.00065858 | south | N | 0.00065858 | 0
8134 | FOR69CG0 | 1 | 79 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
8138 | FOR69CG0 | 2 | 81 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | N | 0.0039774 | 0
8147 | UCAR #2 | 10 | 28 | 0.004793 | south | N | -0.010294 | 0.00081558 | 0.19268 | -0.0042008 | 0.00081558 | south | N | 0.00081558 | 0
8148 | UCAR #1 | 2 | 7 | 0.004793 | south | N | -0.010294 | 0.00081558 | 0.19268 | -0.0042008 | 0.00081558 | south | N | 0.00081558 | 0
8153 | FOR69CG0 | 3 | 79 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
8154 | FOR69CG0 | 4 | 80 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
8156 | FOR69CG0 | 6 | 25 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
8157 | FOR69CG0 | 7 | 46 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
8161 | COLETOU1 | 1 | 629 | 0.00401 | south | Y | -0.011077 | 3.2576e-05 | 0.1919 | -0.0049838 | 3.2576e-05 | south | N | 3.2576e-05 | 0
8173 | VICEC51A | 5 | 144 | 0.00457 | south | Y | -0.010517 | 0.00059258 | 0.19246 | -0.0044238 | 0.00059258 | south | N | 0.00059258 | 0
8174 | VICEC61A | 6 | 188 | 0.00457 | south | Y | -0.010517 | 0.00059258 | 0.19246 | -0.0044238 | 0.00059258 | south | N | 0.00059258 | 0
8189 | CUERO 2 | 1 | 12 | 0.004406 | south | N | -0.010681 | 0.00042858 | 0.19229 | -0.0045878 | 0.00042858 | south | N | 0.00042858 | 0
8262 | ELPS | 1 | 6 | -0.030846 | south | N | -0.045933 | -0.034823 | 0.15704 | -0.03984 | 0.034823 | south | N | 0.034823 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | N | 0.0039774 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | N | 0.0039774 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | N | 0.0039774 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | N | 0.0039774 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | N | 0.0039774 | 0
8442 | NBEC71A | 1 | 336 | 0.00401 | south | Y | -0.011077 | 3.2576e-05 | 0.1919 | -0.0049838 | 3.2576e-05 | south | N | 3.2576e-05 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | N | 0.0039774 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.015087 | -0.0039774 | 0.18789 | -0.0089938 | 0.0039774 | south | N | 0.0039774 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.003985 | south | Y | -0.011102 | 7.5759e-06 | 0.19187 | -0.0050088 | 7.5759e-06 | south | N | 7.5759e-06 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.003985 | south | Y | -0.011102 | 7.5759e-06 | 0.19187 | -0.0050088 | 7.5759e-06 | south | N | 7.5759e-06 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.003953 | south | N | -0.011134 | -2.4424e-05 | 0.19184 | -0.0050408 | 2.4424e-05 | south | N | 2.4424e-05 | 0
8506 | VAL #1 | 1 | 25 | 0.00397 | south | N | -0.011117 | -7.4241e-06 | 0.19186 | -0.0050238 | 7.4241e-06 | south | N | 7.4241e-06 | 0
8507 | VAL #2 | 2 | 25 | 0.00397 | south | N | -0.011117 | -7.4241e-06 | 0.19186 | -0.0050238 | 7.4241e-06 | south | N | 7.4241e-06 | 0
8511 | OXY_CC0A | 1 | 38 | 0.003968 | south | N | -0.011119 | -9.4241e-06 | 0.19186 | -0.0050258 | 9.4241e-06 | south | N | 9.4241e-06 | 0
8517 | CELANEBI | 1 | 29 | 0.003887 | south | N | -0.0112 | -9.0424e-05 | 0.19177 | -0.0051068 | 9.0424e-05 | south | N | 9.0424e-05 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.004009 | south | N | -0.011078 | 3.1576e-05 | 0.1919 | -0.0049848 | 3.1576e-05 | south | N | 3.1576e-05 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.004009 | south | N | -0.011078 | 3.1576e-05 | 0.1919 | -0.0049848 | 3.1576e-05 | south | N | 3.1576e-05 | 0
8562 | CNOPST1 | 3 | 153 | 0.004009 | south | N | -0.011078 | 3.1576e-05 | 0.1919 | -0.0049848 | 3.1576e-05 | south | N | 3.1576e-05 | 0
8926 | LGE_GT10 | 1 | 158 | 0.004139 | south | N | -0.010948 | 0.00016158 | 0.19203 | -0.0048548 | 0.00016158 | south | N | 0.00016158 | 0
8927 | LGE_GT20 | 2 | 153 | 0.004139 | south | N | -0.010948 | 0.00016158 | 0.19203 | -0.0048548 | 0.00016158 | south | N | 0.00016158 | 0
8928 | LGE_STG0 | 3 | 100 | 0.004139 | south | N | -0.010948 | 0.00016158 | 0.19203 | -0.0048548 | 0.00016158 | south | N | 0.00016158 | 0
8930 | ICPGN10A | 1 | 145 | 0.004139 | south | N | -0.010948 | 0.00016158 | 0.19203 | -0.0048548 | 0.00016158 | south | N | 0.00016158 | 0
8931 | ICPGN20A | 2 | 147 | 0.004139 | south | N | -0.010948 | 0.00016158 | 0.19203 | -0.0048548 | 0.00016158 | south | N | 0.00016158 | 0
8932 | ICPGN30A | 3 | 127 | 0.004139 | south | N | -0.010948 | 0.00016158 | 0.19203 | -0.0048548 | 0.00016158 | south | N | 0.00016158 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.003432 | south | Y | -0.011655 | -0.00054542 | 0.19132 | -0.0055618 | 0.00054542 | south | N | 0.00054542 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.003432 | south | Y | -0.011655 | -0.00054542 | 0.19132 | -0.0055618 | 0.00054542 | south | N | 0.00054542 | 0
8935 | FGNTS201 | 3 | 173 | 0.003432 | south | Y | -0.011655 | -0.00054542 | 0.19132 | -0.0055618 | 0.00054542 | south | N | 0.00054542 | 0
8936 | MVGN#1 | 1 | 207 | 0.003646 | south | Y | -0.011441 | -0.00033142 | 0.19153 | -0.0053478 | 0.00033142 | south | N | 0.00033142 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.003646 | south | Y | -0.011441 | -0.00033142 | 0.19153 | -0.0053478 | 0.00033142 | south | N | 0.00033142 | 0
8938 | MVGN#3 | 3 | 242 | 0.003646 | south | Y | -0.011441 | -0.00033142 | 0.19153 | -0.0053478 | 0.00033142 | south | N | 0.00033142 | 0
8981 | HECN1 | 1 | 144 | 0.003646 | south | Y | -0.011441 | -0.00033142 | 0.19153 | -0.0053478 | 0.00033142 | south | N | 0.00033142 | 0
8982 | HECN2 | 2 | 144 | 0.003646 | south | Y | -0.011441 | -0.00033142 | 0.19153 | -0.0053478 | 0.00033142 | south | N | 0.00033142 | 0
8983 | HECN3 | 3 | 171 | 0.003646 | south | Y | -0.011441 | -0.00033142 | 0.19153 | -0.0053478 | 0.00033142 | south | N | 0.00033142 | 0
9000 | DECKR_G1 | 1 | 310 | 0.005015 | south | Y | -0.010072 | 0.0010376 | 0.1929 | -0.0039788 | 0.0010376 | south | N | 0.0010376 | 0
9001 | DECKR_G2 | 2 | 413 | 0.005015 | south | Y | -0.010072 | 0.0010376 | 0.1929 | -0.0039788 | 0.0010376 | south | N | 0.0010376 | 0
9002 | DECKR_G3 | 3 | 42 | 0.005151 | south | Y | -0.0099358 | 0.0011736 | 0.19304 | -0.0038428 | 0.0011736 | south | N | 0.0011736 | 0
9003 | DECKR_G4 | 4 | 44 | 0.005151 | south | Y | -0.0099358 | 0.0011736 | 0.19304 | -0.0038428 | 0.0011736 | south | N | 0.0011736 | 0
9004 | DECKR_G5 | 5 | 44 | 0.005151 | south | Y | -0.0099358 | 0.0011736 | 0.19304 | -0.0038428 | 0.0011736 | south | N | 0.0011736 | 0
9005 | DECKR_G6 | 6 | 47 | 0.005151 | south | Y | -0.0099358 | 0.0011736 | 0.19304 | -0.0038428 | 0.0011736 | south | N | 0.0011736 | 0
9016 | SANDH_G1 | 1 | 49 | 0.004978 | south | Y | -0.010109 | 0.0010006 | 0.19287 | -0.0040158 | 0.0010006 | south | N | 0.0010006 | 0
9017 | SANDH_G2 | 2 | 46 | 0.004978 | south | Y | -0.010109 | 0.0010006 | 0.19287 | -0.0040158 | 0.0010006 | south | N | 0.0010006 | 0
9018 | SANDH_G3 | 3 | 46 | 0.004978 | south | Y | -0.010109 | 0.0010006 | 0.19287 | -0.0040158 | 0.0010006 | south | N | 0.0010006 | 0
9019 | SANDH_G4 | 4 | 47 | 0.004978 | south | Y | -0.010109 | 0.0010006 | 0.19287 | -0.0040158 | 0.0010006 | south | N | 0.0010006 | 0
9020 | SANDHG5A | 5A | 154 | 0.004978 | south | Y | -0.010109 | 0.0010006 | 0.19287 | -0.0040158 | 0.0010006 | south | N | 0.0010006 | 0
9021 | SANDHG5C | 5C | 148 | 0.004978 | south | Y | -0.010109 | 0.0010006 | 0.19287 | -0.0040158 | 0.0010006 | south | N | 0.0010006 | 0
9022 | SANDH_G6 | 6 | 48 | 0.004978 | south | Y | -0.010109 | 0.0010006 | 0.19287 | -0.0040158 | 0.0010006 | south | N | 0.0010006 | 0
9023 | SANDH_G7 | 7 | 48 | 0.004978 | south | Y | -0.010109 | 0.0010006 | 0.19287 | -0.0040158 | 0.0010006 | south | N | 0.0010006 | 0
11001 | NAV1CT | 1 | 70 | -0.16461 | west | Y | -0.17969 | -0.16858 | 0.023282 | -0.1736 | 0.023282 | west | N | 0.023282 | 0
11009 | NAV2CT | 1 | 70 | -0.16461 | west | Y | -0.17969 | -0.16858 | 0.023282 | -0.1736 | 0.023282 | west | N | 0.023282 | 0
11011 | NAV3ST | 1 | 92.8 | -0.16461 | west | Y | -0.17969 | -0.16858 | 0.023282 | -0.1736 | 0.023282 | west | N | 0.023282 | 0
11012 | NAV4CT | 1 | 80 | -0.16461 | west | Y | -0.17969 | -0.16858 | 0.023282 | -0.1736 | 0.023282 | west | N | 0.023282 | 0
11013 | NAV5CT | 1 | 80 | -0.16461 | west | Y | -0.17969 | -0.16858 | 0.023282 | -0.1736 | 0.023282 | west | N | 0.023282 | 0
11014 | NAV6ST | 1 | 115 | -0.16461 | west | Y | -0.17969 | -0.16858 | 0.023282 | -0.1736 | 0.023282 | west | N | 0.023282 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.16459 | west | Y | -0.17968 | -0.16857 | 0.023293 | -0.17359 | 0.023293 | west | N | 0.023293 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.16459 | west | Y | -0.17968 | -0.16857 | 0.023293 | -0.17359 | 0.023293 | west | N | 0.023293 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.16459 | west | Y | -0.17968 | -0.16857 | 0.023293 | -0.17359 | 0.023293 | west | N | 0.023293 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.16459 | west | Y | -0.17968 | -0.16857 | 0.023293 | -0.17359 | 0.023293 | west | N | 0.023293 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.16459 | west | Y | -0.17968 | -0.16857 | 0.023293 | -0.17359 | 0.023293 | west | N | 0.023293 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.16459 | west | Y | -0.17968 | -0.16857 | 0.023293 | -0.17359 | 0.023293 | west | N | 0.023293 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.13871 | west | Y | -0.1538 | -0.14269 | 0.049179 | -0.1477 | 0.049179 | west | N | 0.049179 | 0
11057 | CHAMPION | 1 | 126.5 | -0.13871 | west | Y | -0.1538 | -0.14269 | 0.049179 | -0.1477 | 0.049179 | west | N | 0.049179 | 0
11058 | PYRON_1G | 1 | 249 | -0.13871 | west | Y | -0.1538 | -0.14269 | 0.049179 | -0.1477 | 0.049179 | west | N | 0.049179 | 0
11059 | INADALE_ | 1 | 197 | -0.13871 | west | Y | -0.1538 | -0.14269 | 0.049179 | -0.1477 | 0.049179 | west | N | 0.049179 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.16558 | west | Y | -0.18066 | -0.16956 | 0.02231 | -0.17457 | 0.02231 | west | N | 0.02231 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.16558 | west | Y | -0.18066 | -0.16956 | 0.02231 | -0.17457 | 0.02231 | west | N | 0.02231 | 0
11147 | NOTREES_ | 1 | 149 | -0.16428 | west | Y | -0.17936 | -0.16826 | 0.02361 | -0.17327 | 0.02361 | west | N | 0.02361 | 0
11309 | BULLCREK | 1 | 180 | -0.16999 | west | Y | -0.18507 | -0.17397 | 0.0179 | -0.17898 | 0.0179 | west | N | 0.0179 | 0
11310 | BULLCREK | 1 | 180 | -0.16999 | west | Y | -0.18507 | -0.17397 | 0.0179 | -0.17898 | 0.0179 | west | N | 0.0179 | 0
11320 | COYOTE_1 | 1 | 225 | -0.16977 | west | Y | -0.18485 | -0.17374 | 0.018122 | -0.17876 | 0.018122 | west | N | 0.018122 | 0
11415 | LORAINE_ | 1 | 125 | -0.17129 | west | Y | -0.18637 | -0.17527 | 0.0166 | -0.18028 | 0.0166 | west | N | 0.0166 | 0
11416 | LORAINE_ | 1 | 125 | -0.17129 | west | Y | -0.18637 | -0.17527 | 0.0166 | -0.18028 | 0.0166 | west | N | 0.0166 | 0
11691 | KMICHICT | 1 | 140 | 0.018402 | north | N | 0.0033152 | 0.014425 | 0.20629 | 0.0094082 | 0.0033152 | North | N | 0.0033152 | 0
11692 | KMICHICT | 2 | 141 | 0.018402 | north | N | 0.0033152 | 0.014425 | 0.20629 | 0.0094082 | 0.0033152 | North | N | 0.0033152 | 0
11693 | KMICHIST | 3 | 309 | 0.018402 | north | N | 0.0033152 | 0.014425 | 0.20629 | 0.0094082 | 0.0033152 | North | N | 0.0033152 | 0
11694 | KMICHICT | 4 | 143 | 0.018402 | north | N | 0.0033152 | 0.014425 | 0.20629 | 0.0094082 | 0.0033152 | North | N | 0.0033152 | 0
11695 | KMICHICT | 5 | 144 | 0.018402 | north | N | 0.0033152 | 0.014425 | 0.20629 | 0.0094082 | 0.0033152 | North | N | 0.0033152 | 0
11696 | KMICHIST | 6 | 310 | 0.018402 | north | N | 0.0033152 | 0.014425 | 0.20629 | 0.0094082 | 0.0033152 | North | N | 0.0033152 | 0
12322 | ENNSTRAC | 1 | 196 | 0.015651 | north | Y | 0.00056425 | 0.011674 | 0.20354 | 0.0066572 | 0.00056425 | North | N | 0.00056425 | 0
12323 | ENNSTRAC | 2 | 111 | 0.015651 | north | Y | 0.00056425 | 0.011674 | 0.20354 | 0.0066572 | 0.00056425 | North | N | 0.00056425 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.018851 | north | N | 0.0037642 | 0.014874 | 0.20674 | 0.0098572 | 0.0037642 | North | N | 0.0037642 | 0
12411 | FPLEFR1A | 1 | 161 | 0.017653 | north | Y | 0.0025662 | 0.013676 | 0.20554 | 0.0086592 | 0.0025662 | North | N | 0.0025662 | 0
12412 | FPLEFR1B | 2 | 164 | 0.017653 | north | Y | 0.0025662 | 0.013676 | 0.20554 | 0.0086592 | 0.0025662 | North | N | 0.0025662 | 0
12413 | FPLEFR1C | 3 | 164 | 0.017653 | north | Y | 0.0025662 | 0.013676 | 0.20554 | 0.0086592 | 0.0025662 | North | N | 0.0025662 | 0
12414 | FPLEFR1S | 4 | 414 | 0.017653 | north | Y | 0.0025662 | 0.013676 | 0.20554 | 0.0086592 | 0.0025662 | North | N | 0.0025662 | 0
12421 | FPLEFR2A | 1 | 162 | 0.017653 | north | Y | 0.0025662 | 0.013676 | 0.20554 | 0.0086592 | 0.0025662 | North | N | 0.0025662 | 0
12422 | FPLEFR2B | 2 | 161 | 0.017653 | north | Y | 0.0025662 | 0.013676 | 0.20554 | 0.0086592 | 0.0025662 | North | N | 0.0025662 | 0
12423 | FPLEFR2C | 3 | 163 | 0.017653 | north | Y | 0.0025662 | 0.013676 | 0.20554 | 0.0086592 | 0.0025662 | North | N | 0.0025662 | 0
12424 | FPLEFR2S | 4 | 409 | 0.017653 | north | Y | 0.0025662 | 0.013676 | 0.20554 | 0.0086592 | 0.0025662 | North | N | 0.0025662 | 0
12440 | PARKD_1S | 1 | 0 | 0.017631 | north | N | 0.0025442 | 0.013654 | 0.20552 | 0.0086372 | 0.0025442 | North | N | 0.0025442 | 0
12449 | PARKD_2S | 1 | 0 | 0.017631 | north | N | 0.0025442 | 0.013654 | 0.20552 | 0.0086372 | 0.0025442 | North | N | 0.0025442 | 0
13116 | TGATEWAY | 1 | 148 | 0.016437 | north | N | 0.0013502 | 0.01246 | 0.20432 | 0.0074432 | 0.0013502 | North | N | 0.0013502 | 0
13117 | TGATEWAY | 2 | 130 | 0.016437 | north | N | 0.0013502 | 0.01246 | 0.20432 | 0.0074432 | 0.0013502 | North | N | 0.0013502 | 0
13118 | TGATEWAY | 3 | 145 | 0.016437 | north | N | 0.0013502 | 0.01246 | 0.20432 | 0.0074432 | 0.0013502 | North | N | 0.0013502 | 0
13119 | TGATEWAY | 4 | 399 | 0.016437 | north | N | 0.0013502 | 0.01246 | 0.20432 | 0.0074432 | 0.0013502 | North | N | 0.0013502 | 0
13131 | CALFREST | 1 | 150.7 | 0.01503 | north | Y | -5.6751e-05 | 0.011053 | 0.20292 | 0.0060362 | 5.6751e-05 | North | N | 5.6751e-05 | 0
13132 | CALFREST | 2 | 151 | 0.01503 | north | Y | -5.6751e-05 | 0.011053 | 0.20292 | 0.0060362 | 5.6751e-05 | North | N | 5.6751e-05 | 0
13133 | CALFREST | 3 | 177.4 | 0.01503 | north | Y | -5.6751e-05 | 0.011053 | 0.20292 | 0.0060362 | 5.6751e-05 | North | N | 5.6751e-05 | 0
13134 | CALFREST | 4 | 151.5 | 0.015079 | north | Y | -7.751e-06 | 0.011102 | 0.20297 | 0.0060852 | 7.751e-06 | North | N | 7.751e-06 | 0
13135 | CALFREST | 5 | 152.3 | 0.015079 | north | Y | -7.751e-06 | 0.011102 | 0.20297 | 0.0060852 | 7.751e-06 | North | N | 7.751e-06 | 0
13136 | CALFREST | 6 | 177.5 | 0.015079 | north | Y | -7.751e-06 | 0.011102 | 0.20297 | 0.0060852 | 7.751e-06 | North | N | 7.751e-06 | 0
13432 | SANDOW_5 | 5 | 581 | 0.007336 | south | Y | -0.0077508 | 0.0033586 | 0.19522 | -0.0016578 | 0.0016578 | houston | Y | 0.0033586 | 0.98814
13691 | OAKGROVE | 1 | 855 | 0.012971 | north | Y | -0.0021158 | 0.0089936 | 0.20086 | 0.0039772 | 0.0021158 | North | N | 0.0021158 | 0
13692 | OAKGROVE | 2 | 855 | 0.012971 | north | Y | -0.0021158 | 0.0089936 | 0.20086 | 0.0039772 | 0.0021158 | North | N | 0.0021158 | 0
32798 | BRYN_TAM | 1 | 32 | 0.011756 | north | N | -0.0033308 | 0.0077786 | 0.19964 | 0.0027622 | 0.0027622 | houston | Y | 0.0033308 | 0
32883 | BRYN_DNS | 1 | 48 | 0.011727 | north | Y | -0.0033598 | 0.0077496 | 0.19961 | 0.0027332 | 0.0027332 | houston | Y | 0.0033598 | 0.030075
32884 | BRYN_DNS | 1 | 46 | 0.011727 | north | Y | -0.0033598 | 0.0077496 | 0.19961 | 0.0027332 | 0.0027332 | houston | Y | 0.0033598 | 0.028822
32886 | BRYN_ATK | MB | 12 | 0.011763 | north | Y | -0.0033238 | 0.0077856 | 0.19965 | 0.0027692 | 0.0027692 | houston | Y | 0.0033238 | 0
32887 | BRYN_ATK | MB | 51 | 0.011763 | north | Y | -0.0033238 | 0.0077856 | 0.19965 | 0.0027692 | 0.0027692 | houston | Y | 0.0033238 | 0
32888 | BRYN_ATK | 1 | 17 | 0.011763 | north | Y | -0.0033238 | 0.0077856 | 0.19965 | 0.0027692 | 0.0027692 | houston | Y | 0.0033238 | 0.0094277
32890 | BRYN_ATK | MB | 22 | 0.011763 | north | Y | -0.0033238 | 0.0077856 | 0.19965 | 0.0027692 | 0.0027692 | houston | Y | 0.0033238 | 0
32891 | BRYN_ATK | MB | 25 | 0.011763 | north | Y | -0.0033238 | 0.0077856 | 0.19965 | 0.0027692 | 0.0027692 | houston | Y | 0.0033238 | 0
32892 | BRYN_DNS | 1 | 105 | 0.011727 | north | Y | -0.0033598 | 0.0077496 | 0.19961 | 0.0027332 | 0.0027332 | houston | Y | 0.0033598 | 0.06579
36998 | RDCNYNG1 | 1 | 84 | -0.17574 | west | Y | -0.19083 | -0.17972 | 0.012146 | -0.18474 | 0.012146 | west | N | 0.012146 | 0
38332 | WDWRDU2 | 1 | 80 | -0.15521 | west | Y | -0.1703 | -0.15919 | 0.032677 | -0.1642 | 0.032677 | west | N | 0.032677 | 0
38437 | TNSRBNMS | 1 | 150 | -0.15513 | west | Y | -0.17022 | -0.15911 | 0.032753 | -0.16413 | 0.032753 | west | N | 0.032753 | 0
38438 | TNSRBNMS | 1 | 150 | -0.15513 | west | Y | -0.17022 | -0.15911 | 0.032753 | -0.16413 | 0.032753 | west | N | 0.032753 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.008921 | houston | N | -0.0061658 | 0.0049436 | 0.19681 | -7.282e-05 | 7.282e-05 | houston | N | 7.282e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.008921 | houston | N | -0.0061658 | 0.0049436 | 0.19681 | -7.282e-05 | 7.282e-05 | houston | N | 7.282e-05 | 0
38600 | TNBP_CGN | 5 | 53 | 0.008921 | houston | N | -0.0061658 | 0.0049436 | 0.19681 | -7.282e-05 | 7.282e-05 | houston | N | 7.282e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.008921 | houston | N | -0.0061658 | 0.0049436 | 0.19681 | -7.282e-05 | 7.282e-05 | houston | N | 7.282e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.008921 | houston | N | -0.0061658 | 0.0049436 | 0.19681 | -7.282e-05 | 7.282e-05 | houston | N | 7.282e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.008921 | houston | N | -0.0061658 | 0.0049436 | 0.19681 | -7.282e-05 | 7.282e-05 | houston | N | 7.282e-05 | 0
38614 | TNBPAMCG | 4 | 96 | 0.008921 | houston | N | -0.0061658 | 0.0049436 | 0.19681 | -7.282e-05 | 7.282e-05 | houston | N | 7.282e-05 | 0
38615 | TNBPAMCG | 1 | 244 | 0.008921 | houston | N | -0.0061658 | 0.0049436 | 0.19681 | -7.282e-05 | 7.282e-05 | houston | N | 7.282e-05 | 0
38690 | TNBP_CGN | 3 | 40 | 0.008921 | houston | N | -0.0061658 | 0.0049436 | 0.19681 | -7.282e-05 | 7.282e-05 | houston | N | 7.282e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.00892 | houston | N | -0.0061668 | 0.0049426 | 0.19681 | -7.382e-05 | 7.382e-05 | houston | N | 7.382e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.00892 | houston | N | -0.0061668 | 0.0049426 | 0.19681 | -7.382e-05 | 7.382e-05 | houston | N | 7.382e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.00892 | houston | N | -0.0061668 | 0.0049426 | 0.19681 | -7.382e-05 | 7.382e-05 | houston | N | 7.382e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.00892 | houston | N | -0.0061668 | 0.0049426 | 0.19681 | -7.382e-05 | 7.382e-05 | houston | N | 7.382e-05 | 0
39470 | TNDOWCGN | 1 | 32 | 0.00892 | houston | N | -0.0061668 | 0.0049426 | 0.19681 | -7.382e-05 | 7.382e-05 | houston | N | 7.382e-05 | 0
39480 | TNDOWCGN | 1 | 30 | 0.00892 | houston | N | -0.0061668 | 0.0049426 | 0.19681 | -7.382e-05 | 7.382e-05 | houston | N | 7.382e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.008288 | houston | N | -0.0067988 | 0.0043106 | 0.19618 | -0.00070582 | 0.00070582 | houston | N | 0.00070582 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.008288 | houston | N | -0.0067988 | 0.0043106 | 0.19618 | -0.00070582 | 0.00070582 | houston | N | 0.00070582 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.008288 | houston | N | -0.0067988 | 0.0043106 | 0.19618 | -0.00070582 | 0.00070582 | houston | N | 0.00070582 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.008288 | houston | N | -0.0067988 | 0.0043106 | 0.19618 | -0.00070582 | 0.00070582 | houston | N | 0.00070582 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.012971 | north | Y | -0.0021158 | 0.0089936 | 0.20086 | 0.0039772 | 0.0021158 | North | N | 0.0021158 | 0
39970 | TNTNPONE | 1 | 153 | 0.012971 | north | Y | -0.0021158 | 0.0089936 | 0.20086 | 0.0039772 | 0.0021158 | North | N | 0.0021158 | 0
48500 | APD_GT1_ | 1 | 136 | 0.009299 | houston | N | -0.0057878 | 0.0053216 | 0.19719 | 0.00030518 | 0.00030518 | houston | N | 0.00030518 | 0
48510 | AK_GT1__ | 1 | 33 | 0.008711 | houston | N | -0.0063758 | 0.0047336 | 0.1966 | -0.00028282 | 0.00028282 | houston | N | 0.00028282 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.009298 | houston | Y | -0.0057888 | 0.0053206 | 0.19719 | 0.00030418 | 0.00030418 | houston | N | 0.00030418 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.009298 | houston | Y | -0.0057888 | 0.0053206 | 0.19719 | 0.00030418 | 0.00030418 | houston | N | 0.00030418 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.009298 | houston | Y | -0.0057888 | 0.0053206 | 0.19719 | 0.00030418 | 0.00030418 | houston | N | 0.00030418 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.009298 | houston | Y | -0.0057888 | 0.0053206 | 0.19719 | 0.00030418 | 0.00030418 | houston | N | 0.00030418 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.008174 | houston | N | -0.0069128 | 0.0041966 | 0.19606 | -0.00081982 | 0.00081982 | houston | N | 0.00081982 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.008174 | houston | N | -0.0069128 | 0.0041966 | 0.19606 | -0.00081982 | 0.00081982 | houston | N | 0.00081982 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.008694 | houston | N | -0.0063928 | 0.0047166 | 0.19658 | -0.00029982 | 0.00029982 | houston | N | 0.00029982 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.008694 | houston | N | -0.0063928 | 0.0047166 | 0.19658 | -0.00029982 | 0.00029982 | houston | N | 0.00029982 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.008694 | houston | N | -0.0063928 | 0.0047166 | 0.19658 | -0.00029982 | 0.00029982 | houston | N | 0.00029982 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.009157 | houston | N | -0.0059298 | 0.0051796 | 0.19704 | 0.00016318 | 0.00016318 | houston | N | 0.00016318 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.009157 | houston | N | -0.0059298 | 0.0051796 | 0.19704 | 0.00016318 | 0.00016318 | houston | N | 0.00016318 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.009157 | houston | N | -0.0059298 | 0.0051796 | 0.19704 | 0.00016318 | 0.00016318 | houston | N | 0.00016318 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.009157 | houston | N | -0.0059298 | 0.0051796 | 0.19704 | 0.00016318 | 0.00016318 | houston | N | 0.00016318 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.009248 | houston | N | -0.0058388 | 0.0052706 | 0.19714 | 0.00025418 | 0.00025418 | houston | N | 0.00025418 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.009248 | houston | N | -0.0058388 | 0.0052706 | 0.19714 | 0.00025418 | 0.00025418 | houston | N | 0.00025418 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.00913 | houston | N | -0.0059568 | 0.0051526 | 0.19702 | 0.00013618 | 0.00013618 | houston | N | 0.00013618 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.00913 | houston | N | -0.0059568 | 0.0051526 | 0.19702 | 0.00013618 | 0.00013618 | houston | N | 0.00013618 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.00913 | houston | N | -0.0059568 | 0.0051526 | 0.19702 | 0.00013618 | 0.00013618 | houston | N | 0.00013618 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.00913 | houston | N | -0.0059568 | 0.0051526 | 0.19702 | 0.00013618 | 0.00013618 | houston | N | 0.00013618 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.00913 | houston | N | -0.0059568 | 0.0051526 | 0.19702 | 0.00013618 | 0.00013618 | houston | N | 0.00013618 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.009411 | houston | Y | -0.0056758 | 0.0054336 | 0.1973 | 0.00041718 | 0.00041718 | houston | N | 0.00041718 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.009365 | houston | Y | -0.0057218 | 0.0053876 | 0.19725 | 0.00037118 | 0.00037118 | houston | N | 0.00037118 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.009424 | houston | Y | -0.0056628 | 0.0054466 | 0.19731 | 0.00043018 | 0.00043018 | houston | N | 0.00043018 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.009424 | houston | Y | -0.0056628 | 0.0054466 | 0.19731 | 0.00043018 | 0.00043018 | houston | N | 0.00043018 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.009424 | houston | Y | -0.0056628 | 0.0054466 | 0.19731 | 0.00043018 | 0.00043018 | houston | N | 0.00043018 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.00968 | houston | N | -0.0054068 | 0.0057026 | 0.19757 | 0.00068618 | 0.00068618 | houston | N | 0.00068618 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.009308 | houston | N | -0.0057788 | 0.0053306 | 0.1972 | 0.00031418 | 0.00031418 | houston | N | 0.00031418 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.009308 | houston | N | -0.0057788 | 0.0053306 | 0.1972 | 0.00031418 | 0.00031418 | houston | N | 0.00031418 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.009457 | houston | N | -0.0056298 | 0.0054796 | 0.19734 | 0.00046318 | 0.00046318 | houston | N | 0.00046318 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.009457 | houston | N | -0.0056298 | 0.0054796 | 0.19734 | 0.00046318 | 0.00046318 | houston | N | 0.00046318 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.009457 | houston | N | -0.0056298 | 0.0054796 | 0.19734 | 0.00046318 | 0.00046318 | houston | N | 0.00046318 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.009457 | houston | N | -0.0056298 | 0.0054796 | 0.19734 | 0.00046318 | 0.00046318 | houston | N | 0.00046318 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.009251 | houston | N | -0.0058358 | 0.0052736 | 0.19714 | 0.00025718 | 0.00025718 | houston | N | 0.00025718 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.009251 | houston | N | -0.0058358 | 0.0052736 | 0.19714 | 0.00025718 | 0.00025718 | houston | N | 0.00025718 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.009251 | houston | N | -0.0058358 | 0.0052736 | 0.19714 | 0.00025718 | 0.00025718 | houston | N | 0.00025718 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.009251 | houston | N | -0.0058358 | 0.0052736 | 0.19714 | 0.00025718 | 0.00025718 | houston | N | 0.00025718 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.009219 | houston | N | -0.0058678 | 0.0052416 | 0.19711 | 0.00022518 | 0.00022518 | houston | N | 0.00022518 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.009219 | houston | N | -0.0058678 | 0.0052416 | 0.19711 | 0.00022518 | 0.00022518 | houston | N | 0.00022518 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.009219 | houston | N | -0.0058678 | 0.0052416 | 0.19711 | 0.00022518 | 0.00022518 | houston | N | 0.00022518 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.009219 | houston | N | -0.0058678 | 0.0052416 | 0.19711 | 0.00022518 | 0.00022518 | houston | N | 0.00022518 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.009219 | houston | N | -0.0058678 | 0.0052416 | 0.19711 | 0.00022518 | 0.00022518 | houston | N | 0.00022518 | 0
48651 | EP_1_2 | 1 | 5 | 0.00941 | houston | N | -0.0056768 | 0.0054326 | 0.1973 | 0.00041618 | 0.00041618 | houston | N | 0.00041618 | 0
48651 | EP_1_2 | 2 | 21 | 0.00941 | houston | N | -0.0056768 | 0.0054326 | 0.1973 | 0.00041618 | 0.00041618 | houston | N | 0.00041618 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.011424 | north | N | -0.0036628 | 0.0074466 | 0.19931 | 0.0024302 | 0.0024302 | houston | Y | 0.0036628 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.011424 | north | N | -0.0036628 | 0.0074466 | 0.19931 | 0.0024302 | 0.0024302 | houston | Y | 0.0036628 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.011424 | north | N | -0.0036628 | 0.0074466 | 0.19931 | 0.0024302 | 0.0024302 | houston | Y | 0.0036628 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.011424 | north | N | -0.0036628 | 0.0074466 | 0.19931 | 0.0024302 | 0.0024302 | houston | Y | 0.0036628 | 0
48690 | GBY_GN5_ | 5 | 398 | 0.009471 | houston | Y | -0.0056158 | 0.0054936 | 0.19736 | 0.00047718 | 0.00047718 | houston | N | 0.00047718 | 0
48691 | GBY_7374 | A | 46 | 0.009205 | houston | Y | -0.0058818 | 0.0052276 | 0.19709 | 0.00021118 | 0.00021118 | houston | N | 0.00021118 | 0
48691 | GBY_7374 | B | 46 | 0.009205 | houston | Y | -0.0058818 | 0.0052276 | 0.19709 | 0.00021118 | 0.00021118 | houston | N | 0.00021118 | 0
48692 | GBY_8182 | C | 46 | 0.009205 | houston | Y | -0.0058818 | 0.0052276 | 0.19709 | 0.00021118 | 0.00021118 | houston | N | 0.00021118 | 0
48692 | GBY_8182 | D | 55 | 0.009205 | houston | Y | -0.0058818 | 0.0052276 | 0.19709 | 0.00021118 | 0.00021118 | houston | N | 0.00021118 | 0
48693 | GBY_8384 | E | 55 | 0.009205 | houston | Y | -0.0058818 | 0.0052276 | 0.19709 | 0.00021118 | 0.00021118 | houston | N | 0.00021118 | 0
48693 | GBY_8384 | F | 54 | 0.009205 | houston | Y | -0.0058818 | 0.0052276 | 0.19709 | 0.00021118 | 0.00021118 | houston | N | 0.00021118 | 0
48721 | LEG_1___ | 1 | 827 | 0.013448 | north | Y | -0.0016388 | 0.0094706 | 0.20134 | 0.0044542 | 0.0016388 | North | N | 0.0016388 | 0
48722 | LEG_2___ | 2 | 819 | 0.013448 | north | Y | -0.0016388 | 0.0094706 | 0.20134 | 0.0044542 | 0.0016388 | North | N | 0.0016388 | 0
48730 | MNS_GT | 1 | 46.1 | 0.008656 | houston | N | -0.0064308 | 0.0046786 | 0.19654 | -0.00033782 | 0.00033782 | houston | N | 0.00033782 | 0
48731 | CBE_GT1 | 1 | 76 | 0.00739 | houston | Y | -0.0076968 | 0.0034126 | 0.19528 | -0.0016038 | 0.0016038 | houston | N | 0.0016038 | 0
48732 | CBE_GT2 | 1 | 76 | 0.00739 | houston | Y | -0.0076968 | 0.0034126 | 0.19528 | -0.0016038 | 0.0016038 | houston | N | 0.0016038 | 0
48733 | CBE_ST12 | 1 | 105 | 0.00739 | houston | Y | -0.0076968 | 0.0034126 | 0.19528 | -0.0016038 | 0.0016038 | houston | N | 0.0016038 | 0
48734 | CBE_GT3 | 1 | 74 | 0.00739 | houston | Y | -0.0076968 | 0.0034126 | 0.19528 | -0.0016038 | 0.0016038 | houston | N | 0.0016038 | 0
48735 | CBE_GT4 | 1 | 74 | 0.00739 | houston | Y | -0.0076968 | 0.0034126 | 0.19528 | -0.0016038 | 0.0016038 | houston | N | 0.0016038 | 0
48736 | CBE_ST34 | 1 | 102 | 0.00739 | houston | Y | -0.0076968 | 0.0034126 | 0.19528 | -0.0016038 | 0.0016038 | houston | N | 0.0016038 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.009253 | houston | N | -0.0058338 | 0.0052756 | 0.19714 | 0.00025918 | 0.00025918 | houston | N | 0.00025918 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.009253 | houston | N | -0.0058338 | 0.0052756 | 0.19714 | 0.00025918 | 0.00025918 | houston | N | 0.00025918 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.009253 | houston | N | -0.0058338 | 0.0052756 | 0.19714 | 0.00025918 | 0.00025918 | houston | N | 0.00025918 | 0
48761 | PR_GT1__ | 1 | 35 | 0.009234 | houston | N | -0.0058528 | 0.0052566 | 0.19712 | 0.00024018 | 0.00024018 | houston | N | 0.00024018 | 0
48772 | PHR_GN2_ | MB | 459 | 0.009059 | houston | Y | -0.0060278 | 0.0050816 | 0.19695 | 6.518e-05 | 6.518e-05 | houston | N | 6.518e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.009411 | houston | N | -0.0056758 | 0.0054336 | 0.1973 | 0.00041718 | 0.00041718 | houston | N | 0.00041718 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.009411 | houston | N | -0.0056758 | 0.0054336 | 0.1973 | 0.00041718 | 0.00041718 | houston | N | 0.00041718 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.009411 | houston | N | -0.0056758 | 0.0054336 | 0.1973 | 0.00041718 | 0.00041718 | houston | N | 0.00041718 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.009411 | houston | N | -0.0056758 | 0.0054336 | 0.1973 | 0.00041718 | 0.00041718 | houston | N | 0.00041718 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.009411 | houston | N | -0.0056758 | 0.0054336 | 0.1973 | 0.00041718 | 0.00041718 | houston | N | 0.00041718 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.009411 | houston | N | -0.0056758 | 0.0054336 | 0.1973 | 0.00041718 | 0.00041718 | houston | N | 0.00041718 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.009411 | houston | N | -0.0056758 | 0.0054336 | 0.1973 | 0.00041718 | 0.00041718 | houston | N | 0.00041718 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.00968 | houston | N | -0.0054068 | 0.0057026 | 0.19757 | 0.00068618 | 0.00068618 | houston | N | 0.00068618 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.00968 | houston | N | -0.0054068 | 0.0057026 | 0.19757 | 0.00068618 | 0.00068618 | houston | N | 0.00068618 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.00968 | houston | N | -0.0054068 | 0.0057026 | 0.19757 | 0.00068618 | 0.00068618 | houston | N | 0.00068618 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.00968 | houston | N | -0.0054068 | 0.0057026 | 0.19757 | 0.00068618 | 0.00068618 | houston | N | 0.00068618 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.009421 | houston | N | -0.0056658 | 0.0054436 | 0.19731 | 0.00042718 | 0.00042718 | houston | N | 0.00042718 | 0
48820 | SHELLG1_ | 1 | 71 | 0.009269 | houston | N | -0.0058178 | 0.0052916 | 0.19716 | 0.00027518 | 0.00027518 | houston | N | 0.00027518 | 0
48821 | SHELLG2 | 2 | 72 | 0.009269 | houston | N | -0.0058178 | 0.0052916 | 0.19716 | 0.00027518 | 0.00027518 | houston | N | 0.00027518 | 0
48822 | SHELLG3_ | 1 | 39 | 0.009269 | houston | N | -0.0058178 | 0.0052916 | 0.19716 | 0.00027518 | 0.00027518 | houston | N | 0.00027518 | 0
48822 | SHELLG3_ | 2 | 30 | 0.009269 | houston | N | -0.0058178 | 0.0052916 | 0.19716 | 0.00027518 | 0.00027518 | houston | N | 0.00027518 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.009208 | houston | N | -0.0058788 | 0.0052306 | 0.1971 | 0.00021418 | 0.00021418 | houston | N | 0.00021418 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.009208 | houston | N | -0.0058788 | 0.0052306 | 0.1971 | 0.00021418 | 0.00021418 | houston | N | 0.00021418 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.009251 | houston | N | -0.0058358 | 0.0052736 | 0.19714 | 0.00025718 | 0.00025718 | houston | N | 0.00025718 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.009248 | houston | Y | -0.0058388 | 0.0052706 | 0.19714 | 0.00025418 | 0.00025418 | houston | N | 0.00025418 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.009247 | houston | Y | -0.0058398 | 0.0052696 | 0.19713 | 0.00025318 | 0.00025318 | houston | N | 0.00025318 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.009251 | houston | Y | -0.0058358 | 0.0052736 | 0.19714 | 0.00025718 | 0.00025718 | houston | N | 0.00025718 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.009252 | houston | Y | -0.0058348 | 0.0052746 | 0.19714 | 0.00025818 | 0.00025818 | houston | N | 0.00025818 | 0
48855 | SRB_GT21 | B2 | 12 | 0.009246 | houston | Y | -0.0058408 | 0.0052686 | 0.19713 | 0.00025218 | 0.00025218 | houston | N | 0.00025218 | 0
48855 | SRB_GT21 | MB | 18 | 0.009246 | houston | Y | -0.0058408 | 0.0052686 | 0.19713 | 0.00025218 | 0.00025218 | houston | N | 0.00025218 | 0
48865 | TECO_GT1 | 1 | 50 | 0.00901 | houston | Y | -0.0060768 | 0.0050326 | 0.1969 | 1.618e-05 | 1.618e-05 | houston | N | 1.618e-05 | 0
48873 | THW_ST3_ | 3 | 104 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48874 | THW_ST4_ | 4 | 104 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48875 | THW_3132 | A | 54 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48875 | THW_3132 | B | 53 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48877 | THW_3334 | C | 54 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48877 | THW_3334 | D | 57 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48879 | THW_4142 | E | 54 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48879 | THW_4142 | F | 54 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48881 | THW_4344 | G | 58 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48881 | THW_4344 | H | 58 | 0.009357 | houston | Y | -0.0057298 | 0.0053796 | 0.19724 | 0.00036318 | 0.00036318 | houston | N | 0.00036318 | 0
48883 | THW_GT1_ | B2 | 12 | 0.009398 | houston | Y | -0.0056888 | 0.0054206 | 0.19729 | 0.00040418 | 0.00040418 | houston | N | 0.00040418 | 0
48885 | THW_5152 | A | 56 | 0.009492 | houston | Y | -0.0055948 | 0.0055146 | 0.19738 | 0.00049818 | 0.00049818 | houston | N | 0.00049818 | 0
48885 | THW_5152 | B | 59 | 0.009492 | houston | Y | -0.0055948 | 0.0055146 | 0.19738 | 0.00049818 | 0.00049818 | houston | N | 0.00049818 | 0
48886 | THW_5354 | C | 56 | 0.009492 | houston | Y | -0.0055948 | 0.0055146 | 0.19738 | 0.00049818 | 0.00049818 | houston | N | 0.00049818 | 0
48886 | THW_5354 | D | 56 | 0.009492 | houston | Y | -0.0055948 | 0.0055146 | 0.19738 | 0.00049818 | 0.00049818 | houston | N | 0.00049818 | 0
48887 | THW_5556 | E | 59 | 0.009492 | houston | Y | -0.0055948 | 0.0055146 | 0.19738 | 0.00049818 | 0.00049818 | houston | N | 0.00049818 | 0
48887 | THW_5556 | F | 56 | 0.009492 | houston | Y | -0.0055948 | 0.0055146 | 0.19738 | 0.00049818 | 0.00049818 | houston | N | 0.00049818 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.007479 | houston | Y | -0.0076078 | 0.0035016 | 0.19537 | -0.0015148 | 0.0015148 | houston | N | 0.0015148 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.008762 | houston | Y | -0.0063248 | 0.0047846 | 0.19665 | -0.00023182 | 0.00023182 | houston | N | 0.00023182 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.008762 | houston | Y | -0.0063248 | 0.0047846 | 0.19665 | -0.00023182 | 0.00023182 | houston | N | 0.00023182 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.008762 | houston | Y | -0.0063248 | 0.0047846 | 0.19665 | -0.00023182 | 0.00023182 | houston | N | 0.00023182 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.008762 | houston | Y | -0.0063248 | 0.0047846 | 0.19665 | -0.00023182 | 0.00023182 | houston | N | 0.00023182 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.008762 | houston | N | -0.0063248 | 0.0047846 | 0.19665 | -0.00023182 | 0.00023182 | houston | N | 0.00023182 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.008691 | houston | Y | -0.0063958 | 0.0047136 | 0.19658 | -0.00030282 | 0.00030282 | houston | N | 0.00030282 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.008691 | houston | Y | -0.0063958 | 0.0047136 | 0.19658 | -0.00030282 | 0.00030282 | houston | N | 0.00030282 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.008691 | houston | Y | -0.0063958 | 0.0047136 | 0.19658 | -0.00030282 | 0.00030282 | houston | N | 0.00030282 | 0
48929 | WAPGT21_ | B1 | 13 | 0.008762 | houston | Y | -0.0063248 | 0.0047846 | 0.19665 | -0.00023182 | 0.00023182 | houston | N | 0.00023182 | 0
48940 | WARVUE_G | G1 | 12 | 0.00941 | houston | Y | -0.0056768 | 0.0054326 | 0.1973 | 0.00041618 | 0.00041618 | houston | N | 0.00041618 | 0
49803 | EXN_15GT | 1 | 34 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49826 | EXN938GT | 5 | 45.9 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49828 | EXN941GT | 10 | 17.7 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49829 | EXN942GT | 11 | 20.4 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49830 | EXN943GT | 12 | 19.9 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49831 | EXN944GT | 13 | 35 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49832 | EXN945GT | 9 | 18 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49837 | EXN_GT | 4 | 85.4 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49838 | EXN_14GT | 14 | 148 | 0.009377 | houston | N | -0.0057098 | 0.0053996 | 0.19726 | 0.00038318 | 0.00038318 | houston | N | 0.00038318 | 0
49851 | DOW17000 | 37 | 62 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49858 | DOW38100 | 31 | 71.4 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49859 | DOW38200 | 33 | 45 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49860 | DOW38300 | 32 | 101 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49862 | DOW39100 | 36 | 86 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49863 | DOW39200 | 35 | 88 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49865 | DOW41000 | 41 | 50 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49866 | DOW42000 | 42 | 18 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49869 | DOW49000 | 45 | 94 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49870 | DOW61000 | 61 | 70 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49871 | DOW62000 | 62 | 63 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49872 | DOW63000 | 63 | 72 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49873 | DOW64000 | 64 | 64.8 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49876 | DOW65000 | 65 | 101 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49877 | DOW66000 | 66 | 97 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49878 | DOW67000 | 67 | 103 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49882 | DOW81000 | 81 | 76 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49884 | DOW82000 | 82 | 80 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49885 | DOW83000 | 83 | 80 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
49886 | DOW84000 | 84 | 171 | 0.00804 | houston | N | -0.0070468 | 0.0040626 | 0.19593 | -0.00095382 | 0.00095382 | houston | N | 0.00095382 | 0
58909 | PEARSALL | 1 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58909 | PEARSALL | 2 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58909 | PEARSALL | 3 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58909 | PEARSALL | 4 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58909 | PEARSALL | 5 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58909 | PEARSALL | 6 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58919 | PEARSALL | 1 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58919 | PEARSALL | 2 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58919 | PEARSALL | 3 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58919 | PEARSALL | 4 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58919 | PEARSALL | 5 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58919 | PEARSALL | 6 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58929 | PEARSALL | 1 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58929 | PEARSALL | 2 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58929 | PEARSALL | 3 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58929 | PEARSALL | 4 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58929 | PEARSALL | 5 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58929 | PEARSALL | 6 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58949 | PEARSALL | 1 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58949 | PEARSALL | 2 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58949 | PEARSALL | 3 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58949 | PEARSALL | 4 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58949 | PEARSALL | 5 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
58949 | PEARSALL | 6 | 8.4 | -0.004197 | south | Y | -0.019284 | -0.0081744 | 0.18369 | -0.013191 | 0.0081744 | south | N | 0.0081744 | 0
60000 | DSKY2 | 1 | 76.5 | -0.15161 | west | Y | -0.1667 | -0.15559 | 0.036276 | -0.16061 | 0.036276 | west | N | 0.036276 | 0
60003 | KING_NE1 | 1 | 80 | -0.15535 | west | Y | -0.17043 | -0.15932 | 0.032541 | -0.16434 | 0.032541 | west | N | 0.032541 | 0
60005 | KING_SE1 | 1 | 40 | -0.15535 | west | Y | -0.17043 | -0.15932 | 0.032541 | -0.16434 | 0.032541 | west | N | 0.032541 | 0
60007 | KING_SW1 | 1 | 80 | -0.15591 | west | Y | -0.171 | -0.15989 | 0.031973 | -0.16491 | 0.031973 | west | N | 0.031973 | 0
60016 | WOODWRD1 | 1 | 80 | -0.15523 | west | Y | -0.17031 | -0.15921 | 0.03266 | -0.16422 | 0.03266 | west | N | 0.03266 | 0
60017 | ORNNWP1 | 1 | 80 | -0.15225 | west | Y | -0.16734 | -0.15623 | 0.035634 | -0.16125 | 0.035634 | west | N | 0.035634 | 0
60018 | DSKY1 | 1 | 84 | -0.15128 | west | Y | -0.16637 | -0.15526 | 0.036606 | -0.16028 | 0.036606 | west | N | 0.036606 | 0
60019 | KING_NW1 | 1 | 80 | -0.15591 | west | Y | -0.171 | -0.15989 | 0.031973 | -0.16491 | 0.031973 | west | N | 0.031973 | 0
60057 | CALLAHAN | 1 | 114 | 0.002398 | south | Y | -0.012689 | -0.0015794 | 0.19029 | -0.0065958 | 0.0015794 | south | N | 0.0015794 | 0
60058 | BUFF_GAP | 1 | 120 | -0.19359 | west | Y | -0.20868 | -0.19757 | -0.0057043 | -0.20259 | 0.0057043 | west | N | 0.0057043 | 0
60060 | CIRELLO | 1 | 233 | -0.19359 | west | Y | -0.20868 | -0.19757 | -0.0057043 | -0.20259 | 0.0057043 | west | N | 0.0057043 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.19359 | west | Y | -0.20868 | -0.19757 | -0.0057043 | -0.20259 | 0.0057043 | west | N | 0.0057043 | 0
60066 | H_HOLLOW | 1 | 222 | 0.002398 | south | Y | -0.012689 | -0.0015794 | 0.19029 | -0.0065958 | 0.0015794 | south | N | 0.0015794 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.002398 | south | Y | -0.012689 | -0.0015794 | 0.19029 | -0.0065958 | 0.0015794 | south | N | 0.0015794 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.002398 | south | Y | -0.012689 | -0.0015794 | 0.19029 | -0.0065958 | 0.0015794 | south | N | 0.0015794 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.002398 | south | Y | -0.012689 | -0.0015794 | 0.19029 | -0.0065958 | 0.0015794 | south | N | 0.0015794 | 0
60074 | HORSH5 | 1 | 100 | 0.002398 | south | Y | -0.012689 | -0.0015794 | 0.19029 | -0.0065958 | 0.0015794 | south | N | 0.0015794 | 0
60081 | WHRLWIND | 1 | 60 | -0.23467 | west | Y | -0.24975 | -0.23864 | -0.046777 | -0.24366 | 0.046777 | west | N | 0.046777 | 0
60201 | RIO DRCS | F | 0 | -0.047963 | south | N | -0.06305 | -0.05194 | 0.13992 | -0.056957 | 0.05194 | south | N | 0.05194 | 0
60202 | FRIEND_R | F | 0 | -0.13587 | west | N | -0.15096 | -0.13985 | 0.052014 | -0.14487 | 0.052014 | west | N | 0.052014 | 0
60203 | PRES0A | BT | 4.8 | -0.15816 | west | N | -0.17325 | -0.16214 | 0.029728 | -0.16715 | 0.029728 | west | N | 0.029728 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.19477 | west | Y | -0.20985 | -0.19874 | -0.0068783 | -0.20376 | 0.0068783 | west | N | 0.0068783 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.19477 | west | Y | -0.20985 | -0.19874 | -0.0068783 | -0.20376 | 0.0068783 | west | N | 0.0068783 | 0
71057 | L_SWEETW | W1 | 135 | -0.19477 | west | Y | -0.20985 | -0.19874 | -0.0068783 | -0.20376 | 0.0068783 | west | N | 0.0068783 | 0
71059 | L_SWEETW | W1 | 119 | -0.19477 | west | Y | -0.20985 | -0.19874 | -0.0068783 | -0.20376 | 0.0068783 | west | N | 0.0068783 | 0
71060 | L_SWEETW | W1 | 105 | -0.19477 | west | Y | -0.20985 | -0.19874 | -0.0068783 | -0.20376 | 0.0068783 | west | N | 0.0068783 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.19477 | west | Y | -0.20985 | -0.19874 | -0.0068783 | -0.20376 | 0.0068783 | west | N | 0.0068783 | 0
76031 | L_GASCCR | W1 | 150 | -0.16073 | west | Y | -0.17581 | -0.1647 | 0.027162 | -0.16972 | 0.027162 | west | N | 0.027162 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.15973 | west | Y | -0.17482 | -0.16371 | 0.028159 | -0.16872 | 0.028159 | west | N | 0.028159 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.15973 | west | Y | -0.17482 | -0.16371 | 0.028159 | -0.16872 | 0.028159 | west | N | 0.028159 | 0
76096 | L_CAPRSI | W1 | 186 | -0.15973 | west | Y | -0.17482 | -0.16371 | 0.028159 | -0.16872 | 0.028159 | west | N | 0.028159 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.15973 | west | Y | -0.17482 | -0.16371 | 0.028159 | -0.16872 | 0.028159 | west | N | 0.028159 | 0
80003 | MILHWYS | F | 0 | 0.003774 | south | N | -0.011313 | -0.00020342 | 0.19166 | -0.0052198 | 0.00020342 | south | N | 0.00020342 | 0
80010 | EPLVT1 | F | 0 | -0.027824 | south | N | -0.042911 | -0.031801 | 0.16006 | -0.036818 | 0.031801 | south | N | 0.031801 | 0
80012 | LAR | F | 0 | -0.00049 | south | N | -0.015577 | -0.0044674 | 0.1874 | -0.0094838 | 0.0044674 | south | N | 0.0044674 | 0
80051 | FORPVCM0 | 8 | 28 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
80053 | FOR69CG0 | 10 | 74 | 0.005096 | south | N | -0.0099908 | 0.0011186 | 0.19298 | -0.0038978 | 0.0011186 | south | N | 0.0011186 | 0
80080 | GWINDT11 | 1 | 94 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80080 | GWINDT11 | 2 | 41 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80080 | GWINDT11 | 3 | 38 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80080 | GWINDT11 | 4 | 19 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80081 | GWINDT21 | 1 | 94 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80081 | GWINDT21 | 2 | 36 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80081 | GWINDT21 | 3 | 43 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80081 | GWINDT21 | 4 | 22 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80137 | CSDR89 | 8 | 39 | 0.004793 | south | N | -0.010294 | 0.00081558 | 0.19268 | -0.0042008 | 0.00081558 | south | N | 0.00081558 | 0
80137 | CSDR89 | 9 | 15 | 0.004793 | south | N | -0.010294 | 0.00081558 | 0.19268 | -0.0042008 | 0.00081558 | south | N | 0.00081558 | 0
80138 | CSDR7 | 7 | 7 | 0.004793 | south | N | -0.010294 | 0.00081558 | 0.19268 | -0.0042008 | 0.00081558 | south | N | 0.00081558 | 0
80139 | CSDR56 | 5 | 15 | 0.004793 | south | N | -0.010294 | 0.00081558 | 0.19268 | -0.0042008 | 0.00081558 | south | N | 0.00081558 | 0
80139 | CSDR56 | 6 | 39 | 0.004793 | south | N | -0.010294 | 0.00081558 | 0.19268 | -0.0042008 | 0.00081558 | south | N | 0.00081558 | 0
80140 | CSDR11 | 11 | 39 | 0.004793 | south | N | -0.010294 | 0.00081558 | 0.19268 | -0.0042008 | 0.00081558 | south | N | 0.00081558 | 0
80180 | PNSCALT1 | 1 | 148 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80180 | PNSCALT1 | 2 | 50 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80181 | PNSCALT2 | 1 | 55 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80181 | PNSCALT2 | 2 | 50 | 0.003825 | south | Y | -0.011262 | -0.00015242 | 0.19171 | -0.0051688 | 0.00015242 | south | N | 0.00015242 | 0
80223 | REYSHR G | 1 | 12 | 0.004139 | south | N | -0.010948 | 0.00016158 | 0.19203 | -0.0048548 | 0.00016158 | south | N | 0.00016158 | 0
80224 | VISTRONG | 1 | 15 | 0.004727 | south | N | -0.01036 | 0.00074958 | 0.19261 | -0.0042668 | 0.00074958 | south | N | 0.00074958 | 0
80225 | VISTRONG | 2 | 23 | 0.004727 | south | N | -0.01036 | 0.00074958 | 0.19261 | -0.0042668 | 0.00074958 | south | N | 0.00074958 | 0
80226 | ALCOA G | 1 | 48 | 0.005032 | south | N | -0.010055 | 0.0010546 | 0.19292 | -0.0039618 | 0.0010546 | south | N | 0.0010546 | 0
80227 | AIRCO G | 1 | 8 | 0.004748 | south | N | -0.010339 | 0.00077058 | 0.19264 | -0.0042458 | 0.00077058 | south | N | 0.00077058 | 0
80261 | NBEC81A | 1 | 180 | 0.004006 | south | Y | -0.011081 | 2.8576e-05 | 0.19189 | -0.0049878 | 2.8576e-05 | south | N | 2.8576e-05 | 0
80262 | NBEC91A | 1 | 180 | 0.00401 | south | Y | -0.011077 | 3.2576e-05 | 0.1919 | -0.0049838 | 3.2576e-05 | south | N | 3.2576e-05 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.003985 | south | Y | -0.011102 | 7.5759e-06 | 0.19187 | -0.0050088 | 7.5759e-06 | south | N | 7.5759e-06 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.003985 | south | Y | -0.011102 | 7.5759e-06 | 0.19187 | -0.0050088 | 7.5759e-06 | south | N | 7.5759e-06 | 0
80265 | LARECU40 | 4 | 100 | -0.000487 | south | Y | -0.015574 | -0.0044644 | 0.1874 | -0.0094808 | 0.0044644 | south | N | 0.0044644 | 0
80266 | LARECU50 | 5 | 100 | -0.000487 | south | Y | -0.015574 | -0.0044644 | 0.1874 | -0.0094808 | 0.0044644 | south | N | 0.0044644 | 0
80291 | PAPALOTE | 1 | 25 | 0.004084 | south | Y | -0.011003 | 0.00010658 | 0.19197 | -0.0049098 | 0.00010658 | south | N | 0.00010658 | 0
80291 | PAPALOTE | 2 | 25 | 0.004084 | south | Y | -0.011003 | 0.00010658 | 0.19197 | -0.0049098 | 0.00010658 | south | N | 0.00010658 | 0
80291 | PAPALOTE | 3 | 25 | 0.004084 | south | Y | -0.011003 | 0.00010658 | 0.19197 | -0.0049098 | 0.00010658 | south | N | 0.00010658 | 0
80291 | PAPALOTE | 4 | 16 | 0.004084 | south | Y | -0.011003 | 0.00010658 | 0.19197 | -0.0049098 | 0.00010658 | south | N | 0.00010658 | 0
80294 | PAPALOTE | 5 | 25 | 0.004084 | south | Y | -0.011003 | 0.00010658 | 0.19197 | -0.0049098 | 0.00010658 | south | N | 0.00010658 | 0
80294 | PAPALOTE | 6 | 25 | 0.004084 | south | Y | -0.011003 | 0.00010658 | 0.19197 | -0.0049098 | 0.00010658 | south | N | 0.00010658 | 0
80294 | PAPALOTE | 7 | 25 | 0.004084 | south | Y | -0.011003 | 0.00010658 | 0.19197 | -0.0049098 | 0.00010658 | south | N | 0.00010658 | 0
80294 | PAPALOTE | 8 | 15 | 0.004084 | south | Y | -0.011003 | 0.00010658 | 0.19197 | -0.0049098 | 0.00010658 | south | N | 0.00010658 | 0
86104 | CID-138 | EQ | 0 | -0.000487 | south | N | -0.015574 | -0.0044644 | 0.1874 | -0.0094808 | 0.0044644 | south | N | 0.0044644 | 0
86105 | CID-230 | EQ | 500 | -0.000487 | south | N | -0.015574 | -0.0044644 | 0.1874 | -0.0094808 | 0.0044644 | south | N | 0.0044644 | 0
86106 | CUF-230 | EQ | 500 | -0.000487 | south | N | -0.015574 | -0.0044644 | 0.1874 | -0.0094808 | 0.0044644 | south | N | 0.0044644 | 0
86107 | CUF-138 | EQ | 0 | -0.000487 | south | N | -0.015574 | -0.0044644 | 0.1874 | -0.0094808 | 0.0044644 | south | N | 0.0044644 | 0
88198 | BEEVILLE | F | 0 | 0.003269 | south | N | -0.011818 | -0.00070842 | 0.19116 | -0.0057248 | 0.00070842 | south | N | 0.00070842 | 0
88253 | HAMILTON | F | 0 | -0.043841 | south | N | -0.058928 | -0.047818 | 0.14405 | -0.052835 | 0.047818 | south | N | 0.047818 | 0
88299 | ZAPATA | F | 0 | 0.000923 | south | N | -0.014164 | -0.0030544 | 0.18881 | -0.0080708 | 0.0030544 | south | N | 0.0030544 | 0
88508 | FALFURRI | F | 0 | 0.00316 | south | N | -0.011927 | -0.00081742 | 0.19105 | -0.0058338 | 0.00081742 | south | N | 0.00081742 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1422 BOWMAN5 - 1425 FISHRDSS C: 1430 GRHAMES - 1435 LONGCREK C: 1439 LONCREK2 - 1442 COKFIELD | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.048632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.9209 | 204 | 0.21048 | 42.9373 | 204 | 42.9373
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.048632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.775 | 201 | 0.21048 | 42.3059 | 405 | 85.2432
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.048632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7689 | 242 | 0.21048 | 50.9354 | 647 | 136.1786
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.04277 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.0571 | 165 | 0.20461 | 33.7615 | 812 | 169.94 | Weighted Shift Factors
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.04277 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.6538 | 366 | 0.20461 | 74.8891 | 1178 | 244.8291 | North | 0.015087
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.020617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.237 | 60 | 0.18246 | 10.9477 | 1238 | 255.7768 | West | -0.16184
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.020617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2989 | 63 | 0.18246 | 11.4951 | 1301 | 267.2719 |  | 0.17693
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.019219 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18106 | 0 | 1301 | 267.2719
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.019219 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18106 | 0 | 1301 | 267.2719 | Line Rating | 1079.45
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.019219 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18106 | 0 | 1301 | 267.2719 | Conc Gen | 1671
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.019058 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1809 | 0 | 1301 | 267.2719 | Weighted Imp. | 333.9633
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.018851 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.1807 | 0 | 1301 | 267.2719 | PTDF | 0.19986
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.018402 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.8087 | 370 | 0.18025 | 66.6914 | 1671 | 333.9633
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5763 | 0 | 0.18025 | 0 | 1671 | 333.9633 | Concentration | 1.1296
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5947 | 0 | 0.18025 | 0 | 1671 | 333.9633
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6862 | 0 | 0.18025 | 0 | 1671 | 333.9633
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6315 | 0 | 0.18025 | 0 | 1671 | 333.9633
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6499 | 0 | 0.18025 | 0 | 1671 | 333.9633
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.7046 | 0 | 0.18025 | 0 | 1671 | 333.9633
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.018383 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.2577 | 558 | 0.18023 | 100.5672
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.018383 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.6438 | 579 | 0.18023 | 104.352
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.018383 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.8535 | 808 | 0.18023 | 145.6242
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9395 | 160 | 0.18022 | 28.8347
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.866 | 156 | 0.18022 | 28.1138
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.6009 | 196 | 0.18022 | 35.3225
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.866 | 156 | 0.18022 | 28.1138
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8844 | 157 | 0.18022 | 28.2941
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.6377 | 198 | 0.18022 | 35.683
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.018276 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.3707 | 0 | 0.18012 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.018276 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.4548 | 0 | 0.18012 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.018276 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.6156 | 0 | 0.18012 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.01815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4339 | 79 | 0.17999 | 14.2196
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.01815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9239 | 106 | 0.17999 | 19.0795
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.01815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6499 | 146 | 0.17999 | 26.2793
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.01815 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.3794 | 76 | 0.17999 | 13.6796
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.018075 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.3615 | 20 | 0.17992 | 3.5984
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.018075 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.45188 | 25 | 0.17992 | 4.498
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.018075 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.74108 | 41 | 0.17992 | 7.3767
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.018072 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.72288 | 40 | 0.17992 | 7.1967
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.018032 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0654 | 170 | 0.17988 | 30.5791
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.018032 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.3766 | 520 | 0.17988 | 93.536
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.017821 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.0393 | 395 | 0.17967 | 70.968
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.017821 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.7521 | 435 | 0.17967 | 78.1547
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.017812 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71248 | 0 | 0.17966 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.017812 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71248 | 0 | 0.17966 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.017809 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.7469 | 435 | 0.17965 | 78.1495
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.017736 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.8816 | 388 | 0.17958 | 69.6774
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.017736 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.134 | 515 | 0.17958 | 92.4842
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8421 | 161 | 0.1795 | 28.8992
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8951 | 164 | 0.1795 | 29.4377
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8951 | 164 | 0.1795 | 29.4377
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.3083 | 414 | 0.1795 | 74.3121
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8598 | 162 | 0.1795 | 29.0787
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8421 | 161 | 0.1795 | 28.8992
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8774 | 163 | 0.1795 | 29.2582
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.2201 | 409 | 0.1795 | 73.4147
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017631 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17948 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017631 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17948 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.017291 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0403 | 118 | 0.17914 | 21.138
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.017291 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9885 | 115 | 0.17914 | 20.6006
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.017291 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.6138 | 556 | 0.17914 | 99.5996
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.016582 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.0169 | 785 | 0.17843 | 140.0651
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.016582 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1827 | 795 | 0.17843 | 141.8494
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.016582 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.934 | 780 | 0.17843 | 139.173
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4327 | 0 | 0.17828 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.1368 | 0 | 0.17828 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.3834 | 0 | 0.17828 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.5584 | 0 | 0.17828 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.016315 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.17816 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.016302 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.8151 | 50 | 0.17815 | 8.9073
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.016275 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.9621 | 182 | 0.17812 | 32.4178
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.016275 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.8771 | 484 | 0.17812 | 86.21
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.016178 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5009 | 216.4 | 0.17802 | 38.5242
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.016178 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4961 | 216.1 | 0.17802 | 38.4708
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.015651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0676 | 196 | 0.1775 | 34.7892
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.015651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7373 | 111 | 0.1775 | 19.702
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.015576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.489 | 224 | 0.17742 | 39.7423
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4335 | 224 | 0.17717 | 39.6867
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4641 | 226 | 0.17717 | 40.0411
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2495 | 212 | 0.17717 | 37.5607
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2342 | 211 | 0.17717 | 37.3835
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.015079 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2845 | 151.5 | 0.17692 | 26.804
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.015079 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2965 | 152.3 | 0.17692 | 26.9455
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.015079 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6765 | 177.5 | 0.17692 | 31.404
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.01503 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.265 | 150.7 | 0.17687 | 26.6551
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.01503 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2695 | 151 | 0.17687 | 26.7081
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.01503 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6663 | 177.4 | 0.17687 | 31.3776
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.014787 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.094 | 615 | 0.17663 | 108.6286
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.014787 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.68 | 587 | 0.17663 | 103.6829
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.014078 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17592 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.013448 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.1215 | 827 | 0.17529 | 144.9672
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.013448 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.0139 | 819 | 0.17529 | 143.5649
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.0902 | 855 | 0.17482 | 149.4676
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.0902 | 855 | 0.17482 | 149.4676
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.9755 | 152.3 | 0.17482 | 26.6245
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.9846 | 153 | 0.17482 | 26.7468
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.011782 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.4551 | 463 | 0.17363 | 80.3893
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17361 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17361 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.011763 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.19997 | 17 | 0.17361 | 2.9513
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17361 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17361 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.011756 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.37619 | 0 | 0.1736 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.011727 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5629 | 48 | 0.17357 | 8.3315
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.011727 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.53944 | 46 | 0.17357 | 7.9843
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.011727 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2313 | 105 | 0.17357 | 18.2251
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7616 | 0 | 0.17327 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7821 | 0 | 0.17327 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7821 | 0 | 0.17327 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.3411 | 0 | 0.17327 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.011343 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17319 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.011343 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.9269 | 787 | 0.17319 | 136.2989
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.011221 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4383 | 217.3 | 0.17307 | 37.6072
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.011221 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3003 | 205 | 0.17307 | 35.4785
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.011221 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0566 | 272.4 | 0.17307 | 47.1432
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.010831 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17268 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.010831 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17268 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.010416 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7499 | 168 | 0.17226 | 28.9398
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.010416 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.93744 | 90 | 0.17226 | 15.5035
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.010276 | north | 3 | N | N | Nnorth | Nnorth | 1 | 11.8893 | 0 | 0.17212 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.010276 | north | 3 | N | N | Nnorth | Nnorth | 1 | 11.8996 | 0 | 0.17212 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.010119 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5803 | 255 | 0.17196 | 43.8508
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.010119 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5077 | 149 | 0.17196 | 25.6226
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.010119 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5482 | 153 | 0.17196 | 26.3105
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.009156 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3734 | 150 | 0.171 | 25.6501
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.009156 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.73248 | 80 | 0.171 | 13.6801
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.63896 | 70 | 0.17097 | 11.9681
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.62983 | 69 | 0.17097 | 11.7971
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.62983 | 69 | 0.17097 | 11.7971
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.6207 | 68 | 0.17097 | 11.6262
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.008977 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.13465 | 0 | 0.17082 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.008977 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.13465 | 0 | 0.17082 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.2398 | 100 | 0.16424 | 16.4243
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.16184 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.16184 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.000117 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.002106 | 18 | 0.16173 | 2.9111
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.000117 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.002106 | 18 | 0.16173 | 2.9111
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.000117 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.004446 | 38 | 0.16173 | 6.1457
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.004576 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.33405 | 73 | 0.15727 | 11.4806
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.004576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.54454 | 119 | 0.15727 | 18.715
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.004576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.93808 | 205 | 0.15727 | 32.2401
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.004576 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.46675 | 102 | 0.15727 | 16.0414
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.004576 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.4393 | 96 | 0.15727 | 15.0978
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.005011 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.56374 | 112.5 | 0.15683 | 17.6438
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.005328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.5345 | 288 | 0.15652 | 45.0769
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.005328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.78322 | 147 | 0.15652 | 23.008
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.005328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.78322 | 147 | 0.15652 | 23.008
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.013707 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.6448 | 120 | 0.14814 | 17.7766
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.023281 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.634 | 242 | 0.13856 | 33.5325
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.029517 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.3542 | 0 | 0.13233 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.029517 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.3542 | 0 | 0.13233 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.031383 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.883 | 60 | 0.13046 | 7.8277
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.047963 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.11388 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3587 | 20 | 0.093909 | 1.8782
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3587 | 20 | 0.093909 | 1.8782
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3587 | 20 | 0.093909 | 1.8782
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.1549 | 17 | 0.093909 | 1.5965
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.12248 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.3723 | 150 | 0.039363 | 5.9044
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.13587 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.025971 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.9902 | 209 | 0.023136 | 4.8354
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.5467 | 126.5 | 0.023136 | 2.9267
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.5385 | 249 | 0.023136 | 5.7608
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.3257 | 197 | 0.023136 | 4.5578
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.15128 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.7077 | 84 | 0.010563 | 0.88729
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.15161 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.5983 | 76.5 | 0.010233 | 0.78282
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15225 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.1803 | 80 | 0.0095909 | 0.76727
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.15513 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.2703 | 150 | 0.0067099 | 1.0065
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.15513 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.2703 | 150 | 0.0067099 | 1.0065
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.15521 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4169 | 80 | 0.0066339 | 0.53071
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15523 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4182 | 80 | 0.0066169 | 0.52935
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.15535 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.651 | 75 | 0.0064979 | 0.48734
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15535 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4278 | 80 | 0.0064979 | 0.51983
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.15535 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.2139 | 40 | 0.0064979 | 0.25992
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4732 | 80 | 0.0059299 | 0.47439
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4732 | 80 | 0.0059299 | 0.47439
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.15816 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.75917 | 0 | 0.0036849 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.9695 | 112.5 | 0.0021159 | 0.23804
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.8795 | 149.5 | 0.0021159 | 0.31633
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.7096 | 186 | 0.0021159 | 0.39356
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.2619 | 214.5 | 0.0021159 | 0.45387
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.16073 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.1089 | 150 | 0.0011189 | 0.16784
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.7906 | 66 | -0.0016491 | -0.10884
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.6271 | 65 | -0.0016491 | -0.10719
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.9541 | 67 | -0.0016491 | -0.11049
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.9541 | 67 | -0.0016491 | -0.11049
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.9541 | 67 | -0.0016491 | -0.11049
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.16349 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016491 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.16349 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016491 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.16371 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.7299 | 35 | -0.0018661 | -0.065313
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.16371 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9113 | 30 | -0.0018661 | -0.055982
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.16428 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.4774 | 149 | -0.0024331 | -0.36253
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -34.2687 | 208.2 | -0.0027501 | -0.57257
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -23.3889 | 142.1 | -0.0027501 | -0.39079
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -21.7924 | 132.4 | -0.0027501 | -0.36411
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.3849 | 136 | -0.0027501 | -0.37401
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -24.1955 | 147 | -0.0027501 | -0.40426
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -34.565 | 210 | -0.0027501 | -0.57752
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -11.5224 | 70 | -0.0027611 | -0.19328
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -11.5224 | 70 | -0.0027611 | -0.19328
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -15.2754 | 92.8 | -0.0027611 | -0.25623
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -13.1685 | 80 | -0.0027611 | -0.22089
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -13.1685 | 80 | -0.0027611 | -0.22089
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -18.9297 | 115 | -0.0027611 | -0.31752
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.16513 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.0899 | 6.6 | -0.0032841 | -0.021675
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.16513 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6639 | 34.3 | -0.0032841 | -0.11264
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.16544 | west | 8 | N | N | Nwest | Nwest | 1 | -11.5806 | 0 | -0.0035921 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.16544 | west | 8 | N | N | Nwest | Nwest | 1 | -12.1431 | 0 | -0.0035921 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.16544 | west | 8 | N | N | Nwest | Nwest | 1 | -11.6468 | 0 | -0.0035921 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.8367 | 150 | -0.0037331 | -0.55996
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.4272 | 220 | -0.0037331 | -0.82128
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.1156 | 200 | -0.0037331 | -0.74662
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.184 | 121.9 | -0.0037331 | -0.45506
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.16584 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.6669 | 100.5 | -0.0039951 | -0.40151
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.16601 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.6287 | 58 | -0.0041671 | -0.24169
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.16633 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.6281 | 214.2 | -0.0044861 | -0.96092
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.16715 | west | 8 | N | N | Nwest | Nwest | 1 | -4.3126 | 0 | -0.0053091 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6746 | 0 | -0.0054068 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5101 | 0 | -0.0054068 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4907 | 0 | -0.0054068 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4907 | 0 | -0.0054068 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.00968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5682 | 0 | -0.0054068 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53155 | 56 | -0.0055948 | -0.31331
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.56003 | 59 | -0.0055948 | -0.33009
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53155 | 56 | -0.0055948 | -0.31331
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53155 | 56 | -0.0055948 | -0.31331
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.56003 | 59 | -0.0055948 | -0.33009
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53155 | 56 | -0.0055948 | -0.31331
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.009471 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.7695 | 398 | -0.0056158 | -2.2351
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5396 | 0 | -0.0056298 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5264 | 0 | -0.0056298 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5027 | 0 | -0.0056298 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.5458 | 0 | -0.0056298 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.009424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6209 | 172 | -0.0056628 | -0.97399
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.009424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6209 | 172 | -0.0056628 | -0.97399
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.009424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6209 | 172 | -0.0056628 | -0.97399
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.009421 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4791 | 0 | -0.0056658 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.009411 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.9924 | 743 | -0.0056758 | -4.2171
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61172 | 0 | -0.0056758 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.62113 | 0 | -0.0056758 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65877 | 0 | -0.0056758 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59289 | 0 | -0.0056758 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58348 | 0 | -0.0056758 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97874 | 0 | -0.0056758 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55525 | 0 | -0.0056758 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.00941 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.11292 | 12 | -0.0056768 | -0.068121
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.00941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.04705 | 0 | -0.0056768 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.00941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19761 | 0 | -0.0056768 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009398 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11278 | 12 | -0.0056888 | -0.068265
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31882 | 0 | -0.0057098 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32538 | 0 | -0.0057098 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30663 | 0 | -0.0057098 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4304 | 0 | -0.0057098 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16597 | 0 | -0.0057098 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19129 | 0 | -0.0057098 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1866 | 0 | -0.0057098 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3282 | 0 | -0.0057098 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16879 | 0 | -0.0057098 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.8008 | 0 | -0.0057098 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3878 | 0 | -0.0057098 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.009365 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.8833 | 735 | -0.0057218 | -4.2055
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.97313 | 104 | -0.0057298 | -0.59589
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.97313 | 104 | -0.0057298 | -0.59589
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50528 | 54 | -0.0057298 | -0.30941
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.49592 | 53 | -0.0057298 | -0.30368
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50528 | 54 | -0.0057298 | -0.30941
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.53335 | 57 | -0.0057298 | -0.3266
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50528 | 54 | -0.0057298 | -0.30941
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50528 | 54 | -0.0057298 | -0.30941
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54271 | 58 | -0.0057298 | -0.33233
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54271 | 58 | -0.0057298 | -0.33233
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.009308 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6103 | 0 | -0.0057788 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.009308 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2566 | 0 | -0.0057788 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.009299 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2647 | 0 | -0.0057878 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.39052 | 42 | -0.0057888 | -0.24313
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.39052 | 42 | -0.0057888 | -0.24313
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35332 | 38 | -0.0057888 | -0.21997
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35332 | 38 | -0.0057888 | -0.21997
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6581 | 0 | -0.0058178 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66737 | 0 | -0.0058178 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36149 | 0 | -0.0058178 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27807 | 0 | -0.0058178 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6655 | 0 | -0.0058338 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4675 | 0 | -0.0058338 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4527 | 0 | -0.0058338 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.009252 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.1095 | 228 | -0.0058348 | -1.3303
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59206 | 0 | -0.0058358 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58466 | 0 | -0.0058358 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76413 | 0 | -0.0058358 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68087 | 0 | -0.0058358 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14987 | 0 | -0.0058358 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.009251 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.9705 | 213 | -0.0058358 | -1.243
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.009248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.378 | 0 | -0.0058388 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.009248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60204 | 0 | -0.0058388 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.009248 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.5259 | 165 | -0.0058388 | -0.96339
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.009247 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.5627 | 169 | -0.0058398 | -0.98692
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009246 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11095 | 12 | -0.0058408 | -0.070089
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.009246 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0058408 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.009234 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32319 | 0 | -0.0058528 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5045 | 0 | -0.0058678 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4483 | 0 | -0.0058678 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.452 | 0 | -0.0058678 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4474 | 0 | -0.0058678 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4799 | 0 | -0.0058678 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.009208 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.71822 | 0 | -0.0058788 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.009208 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73664 | 0 | -0.0058788 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.42343 | 46 | -0.0058818 | -0.27056
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.42343 | 46 | -0.0058818 | -0.27056
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.42343 | 46 | -0.0058818 | -0.27056
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50628 | 55 | -0.0058818 | -0.3235
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50628 | 55 | -0.0058818 | -0.3235
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.49707 | 54 | -0.0058818 | -0.31761
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5952 | 0 | -0.0059298 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54942 | 0 | -0.0059298 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5952 | 0 | -0.0059298 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5952 | 0 | -0.0059298 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83083 | 0 | -0.0059568 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79979 | 0 | -0.0059568 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79431 | 0 | -0.0059568 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49758 | 0 | -0.0059568 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11139 | 0 | -0.0059568 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.009059 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0060278 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.00901 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.4505 | 50 | -0.0060768 | -0.30384
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.63161 | 0 | -0.0061658 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59503 | 0 | -0.0061658 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47281 | 0 | -0.0061658 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3667 | 0 | -0.0061658 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3694 | 0 | -0.0061658 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3587 | 0 | -0.0061658 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.85642 | 0 | -0.0061658 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.1767 | 0 | -0.0061658 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35684 | 0 | -0.0061658 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.00892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28544 | 0 | -0.0061668 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.00892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2676 | 0 | -0.0061668 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.89468 | 0 | -0.0061668 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.82867 | 0 | -0.0061668 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91608 | 0 | -0.0061668 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90984 | 0 | -0.0061668 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.16808 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.1698 | 120 | -0.0062371 | -0.74845
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.008762 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4107 | 161 | -0.0063248 | -1.0183
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.008762 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4545 | 166 | -0.0063248 | -1.0499
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.008762 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.173 | 248 | -0.0063248 | -1.5685
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.008762 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.7841 | 546 | -0.0063248 | -3.4533
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.008762 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 5.634 | 0 | -0.0063248 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.008762 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11391 | 13 | -0.0063248 | -0.082222
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.008711 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28746 | 0 | -0.0063758 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.008694 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4171 | 0 | -0.0063928 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.008694 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4171 | 0 | -0.0063928 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.008694 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.13 | 0 | -0.0063928 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.008691 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.6578 | 651 | -0.0063958 | -4.1636
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.008691 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.9017 | 564 | -0.0063958 | -3.6072
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.008691 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.2146 | 600 | -0.0063958 | -3.8375
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.008656 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39904 | 0 | -0.0064308 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.1073 | 66 | -0.0064471 | -0.42551
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.6121 | 69 | -0.0064471 | -0.44485
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.6121 | 69 | -0.0064471 | -0.44485
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.2756 | 67 | -0.0064471 | -0.43195
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.2756 | 67 | -0.0064471 | -0.43195
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.939 | 65 | -0.0064471 | -0.41906
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.16843 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.2117 | 120 | -0.0065861 | -0.79033
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91997 | 0 | -0.0067988 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91997 | 0 | -0.0067988 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.98627 | 0 | -0.0067988 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90754 | 0 | -0.0067988 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.008174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58035 | 0 | -0.0069128 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.008174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.08174 | 0 | -0.0069128 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49848 | 0 | -0.0070468 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57406 | 0 | -0.0070468 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3618 | 0 | -0.0070468 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81204 | 0 | -0.0070468 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.69144 | 0 | -0.0070468 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.70752 | 0 | -0.0070468 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.402 | 0 | -0.0070468 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14472 | 0 | -0.0070468 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75576 | 0 | -0.0070468 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5628 | 0 | -0.0070468 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50652 | 0 | -0.0070468 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57888 | 0 | -0.0070468 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52099 | 0 | -0.0070468 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81204 | 0 | -0.0070468 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77988 | 0 | -0.0070468 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82812 | 0 | -0.0070468 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61104 | 0 | -0.0070468 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6432 | 0 | -0.0070468 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6432 | 0 | -0.0070468 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3748 | 0 | -0.0070468 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.007479 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.49361 | 66 | -0.0076078 | -0.50211
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.56164 | 76 | -0.0076968 | -0.58495
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.56164 | 76 | -0.0076968 | -0.58495
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.77595 | 105 | -0.0076968 | -0.80816
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54686 | 74 | -0.0076968 | -0.56956
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54686 | 74 | -0.0076968 | -0.56956
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.75378 | 102 | -0.0076968 | -0.78507
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.007336 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.1742 | 569 | -0.0077508 | -4.4102
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.007336 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.2622 | 581 | -0.0077508 | -4.5032
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.00729 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 9.7176 | 0 | -0.0077968 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.00729 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 9.6811 | 0 | -0.0077968 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.16977 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.1974 | 225 | -0.0079211 | -1.7822
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.16999 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.5978 | 180 | -0.0081431 | -1.4658
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.16999 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.5978 | 180 | -0.0081431 | -1.4658
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.005915 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.4544 | 584 | -0.0091718 | -5.3563
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.005915 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.5194 | 595 | -0.0091718 | -5.4572
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.005914 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.5608 | 433 | -0.0091728 | -3.9718
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.005862 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.9262 | 158 | -0.0092248 | -1.4575
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.005862 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.93792 | 160 | -0.0092248 | -1.476
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.005862 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0258 | 175 | -0.0092248 | -1.6143
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28815 | 50 | -0.0093238 | -0.46619
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28815 | 50 | -0.0093238 | -0.46619
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28815 | 50 | -0.0093238 | -0.46619
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28815 | 50 | -0.0093238 | -0.46619
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.17129 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.411 | 125 | -0.0094431 | -1.1804
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.17129 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.411 | 125 | -0.0094431 | -1.1804
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.005534 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.84393 | 152.5 | -0.0095528 | -1.4568
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.005534 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.82733 | 149.5 | -0.0095528 | -1.4281
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.005534 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2872 | 232.6 | -0.0095528 | -2.222
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.005508 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.72706 | 132 | -0.0095788 | -1.2644
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.005508 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73807 | 134 | -0.0095788 | -1.2836
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.005508 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7791 | 323 | -0.0095788 | -3.0939
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.17161 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.8112 | 63 | -0.0097611 | -0.61495
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21634 | 42 | -0.0099358 | -0.4173
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22664 | 44 | -0.0099358 | -0.43717
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22664 | 44 | -0.0099358 | -0.43717
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2421 | 47 | -0.0099358 | -0.46698
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.40258 | 0 | -0.0099908 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.41278 | 0 | -0.0099908 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.40258 | 0 | -0.0099908 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.40768 | 0 | -0.0099908 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.39953 | 0 | -0.0099908 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1274 | 0 | -0.0099908 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.23442 | 0 | -0.0099908 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14269 | 0 | -0.0099908 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22219 | 0 | -0.0099908 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3771 | 0 | -0.0099908 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.005032 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.24154 | 0 | -0.010055 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.005015 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5547 | 310 | -0.010072 | -3.1222
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.005015 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.0712 | 413 | -0.010072 | -4.1596
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.24392 | 49 | -0.010109 | -0.49533
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22899 | 46 | -0.010109 | -0.465
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22899 | 46 | -0.010109 | -0.465
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23397 | 47 | -0.010109 | -0.47511
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004978 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.76661 | 154 | -0.010109 | -1.5567
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004978 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.73674 | 148 | -0.010109 | -1.4961
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23894 | 48 | -0.010109 | -0.48522
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23894 | 48 | -0.010109 | -0.48522
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.004849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.038792 | 0 | -0.010238 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.004849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.038792 | 0 | -0.010238 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1342 | 0 | -0.010294 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.033551 | 0 | -0.010294 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18693 | 0 | -0.010294 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.071895 | 0 | -0.010294 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.033551 | 0 | -0.010294 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.071895 | 0 | -0.010294 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18693 | 0 | -0.010294 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18693 | 0 | -0.010294 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.004748 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.037984 | 0 | -0.010339 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.004727 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.070905 | 0 | -0.01036 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.004727 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10872 | 0 | -0.01036 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.004636 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33843 | 0 | -0.010451 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.00457 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.65808 | 144 | -0.010517 | -1.5144
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.00457 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.85916 | 188 | -0.010517 | -1.9771
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2156 | 47.7 | -0.010567 | -0.50403
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1686 | 37.3 | -0.010567 | -0.39414
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.20792 | 46 | -0.010567 | -0.48607
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.21696 | 48 | -0.010567 | -0.5072
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.004406 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.052872 | 0 | -0.010681 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.004405 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.09691 | 22 | -0.010682 | -0.235
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.004405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.048455 | 11 | -0.010682 | -0.1175
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.004405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.048455 | 11 | -0.010682 | -0.1175
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.00438 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010512 | 0 | -0.010707 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.00438 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010512 | 0 | -0.010707 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.17262 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.3394 | 141 | -0.010775 | -1.5193
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.17262 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7144 | 120 | -0.010775 | -1.293
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.95381 | 223.9 | -0.010827 | -2.4241
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.9585 | 225 | -0.010827 | -2.436
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.9568 | 224.6 | -0.010827 | -2.4317
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.96574 | 226.7 | -0.010827 | -2.4544
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.65396 | 0 | -0.010948 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.63327 | 0 | -0.010948 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.4139 | 0 | -0.010948 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.60015 | 0 | -0.010948 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.60843 | 0 | -0.010948 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.52565 | 0 | -0.010948 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.004139 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049668 | 0 | -0.010948 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.17279 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.1066 | 99 | -0.010949 | -1.084
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.17279 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.5404 | 61 | -0.010949 | -0.66789
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.17279 | west | 7 | N | N | Nwest | Nwest | 1 | -4.3198 | 0 | -0.010949 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.17279 | west | 7 | N | N | Nwest | Nwest | 1 | -7.8967 | 0 | -0.010949 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.17279 | west | 7 | N | N | Nwest | Nwest | 1 | -7.8967 | 0 | -0.010949 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.58291 | 142 | -0.010982 | -1.5594
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.59523 | 145 | -0.010982 | -1.5924
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.61986 | 151 | -0.010982 | -1.6582
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.1905 | 290 | -0.010982 | -3.1847
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.004096 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0098304 | 0 | -0.010991 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.004096 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0098304 | 0 | -0.010991 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.004096 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011469 | 0 | -0.010991 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 25 | -0.011003 | -0.27507
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 25 | -0.011003 | -0.27507
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 25 | -0.011003 | -0.27507
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.065344 | 16 | -0.011003 | -0.17604
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 25 | -0.011003 | -0.27507
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 25 | -0.011003 | -0.27507
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 25 | -0.011003 | -0.27507
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.06126 | 15 | -0.011003 | -0.16504
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.00401 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.3474 | 336 | -0.011077 | -3.7218
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.00401 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7218 | 180 | -0.011077 | -1.9938
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.00401 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.5223 | 629 | -0.011077 | -6.9673
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.004009 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.59453 | 0 | -0.011078 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.004009 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.59574 | 0 | -0.011078 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.004009 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.61338 | 0 | -0.011078 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.004006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.72108 | 180 | -0.011081 | -1.9945
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.003985 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.331 | 334 | -0.011102 | -3.708
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.003985 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3549 | 340 | -0.011102 | -3.7746
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.003985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7173 | 180 | -0.011102 | -1.9983
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.003985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7173 | 180 | -0.011102 | -1.9983
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.00397 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.09925 | 0 | -0.011117 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.00397 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.09925 | 0 | -0.011117 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.003968 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15078 | 0 | -0.011119 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.003953 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15021 | 0 | -0.011134 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57977 | 147 | -0.011143 | -1.638
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54427 | 138 | -0.011143 | -1.5377
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55216 | 140 | -0.011143 | -1.56
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57977 | 147 | -0.011143 | -1.638
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71781 | 182 | -0.011143 | -2.028
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.78091 | 198 | -0.011143 | -2.2063
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.003887 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11272 | 0 | -0.0112 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.003837 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.023022 | 0 | -0.01125 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.00383 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01532 | 0 | -0.011257 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.35955 | 94 | -0.011262 | -1.0586
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15682 | 41 | -0.011262 | -0.46173
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.14535 | 38 | -0.011262 | -0.42795
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.072675 | 19 | -0.011262 | -0.21397
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.35955 | 94 | -0.011262 | -1.0586
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1377 | 36 | -0.011262 | -0.40542
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.16448 | 43 | -0.011262 | -0.48426
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08415 | 22 | -0.011262 | -0.24776
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.5661 | 148 | -0.011262 | -1.6667
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.19125 | 50 | -0.011262 | -0.56309
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.21038 | 55 | -0.011262 | -0.6194
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.19125 | 50 | -0.011262 | -0.56309
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.003774 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.011313 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.003774 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.14341 | 38 | -0.011313 | -0.42988
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.003774 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.072838 | 19.3 | -0.011313 | -0.21834
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.003774 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.05661 | 15 | -0.011313 | -0.16969
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.003774 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.17738 | 47 | -0.011313 | -0.5317
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52502 | 144 | -0.011441 | -1.6475
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52502 | 144 | -0.011441 | -1.6475
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.62347 | 171 | -0.011441 | -1.9564
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.75472 | 207 | -0.011441 | -2.3682
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.79009 | 216.7 | -0.011441 | -2.4792
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.88233 | 242 | -0.011441 | -2.7687
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.003485 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.9028 | 546 | -0.011602 | -6.3346
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.003485 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.6138 | 750 | -0.011602 | -8.7013
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.50279 | 146.5 | -0.011655 | -1.7074
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.50759 | 147.9 | -0.011655 | -1.7237
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.59374 | 173 | -0.011655 | -2.0163
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.003384 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52452 | 155 | -0.011703 | -1.8139
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.003384 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57528 | 170 | -0.011703 | -1.9895
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.003384 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52452 | 155 | -0.011703 | -1.8139
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.00332 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.011767 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.00332 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.011767 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.00332 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.011767 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.003269 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.011818 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.00316 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.011927 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.003104 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.3161 | 424 | -0.011983 | -5.0807
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.003104 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.3192 | 425 | -0.011983 | -5.0927
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.003085 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10798 | 0 | -0.012002 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.003085 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10489 | 0 | -0.012002 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.003085 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10798 | 0 | -0.012002 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.003054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2582 | 412 | -0.012033 | -4.9575
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.003054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2216 | 400 | -0.012033 | -4.8131
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.003053 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.63808 | 209 | -0.012034 | -2.5151
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.003053 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.65945 | 216 | -0.012034 | -2.5993
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14044 | 46 | -0.012034 | -0.55355
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14349 | 47 | -0.012034 | -0.56559
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14044 | 46 | -0.012034 | -0.55355
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14044 | 46 | -0.012034 | -0.55355
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.003037 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2027 | 396 | -0.01205 | -4.7717
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.002952 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2015 | 407 | -0.012135 | -4.9388
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.002662 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.1544 | 58 | -0.012425 | -0.72064
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.002662 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.23692 | 89 | -0.012425 | -1.1058
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11713 | 44 | -0.012425 | -0.54669
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11713 | 44 | -0.012425 | -0.54669
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11447 | 43 | -0.012425 | -0.53426
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11979 | 45 | -0.012425 | -0.55911
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.27337 | 114 | -0.012689 | -1.4465
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.53236 | 222 | -0.012689 | -2.8169
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.44123 | 184 | -0.012689 | -2.3347
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.53715 | 224 | -0.012689 | -2.8423
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.27577 | 115 | -0.012689 | -1.4592
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.00215 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0258 | 0 | -0.012937 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.00215 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02365 | 0 | -0.012937 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.00215 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0258 | 0 | -0.012937 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.17574 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.7623 | 84 | -0.013897 | -1.1674
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.000923 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.014164 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015087 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015087 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.000487 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0487 | 100 | -0.015574 | -1.5574
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.000487 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0487 | 100 | -0.015574 | -1.5574
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000487 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015574 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000487 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015574 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000487 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015574 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000487 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015574 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.00049 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015577 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.000816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014688 | 0 | -0.015903 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.000816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014688 | 0 | -0.015903 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.002115 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.05922 | 0 | -0.017202 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.002115 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.061335 | 0 | -0.017202 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.002537 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0706 | 422 | -0.017624 | -7.4372
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002926 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.052668 | 0 | -0.018013 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002926 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.052668 | 0 | -0.018013 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002926 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04389 | 0 | -0.018013 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.002958 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.070992 | 24 | -0.018045 | -0.43307
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.002958 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.070992 | 24 | -0.018045 | -0.43307
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.002958 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.068034 | 23 | -0.018045 | -0.41503
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.1816 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.2392 | 150 | -0.01975 | -2.9625
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.1816 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.3411 | 101 | -0.01975 | -1.9948
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.004838 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.066281 | 0 | -0.019925 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.18266 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.9612 | 169.5 | -0.020817 | -3.5285
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.18868 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.3012 | 150 | -0.02683 | -4.0245
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.19359 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.231 | 120 | -0.031747 | -3.8096
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.19359 | west | 6 | Y | N | Ywest | Nwest | 1 | -45.1069 | 233 | -0.031747 | -7.3971
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.19359 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.9494 | 170.2 | -0.031747 | -5.4034
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3037 | 37.5 | -0.032921 | -1.2345
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.9373 | 107.5 | -0.032921 | -3.539
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.2934 | 135 | -0.032921 | -4.4443
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.1772 | 119 | -0.032921 | -3.9176
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.4504 | 105 | -0.032921 | -3.4567
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.6787 | 80.5 | -0.032921 | -2.6501
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.027824 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.042911 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.030846 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18508 | 0 | -0.045933 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.21235 | west | 6 | Y | N | Ywest | Nwest | 1 | -50.1141 | 236 | -0.050503 | -11.9187
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.21245 | west | 6 | Y | N | Ywest | Nwest | 1 | -84.9796 | 400 | -0.050604 | -20.2416
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.043841 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4468 | 0 | -0.058928 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.043841 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.096 | 0 | -0.058928 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.043841 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.058928 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.23467 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.0799 | 60 | -0.07282 | -4.3692
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.55475 | west | 4 | Y | N | Ywest | Nwest | 1 | -360.423 | 649.7 | -0.39291 | -255.2724

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1422 BOWMAN5 - 1425 FISHRDSS C: 1430 GRHAMES - 1435 LONGCREK C: 1439 LONCREK2 - 1442 COKFIELD | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.55475 | west | 4 | Y | N | Ywest | Nwest | 1 | -360.423 | 0 | -0.39291 | 0 | 0 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.23467 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.0799 | 0 | -0.07282 | 0 | 0 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.043841 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4468 | 0 | -0.058928 | 0 | 0 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.043841 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.096 | 0 | -0.058928 | 0 | 0 | 0 | Weighted Shift Factors
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.043841 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.058928 | 0 | 0 | 0 | North | 0.015087
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.21245 | west | 6 | Y | N | Ywest | Nwest | 1 | -84.9796 | 0 | -0.050604 | 0 | 0 | 0 | West | -0.16184
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.21235 | west | 6 | Y | N | Ywest | Nwest | 1 | -50.1141 | 0 | -0.050503 | 0 | 0 | 0 |  | 0.17693
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.030846 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18508 | 0 | -0.045933 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.027824 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.042911 | 0 | 0 | 0 | Line Rating | 1079.45
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3037 | 0 | -0.032921 | 0 | 0 | 0 | Conc Gen | 2142.6
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.9373 | 0 | -0.032921 | 0 | 0 | 0 | Weighted Imp. | 30.9063
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.2934 | 0 | -0.032921 | 0 | 0 | 0 | PTDF | 0.014425
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.1772 | 0 | -0.032921 | 0 | 0 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.4504 | 0 | -0.032921 | 0 | 0 | 0 | Concentration | 0.081527
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.19477 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.6787 | 0 | -0.032921 | 0 | 0 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.19359 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.231 | 0 | -0.031747 | 0 | 0 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.19359 | west | 6 | Y | N | Ywest | Nwest | 1 | -45.1069 | 0 | -0.031747 | 0 | 0 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.19359 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.9494 | 0 | -0.031747 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.18868 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.3012 | 0 | -0.02683 | 0 | 0 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.18266 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.9612 | 0 | -0.020817 | 0 | 0 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.004838 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.066281 | 0 | -0.019925 | 0 | 0 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.1816 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.2392 | 0 | -0.01975 | 0 | 0 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.1816 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.3411 | 0 | -0.01975 | 0 | 0 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 8.4 | 0.16198
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 16.8 | 0.32397
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 25.2 | 0.48595
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 33.6 | 0.64793
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 42 | 0.80992
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 50.4 | 0.9719
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 58.8 | 1.1339
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 67.2 | 1.2959
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 75.6 | 1.4579
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 84 | 1.6198
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 92.4 | 1.7818
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 100.8 | 1.9438
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 109.2 | 2.1058
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 117.6 | 2.2678
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 126 | 2.4298
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 134.4 | 2.5917
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 142.8 | 2.7537
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 151.2 | 2.9157
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 159.6 | 3.0777
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 168 | 3.2397
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 176.4 | 3.4017
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 184.8 | 3.5636
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 193.2 | 3.7256
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.004197 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.035255 | 8.4 | -0.019284 | -0.16198 | 201.6 | 3.8876
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.002958 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.070992 | 24 | -0.018045 | -0.43307 | 225.6 | 4.3207
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.002958 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.070992 | 24 | -0.018045 | -0.43307 | 249.6 | 4.7538
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.002958 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.068034 | 23 | -0.018045 | -0.41503 | 272.6 | 5.1688
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002926 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.052668 | 0 | -0.018013 | 0 | 272.6 | 5.1688
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002926 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.052668 | 0 | -0.018013 | 0 | 272.6 | 5.1688
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002926 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04389 | 0 | -0.018013 | 0 | 272.6 | 5.1688
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.002537 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0706 | 422 | -0.017624 | -7.4372 | 694.6 | 12.606
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.002115 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.05922 | 0 | -0.017202 | 0 | 694.6 | 12.606
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.002115 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.061335 | 0 | -0.017202 | 0 | 694.6 | 12.606
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.000816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014688 | 0 | -0.015903 | 0 | 694.6 | 12.606
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.000816 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014688 | 0 | -0.015903 | 0 | 694.6 | 12.606
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.00049 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015577 | 0 | 694.6 | 12.606
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.000487 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0487 | 100 | -0.015574 | -1.5574 | 794.6 | 14.1634
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.000487 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0487 | 100 | -0.015574 | -1.5574 | 894.6 | 15.7208
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000487 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015574 | 0 | 894.6 | 15.7208
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000487 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015574 | 0 | 894.6 | 15.7208
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000487 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015574 | 0 | 894.6 | 15.7208
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000487 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015574 | 0 | 894.6 | 15.7208
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0 | 894.6 | 15.7208
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0 | 894.6 | 15.7208
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0 | 894.6 | 15.7208
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0 | 894.6 | 15.7208
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0 | 894.6 | 15.7208
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.015087 | 0 | 894.6 | 15.7208
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015087 | 0 | 894.6 | 15.7208
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015087 | 0 | 894.6 | 15.7208
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.000923 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.014164 | 0 | 894.6 | 15.7208
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.17574 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.7623 | 0 | -0.013897 | 0 | 894.6 | 15.7208
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.00215 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0258 | 0 | -0.012937 | 0 | 894.6 | 15.7208
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.00215 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02365 | 0 | -0.012937 | 0 | 894.6 | 15.7208
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.00215 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0258 | 0 | -0.012937 | 0 | 894.6 | 15.7208
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.27337 | 0 | -0.012689 | 0 | 894.6 | 15.7208
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.53236 | 0 | -0.012689 | 0 | 894.6 | 15.7208
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.44123 | 0 | -0.012689 | 0 | 894.6 | 15.7208
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.53715 | 0 | -0.012689 | 0 | 894.6 | 15.7208
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.27577 | 0 | -0.012689 | 0 | 894.6 | 15.7208
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.002662 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.1544 | 58 | -0.012425 | -0.72064 | 952.6 | 16.4414
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.002662 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.23692 | 89 | -0.012425 | -1.1058 | 1041.6 | 17.5472
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11713 | 44 | -0.012425 | -0.54669 | 1085.6 | 18.0939
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11713 | 44 | -0.012425 | -0.54669 | 1129.6 | 18.6406
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11447 | 43 | -0.012425 | -0.53426 | 1172.6 | 19.1748
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.002662 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11979 | 45 | -0.012425 | -0.55911 | 1217.6 | 19.7339
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.002952 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2015 | 407 | -0.012135 | -4.9388 | 1624.6 | 24.6728
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.003037 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2027 | 0 | -0.01205 | 0 | 1624.6 | 24.6728
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.003053 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.63808 | 209 | -0.012034 | -2.5151 | 1833.6 | 27.1878
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.003053 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.65945 | 216 | -0.012034 | -2.5993 | 2049.6 | 29.7871
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14044 | 46 | -0.012034 | -0.55355 | 2095.6 | 30.3407
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14349 | 47 | -0.012034 | -0.56559 | 2142.6 | 30.9063
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14044 | 46 | -0.012034 | -0.55355
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.003053 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14044 | 46 | -0.012034 | -0.55355
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.003054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2582 | 412 | -0.012033 | -4.9575
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.003054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2216 | 400 | -0.012033 | -4.8131
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.003085 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10798 | 0 | -0.012002 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.003085 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10489 | 0 | -0.012002 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.003085 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10798 | 0 | -0.012002 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.003104 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.3161 | 0 | -0.011983 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.003104 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.3192 | 0 | -0.011983 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.00316 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.011927 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.003269 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.011818 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.00332 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.011767 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.00332 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.011767 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.00332 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.011767 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.003384 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52452 | 155 | -0.011703 | -1.8139
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.003384 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57528 | 170 | -0.011703 | -1.9895
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.003384 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52452 | 155 | -0.011703 | -1.8139
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.50279 | 146.5 | -0.011655 | -1.7074
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.50759 | 147.9 | -0.011655 | -1.7237
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.59374 | 173 | -0.011655 | -2.0163
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.003485 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.9028 | 0 | -0.011602 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.003485 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.6138 | 0 | -0.011602 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.75472 | 207 | -0.011441 | -2.3682
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.79009 | 216.7 | -0.011441 | -2.4792
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.88233 | 242 | -0.011441 | -2.7687
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52502 | 144 | -0.011441 | -1.6475
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52502 | 144 | -0.011441 | -1.6475
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.003646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.62347 | 171 | -0.011441 | -1.9564
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.003774 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.14341 | 38 | -0.011313 | -0.42988
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.003774 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.072838 | 19.3 | -0.011313 | -0.21834
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.003774 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.05661 | 15 | -0.011313 | -0.16969
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.003774 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.17738 | 47 | -0.011313 | -0.5317
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.003774 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.011313 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.35955 | 0 | -0.011262 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15682 | 0 | -0.011262 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.14535 | 0 | -0.011262 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.072675 | 0 | -0.011262 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.35955 | 0 | -0.011262 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1377 | 0 | -0.011262 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.16448 | 0 | -0.011262 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08415 | 0 | -0.011262 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.5661 | 0 | -0.011262 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.19125 | 0 | -0.011262 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.21038 | 0 | -0.011262 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.003825 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.19125 | 0 | -0.011262 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.00383 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01532 | 0 | -0.011257 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.003837 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.023022 | 0 | -0.01125 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.003887 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11272 | 0 | -0.0112 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57977 | 147 | -0.011143 | -1.638
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54427 | 138 | -0.011143 | -1.5377
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55216 | 140 | -0.011143 | -1.56
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57977 | 147 | -0.011143 | -1.638
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71781 | 182 | -0.011143 | -2.028
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.003944 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.78091 | 198 | -0.011143 | -2.2063
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.003953 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15021 | 0 | -0.011134 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.003968 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15078 | 0 | -0.011119 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.00397 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.09925 | 0 | -0.011117 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.00397 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.09925 | 0 | -0.011117 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.003985 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.331 | 334 | -0.011102 | -3.708
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.003985 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3549 | 340 | -0.011102 | -3.7746
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.003985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7173 | 180 | -0.011102 | -1.9983
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.003985 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7173 | 180 | -0.011102 | -1.9983
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.004006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.72108 | 180 | -0.011081 | -1.9945
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.004009 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.59453 | 0 | -0.011078 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.004009 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.59574 | 0 | -0.011078 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.004009 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.61338 | 0 | -0.011078 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.00401 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.5223 | 0 | -0.011077 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.00401 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.3474 | 336 | -0.011077 | -3.7218
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.00401 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7218 | 180 | -0.011077 | -1.9938
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 0 | -0.011003 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 0 | -0.011003 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 0 | -0.011003 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.065344 | 0 | -0.011003 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 0 | -0.011003 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 0 | -0.011003 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1021 | 0 | -0.011003 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.004084 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.06126 | 0 | -0.011003 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.004096 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0098304 | 0 | -0.010991 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.004096 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0098304 | 0 | -0.010991 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.004096 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011469 | 0 | -0.010991 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.58291 | 142 | -0.010982 | -1.5594
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.59523 | 145 | -0.010982 | -1.5924
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.61986 | 151 | -0.010982 | -1.6582
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.004105 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.1905 | 290 | -0.010982 | -3.1847
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.17279 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.1066 | 0 | -0.010949 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.17279 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.5404 | 0 | -0.010949 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.17279 | west | 7 | N | N | Nwest | Nwest | 1 | -4.3198 | 0 | -0.010949 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.17279 | west | 7 | N | N | Nwest | Nwest | 1 | -7.8967 | 0 | -0.010949 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.17279 | west | 7 | N | N | Nwest | Nwest | 1 | -7.8967 | 0 | -0.010949 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.65396 | 0 | -0.010948 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.63327 | 0 | -0.010948 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.4139 | 0 | -0.010948 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.60015 | 0 | -0.010948 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.60843 | 0 | -0.010948 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.004139 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.52565 | 0 | -0.010948 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.004139 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049668 | 0 | -0.010948 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.95381 | 223.9 | -0.010827 | -2.4241
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.9585 | 225 | -0.010827 | -2.436
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.9568 | 224.6 | -0.010827 | -2.4317
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.00426 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.96574 | 226.7 | -0.010827 | -2.4544
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.17262 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.3394 | 0 | -0.010775 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.17262 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7144 | 0 | -0.010775 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.00438 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010512 | 0 | -0.010707 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.00438 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010512 | 0 | -0.010707 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.004405 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.09691 | 22 | -0.010682 | -0.235
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.004405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.048455 | 11 | -0.010682 | -0.1175
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.004405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.048455 | 11 | -0.010682 | -0.1175
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.004406 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.052872 | 0 | -0.010681 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2156 | 47.7 | -0.010567 | -0.50403
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1686 | 37.3 | -0.010567 | -0.39414
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.20792 | 46 | -0.010567 | -0.48607
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.00452 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.21696 | 48 | -0.010567 | -0.5072
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.00457 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.65808 | 144 | -0.010517 | -1.5144
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.00457 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.85916 | 188 | -0.010517 | -1.9771
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.004636 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33843 | 0 | -0.010451 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.004727 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.070905 | 0 | -0.01036 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.004727 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10872 | 0 | -0.01036 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.004748 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.037984 | 0 | -0.010339 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1342 | 0 | -0.010294 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.033551 | 0 | -0.010294 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18693 | 0 | -0.010294 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.071895 | 0 | -0.010294 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.033551 | 0 | -0.010294 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.071895 | 0 | -0.010294 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18693 | 0 | -0.010294 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.004793 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18693 | 0 | -0.010294 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.004849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.038792 | 0 | -0.010238 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.004849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.038792 | 0 | -0.010238 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.24392 | 49 | -0.010109 | -0.49533
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22899 | 46 | -0.010109 | -0.465
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22899 | 46 | -0.010109 | -0.465
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23397 | 47 | -0.010109 | -0.47511
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004978 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.76661 | 154 | -0.010109 | -1.5567
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004978 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.73674 | 148 | -0.010109 | -1.4961
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23894 | 48 | -0.010109 | -0.48522
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23894 | 48 | -0.010109 | -0.48522
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.005015 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5547 | 310 | -0.010072 | -3.1222
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.005015 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.0712 | 413 | -0.010072 | -4.1596
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.005032 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.24154 | 0 | -0.010055 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.40258 | 0 | -0.0099908 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.41278 | 0 | -0.0099908 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.40258 | 0 | -0.0099908 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.40768 | 0 | -0.0099908 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.39953 | 0 | -0.0099908 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1274 | 0 | -0.0099908 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.23442 | 0 | -0.0099908 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14269 | 0 | -0.0099908 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22219 | 0 | -0.0099908 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.005096 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3771 | 0 | -0.0099908 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21634 | 42 | -0.0099358 | -0.4173
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22664 | 44 | -0.0099358 | -0.43717
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22664 | 44 | -0.0099358 | -0.43717
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.005151 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2421 | 47 | -0.0099358 | -0.46698
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.17161 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.8112 | 0 | -0.0097611 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.005508 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.72706 | 132 | -0.0095788 | -1.2644
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.005508 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73807 | 134 | -0.0095788 | -1.2836
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.005508 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7791 | 323 | -0.0095788 | -3.0939
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.005534 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.84393 | 152.5 | -0.0095528 | -1.4568
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.005534 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.82733 | 149.5 | -0.0095528 | -1.4281
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.005534 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2872 | 232.6 | -0.0095528 | -2.222
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.17129 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.411 | 0 | -0.0094431 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.17129 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.411 | 0 | -0.0094431 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28815 | 50 | -0.0093238 | -0.46619
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28815 | 50 | -0.0093238 | -0.46619
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28815 | 50 | -0.0093238 | -0.46619
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.005763 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28815 | 50 | -0.0093238 | -0.46619
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.005862 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.9262 | 158 | -0.0092248 | -1.4575
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.005862 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.93792 | 160 | -0.0092248 | -1.476
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.005862 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0258 | 175 | -0.0092248 | -1.6143
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.005914 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.5608 | 0 | -0.0091728 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.005915 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.4544 | 0 | -0.0091718 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.005915 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.5194 | 0 | -0.0091718 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.16999 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.5978 | 0 | -0.0081431 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.16999 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.5978 | 0 | -0.0081431 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.16977 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.1974 | 0 | -0.0079211 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.00729 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 9.7176 | 0 | -0.0077968 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.00729 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 9.6811 | 0 | -0.0077968 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.007336 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.1742 | 0 | -0.0077508 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.007336 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.2622 | 0 | -0.0077508 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.56164 | 76 | -0.0076968 | -0.58495
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.56164 | 76 | -0.0076968 | -0.58495
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.77595 | 105 | -0.0076968 | -0.80816
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54686 | 74 | -0.0076968 | -0.56956
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54686 | 74 | -0.0076968 | -0.56956
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.00739 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.75378 | 102 | -0.0076968 | -0.78507
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.007479 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.49361 | 66 | -0.0076078 | -0.50211
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49848 | 0 | -0.0070468 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57406 | 0 | -0.0070468 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3618 | 0 | -0.0070468 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81204 | 0 | -0.0070468 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.69144 | 0 | -0.0070468 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.70752 | 0 | -0.0070468 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.402 | 0 | -0.0070468 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14472 | 0 | -0.0070468 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75576 | 0 | -0.0070468 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5628 | 0 | -0.0070468 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50652 | 0 | -0.0070468 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57888 | 0 | -0.0070468 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52099 | 0 | -0.0070468 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81204 | 0 | -0.0070468 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77988 | 0 | -0.0070468 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82812 | 0 | -0.0070468 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61104 | 0 | -0.0070468 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6432 | 0 | -0.0070468 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6432 | 0 | -0.0070468 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.00804 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3748 | 0 | -0.0070468 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.008174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58035 | 0 | -0.0069128 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.008174 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.08174 | 0 | -0.0069128 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91997 | 0 | -0.0067988 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91997 | 0 | -0.0067988 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.98627 | 0 | -0.0067988 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.008288 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90754 | 0 | -0.0067988 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.16843 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.2117 | 0 | -0.0065861 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.1073 | 66 | -0.0064471 | -0.42551
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.6121 | 69 | -0.0064471 | -0.44485
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.6121 | 69 | -0.0064471 | -0.44485
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.2756 | 67 | -0.0064471 | -0.43195
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -11.2756 | 67 | -0.0064471 | -0.43195
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.16829 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.939 | 65 | -0.0064471 | -0.41906
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.008656 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39904 | 0 | -0.0064308 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.008691 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.6578 | 0 | -0.0063958 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.008691 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.9017 | 0 | -0.0063958 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.008691 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.2146 | 0 | -0.0063958 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.008694 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4171 | 0 | -0.0063928 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.008694 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4171 | 0 | -0.0063928 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.008694 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.13 | 0 | -0.0063928 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.008711 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28746 | 0 | -0.0063758 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.008762 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4107 | 161 | -0.0063248 | -1.0183
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.008762 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4545 | 166 | -0.0063248 | -1.0499
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.008762 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.173 | 248 | -0.0063248 | -1.5685
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.008762 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.7841 | 546 | -0.0063248 | -3.4533
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.008762 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 5.634 | 0 | -0.0063248 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.008762 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11391 | 13 | -0.0063248 | -0.082222
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.16808 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.1698 | 0 | -0.0062371 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.89468 | 0 | -0.0061668 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.82867 | 0 | -0.0061668 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91608 | 0 | -0.0061668 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.00892 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90984 | 0 | -0.0061668 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.00892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28544 | 0 | -0.0061668 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.00892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2676 | 0 | -0.0061668 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.63161 | 0 | -0.0061658 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59503 | 0 | -0.0061658 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47281 | 0 | -0.0061658 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3667 | 0 | -0.0061658 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3694 | 0 | -0.0061658 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3587 | 0 | -0.0061658 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.85642 | 0 | -0.0061658 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.008921 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.1767 | 0 | -0.0061658 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.008921 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35684 | 0 | -0.0061658 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.00901 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.4505 | 50 | -0.0060768 | -0.30384
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.009059 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0060278 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83083 | 0 | -0.0059568 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79979 | 0 | -0.0059568 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79431 | 0 | -0.0059568 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49758 | 0 | -0.0059568 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.00913 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11139 | 0 | -0.0059568 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5952 | 0 | -0.0059298 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54942 | 0 | -0.0059298 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5952 | 0 | -0.0059298 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.009157 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.5952 | 0 | -0.0059298 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.42343 | 46 | -0.0058818 | -0.27056
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.42343 | 46 | -0.0058818 | -0.27056
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.42343 | 46 | -0.0058818 | -0.27056
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50628 | 55 | -0.0058818 | -0.3235
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50628 | 55 | -0.0058818 | -0.3235
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.009205 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.49707 | 54 | -0.0058818 | -0.31761
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.009208 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.71822 | 0 | -0.0058788 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.009208 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73664 | 0 | -0.0058788 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5045 | 0 | -0.0058678 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4483 | 0 | -0.0058678 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.452 | 0 | -0.0058678 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4474 | 0 | -0.0058678 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.009219 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4799 | 0 | -0.0058678 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.009234 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32319 | 0 | -0.0058528 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009246 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11095 | 12 | -0.0058408 | -0.070089
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.009246 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0058408 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.009247 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.5627 | 169 | -0.0058398 | -0.98692
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.009248 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.5259 | 165 | -0.0058388 | -0.96339
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.009248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.378 | 0 | -0.0058388 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.009248 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60204 | 0 | -0.0058388 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.009251 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.9705 | 213 | -0.0058358 | -1.243
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14987 | 0 | -0.0058358 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59206 | 0 | -0.0058358 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58466 | 0 | -0.0058358 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76413 | 0 | -0.0058358 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.009251 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68087 | 0 | -0.0058358 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.009252 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.1095 | 228 | -0.0058348 | -1.3303
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6655 | 0 | -0.0058338 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4675 | 0 | -0.0058338 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4527 | 0 | -0.0058338 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6581 | 0 | -0.0058178 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66737 | 0 | -0.0058178 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36149 | 0 | -0.0058178 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.009269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27807 | 0 | -0.0058178 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.39052 | 42 | -0.0057888 | -0.24313
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.39052 | 42 | -0.0057888 | -0.24313
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35332 | 38 | -0.0057888 | -0.21997
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.009298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35332 | 38 | -0.0057888 | -0.21997
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.009299 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2647 | 0 | -0.0057878 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.009308 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6103 | 0 | -0.0057788 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.009308 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2566 | 0 | -0.0057788 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.97313 | 104 | -0.0057298 | -0.59589
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.97313 | 104 | -0.0057298 | -0.59589
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50528 | 54 | -0.0057298 | -0.30941
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.49592 | 53 | -0.0057298 | -0.30368
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50528 | 54 | -0.0057298 | -0.30941
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.53335 | 57 | -0.0057298 | -0.3266
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50528 | 54 | -0.0057298 | -0.30941
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50528 | 54 | -0.0057298 | -0.30941
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54271 | 58 | -0.0057298 | -0.33233
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.009357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54271 | 58 | -0.0057298 | -0.33233
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.009365 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.8833 | 735 | -0.0057218 | -4.2055
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31882 | 0 | -0.0057098 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32538 | 0 | -0.0057098 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30663 | 0 | -0.0057098 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4304 | 0 | -0.0057098 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16597 | 0 | -0.0057098 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19129 | 0 | -0.0057098 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1866 | 0 | -0.0057098 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3282 | 0 | -0.0057098 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16879 | 0 | -0.0057098 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.8008 | 0 | -0.0057098 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.009377 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3878 | 0 | -0.0057098 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009398 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11278 | 12 | -0.0056888 | -0.068265
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.00941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.04705 | 0 | -0.0056768 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.00941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19761 | 0 | -0.0056768 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.00941 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.11292 | 0 | -0.0056768 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61172 | 0 | -0.0056758 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.62113 | 0 | -0.0056758 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65877 | 0 | -0.0056758 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59289 | 0 | -0.0056758 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58348 | 0 | -0.0056758 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97874 | 0 | -0.0056758 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.009411 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55525 | 0 | -0.0056758 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.009411 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.9924 | 743 | -0.0056758 | -4.2171
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.009421 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4791 | 0 | -0.0056658 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.009424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6209 | 172 | -0.0056628 | -0.97399
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.009424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6209 | 172 | -0.0056628 | -0.97399
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.009424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6209 | 172 | -0.0056628 | -0.97399
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5396 | 0 | -0.0056298 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5264 | 0 | -0.0056298 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5027 | 0 | -0.0056298 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.009457 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.5458 | 0 | -0.0056298 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.009471 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.7695 | 398 | -0.0056158 | -2.2351
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53155 | 56 | -0.0055948 | -0.31331
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.56003 | 59 | -0.0055948 | -0.33009
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53155 | 56 | -0.0055948 | -0.31331
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53155 | 56 | -0.0055948 | -0.31331
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.56003 | 59 | -0.0055948 | -0.33009
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.009492 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53155 | 56 | -0.0055948 | -0.31331
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6746 | 0 | -0.0054068 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5101 | 0 | -0.0054068 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4907 | 0 | -0.0054068 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4907 | 0 | -0.0054068 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.00968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5682 | 0 | -0.0054068 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.16715 | west | 8 | N | N | Nwest | Nwest | 1 | -4.3126 | 0 | -0.0053091 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.16633 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.6281 | 0 | -0.0044861 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.16601 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.6287 | 0 | -0.0041671 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.16584 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.6669 | 0 | -0.0039951 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.8367 | 0 | -0.0037331 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.4272 | 0 | -0.0037331 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.1156 | 0 | -0.0037331 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.16558 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.184 | 0 | -0.0037331 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.16544 | west | 8 | N | N | Nwest | Nwest | 1 | -11.5806 | 0 | -0.0035921 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.16544 | west | 8 | N | N | Nwest | Nwest | 1 | -12.1431 | 0 | -0.0035921 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.16544 | west | 8 | N | N | Nwest | Nwest | 1 | -11.6468 | 0 | -0.0035921 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.16513 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.0899 | 0 | -0.0032841 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.16513 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6639 | 0 | -0.0032841 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -11.5224 | 70 | -0.0027611 | -0.19328
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -11.5224 | 70 | -0.0027611 | -0.19328
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -15.2754 | 92.8 | -0.0027611 | -0.25623
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -13.1685 | 80 | -0.0027611 | -0.22089
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -13.1685 | 80 | -0.0027611 | -0.22089
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.16461 | west | 9 | Y | Y | Ywest | Ywest | 1 | -18.9297 | 115 | -0.0027611 | -0.31752
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -34.2687 | 208.2 | -0.0027501 | -0.57257
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -23.3889 | 142.1 | -0.0027501 | -0.39079
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -21.7924 | 132.4 | -0.0027501 | -0.36411
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.3849 | 136 | -0.0027501 | -0.37401
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -24.1955 | 147 | -0.0027501 | -0.40426
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.16459 | west | 9 | Y | Y | Ywest | Ywest | 1 | -34.565 | 210 | -0.0027501 | -0.57752
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.16428 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.4774 | 0 | -0.0024331 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.16371 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.7299 | 0 | -0.0018661 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.16371 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9113 | 0 | -0.0018661 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.7906 | 66 | -0.0016491 | -0.10884
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.6271 | 65 | -0.0016491 | -0.10719
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.9541 | 67 | -0.0016491 | -0.11049
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.9541 | 67 | -0.0016491 | -0.11049
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.16349 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.9541 | 67 | -0.0016491 | -0.11049
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.16349 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016491 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.16349 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016491 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.16073 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.1089 | 0 | 0.0011189 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.9695 | 0 | 0.0021159 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.8795 | 0 | 0.0021159 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.7096 | 0 | 0.0021159 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.15973 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.2619 | 0 | 0.0021159 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.15816 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.75917 | 0 | 0.0036849 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4732 | 0 | 0.0059299 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4732 | 0 | 0.0059299 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.15535 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.651 | 0 | 0.0064979 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15535 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4278 | 0 | 0.0064979 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.15535 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.2139 | 0 | 0.0064979 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15523 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4182 | 0 | 0.0066169 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.15521 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4169 | 0 | 0.0066339 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.15513 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.2703 | 0 | 0.0067099 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.15513 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.2703 | 0 | 0.0067099 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.15225 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.1803 | 0 | 0.0095909 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.15161 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.5983 | 0 | 0.010233 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.15128 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.7077 | 0 | 0.010563 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.9902 | 0 | 0.023136 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.5467 | 0 | 0.023136 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.5385 | 0 | 0.023136 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.13871 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.3257 | 0 | 0.023136 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.13587 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.025971 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.12248 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.3723 | 0 | 0.039363 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3587 | 20 | 0.093909 | 1.8782
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3587 | 20 | 0.093909 | 1.8782
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3587 | 20 | 0.093909 | 1.8782
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.067936 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.1549 | 17 | 0.093909 | 1.5965
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.047963 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.11388 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.031383 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.883 | 0 | 0.13046 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.029517 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.3542 | 0 | 0.13233 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.029517 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.3542 | 0 | 0.13233 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.023281 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.634 | 242 | 0.13856 | 33.5325
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.013707 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.6448 | 0 | 0.14814 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.005328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.5345 | 288 | 0.15652 | 45.0769
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.005328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.78322 | 147 | 0.15652 | 23.008
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.005328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.78322 | 147 | 0.15652 | 23.008
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.005011 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.56374 | 0 | 0.15683 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.004576 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.33405 | 73 | 0.15727 | 11.4806
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.004576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.54454 | 119 | 0.15727 | 18.715
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.004576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.93808 | 205 | 0.15727 | 32.2401
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.004576 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.46675 | 102 | 0.15727 | 16.0414
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.004576 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.4393 | 96 | 0.15727 | 15.0978
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.000117 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.002106 | 18 | 0.16173 | 2.9111
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.000117 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.002106 | 18 | 0.16173 | 2.9111
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.000117 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.004446 | 38 | 0.16173 | 6.1457
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.16184 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.16184 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.002398 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.2398 | 0 | 0.16424 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.008977 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.13465 | 0 | 0.17082 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.008977 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.13465 | 0 | 0.17082 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.63896 | 70 | 0.17097 | 11.9681
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.62983 | 69 | 0.17097 | 11.7971
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.62983 | 69 | 0.17097 | 11.7971
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.009128 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.6207 | 68 | 0.17097 | 11.6262
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.009156 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3734 | 150 | 0.171 | 25.6501
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.009156 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.73248 | 80 | 0.171 | 13.6801
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.010119 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5803 | 255 | 0.17196 | 43.8508
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.010119 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5077 | 149 | 0.17196 | 25.6226
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.010119 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5482 | 153 | 0.17196 | 26.3105
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.010276 | north | 3 | N | N | Nnorth | Nnorth | 1 | 11.8893 | 0 | 0.17212 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.010276 | north | 3 | N | N | Nnorth | Nnorth | 1 | 11.8996 | 0 | 0.17212 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.010416 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7499 | 168 | 0.17226 | 28.9398
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.010416 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.93744 | 90 | 0.17226 | 15.5035
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.010831 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17268 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.010831 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17268 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.011221 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4383 | 217.3 | 0.17307 | 37.6072
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.011221 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3003 | 205 | 0.17307 | 35.4785
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.011221 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0566 | 272.4 | 0.17307 | 47.1432
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.011343 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17319 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.011343 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.9269 | 787 | 0.17319 | 136.2989
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7616 | 0 | 0.17327 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7821 | 0 | 0.17327 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7821 | 0 | 0.17327 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.011424 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.3411 | 0 | 0.17327 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.011727 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5629 | 48 | 0.17357 | 8.3315
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.011727 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.53944 | 46 | 0.17357 | 7.9843
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.011727 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2313 | 105 | 0.17357 | 18.2251
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.011756 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.37619 | 0 | 0.1736 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17361 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17361 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.011763 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.19997 | 17 | 0.17361 | 2.9513
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17361 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.011763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17361 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.011782 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.4551 | 0 | 0.17363 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.0902 | 0 | 0.17482 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.0902 | 0 | 0.17482 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.9755 | 0 | 0.17482 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.012971 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.9846 | 0 | 0.17482 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.013448 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.1215 | 0 | 0.17529 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.013448 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.0139 | 0 | 0.17529 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.014078 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17592 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.014787 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.094 | 0 | 0.17663 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.014787 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.68 | 0 | 0.17663 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.01503 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.265 | 150.7 | 0.17687 | 26.6551
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.01503 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2695 | 151 | 0.17687 | 26.7081
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.01503 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6663 | 177.4 | 0.17687 | 31.3776
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.015079 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2845 | 151.5 | 0.17692 | 26.804
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.015079 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2965 | 152.3 | 0.17692 | 26.9455
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.015079 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6765 | 177.5 | 0.17692 | 31.404
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4335 | 224 | 0.17717 | 39.6867
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4641 | 226 | 0.17717 | 40.0411
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2495 | 212 | 0.17717 | 37.5607
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.015328 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2342 | 211 | 0.17717 | 37.3835
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.015576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.489 | 224 | 0.17742 | 39.7423
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.015651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0676 | 196 | 0.1775 | 34.7892
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.015651 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7373 | 111 | 0.1775 | 19.702
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.016178 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5009 | 216.4 | 0.17802 | 38.5242
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.016178 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4961 | 216.1 | 0.17802 | 38.4708
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.016275 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.9621 | 182 | 0.17812 | 32.4178
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.016275 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.8771 | 484 | 0.17812 | 86.21
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.016302 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.8151 | 0 | 0.17815 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.016315 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.17816 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4327 | 0 | 0.17828 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.1368 | 0 | 0.17828 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.3834 | 0 | 0.17828 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.016437 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.5584 | 0 | 0.17828 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.016582 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.0169 | 0 | 0.17843 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.016582 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1827 | 0 | 0.17843 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.016582 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.934 | 0 | 0.17843 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.017291 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0403 | 118 | 0.17914 | 21.138
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.017291 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9885 | 115 | 0.17914 | 20.6006
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.017291 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.6138 | 556 | 0.17914 | 99.5996
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017631 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17948 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017631 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17948 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8421 | 161 | 0.1795 | 28.8992
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8951 | 164 | 0.1795 | 29.4377
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8951 | 164 | 0.1795 | 29.4377
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.3083 | 414 | 0.1795 | 74.3121
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8598 | 162 | 0.1795 | 29.0787
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8421 | 161 | 0.1795 | 28.8992
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8774 | 163 | 0.1795 | 29.2582
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.017653 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.2201 | 409 | 0.1795 | 73.4147
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.017736 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.8816 | 388 | 0.17958 | 69.6774
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.017736 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.134 | 515 | 0.17958 | 92.4842
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.017809 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.7469 | 435 | 0.17965 | 78.1495
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.017812 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71248 | 0 | 0.17966 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.017812 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71248 | 0 | 0.17966 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.017821 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.0393 | 395 | 0.17967 | 70.968
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.017821 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.7521 | 435 | 0.17967 | 78.1547
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.018032 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0654 | 170 | 0.17988 | 30.5791
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.018032 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.3766 | 520 | 0.17988 | 93.536
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.018072 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.72288 | 40 | 0.17992 | 7.1967
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.018075 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.3615 | 20 | 0.17992 | 3.5984
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.018075 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.45188 | 25 | 0.17992 | 4.498
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.018075 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.74108 | 41 | 0.17992 | 7.3767
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.01815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4339 | 79 | 0.17999 | 14.2196
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.01815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9239 | 106 | 0.17999 | 19.0795
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.01815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6499 | 146 | 0.17999 | 26.2793
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.01815 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.3794 | 76 | 0.17999 | 13.6796
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.018276 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.3707 | 0 | 0.18012 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.018276 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.4548 | 0 | 0.18012 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.018276 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.6156 | 0 | 0.18012 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9395 | 160 | 0.18022 | 28.8347
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.866 | 156 | 0.18022 | 28.1138
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.6009 | 196 | 0.18022 | 35.3225
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.866 | 156 | 0.18022 | 28.1138
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8844 | 157 | 0.18022 | 28.2941
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.018372 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.6377 | 198 | 0.18022 | 35.683
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.018383 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.2577 | 0 | 0.18023 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.018383 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.6438 | 0 | 0.18023 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.018383 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.8535 | 0 | 0.18023 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.018402 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.8087 | 370 | 0.18025 | 66.6914
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5763 | 0 | 0.18025 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5947 | 0 | 0.18025 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6862 | 0 | 0.18025 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6315 | 0 | 0.18025 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6499 | 0 | 0.18025 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.018402 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.7046 | 0 | 0.18025 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.018851 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.1807 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.019058 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1809 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.019219 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18106 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.019219 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18106 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.019219 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18106 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.020617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.237 | 60 | 0.18246 | 10.9477
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.020617 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2989 | 63 | 0.18246 | 11.4951
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.04277 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.6538 | 366 | 0.20461 | 74.8891
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.04277 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.0571 | 0 | 0.20461 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.048632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.9209 | 204 | 0.21048 | 42.9373
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.048632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.775 | 201 | 0.21048 | 42.3059
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.048632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7689 | 242 | 0.21048 | 50.9354

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1195
| 25 | 1195
| 30 | 1195
| 35 | 1186
| 40 | 1186
| 45 | 1157
| 50 | 1157
| 55 | 1128
| 60 | 1100
| 65 | 1100
| 70 | 1071
| 75 | 1042
| 80 | 1042
| 85 | 1013
| 90 | 1013
| 95 | 985
| 100 | 956
| 105 | 956
| 110 | 956
| 115 | 956
| Max | 1195
| Min | 956
| Avg | 1079.45