## test results
CRE test for: |  | 1596 GRAHAMSW - 1601 GRAHAME_ | [5 empty] | FAIL
Line Rating: |  | 290.5
Direction |  | North | → | West |  | N-W
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1596 GRAHAMSW - 1601 GRAHAME_
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.0045532
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -1.1955e-06
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.027633
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0003095
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1596 GRAHAMSW - 1601 GRAHAME_
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.0036621
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -4.0681e-05
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.027633
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.00031413
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 1596 GRAHAMSW - 1601 GRAHAME_
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.0045939
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.032186
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.0042391
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.027632
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.00031069
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.027948
PTDF tests
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.032186 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.032186 | 0.0045939
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.21421
[6 empty] | Concentration |  | 6.6555 | FAIL
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.04706
[6 empty] | Concentration |  | 1.4621 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 112.4904
| Percent of line rating => | [6 empty] | 38.72% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 25.3142
[7 empty] | B1(N-S) | -0.076164 | 0.040127 | 0.11629 | -0.076164
[7 empty] | B2 (N-W) | 0 | 0.81477 | 0.81477 | 0
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.088334 | 0.018975 | 0.10731 | -0.088334
[7 empty] | B4 (S-W) | 0.076293 | 0.77577 | 0.69948 | 0.076293
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.012159 | -0.020024 | -0.007865 | -0.012159
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.085466 | -0.79294 | -0.70747 | -0.085466
[7 empty] | test | 0 | 0.81477 | 0.81477 | 0
[7 empty] | B1 | -9.348%
Deployment Error Percent | [6 empty] | B2 | 0%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -10.84%
[7 empty] | B4 | 9.364%
[7 empty] | B5 | -1.492%
[7 empty] | B6 | -10.49%
[7 empty] | Max Abs Error | 10.84% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-W
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:1596 GRAHAMSW - 1601 GRAHAME_ C: 37980 TNWICKET- 38000 TNPYOTE C: 38000 TNPYOTE_ - 38020 TNWORSHA C: 38020 TNWORSHA - 38040 TNH20__ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:1596 GRAHAMSW - 1601 GRAHAME_ C: 37980 TNWICKET- 38000 TNPYOTE C: 38000 TNPYOTE_ - 38020 TNWORSHA C: 38020 TNWORSHA - 38040 TNH20__
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.002962 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 0.75531
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.002962 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 0.44134
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.007906 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.11859
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.007906 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.11859
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.002962 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 0.45319
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.004311 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 0.64665
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.004311 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.34488
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.1074 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 7.8403
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.1074 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 12.7807
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.1074 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 22.0172
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.1074 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 10.9549
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.1074 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 10.3105
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.12102 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.4523
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.12102 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.4523
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.009589 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 1.611
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.009589 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 0.86301
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.095506 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.7191
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.095506 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.7191
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.095506 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 3.6292
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.04712 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 13.5706
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.04712 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 6.9266
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.04712 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 6.9266
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.013082 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 1.4717
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.000341 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.01364
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.000328 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 0.025912
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.000328 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 0.034768
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.000328 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 0.047888
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.000328 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 0.024928
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.001027 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 0.06162
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.001027 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 0.064701
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.000336 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.00672
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.000336 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.0084
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.000336 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.013776
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.000459 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 0.21252
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -1.7855
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -1.7584
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.8126
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.8126
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.8126
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.027053 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -3.084
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.027053 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -13.9323
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -1.8666
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -1.9515
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -1.9515
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -1.8949
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -1.8949
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -1.8383
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.027389 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -1.9172
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.027389 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -2.0104
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.027389 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -1.9282
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -4.1112
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -6.0298
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.03019 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -2.9888
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.03019 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -1.8416
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.030131 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -4.2485
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.03019 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -0.75475
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.03019 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -1.3797
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.03019 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -1.3797
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.030131 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -3.6157
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.028011 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -0.72268
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.02767 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -2.7808
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.028429 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -3.4115
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.027687 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -1.6058
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.027771 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -5.9485
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.029654 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -4.4481
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.027273 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -0.18
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.027273 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -0.93546
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.029654 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -2.9951
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.028584 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -3.4301
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.03045 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -11.1447
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.1301 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -31.4835
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.028914 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -11.5656
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.028916 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -6.8242
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.029284 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -4.8319
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.01584 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -3.2314
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.01584 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -3.1838
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.01584 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -3.8333
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.68792
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.68792
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.68792
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.58473
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.44854 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 53.8244
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.00853 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 0.5118
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.000518 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 0.03885
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.000518 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 0.041233
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.000518 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 0.045791
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 0.07328
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.071448
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 0.089768
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.071448
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 0.071906
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 0.090684
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.000979 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 0.16643
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.000979 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 0.50908
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.000484 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 0.17908
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.000346 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 0.19307
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.000346 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 0.20033
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.000346 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 0.27957
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.006602 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 0.73942
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.006602 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 0.6602
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.006602 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 2.4956
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000931 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -0.20231
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000931 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -0.19085
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000931 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -0.2536
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 3.4e-05 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 0.02618
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 0.85022
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.83807
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.83807
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.82593
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.00101 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -1.1686
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.00101 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -1.1696
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 0.13216
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 0.13334
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.000151 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 0.032676
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.000151 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 0.032631
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 0.12508
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 0.12449
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.000817 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 0.32271
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.000909 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 0.39542
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.000817 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 0.3554
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.000445 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 0.06141
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.000428 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 0.050504
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.000428 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 0.04922
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.000428 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 0.23797
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.000353 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 0.13696
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.000353 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 0.1818
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.000411 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 0.32264
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.000411 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 0.32675
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.000411 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 0.32058
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.000436 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 0.079352
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.000436 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 0.21102
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.000971 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 0.2175
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.000424 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.0212
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.000424 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.017808
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.000467 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 0.2872
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.000467 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 0.27413
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.001265 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 0.67931
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.001265 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 0.99555
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.001393 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.10447
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.001393 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 0.30925
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.000637 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 0.36245
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000152 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -0.031768
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000152 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -0.032832
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.000166 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -0.067562
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.006992
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -0.007144
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.006992
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.006992
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.000143 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -0.060632
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.000143 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -0.060775
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00021 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -0.01218
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00021 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -0.01869
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.00924
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.00924
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.00903
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -0.00945
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.000151 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -0.062212
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.000151 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -0.0604
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -9.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -0.05187
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -9.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -0.07125
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.000112 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -0.006832
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.000112 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -0.01064
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.000112 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -0.016912
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.000106 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.01643
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.000106 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -0.01802
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.000106 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.01643
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -6.3e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.001386
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -6.3e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.000693
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -6.3e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.000693
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.0020511
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.0016039
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.001978
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.002064
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.000363 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.004356
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.000363 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.003993
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.001073 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.025752
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.001073 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.025752
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.001073 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.024679
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.00019 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -0.07524
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.000205 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 0.27326
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.000205 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 0.27224
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.000137 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.005206
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.000137 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.0026441
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.000137 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.002055
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.000137 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.006439
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.025268 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -1.8951
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.036236 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -5.4354
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.025094 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -4.2534
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.01821 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -2.7315
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.029694 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -1.8707
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.029354 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -19.0713
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.001299 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.05196
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.001299 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.05196
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.000525 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -0.22155
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.000307 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.040524
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.000307 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.041138
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.000307 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 0.099161
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.000332 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.052456
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.000332 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.05312
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.000332 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 0.0581
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.000286 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 0.16702
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.000286 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 0.17017
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.000285 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 0.12341
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.013434
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.0135
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.013476
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.013602
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.000272 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.002176
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.000272 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.002176
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.000381 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.006858
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.000381 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.006858
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.000381 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.005715
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.000743 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.010179
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.000335 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.00603
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.000335 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.00603
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 9.5e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.003325
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 9.5e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.00323
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 9.5e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.003325
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.000458 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.012824
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.000458 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.013282
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.027128 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -0.94948
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.027128 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -0.81384
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.0141
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.0141
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.0141
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.0141
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 3.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.000222
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 2.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 6.48e-05
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 2.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 6.48e-05
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 2.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 7.56e-05
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -1.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -7.2e-05
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 5.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0001368
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 5.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0001368
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.002646
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -0.002484
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -0.00252
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.002646
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -0.003276
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -0.003564
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.000299 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.045597
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.000299 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.0447
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.000299 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 0.069547
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.002982
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.003045
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.003171
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 0.00609
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.007137 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.23552
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.007137 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.17843
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.000363 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.004356
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -2.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -0.001898
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.001027
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.001053
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.000448
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.000112
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.001027
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.00104
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.0010192
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.000325
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.000598
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -9e-05 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -0.05661
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -3.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -0.004464
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -3.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -0.005828
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 2.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.000336
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.005211 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.031266
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.000108 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -0.036288
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.00011 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -0.03674
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.00011 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -0.0374
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.000114 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.004332
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.000112 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.0028
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.000112 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.0028
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.000112 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.004256
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.000122 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.003538
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.000108 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -0.016016
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.000108 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -0.016049
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.000108 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -0.016524
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -0.014852
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -0.014382
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -0.0094
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -0.01363
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -0.013818
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -0.011938
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.000184 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -0.026956
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.000184 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -0.027214
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.000184 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -0.031832
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.000155 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -0.032085
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.000155 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -0.033589
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.000155 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -0.03751
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.000154 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.022176
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.000154 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.022176
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.000154 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -0.026334
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.000289 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 0.08959
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.000289 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 0.11936
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.01302
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.01364
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.01364
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.01457
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.013475
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.01265
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.01265
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.012925
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000275 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.04235
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000275 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.0407
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.0132
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.0132
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -1.9065
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -1.9065
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -2.5275
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -2.1789
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -2.1789
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -3.1321
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -5.6703
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -3.8701
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -3.6059
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -3.704
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -4.0035
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -5.7194
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -5.8192
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -3.5221
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -6.9329
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -5.4851
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -5.4816
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -3.341
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.027311 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -4.0693
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.029234 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -5.2621
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.029234 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -5.2621
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.029156 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -6.5601
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.027625 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -3.4531
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.027625 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -3.4531
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 0.06776
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 0.068244
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 0.14956
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 0.069212
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 0.069696
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 0.15004
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.001318 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 0.25833
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.001318 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 0.1463
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.00027 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.056028
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.057072
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.057072
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 0.14407
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 0.056376
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.056028
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 0.056724
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 0.14233
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.000357 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.000357 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 0.062012
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 0.05447
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 0.060755
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 0.16718
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.000454 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 0.068418
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.000454 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 0.068554
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.000454 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 0.08054
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.000464 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 0.070296
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.000464 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 0.070667
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.000464 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 0.08236
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.000637 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 0.3701
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 0.42664
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 0.42664
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.000492 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.015744
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.000502 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.024096
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.000502 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.023092
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.005904
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.025092
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.000492 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.008364
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.010824
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.0123
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.000502 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.05271
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.031312 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -2.6302
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.025242 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -2.0194
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.025225 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -3.7837
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.025225 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -3.7837
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.021594
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.020344
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.016165
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 0.046726
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 0.046817
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 0.046451
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 0.02928
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 0.07442
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.0122
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 0.030592
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 0.028334
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 0.031323
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 0.03111
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.00976
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.00915
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.029748
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.029748
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 0.031892
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 0.029346
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 0.075998
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 0.076347
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.000327 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 0.044472
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.000293 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.009669
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.013692
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.013692
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.012388
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.012388
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.00026 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.01846
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.00026 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.0026
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.000293 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 0.047759
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.000293 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 0.047759
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.000293 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 0.071785
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.02067
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.01908
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.02067
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.02067
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 0.048276
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.021092
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 0.028847
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.027769
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.027579
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.017277
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.0038674
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.000333 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 0.24742
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.00033 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 0.24255
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.000333 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.057276
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.000333 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.057276
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.000333 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.057276
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 0.060031
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 0.056571
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.000327 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 0.044145
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 0.054538
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 0.054069
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 0.053232
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 0.090182
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.020736
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.020477
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.026762
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.023846
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 0.05255
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 0.050586
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 0.050715
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 0.050554
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 0.086618
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.001665
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.006993
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 0.067848
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.06864
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.06864
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 0.1672
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.000336 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 0.13373
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.014812
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.014812
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.014812
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.01771
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.01771
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.017388
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.000515 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 0.4259
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.000515 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 0.42179
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.000289 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.013323
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.016492
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.016492
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 0.022785
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.016058
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.016058
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 0.022134
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.000324 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 0.05832
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.000324 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 0.051386
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.000324 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 0.050868
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.000323 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.011305
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.000313 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 0.14367
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.021645
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.021978
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.02331
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.020979
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.020646
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 0.034632
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.019647
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 0.054132
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.053438
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.053438
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 0.056214
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.000333 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 0.052281
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.023075
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.0234
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.012675
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.00975
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.000321 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.025038
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.000321 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.02568
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.0052488
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.000323 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 0.053295
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.000323 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 0.054587
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.000324 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 0.069012
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.000324 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 0.073872
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.000323 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.003876
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.000323 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.005814
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.000311 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.01555
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.03432
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.03432
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.01782
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.01749
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.01782
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.01881
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.01782
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.01782
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.01914
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.01914
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.000332 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.003984
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.018872
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.019883
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.018872
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.018872
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.019883
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.018872
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.000216 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.014256
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.000298 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 0.047978
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.000298 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 0.049468
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.000298 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 0.073904
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.000298 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 0.16271
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.000298 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 0.19161
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.000293 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 0.19074
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.000293 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 0.16525
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.000293 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 0.1758
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.000298 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.003874
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.000333 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.003996
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.011254
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.011486
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.010824
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.015193
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.0058587
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.0067524
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.0065869
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.011585
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.005958
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.028267
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 0.048988
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.015624
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.017993
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.01134
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.025452
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.021672
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.022176
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.0126
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.004536
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 0.023688
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.01764
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.015876
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.018144
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.01633
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.025452
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 0.024444
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 0.025956
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.019152
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.02016
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.02016
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 0.043092
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.01055
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.024446 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -1.8701
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.025268 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -2.0214
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.025268 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -1.0107
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.025384 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -2.0307
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.025246 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -2.0197
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.024626 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -1.9701
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.024423 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -2.0515
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.025384 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -2.0307
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -0.022458
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.026269 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -3.1523
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.026269 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -6.1207
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.026269 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -4.471
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -0.043734
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -0.036248
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -0.044128
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -0.022655
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -0.0197
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.038454 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -2.3072
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.007191 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.021242 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.025887 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.12426
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -1.042
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -2.9871
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -3.7512
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -3.3067
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -2.9176
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -2.2369
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.025403 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -3.8104
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -2.8128
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -3.7379
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -4.6506
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -5.3631
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.000137 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.004763 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.000725 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.000364
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.0005668
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.000962
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.01222
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.00533
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.00494
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.00247
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.01222
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.00468
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.00559
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.00286
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.000624
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.00024
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.000112
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.00024
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.000624
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.000624
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -0.01924
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.0065
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -0.00715
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.0065
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -9.4e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.001128
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -2.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.000315
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -2.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.000483
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 7e-06 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.000336
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -2.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.000168
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.000108 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -0.01944
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.000108 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -0.01944
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.00011 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.0198
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.00011 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.0198
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000724 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.0724
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000724 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.0724
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.0025
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.0025
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.0025
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.0016
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.0025
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.0025
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.0025
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.0015
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000724 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000724 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -0.362
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000724 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -0.362
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.000724 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.00019 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.007137 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.000533 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.000218 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:1596 GRAHAMSW - 1601 GRAHAME_ C: 37980 TNWICKET- 38000 TNPYOTE C: 38000 TNPYOTE_ - 38020 TNWORSHA C: 38020 TNWORSHA - 38040 TNH20__ | [7 empty] | 112.4904
Number of Bus | Name of Bus | ID | Max MW | L:1596 GRAHAMSW - 1601 GRAHAME_ C: 37980 TNWICKET- 38000 TNPYOTE C: 38000 TNPYOTE_ - 38020 TNWORSHA C: 38020 TNWORSHA - 38040 TNH20__ | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.002962 | north | Y | -0.0015912 | 0.0029632 | 0.030595 | 0.0026525 | 0.0015912 | North | N | 0.0015912 | 0
239 | BOSQUESW | 1 | 149 | 0.002962 | north | Y | -0.0015912 | 0.0029632 | 0.030595 | 0.0026525 | 0.0015912 | North | N | 0.0015912 | 0
244 | WHITNYDM | 1 | 15 | 0.007906 | north | N | 0.0033528 | 0.0079072 | 0.035539 | 0.0075965 | 0.0033528 | North | N | 0.0033528 | 0
245 | WHITNYDM | 2 | 15 | 0.007906 | north | N | 0.0033528 | 0.0079072 | 0.035539 | 0.0075965 | 0.0033528 | North | N | 0.0033528 | 0
247 | BOSQUESW | 2 | 153 | 0.002962 | north | Y | -0.0015912 | 0.0029632 | 0.030595 | 0.0026525 | 0.0015912 | North | N | 0.0015912 | 0
251 | BOSQUESW | 2 | 150 | 0.004311 | north | Y | -0.00024221 | 0.0043122 | 0.031944 | 0.0040015 | 0.00024221 | North | N | 0.00024221 | 0
253 | BOSQUESW | 2 | 80 | 0.004311 | north | Y | -0.00024221 | 0.0043122 | 0.031944 | 0.0040015 | 0.00024221 | North | N | 0.00024221 | 0
332 | RWMILLER | 1 | 73 | 0.1074 | north | Y | 0.10285 | 0.1074 | 0.13503 | 0.10709 | 0.10285 | North | N | 0.10285 | 0
333 | RWMILLER | 2 | 119 | 0.1074 | north | Y | 0.10285 | 0.1074 | 0.13503 | 0.10709 | 0.10285 | North | N | 0.10285 | 0
334 | RWMILLER | 3 | 205 | 0.1074 | north | Y | 0.10285 | 0.1074 | 0.13503 | 0.10709 | 0.10285 | North | N | 0.10285 | 0
335 | RWMILLER | 4 | 102 | 0.1074 | north | Y | 0.10285 | 0.1074 | 0.13503 | 0.10709 | 0.10285 | North | N | 0.10285 | 0
336 | RWMILLER | 5 | 96 | 0.1074 | north | Y | 0.10285 | 0.1074 | 0.13503 | 0.10709 | 0.10285 | North | N | 0.10285 | 0
344 | MRSSHPRD | 1 | 12 | 0.12102 | north | N | 0.11647 | 0.12102 | 0.14866 | 0.12071 | 0.11647 | North | N | 0.11647 | 0
345 | MRSSHPRD | 2 | 12 | 0.12102 | north | N | 0.11647 | 0.12102 | 0.14866 | 0.12071 | 0.11647 | North | N | 0.11647 | 0
366 | JNSNCNTY | 1 | 168 | 0.009589 | north | Y | 0.0050358 | 0.0095902 | 0.037222 | 0.0092795 | 0.0050358 | North | N | 0.0050358 | 0
367 | JNSNCNTY | 2 | 90 | 0.009589 | north | Y | 0.0050358 | 0.0095902 | 0.037222 | 0.0092795 | 0.0050358 | North | N | 0.0050358 | 0
503 | NTHTEXAS | 1 | 18 | 0.095506 | north | Y | 0.090953 | 0.095507 | 0.12314 | 0.095197 | 0.090953 | North | N | 0.090953 | 0
504 | NTHTEXAS | 2 | 18 | 0.095506 | north | Y | 0.090953 | 0.095507 | 0.12314 | 0.095197 | 0.090953 | North | N | 0.090953 | 0
505 | NTHTEXAS | 3 | 38 | 0.095506 | north | Y | 0.090953 | 0.095507 | 0.12314 | 0.095197 | 0.090953 | North | N | 0.090953 | 0
580 | JCKCNTY8 | 1 | 288 | 0.04712 | north | Y | 0.042567 | 0.047121 | 0.074753 | 0.046811 | 0.042567 | North | N | 0.042567 | 0
581 | JCKCNTY8 | 2 | 147 | 0.04712 | north | Y | 0.042567 | 0.047121 | 0.074753 | 0.046811 | 0.042567 | North | N | 0.042567 | 0
582 | JCKCNTY8 | 3 | 147 | 0.04712 | north | Y | 0.042567 | 0.047121 | 0.074753 | 0.046811 | 0.042567 | North | N | 0.042567 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.013082 | north | Y | 0.0085288 | 0.013083 | 0.040715 | 0.012773 | 0.0085288 | North | N | 0.0085288 | 0
837 | NEWMAN_G | 1 | 40 | 0.000341 | north | Y | -0.0042122 | 0.0003422 | 0.027974 | 3.1502e-05 | 3.1502e-05 | houston | Y | 0.0042122 | 0.16723
842 | OLINGER_ | 1 | 79 | 0.000328 | north | Y | -0.0042252 | 0.0003292 | 0.027961 | 1.8502e-05 | 1.8502e-05 | houston | Y | 0.0042252 | 0.33233
843 | OLINGER_ | 1 | 106 | 0.000328 | north | Y | -0.0042252 | 0.0003292 | 0.027961 | 1.8502e-05 | 1.8502e-05 | houston | Y | 0.0042252 | 0.44591
844 | OLINGER_ | 1 | 146 | 0.000328 | north | Y | -0.0042252 | 0.0003292 | 0.027961 | 1.8502e-05 | 1.8502e-05 | houston | Y | 0.0042252 | 0.61418
845 | OLINGER_ | 1 | 76 | 0.000328 | north | Y | -0.0042252 | 0.0003292 | 0.027961 | 1.8502e-05 | 1.8502e-05 | houston | Y | 0.0042252 | 0.31971
923 | SPENCER_ | 1 | 60 | 0.001027 | north | Y | -0.0035262 | 0.0010282 | 0.02866 | 0.0007175 | 0.0007175 | houston | Y | 0.0035262 | 0.16852
924 | SPENCER_ | 1 | 63 | 0.001027 | north | Y | -0.0035262 | 0.0010282 | 0.02866 | 0.0007175 | 0.0007175 | houston | Y | 0.0035262 | 0.17695
948 | STEAM1 | 1 | 20 | 0.000336 | north | Y | -0.0042172 | 0.0003372 | 0.027969 | 2.6502e-05 | 2.6502e-05 | houston | Y | 0.0042172 | 0.083814
949 | STEAM2 | 1 | 25 | 0.000336 | north | Y | -0.0042172 | 0.0003372 | 0.027969 | 2.6502e-05 | 2.6502e-05 | houston | Y | 0.0042172 | 0.10477
950 | STEAM3 | 1 | 41 | 0.000336 | north | Y | -0.0042172 | 0.0003372 | 0.027969 | 2.6502e-05 | 2.6502e-05 | houston | Y | 0.0042172 | 0.17182
990 | GIBN_CRE | 1 | 463 | 0.000459 | north | Y | -0.0040942 | 0.0004602 | 0.028092 | 0.0001495 | 0.0001495 | houston | Y | 0.0040942 | 1.8264
1002 | PBCTAGE_ | A | 66 | -0.027053 | west | Y | -0.031606 | -0.027052 | 0.0005804 | -0.027362 | 0.0005804 | west | N | 0.0005804 | 0
1003 | PBCTBGE_ | B | 65 | -0.027053 | west | Y | -0.031606 | -0.027052 | 0.0005804 | -0.027362 | 0.0005804 | west | N | 0.0005804 | 0
1004 | PBCTCGE_ | C | 67 | -0.027053 | west | Y | -0.031606 | -0.027052 | 0.0005804 | -0.027362 | 0.0005804 | west | N | 0.0005804 | 0
1005 | PBCTDGE_ | D | 67 | -0.027053 | west | Y | -0.031606 | -0.027052 | 0.0005804 | -0.027362 | 0.0005804 | west | N | 0.0005804 | 0
1006 | PBCTEGE_ | E | 67 | -0.027053 | west | Y | -0.031606 | -0.027052 | 0.0005804 | -0.027362 | 0.0005804 | west | N | 0.0005804 | 0
1007 | PB5GEN_6 | MB | 114 | -0.027053 | west | Y | -0.031606 | -0.027052 | 0.0005804 | -0.027362 | 0.0005804 | west | N | 0.0005804 | 0
1008 | PB6GEN_7 | MB | 515 | -0.027053 | west | Y | -0.031606 | -0.027052 | 0.0005804 | -0.027362 | 0.0005804 | west | N | 0.0005804 | 0
1039 | MRGNAG_1 | A | 66 | -0.028282 | west | Y | -0.032835 | -0.028281 | -0.0006486 | -0.028591 | 0.0006486 | west | N | 0.0006486 | 0
1040 | MRGNBG_2 | B | 69 | -0.028282 | west | Y | -0.032835 | -0.028281 | -0.0006486 | -0.028591 | 0.0006486 | west | N | 0.0006486 | 0
1041 | MRGNCG_3 | C | 69 | -0.028282 | west | Y | -0.032835 | -0.028281 | -0.0006486 | -0.028591 | 0.0006486 | west | N | 0.0006486 | 0
1042 | MRGNDG_4 | D | 67 | -0.028282 | west | Y | -0.032835 | -0.028281 | -0.0006486 | -0.028591 | 0.0006486 | west | N | 0.0006486 | 0
1043 | MRGNEG_5 | E | 67 | -0.028282 | west | Y | -0.032835 | -0.028281 | -0.0006486 | -0.028591 | 0.0006486 | west | N | 0.0006486 | 0
1044 | MRGNFG_6 | F | 65 | -0.028282 | west | Y | -0.032835 | -0.028281 | -0.0006486 | -0.028591 | 0.0006486 | west | N | 0.0006486 | 0
1045 | CALENG1G | 1 | 70 | -0.027389 | west | N | -0.031942 | -0.027388 | 0.0002444 | -0.027698 | 0.0002444 | west | N | 0.0002444 | 0
1046 | CALENG2G | 2 | 73.4 | -0.027389 | west | N | -0.031942 | -0.027388 | 0.0002444 | -0.027698 | 0.0002444 | west | N | 0.0002444 | 0
1047 | CALENG3G | 3 | 70.4 | -0.027389 | west | N | -0.031942 | -0.027388 | 0.0002444 | -0.027698 | 0.0002444 | west | N | 0.0002444 | 0
1058 | LONGSHOR | 1 | 150 | -0.027408 | west | Y | -0.031961 | -0.027407 | 0.0002254 | -0.027717 | 0.0002254 | west | N | 0.0002254 | 0
1058 | LONGSHOR | 2 | 220 | -0.027408 | west | Y | -0.031961 | -0.027407 | 0.0002254 | -0.027717 | 0.0002254 | west | N | 0.0002254 | 0
1061 | CIELOGEN | 1 | 99 | -0.03019 | west | Y | -0.034743 | -0.030189 | -0.0025566 | -0.030499 | 0.0025566 | west | N | 0.0025566 | 0
1062 | CIELOGEN | 1 | 61 | -0.03019 | west | Y | -0.034743 | -0.030189 | -0.0025566 | -0.030499 | 0.0025566 | west | N | 0.0025566 | 0
1068 | SCURRYCW | 1 | 141 | -0.030131 | west | Y | -0.034684 | -0.03013 | -0.0024976 | -0.03044 | 0.0024976 | west | N | 0.0024976 | 0
1069 | KINDERMG | 1 | 25 | -0.03019 | west | N | -0.034743 | -0.030189 | -0.0025566 | -0.030499 | 0.0025566 | west | N | 0.0025566 | 0
1070 | KINDERMG | 1 | 45.7 | -0.03019 | west | N | -0.034743 | -0.030189 | -0.0025566 | -0.030499 | 0.0025566 | west | N | 0.0025566 | 0
1071 | KINDERMG | 1 | 45.7 | -0.03019 | west | N | -0.034743 | -0.030189 | -0.0025566 | -0.030499 | 0.0025566 | west | N | 0.0025566 | 0
1073 | SCURRYCW | 2 | 120 | -0.030131 | west | Y | -0.034684 | -0.03013 | -0.0024976 | -0.03044 | 0.0024976 | west | N | 0.0024976 | 0
1320 | BSP 1 | 1 | 25.8 | -0.028011 | west | N | -0.032564 | -0.02801 | -0.0003776 | -0.02832 | 0.0003776 | west | N | 0.0003776 | 0
1326 | STANTONW | 1 | 100.5 | -0.02767 | west | Y | -0.032223 | -0.027669 | -3.6598e-05 | -0.027979 | 3.6598e-05 | west | N | 3.6598e-05 | 0
1327 | WILDHRSE | 1 | 120 | -0.028429 | west | Y | -0.032982 | -0.028428 | -0.0007956 | -0.028738 | 0.0007956 | west | N | 0.0007956 | 0
1328 | OCOTILLO | 1 | 58 | -0.027687 | west | Y | -0.03224 | -0.027686 | -5.3598e-05 | -0.027996 | 5.3598e-05 | west | N | 5.3598e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.027771 | west | Y | -0.032324 | -0.02777 | -0.0001376 | -0.02808 | 0.0001376 | west | N | 0.0001376 | 0
1343 | TRENTIPP | 1 | 150 | -0.029654 | west | Y | -0.034207 | -0.029653 | -0.0020206 | -0.029963 | 0.0020206 | west | N | 0.0020206 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.027273 | west | Y | -0.031826 | -0.027272 | 0.0003604 | -0.027582 | 0.0003604 | west | N | 0.0003604 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.027273 | west | Y | -0.031826 | -0.027272 | 0.0003604 | -0.027582 | 0.0003604 | west | N | 0.0003604 | 0
1354 | AEPWIND_ | 1 | 101 | -0.029654 | west | Y | -0.034207 | -0.029653 | -0.0020206 | -0.029963 | 0.0020206 | west | N | 0.0020206 | 0
1360 | GUNSIGHT | 1 | 120 | -0.028584 | west | Y | -0.033137 | -0.028583 | -0.0009506 | -0.028893 | 0.0009506 | west | N | 0.0009506 | 0
1432 | GRHAMSES | 2 | 366 | -0.03045 | north | Y | -0.035003 | -0.030449 | -0.0028166 | -0.030759 | 0.0028166 | west | Y | 0.035003 | 11.7803
1433 | GRHAMSES | 1 | 242 | -0.1301 | north | Y | -0.13465 | -0.1301 | -0.10246 | -0.13041 | 0.10246 | west | Y | 0.13465 | 7.7892
1437 | MESQUITW | 1 | 400 | -0.028914 | west | Y | -0.033467 | -0.028913 | -0.0012806 | -0.029223 | 0.0012806 | west | N | 0.0012806 | 0
1438 | MESQUITW | 1 | 236 | -0.028916 | west | Y | -0.033469 | -0.028915 | -0.0012826 | -0.029225 | 0.0012826 | west | N | 0.0012826 | 0
1442 | COKFIELD | 1 | 165 | -0.029284 | west | Y | -0.033837 | -0.029283 | -0.0016506 | -0.029593 | 0.0016506 | west | N | 0.0016506 | 0
1453 | WCPWRCO_ | 1 | 204 | -0.01584 | north | Y | -0.020393 | -0.015839 | 0.011793 | -0.016149 | 0.011793 | west | Y | 0.020393 | 1.7544
1454 | WCPWRCO_ | 2 | 201 | -0.01584 | north | Y | -0.020393 | -0.015839 | 0.011793 | -0.016149 | 0.011793 | west | Y | 0.020393 | 1.7286
1455 | WCPWRCO_ | 3 | 242 | -0.01584 | north | Y | -0.020393 | -0.015839 | 0.011793 | -0.016149 | 0.011793 | west | Y | 0.020393 | 2.0812
1479 | WFCOGEN_ | 1 | 20 | -0.034396 | west | Y | -0.038949 | -0.034395 | -0.0067626 | -0.034705 | 0.0067626 | west | N | 0.0067626 | 0
1479 | WFCOGEN_ | 2 | 20 | -0.034396 | west | Y | -0.038949 | -0.034395 | -0.0067626 | -0.034705 | 0.0067626 | west | N | 0.0067626 | 0
1482 | WFCOGEN_ | 1 | 20 | -0.034396 | west | Y | -0.038949 | -0.034395 | -0.0067626 | -0.034705 | 0.0067626 | west | N | 0.0067626 | 0
1482 | WFCOGEN_ | 2 | 17 | -0.034396 | west | Y | -0.038949 | -0.034395 | -0.0067626 | -0.034705 | 0.0067626 | west | N | 0.0067626 | 0
1600 | BARTNWND | 1 | 120 | 0.44854 | north | Y | 0.44398 | 0.44854 | 0.47617 | 0.44823 | 0.44398 | North | N | 0.44398 | 0
1643 | SLSTR1PP | 1 | 60 | 0.00853 | north | Y | 0.0039768 | 0.0085312 | 0.036163 | 0.0082205 | 0.0039768 | North | N | 0.0039768 | 0
1675 | PEC_1G | 1 | 75 | 0.000518 | north | N | -0.0040352 | 0.0005192 | 0.028151 | 0.0002085 | 0.0002085 | houston | Y | 0.0040352 | 0
1676 | PEC_2G | 2 | 79.6 | 0.000518 | north | N | -0.0040352 | 0.0005192 | 0.028151 | 0.0002085 | 0.0002085 | houston | Y | 0.0040352 | 0
1677 | PEC_3G | 3 | 88.4 | 0.000518 | north | N | -0.0040352 | 0.0005192 | 0.028151 | 0.0002085 | 0.0002085 | houston | Y | 0.0040352 | 0
1678 | LAMARPWR | 1 | 160 | 0.000458 | north | Y | -0.0040952 | 0.0004592 | 0.028091 | 0.0001485 | 0.0001485 | houston | Y | 0.0040952 | 0.63147
1679 | LAMARPWR | 2 | 156 | 0.000458 | north | Y | -0.0040952 | 0.0004592 | 0.028091 | 0.0001485 | 0.0001485 | houston | Y | 0.0040952 | 0.61569
1680 | LAMARPWR | 3 | 196 | 0.000458 | north | Y | -0.0040952 | 0.0004592 | 0.028091 | 0.0001485 | 0.0001485 | houston | Y | 0.0040952 | 0.77356
1681 | LAMARPWR | 4 | 156 | 0.000458 | north | Y | -0.0040952 | 0.0004592 | 0.028091 | 0.0001485 | 0.0001485 | houston | Y | 0.0040952 | 0.61569
1682 | LAMARPWR | 5 | 157 | 0.000458 | north | Y | -0.0040952 | 0.0004592 | 0.028091 | 0.0001485 | 0.0001485 | houston | Y | 0.0040952 | 0.61963
1683 | LAMARPWR | 6 | 198 | 0.000458 | north | Y | -0.0040952 | 0.0004592 | 0.028091 | 0.0001485 | 0.0001485 | houston | Y | 0.0040952 | 0.78145
1687 | VALLEY_1 | 1 | 170 | 0.000979 | north | Y | -0.0035742 | 0.0009802 | 0.028612 | 0.0006695 | 0.0006695 | houston | Y | 0.0035742 | 0.4938
1688 | VALLEY_2 | 2 | 520 | 0.000979 | north | Y | -0.0035742 | 0.0009802 | 0.028612 | 0.0006695 | 0.0006695 | houston | Y | 0.0035742 | 1.5104
1689 | VALLEY_3 | 3 | 370 | 0.000484 | north | Y | -0.0040692 | 0.0004852 | 0.028117 | 0.0001745 | 0.0001745 | houston | Y | 0.0040692 | 1.441
1701 | MOSES_1G | 1 | 558 | 0.000346 | north | Y | -0.0042072 | 0.0003472 | 0.027979 | 3.6502e-05 | 3.6502e-05 | houston | Y | 0.0042072 | 2.3273
1702 | MOSES_2G | 2 | 579 | 0.000346 | north | Y | -0.0042072 | 0.0003472 | 0.027979 | 3.6502e-05 | 3.6502e-05 | houston | Y | 0.0042072 | 2.4148
1703 | MOSES_3G | 3 | 808 | 0.000346 | north | Y | -0.0042072 | 0.0003472 | 0.027979 | 3.6502e-05 | 3.6502e-05 | houston | Y | 0.0042072 | 3.3699
1861 | EAGLEMNT | MB | 112 | 0.006602 | north | Y | 0.0020488 | 0.0066032 | 0.034235 | 0.0062925 | 0.0020488 | North | N | 0.0020488 | 0
1862 | EAGLEMNT | MB | 100 | 0.006602 | north | Y | 0.0020488 | 0.0066032 | 0.034235 | 0.0062925 | 0.0020488 | North | N | 0.0020488 | 0
1863 | EAGLEMNT | MB | 378 | 0.006602 | north | Y | 0.0020488 | 0.0066032 | 0.034235 | 0.0062925 | 0.0020488 | North | N | 0.0020488 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.000931 | north | Y | -0.0054842 | -0.0009298 | 0.026702 | -0.0012405 | 0.0009298 | south | Y | 0.0054842 | 0.98967
1878 | WLFHOLW_ | 2 | 205 | -0.000931 | north | Y | -0.0054842 | -0.0009298 | 0.026702 | -0.0012405 | 0.0009298 | south | Y | 0.0054842 | 0.93365
1879 | WLFHOLW_ | 3 | 272.4 | -0.000931 | north | Y | -0.0054842 | -0.0009298 | 0.026702 | -0.0012405 | 0.0009298 | south | Y | 0.0054842 | 1.2406
1889 | DECRDOVA | MB | 770 | 3.4e-05 | north | Y | -0.0045192 | 3.5196e-05 | 0.027667 | -0.0002755 | 3.5196e-05 | south | Y | 0.0045192 | 0
1892 | DECRDOVA | A | 70 | 0.012146 | north | Y | 0.0075928 | 0.012147 | 0.039779 | 0.011837 | 0.0075928 | North | N | 0.0075928 | 0
1893 | DECRDOVA | B | 69 | 0.012146 | north | Y | 0.0075928 | 0.012147 | 0.039779 | 0.011837 | 0.0075928 | North | N | 0.0075928 | 0
1894 | DECRDOVA | C | 69 | 0.012146 | north | Y | 0.0075928 | 0.012147 | 0.039779 | 0.011837 | 0.0075928 | North | N | 0.0075928 | 0
1895 | DECRDOVA | D | 68 | 0.012146 | north | Y | 0.0075928 | 0.012147 | 0.039779 | 0.011837 | 0.0075928 | North | N | 0.0075928 | 0
1898 | COMCHEPK | 1 | 1157 | -0.00101 | north | N | -0.0055632 | -0.0010088 | 0.026623 | -0.0013195 | 0.0010088 | south | Y | 0.0055632 | 0
1899 | COMCHEPK | 2 | 1158 | -0.00101 | north | N | -0.0055632 | -0.0010088 | 0.026623 | -0.0013195 | 0.0010088 | south | Y | 0.0055632 | 0
1937 | MDLTHELP | 5 | 224 | 0.00059 | north | Y | -0.0039632 | 0.0005912 | 0.028223 | 0.0002805 | 0.0002805 | houston | Y | 0.0039632 | 0.82493
1938 | MDLTHELP | 6 | 226 | 0.00059 | north | Y | -0.0039632 | 0.0005912 | 0.028223 | 0.0002805 | 0.0002805 | houston | Y | 0.0039632 | 0.83229
1941 | MDLTHELP | 1 | 216.4 | 0.000151 | north | Y | -0.0044022 | 0.0001522 | 0.027784 | -0.0001585 | 0.0001522 | south | Y | 0.0044022 | 0.9197
1942 | MDLTHELP | 2 | 216.1 | 0.000151 | north | Y | -0.0044022 | 0.0001522 | 0.027784 | -0.0001585 | 0.0001522 | south | Y | 0.0044022 | 0.91843
1943 | MDLTHELP | 3 | 212 | 0.00059 | north | Y | -0.0039632 | 0.0005912 | 0.028223 | 0.0002805 | 0.0002805 | houston | Y | 0.0039632 | 0.78073
1944 | MDLTHELP | 4 | 211 | 0.00059 | north | Y | -0.0039632 | 0.0005912 | 0.028223 | 0.0002805 | 0.0002805 | houston | Y | 0.0039632 | 0.77705
1947 | HANDLEY_ | 3 | 395 | 0.000817 | north | Y | -0.0037362 | 0.0008182 | 0.02845 | 0.0005075 | 0.0005075 | houston | Y | 0.0037362 | 1.2753
1948 | HANDLEY_ | 4 | 435 | 0.000909 | north | Y | -0.0036442 | 0.0009102 | 0.028542 | 0.0005995 | 0.0005995 | houston | Y | 0.0036442 | 1.3244
1949 | HANDLEY_ | 5 | 435 | 0.000817 | north | Y | -0.0037362 | 0.0008182 | 0.02845 | 0.0005075 | 0.0005075 | houston | Y | 0.0037362 | 1.4045
2371 | COLLIN_1 | MB | 138 | 0.000445 | north | Y | -0.0041082 | 0.0004462 | 0.028078 | 0.0001355 | 0.0001355 | houston | Y | 0.0041082 | 0
2413 | MTCK6_G | 6 | 118 | 0.000428 | north | Y | -0.0041252 | 0.0004292 | 0.028061 | 0.0001185 | 0.0001185 | houston | Y | 0.0041252 | 0.47279
2414 | MTCK7_G | 7 | 115 | 0.000428 | north | Y | -0.0041252 | 0.0004292 | 0.028061 | 0.0001185 | 0.0001185 | houston | Y | 0.0041252 | 0.46077
2417 | MTCK8_G | 8 | 556 | 0.000428 | north | Y | -0.0041252 | 0.0004292 | 0.028061 | 0.0001185 | 0.0001185 | houston | Y | 0.0041252 | 2.2277
2451 | LKHB1_G | 1 | 388 | 0.000353 | north | Y | -0.0042002 | 0.0003542 | 0.027986 | 4.3502e-05 | 4.3502e-05 | houston | Y | 0.0042002 | 1.6128
2452 | LKHB2_G | 2 | 515 | 0.000353 | north | Y | -0.0042002 | 0.0003542 | 0.027986 | 4.3502e-05 | 4.3502e-05 | houston | Y | 0.0042002 | 2.1407
3097 | MARTLAKE | 1 | 785 | 0.000411 | north | Y | -0.0041422 | 0.0004122 | 0.028044 | 0.0001015 | 0.0001015 | houston | Y | 0.0041422 | 3.172
3098 | MARTLAKE | 2 | 795 | 0.000411 | north | Y | -0.0041422 | 0.0004122 | 0.028044 | 0.0001015 | 0.0001015 | houston | Y | 0.0041422 | 3.2124
3099 | MARTLAKE | 3 | 780 | 0.000411 | north | Y | -0.0041422 | 0.0004122 | 0.028044 | 0.0001015 | 0.0001015 | houston | Y | 0.0041422 | 3.1518
3107 | STRYKER_ | 1 | 182 | 0.000436 | north | Y | -0.0041172 | 0.0004372 | 0.028069 | 0.0001265 | 0.0001265 | houston | Y | 0.0041172 | 0.72631
3108 | STRYKER_ | 2 | 484 | 0.000436 | north | Y | -0.0041172 | 0.0004372 | 0.028069 | 0.0001265 | 0.0001265 | houston | Y | 0.0041172 | 1.9315
3126 | TRINIDAD | 1 | 224 | 0.000971 | north | Y | -0.0035822 | 0.0009722 | 0.028604 | 0.0006615 | 0.0006615 | houston | Y | 0.0035822 | 0.65424
3309 | ASPN_G | 1 | 50 | 0.000424 | north | Y | -0.0041292 | 0.0004252 | 0.028057 | 0.0001145 | 0.0001145 | houston | Y | 0.0041292 | 0.20074
3348 | CHAMPION | MB | 42 | 0.000424 | north | N | -0.0041292 | 0.0004252 | 0.028057 | 0.0001145 | 0.0001145 | houston | Y | 0.0041292 | 0
3381 | BBRN_1G | 1 | 615 | 0.000467 | north | Y | -0.0040862 | 0.0004682 | 0.0281 | 0.0001575 | 0.0001575 | houston | Y | 0.0040862 | 2.4162
3382 | BBRN_2G | 2 | 587 | 0.000467 | north | Y | -0.0040862 | 0.0004682 | 0.0281 | 0.0001575 | 0.0001575 | houston | Y | 0.0040862 | 2.3062
3403 | THOUSE_1 | MB | 537 | 0.001265 | north | Y | -0.0032882 | 0.0012662 | 0.028898 | 0.0009555 | 0.0009555 | houston | Y | 0.0032882 | 0
3404 | THOUSE_2 | 2 | 787 | 0.001265 | north | Y | -0.0032882 | 0.0012662 | 0.028898 | 0.0009555 | 0.0009555 | houston | Y | 0.0032882 | 1.8358
3416 | LAKE_CRK | MB | 75 | 0.001393 | north | Y | -0.0031602 | 0.0013942 | 0.029026 | 0.0010835 | 0.0010835 | houston | Y | 0.0031602 | 0
3417 | LAKE_CRK | MB | 222 | 0.001393 | north | Y | -0.0031602 | 0.0013942 | 0.029026 | 0.0010835 | 0.0010835 | houston | Y | 0.0031602 | 0
3432 | SANDOW_4 | 4 | 569 | 0.000637 | south | Y | -0.0039162 | 0.0006382 | 0.02827 | 0.0003275 | 0.0003275 | houston | Y | 0.0006382 | 0.17678
5026 | BRAUNIG_ | 1 | 209 | -0.000152 | south | Y | -0.0047052 | -0.0001508 | 0.027481 | -0.0004615 | 0.0001508 | south | N | 0.0001508 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.000152 | south | Y | -0.0047052 | -0.0001508 | 0.027481 | -0.0004615 | 0.0001508 | south | N | 0.0001508 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.000166 | south | Y | -0.0047192 | -0.0001648 | 0.027467 | -0.0004755 | 0.0001648 | south | N | 0.0001648 | 0
5031 | BRA_VHBC | 1 | 46 | -0.000152 | south | Y | -0.0047052 | -0.0001508 | 0.027481 | -0.0004615 | 0.0001508 | south | N | 0.0001508 | 0
5032 | BRA_VHBC | 2 | 47 | -0.000152 | south | Y | -0.0047052 | -0.0001508 | 0.027481 | -0.0004615 | 0.0001508 | south | N | 0.0001508 | 0
5033 | BRA_VHBC | 3 | 46 | -0.000152 | south | Y | -0.0047052 | -0.0001508 | 0.027481 | -0.0004615 | 0.0001508 | south | N | 0.0001508 | 0
5034 | BRA_VHBC | 4 | 46 | -0.000152 | south | Y | -0.0047052 | -0.0001508 | 0.027481 | -0.0004615 | 0.0001508 | south | N | 0.0001508 | 0
5111 | CALAVER_ | 1 | 424 | -0.000143 | south | Y | -0.0046962 | -0.0001418 | 0.02749 | -0.0004525 | 0.0001418 | south | N | 0.0001418 | 0
5112 | CALAVER_ | 2 | 425 | -0.000143 | south | Y | -0.0046962 | -0.0001418 | 0.02749 | -0.0004525 | 0.0001418 | south | N | 0.0001418 | 0
5264 | LEON_LCP | 3 | 58 | -0.00021 | south | Y | -0.0047632 | -0.0002088 | 0.027423 | -0.0005195 | 0.0002088 | south | N | 0.0002088 | 0
5265 | LEON_LCP | 4 | 89 | -0.00021 | south | Y | -0.0047632 | -0.0002088 | 0.027423 | -0.0005195 | 0.0002088 | south | N | 0.0002088 | 0
5266 | LEON_LCP | 1 | 44 | -0.00021 | south | Y | -0.0047632 | -0.0002088 | 0.027423 | -0.0005195 | 0.0002088 | south | N | 0.0002088 | 0
5267 | LEON_LCP | 2 | 44 | -0.00021 | south | Y | -0.0047632 | -0.0002088 | 0.027423 | -0.0005195 | 0.0002088 | south | N | 0.0002088 | 0
5268 | LEON_LCP | 3 | 43 | -0.00021 | south | Y | -0.0047632 | -0.0002088 | 0.027423 | -0.0005195 | 0.0002088 | south | N | 0.0002088 | 0
5269 | LEON_LCP | 4 | 45 | -0.00021 | south | Y | -0.0047632 | -0.0002088 | 0.027423 | -0.0005195 | 0.0002088 | south | N | 0.0002088 | 0
5396 | CALAVER_ | 1 | 412 | -0.000151 | south | Y | -0.0047042 | -0.0001498 | 0.027482 | -0.0004605 | 0.0001498 | south | N | 0.0001498 | 0
5397 | CALAVER_ | 2 | 400 | -0.000151 | south | Y | -0.0047042 | -0.0001498 | 0.027482 | -0.0004605 | 0.0001498 | south | N | 0.0001498 | 0
5401 | CALAVER_ | 1 | 546 | -9.5e-05 | south | Y | -0.0046482 | -9.3804e-05 | 0.027538 | -0.0004045 | 9.3804e-05 | south | N | 9.3804e-05 | 0
5402 | CALAVER_ | 2 | 750 | -9.5e-05 | south | Y | -0.0046482 | -9.3804e-05 | 0.027538 | -0.0004045 | 9.3804e-05 | south | N | 9.3804e-05 | 0
5436 | TUTTL_WB | MB | 61 | -0.000112 | south | Y | -0.0046652 | -0.0001108 | 0.027521 | -0.0004215 | 0.0001108 | south | N | 0.0001108 | 0
5438 | TUTTL_WB | MB | 95 | -0.000112 | south | Y | -0.0046652 | -0.0001108 | 0.027521 | -0.0004215 | 0.0001108 | south | N | 0.0001108 | 0
5439 | TUTTL_WB | MB | 151 | -0.000112 | south | Y | -0.0046652 | -0.0001108 | 0.027521 | -0.0004215 | 0.0001108 | south | N | 0.0001108 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.000106 | south | Y | -0.0046592 | -0.0001048 | 0.027527 | -0.0004155 | 0.0001048 | south | N | 0.0001048 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.000106 | south | Y | -0.0046592 | -0.0001048 | 0.027527 | -0.0004155 | 0.0001048 | south | N | 0.0001048 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.000106 | south | Y | -0.0046592 | -0.0001048 | 0.027527 | -0.0004155 | 0.0001048 | south | N | 0.0001048 | 0
5503 | RAYBURNG | 1 | 22 | -6.3e-05 | south | Y | -0.0046162 | -6.1804e-05 | 0.02757 | -0.0003725 | 6.1804e-05 | south | N | 6.1804e-05 | 0
5505 | RAYBURNG | 1 | 11 | -6.3e-05 | south | Y | -0.0046162 | -6.1804e-05 | 0.02757 | -0.0003725 | 6.1804e-05 | south | N | 6.1804e-05 | 0
5506 | RAYBURNG | 1 | 11 | -6.3e-05 | south | Y | -0.0046162 | -6.1804e-05 | 0.02757 | -0.0003725 | 6.1804e-05 | south | N | 6.1804e-05 | 0
5508 | RAYBURNC | 1 | 47.7 | -4.3e-05 | south | Y | -0.0045962 | -4.1804e-05 | 0.02759 | -0.0003525 | 4.1804e-05 | south | N | 4.1804e-05 | 0
5509 | RAYBURNC | 1 | 37.3 | -4.3e-05 | south | Y | -0.0045962 | -4.1804e-05 | 0.02759 | -0.0003525 | 4.1804e-05 | south | N | 4.1804e-05 | 0
5511 | RAYBURNC | 1 | 46 | -4.3e-05 | south | Y | -0.0045962 | -4.1804e-05 | 0.02759 | -0.0003525 | 4.1804e-05 | south | N | 4.1804e-05 | 0
5512 | RAYBURNC | 1 | 48 | -4.3e-05 | south | Y | -0.0045962 | -4.1804e-05 | 0.02759 | -0.0003525 | 4.1804e-05 | south | N | 4.1804e-05 | 0
5728 | FALCONHY | 2 | 12 | -0.000363 | south | N | -0.0049162 | -0.0003618 | 0.02727 | -0.0006725 | 0.0003618 | south | N | 0.0003618 | 0
5729 | FALCONHY | 3 | 11 | -0.000363 | south | N | -0.0049162 | -0.0003618 | 0.02727 | -0.0006725 | 0.0003618 | south | N | 0.0003618 | 0
5890 | PEARSALL | 1 | 24 | -0.001073 | south | Y | -0.0056262 | -0.0010718 | 0.02656 | -0.0013825 | 0.0010718 | south | N | 0.0010718 | 0
5891 | PEARSALL | 1 | 24 | -0.001073 | south | Y | -0.0056262 | -0.0010718 | 0.02656 | -0.0013825 | 0.0010718 | south | N | 0.0010718 | 0
5892 | PEARSALL | 1 | 23 | -0.001073 | south | Y | -0.0056262 | -0.0010718 | 0.02656 | -0.0013825 | 0.0010718 | south | N | 0.0010718 | 0
5903 | SANMIGUE | 1 | 396 | -0.00019 | south | Y | -0.0047432 | -0.0001888 | 0.027443 | -0.0004995 | 0.0001888 | south | N | 0.0001888 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.000205 | houston | N | -0.0043482 | 0.0002062 | 0.027838 | -0.0001045 | 0.0001045 | houston | N | 0.0001045 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.000205 | houston | N | -0.0043482 | 0.0002062 | 0.027838 | -0.0001045 | 0.0001045 | houston | N | 0.0001045 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | Y | 0.0045532 | 0
5932 | SI_RAY9 | 9 | 38 | -0.000137 | south | Y | -0.0046902 | -0.0001358 | 0.027496 | -0.0004465 | 0.0001358 | south | N | 0.0001358 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.000137 | south | Y | -0.0046902 | -0.0001358 | 0.027496 | -0.0004465 | 0.0001358 | south | N | 0.0001358 | 0
5934 | SI_RAY5 | 5 | 15 | -0.000137 | south | Y | -0.0046902 | -0.0001358 | 0.027496 | -0.0004465 | 0.0001358 | south | N | 0.0001358 | 0
5935 | SI_RAY10 | 10 | 47 | -0.000137 | south | Y | -0.0046902 | -0.0001358 | 0.027496 | -0.0004465 | 0.0001358 | south | N | 0.0001358 | 0
6016 | SWMESA | 1 | 75 | -0.025268 | west | Y | -0.029821 | -0.025267 | 0.0023654 | -0.025577 | 0.0023654 | west | N | 0.0023654 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | Y | 0.027633 | 0
6144 | MCADOO1A | 1 | 150 | -0.036236 | west | Y | -0.040789 | -0.036235 | -0.0086026 | -0.036545 | 0.0086026 | west | N | 0.0086026 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.025094 | west | Y | -0.029647 | -0.025093 | 0.0025394 | -0.025403 | 0.0025394 | west | N | 0.0025394 | 0
6476 | LANGFORD | 1 | 150 | -0.01821 | west | Y | -0.022763 | -0.018209 | 0.0094234 | -0.018519 | 0.0094234 | west | N | 0.0094234 | 0
6637 | SNYDERW1 | 1 | 63 | -0.029694 | west | Y | -0.034247 | -0.029693 | -0.0020606 | -0.030003 | 0.0020606 | west | N | 0.0020606 | 0
6752 | OKLA0A | 1 | 649.7 | -0.029354 | west | Y | -0.033907 | -0.029353 | -0.0017206 | -0.029663 | 0.0017206 | west | N | 0.0017206 | 0
6948 | DENISNDM | 1 | 40 | 0.001299 | north | N | -0.0032542 | 0.0013002 | 0.028932 | 0.0009895 | 0.0009895 | houston | Y | 0.0032542 | 0
6948 | DENISNDM | 2 | 40 | 0.001299 | north | N | -0.0032542 | 0.0013002 | 0.028932 | 0.0009895 | 0.0009895 | houston | Y | 0.0032542 | 0
7000 | L_FERGUS | 1 | 422 | -0.000525 | south | Y | -0.0050782 | -0.0005238 | 0.027108 | -0.0008345 | 0.0005238 | south | N | 0.0005238 | 0
7004 | L_SIMGID | 1 | 132 | 0.000307 | south | Y | -0.0042462 | 0.0003082 | 0.02794 | -2.4978e-06 | 2.4978e-06 | houston | Y | 0.0003082 | 0.040352
7005 | L_SIMGID | 2 | 134 | 0.000307 | south | Y | -0.0042462 | 0.0003082 | 0.02794 | -2.4978e-06 | 2.4978e-06 | houston | Y | 0.0003082 | 0.040964
7006 | L_SIMGID | 3 | 323 | 0.000307 | south | Y | -0.0042462 | 0.0003082 | 0.02794 | -2.4978e-06 | 2.4978e-06 | houston | Y | 0.0003082 | 0.09874
7007 | L_LOSTPI | 1 | 158 | 0.000332 | south | Y | -0.0042212 | 0.0003332 | 0.027965 | 2.2502e-05 | 2.2502e-05 | houston | Y | 0.0003332 | 0.04909
7008 | L_LOSTPI | 2 | 160 | 0.000332 | south | Y | -0.0042212 | 0.0003332 | 0.027965 | 2.2502e-05 | 2.2502e-05 | houston | Y | 0.0003332 | 0.049711
7009 | L_LOSTPI | 3 | 175 | 0.000332 | south | Y | -0.0042212 | 0.0003332 | 0.027965 | 2.2502e-05 | 2.2502e-05 | houston | Y | 0.0003332 | 0.054371
7010 | L_FPPYD1 | 1 | 584 | 0.000286 | south | Y | -0.0042672 | 0.0002872 | 0.027919 | -2.3498e-05 | 2.3498e-05 | houston | Y | 0.0002872 | 0.154
7011 | L_FPPYD1 | 2 | 595 | 0.000286 | south | Y | -0.0042672 | 0.0002872 | 0.027919 | -2.3498e-05 | 2.3498e-05 | houston | Y | 0.0002872 | 0.1569
7012 | L_FPPYD2 | 3 | 433 | 0.000285 | south | Y | -0.0042682 | 0.0002862 | 0.027918 | -2.4498e-05 | 2.4498e-05 | houston | Y | 0.0002862 | 0.11332
7014 | L_HAYSEN | 1 | 223.9 | 6e-05 | south | Y | -0.0044932 | 6.1196e-05 | 0.027693 | -0.0002495 | 6.1196e-05 | south | N | 6.1196e-05 | 0
7015 | L_HAYSEN | 2 | 225 | 6e-05 | south | Y | -0.0044932 | 6.1196e-05 | 0.027693 | -0.0002495 | 6.1196e-05 | south | N | 6.1196e-05 | 0
7016 | L_HAYSEN | 3 | 224.6 | 6e-05 | south | Y | -0.0044932 | 6.1196e-05 | 0.027693 | -0.0002495 | 6.1196e-05 | south | N | 6.1196e-05 | 0
7017 | L_HAYSEN | 4 | 226.7 | 6e-05 | south | Y | -0.0044932 | 6.1196e-05 | 0.027693 | -0.0002495 | 6.1196e-05 | south | N | 6.1196e-05 | 0
7020 | L_AUSTPL | 1 | 8 | 0.000272 | south | N | -0.0042812 | 0.0002732 | 0.027905 | -3.7498e-05 | 3.7498e-05 | houston | Y | 0.0002732 | 0
7020 | L_AUSTPL | 2 | 8 | 0.000272 | south | N | -0.0042812 | 0.0002732 | 0.027905 | -3.7498e-05 | 3.7498e-05 | houston | Y | 0.0002732 | 0
7022 | L_BUCHAN | 1 | 18 | -0.000381 | south | N | -0.0049342 | -0.0003798 | 0.027252 | -0.0006905 | 0.0003798 | south | N | 0.0003798 | 0
7023 | L_BUCHAN | 2 | 18 | -0.000381 | south | N | -0.0049342 | -0.0003798 | 0.027252 | -0.0006905 | 0.0003798 | south | N | 0.0003798 | 0
7024 | L_BUCHAN | 3 | 15 | -0.000381 | south | N | -0.0049342 | -0.0003798 | 0.027252 | -0.0006905 | 0.0003798 | south | N | 0.0003798 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.000743 | south | N | -0.0052962 | -0.0007418 | 0.02689 | -0.0010525 | 0.0007418 | south | N | 0.0007418 | 0
7028 | L_MARBFA | 1 | 18 | -0.000335 | south | N | -0.0048882 | -0.0003338 | 0.027298 | -0.0006445 | 0.0003338 | south | N | 0.0003338 | 0
7029 | L_MARBFA | 2 | 18 | -0.000335 | south | N | -0.0048882 | -0.0003338 | 0.027298 | -0.0006445 | 0.0003338 | south | N | 0.0003338 | 0
7031 | L_MARSFO | 1 | 35 | 9.5e-05 | south | N | -0.0044582 | 9.6196e-05 | 0.027728 | -0.0002145 | 9.6196e-05 | south | N | 9.6196e-05 | 0
7032 | L_MARSFO | 2 | 34 | 9.5e-05 | south | N | -0.0044582 | 9.6196e-05 | 0.027728 | -0.0002145 | 9.6196e-05 | south | N | 9.6196e-05 | 0
7033 | L_MARSFO | 3 | 35 | 9.5e-05 | south | N | -0.0044582 | 9.6196e-05 | 0.027728 | -0.0002145 | 9.6196e-05 | south | N | 9.6196e-05 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.000458 | south | N | -0.0050112 | -0.0004568 | 0.027175 | -0.0007675 | 0.0004568 | south | N | 0.0004568 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.000458 | south | N | -0.0050112 | -0.0004568 | 0.027175 | -0.0007675 | 0.0004568 | south | N | 0.0004568 | 0
7038 | L_DELAWA | 1 | 35 | -0.027128 | west | Y | -0.031681 | -0.027127 | 0.0005054 | -0.027437 | 0.0005054 | west | N | 0.0005054 | 0
7038 | L_DELAWA | 2 | 30 | -0.027128 | west | Y | -0.031681 | -0.027127 | 0.0005054 | -0.027437 | 0.0005054 | west | N | 0.0005054 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.000282 | south | Y | -0.0042712 | 0.0002832 | 0.027915 | -2.7498e-05 | 2.7498e-05 | houston | Y | 0.0002832 | 0.012785
7303 | L_WPPGS1 | 2 | 50 | 0.000282 | south | Y | -0.0042712 | 0.0002832 | 0.027915 | -2.7498e-05 | 2.7498e-05 | houston | Y | 0.0002832 | 0.012785
7305 | L_WPPGS3 | 3 | 50 | 0.000282 | south | Y | -0.0042712 | 0.0002832 | 0.027915 | -2.7498e-05 | 2.7498e-05 | houston | Y | 0.0002832 | 0.012785
7305 | L_WPPGS3 | 4 | 50 | 0.000282 | south | Y | -0.0042712 | 0.0002832 | 0.027915 | -2.7498e-05 | 2.7498e-05 | houston | Y | 0.0002832 | 0.012785
7487 | L_CANYHY | 1 | 6 | 3.7e-05 | south | N | -0.0045162 | 3.8196e-05 | 0.02767 | -0.0002725 | 3.8196e-05 | south | N | 3.8196e-05 | 0
7605 | L_MCQUEE | 1 | 2.4 | 2.7e-05 | south | N | -0.0045262 | 2.8196e-05 | 0.02766 | -0.0002825 | 2.8196e-05 | south | N | 2.8196e-05 | 0
7605 | L_MCQUEE | 2 | 2.4 | 2.7e-05 | south | N | -0.0045262 | 2.8196e-05 | 0.02766 | -0.0002825 | 2.8196e-05 | south | N | 2.8196e-05 | 0
7605 | L_MCQUEE | 3 | 2.8 | 2.7e-05 | south | N | -0.0045262 | 2.8196e-05 | 0.02766 | -0.0002825 | 2.8196e-05 | south | N | 2.8196e-05 | 0
7609 | L_SCHUMA | 1 | 4 | -1.8e-05 | south | N | -0.0045712 | -1.6804e-05 | 0.027615 | -0.0003275 | 1.6804e-05 | south | N | 1.6804e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | 5.7e-05 | south | N | -0.0044962 | 5.8196e-05 | 0.02769 | -0.0002525 | 5.8196e-05 | south | N | 5.8196e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | 5.7e-05 | south | N | -0.0044962 | 5.8196e-05 | 0.02769 | -0.0002525 | 5.8196e-05 | south | N | 5.8196e-05 | 0
7800 | L_GUADGE | 1 | 147 | -1.8e-05 | south | Y | -0.0045712 | -1.6804e-05 | 0.027615 | -0.0003275 | 1.6804e-05 | south | N | 1.6804e-05 | 0
7801 | L_GUADGE | 2 | 138 | -1.8e-05 | south | Y | -0.0045712 | -1.6804e-05 | 0.027615 | -0.0003275 | 1.6804e-05 | south | N | 1.6804e-05 | 0
7802 | L_GUADGE | 3 | 140 | -1.8e-05 | south | Y | -0.0045712 | -1.6804e-05 | 0.027615 | -0.0003275 | 1.6804e-05 | south | N | 1.6804e-05 | 0
7803 | L_GUADGE | 4 | 147 | -1.8e-05 | south | Y | -0.0045712 | -1.6804e-05 | 0.027615 | -0.0003275 | 1.6804e-05 | south | N | 1.6804e-05 | 0
7804 | L_GUADGE | 5 | 182 | -1.8e-05 | south | Y | -0.0045712 | -1.6804e-05 | 0.027615 | -0.0003275 | 1.6804e-05 | south | N | 1.6804e-05 | 0
7805 | L_GUADGE | 6 | 198 | -1.8e-05 | south | Y | -0.0045712 | -1.6804e-05 | 0.027615 | -0.0003275 | 1.6804e-05 | south | N | 1.6804e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.000299 | south | Y | -0.0042542 | 0.0003002 | 0.027932 | -1.0498e-05 | 1.0498e-05 | houston | Y | 0.0003002 | 0.044179
7808 | L_BASTEN | 1 | 149.5 | 0.000299 | south | Y | -0.0042542 | 0.0003002 | 0.027932 | -1.0498e-05 | 1.0498e-05 | houston | Y | 0.0003002 | 0.04331
7809 | L_BASTEN | 1 | 232.6 | 0.000299 | south | Y | -0.0042542 | 0.0003002 | 0.027932 | -1.0498e-05 | 1.0498e-05 | houston | Y | 0.0003002 | 0.067384
7810 | L_RIONOG | 1 | 142 | 2.1e-05 | south | Y | -0.0045322 | 2.2196e-05 | 0.027654 | -0.0002885 | 2.2196e-05 | south | N | 2.2196e-05 | 0
7811 | L_RIONOG | 2 | 145 | 2.1e-05 | south | Y | -0.0045322 | 2.2196e-05 | 0.027654 | -0.0002885 | 2.2196e-05 | south | N | 2.2196e-05 | 0
7812 | L_RIONOG | 3 | 151 | 2.1e-05 | south | Y | -0.0045322 | 2.2196e-05 | 0.027654 | -0.0002885 | 2.2196e-05 | south | N | 2.2196e-05 | 0
7813 | L_RIONOG | 4 | 290 | 2.1e-05 | south | Y | -0.0045322 | 2.2196e-05 | 0.027654 | -0.0002885 | 2.2196e-05 | south | N | 2.2196e-05 | 0
8032 | AMISTADH | 1 | 33 | -0.007137 | south | N | -0.01169 | -0.0071358 | 0.020496 | -0.0074465 | 0.0071358 | south | N | 0.0071358 | 0
8033 | AMISTADH | 2 | 25 | -0.007137 | south | N | -0.01169 | -0.0071358 | 0.020496 | -0.0074465 | 0.0071358 | south | N | 0.0071358 | 0
8048 | FALCONHY | 1 | 12 | -0.000363 | south | N | -0.0049162 | -0.0003618 | 0.02727 | -0.0006725 | 0.0003618 | south | N | 0.0003618 | 0
8066 | DUP1V#1 | 1 | 73 | -2.6e-05 | south | N | -0.0045792 | -2.4804e-05 | 0.027607 | -0.0003355 | 2.4804e-05 | south | N | 2.4804e-05 | 0
8134 | FOR69CG0 | 1 | 79 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
8138 | FOR69CG0 | 2 | 81 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | N | 1.1955e-06 | 0
8147 | UCAR #2 | 10 | 28 | -1.6e-05 | south | N | -0.0045692 | -1.4804e-05 | 0.027617 | -0.0003255 | 1.4804e-05 | south | N | 1.4804e-05 | 0
8148 | UCAR #1 | 2 | 7 | -1.6e-05 | south | N | -0.0045692 | -1.4804e-05 | 0.027617 | -0.0003255 | 1.4804e-05 | south | N | 1.4804e-05 | 0
8153 | FOR69CG0 | 3 | 79 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
8154 | FOR69CG0 | 4 | 80 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
8155 | FOR69CG0 | 5 | 78.4 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
8156 | FOR69CG0 | 6 | 25 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
8157 | FOR69CG0 | 7 | 46 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
8161 | COLETOU1 | 1 | 629 | -9e-05 | south | Y | -0.0046432 | -8.8804e-05 | 0.027543 | -0.0003995 | 8.8804e-05 | south | N | 8.8804e-05 | 0
8173 | VICEC51A | 5 | 144 | -3.1e-05 | south | Y | -0.0045842 | -2.9804e-05 | 0.027602 | -0.0003405 | 2.9804e-05 | south | N | 2.9804e-05 | 0
8174 | VICEC61A | 6 | 188 | -3.1e-05 | south | Y | -0.0045842 | -2.9804e-05 | 0.027602 | -0.0003405 | 2.9804e-05 | south | N | 2.9804e-05 | 0
8189 | CUERO 2 | 1 | 12 | 2.8e-05 | south | N | -0.0045252 | 2.9196e-05 | 0.027661 | -0.0002815 | 2.9196e-05 | south | N | 2.9196e-05 | 0
8262 | ELPS | 1 | 6 | -0.005211 | south | N | -0.0097642 | -0.0052098 | 0.022422 | -0.0055205 | 0.0052098 | south | N | 0.0052098 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | N | 1.1955e-06 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | N | 1.1955e-06 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | N | 1.1955e-06 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | N | 1.1955e-06 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | N | 1.1955e-06 | 0
8442 | NBEC71A | 1 | 336 | -0.000108 | south | Y | -0.0046612 | -0.0001068 | 0.027525 | -0.0004175 | 0.0001068 | south | N | 0.0001068 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | N | 1.1955e-06 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.0045532 | 1.1955e-06 | 0.027633 | -0.0003095 | 1.1955e-06 | south | N | 1.1955e-06 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.00011 | south | Y | -0.0046632 | -0.0001088 | 0.027523 | -0.0004195 | 0.0001088 | south | N | 0.0001088 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.00011 | south | Y | -0.0046632 | -0.0001088 | 0.027523 | -0.0004195 | 0.0001088 | south | N | 0.0001088 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.000114 | south | N | -0.0046672 | -0.0001128 | 0.027519 | -0.0004235 | 0.0001128 | south | N | 0.0001128 | 0
8506 | VAL #1 | 1 | 25 | -0.000112 | south | N | -0.0046652 | -0.0001108 | 0.027521 | -0.0004215 | 0.0001108 | south | N | 0.0001108 | 0
8507 | VAL #2 | 2 | 25 | -0.000112 | south | N | -0.0046652 | -0.0001108 | 0.027521 | -0.0004215 | 0.0001108 | south | N | 0.0001108 | 0
8511 | OXY_CC0A | 1 | 38 | -0.000112 | south | N | -0.0046652 | -0.0001108 | 0.027521 | -0.0004215 | 0.0001108 | south | N | 0.0001108 | 0
8517 | CELANEBI | 1 | 29 | -0.000122 | south | N | -0.0046752 | -0.0001208 | 0.027511 | -0.0004315 | 0.0001208 | south | N | 0.0001208 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.000108 | south | N | -0.0046612 | -0.0001068 | 0.027525 | -0.0004175 | 0.0001068 | south | N | 0.0001068 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.000108 | south | N | -0.0046612 | -0.0001068 | 0.027525 | -0.0004175 | 0.0001068 | south | N | 0.0001068 | 0
8562 | CNOPST1 | 3 | 153 | -0.000108 | south | N | -0.0046612 | -0.0001068 | 0.027525 | -0.0004175 | 0.0001068 | south | N | 0.0001068 | 0
8926 | LGE_GT10 | 1 | 158 | -9.4e-05 | south | N | -0.0046472 | -9.2804e-05 | 0.027539 | -0.0004035 | 9.2804e-05 | south | N | 9.2804e-05 | 0
8927 | LGE_GT20 | 2 | 153 | -9.4e-05 | south | N | -0.0046472 | -9.2804e-05 | 0.027539 | -0.0004035 | 9.2804e-05 | south | N | 9.2804e-05 | 0
8928 | LGE_STG0 | 3 | 100 | -9.4e-05 | south | N | -0.0046472 | -9.2804e-05 | 0.027539 | -0.0004035 | 9.2804e-05 | south | N | 9.2804e-05 | 0
8930 | ICPGN10A | 1 | 145 | -9.4e-05 | south | N | -0.0046472 | -9.2804e-05 | 0.027539 | -0.0004035 | 9.2804e-05 | south | N | 9.2804e-05 | 0
8931 | ICPGN20A | 2 | 147 | -9.4e-05 | south | N | -0.0046472 | -9.2804e-05 | 0.027539 | -0.0004035 | 9.2804e-05 | south | N | 9.2804e-05 | 0
8932 | ICPGN30A | 3 | 127 | -9.4e-05 | south | N | -0.0046472 | -9.2804e-05 | 0.027539 | -0.0004035 | 9.2804e-05 | south | N | 9.2804e-05 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.000184 | south | Y | -0.0047372 | -0.0001828 | 0.027449 | -0.0004935 | 0.0001828 | south | N | 0.0001828 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.000184 | south | Y | -0.0047372 | -0.0001828 | 0.027449 | -0.0004935 | 0.0001828 | south | N | 0.0001828 | 0
8935 | FGNTS201 | 3 | 173 | -0.000184 | south | Y | -0.0047372 | -0.0001828 | 0.027449 | -0.0004935 | 0.0001828 | south | N | 0.0001828 | 0
8936 | MVGN#1 | 1 | 207 | -0.000155 | south | Y | -0.0047082 | -0.0001538 | 0.027478 | -0.0004645 | 0.0001538 | south | N | 0.0001538 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.000155 | south | Y | -0.0047082 | -0.0001538 | 0.027478 | -0.0004645 | 0.0001538 | south | N | 0.0001538 | 0
8938 | MVGN#3 | 3 | 242 | -0.000155 | south | Y | -0.0047082 | -0.0001538 | 0.027478 | -0.0004645 | 0.0001538 | south | N | 0.0001538 | 0
8981 | HECN1 | 1 | 144 | -0.000154 | south | Y | -0.0047072 | -0.0001528 | 0.027479 | -0.0004635 | 0.0001528 | south | N | 0.0001528 | 0
8982 | HECN2 | 2 | 144 | -0.000154 | south | Y | -0.0047072 | -0.0001528 | 0.027479 | -0.0004635 | 0.0001528 | south | N | 0.0001528 | 0
8983 | HECN3 | 3 | 171 | -0.000154 | south | Y | -0.0047072 | -0.0001528 | 0.027479 | -0.0004635 | 0.0001528 | south | N | 0.0001528 | 0
9000 | DECKR_G1 | 1 | 310 | 0.000289 | south | Y | -0.0042642 | 0.0002902 | 0.027922 | -2.0498e-05 | 2.0498e-05 | houston | Y | 0.0002902 | 0.083606
9001 | DECKR_G2 | 2 | 413 | 0.000289 | south | Y | -0.0042642 | 0.0002902 | 0.027922 | -2.0498e-05 | 2.0498e-05 | houston | Y | 0.0002902 | 0.11139
9002 | DECKR_G3 | 3 | 42 | 0.00031 | south | Y | -0.0042432 | 0.0003112 | 0.027943 | 5.0225e-07 | 5.0225e-07 | houston | Y | 0.0003112 | 0.013049
9003 | DECKR_G4 | 4 | 44 | 0.00031 | south | Y | -0.0042432 | 0.0003112 | 0.027943 | 5.0225e-07 | 5.0225e-07 | houston | Y | 0.0003112 | 0.013671
9004 | DECKR_G5 | 5 | 44 | 0.00031 | south | Y | -0.0042432 | 0.0003112 | 0.027943 | 5.0225e-07 | 5.0225e-07 | houston | Y | 0.0003112 | 0.013671
9005 | DECKR_G6 | 6 | 47 | 0.00031 | south | Y | -0.0042432 | 0.0003112 | 0.027943 | 5.0225e-07 | 5.0225e-07 | houston | Y | 0.0003112 | 0.014603
9016 | SANDH_G1 | 1 | 49 | 0.000275 | south | Y | -0.0042782 | 0.0002762 | 0.027908 | -3.4498e-05 | 3.4498e-05 | houston | Y | 0.0002762 | 0.011843
9017 | SANDH_G2 | 2 | 46 | 0.000275 | south | Y | -0.0042782 | 0.0002762 | 0.027908 | -3.4498e-05 | 3.4498e-05 | houston | Y | 0.0002762 | 0.011118
9018 | SANDH_G3 | 3 | 46 | 0.000275 | south | Y | -0.0042782 | 0.0002762 | 0.027908 | -3.4498e-05 | 3.4498e-05 | houston | Y | 0.0002762 | 0.011118
9019 | SANDH_G4 | 4 | 47 | 0.000275 | south | Y | -0.0042782 | 0.0002762 | 0.027908 | -3.4498e-05 | 3.4498e-05 | houston | Y | 0.0002762 | 0.01136
9020 | SANDHG5A | 5A | 154 | 0.000275 | south | Y | -0.0042782 | 0.0002762 | 0.027908 | -3.4498e-05 | 3.4498e-05 | houston | Y | 0.0002762 | 0.037221
9021 | SANDHG5C | 5C | 148 | 0.000275 | south | Y | -0.0042782 | 0.0002762 | 0.027908 | -3.4498e-05 | 3.4498e-05 | houston | Y | 0.0002762 | 0.035771
9022 | SANDH_G6 | 6 | 48 | 0.000275 | south | Y | -0.0042782 | 0.0002762 | 0.027908 | -3.4498e-05 | 3.4498e-05 | houston | Y | 0.0002762 | 0.011601
9023 | SANDH_G7 | 7 | 48 | 0.000275 | south | Y | -0.0042782 | 0.0002762 | 0.027908 | -3.4498e-05 | 3.4498e-05 | houston | Y | 0.0002762 | 0.011601
11001 | NAV1CT | 1 | 70 | -0.027236 | west | Y | -0.031789 | -0.027235 | 0.0003974 | -0.027545 | 0.0003974 | west | N | 0.0003974 | 0
11009 | NAV2CT | 1 | 70 | -0.027236 | west | Y | -0.031789 | -0.027235 | 0.0003974 | -0.027545 | 0.0003974 | west | N | 0.0003974 | 0
11011 | NAV3ST | 1 | 92.8 | -0.027236 | west | Y | -0.031789 | -0.027235 | 0.0003974 | -0.027545 | 0.0003974 | west | N | 0.0003974 | 0
11012 | NAV4CT | 1 | 80 | -0.027236 | west | Y | -0.031789 | -0.027235 | 0.0003974 | -0.027545 | 0.0003974 | west | N | 0.0003974 | 0
11013 | NAV5CT | 1 | 80 | -0.027236 | west | Y | -0.031789 | -0.027235 | 0.0003974 | -0.027545 | 0.0003974 | west | N | 0.0003974 | 0
11014 | NAV6ST | 1 | 115 | -0.027236 | west | Y | -0.031789 | -0.027235 | 0.0003974 | -0.027545 | 0.0003974 | west | N | 0.0003974 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.027235 | west | Y | -0.031788 | -0.027234 | 0.0003984 | -0.027544 | 0.0003984 | west | N | 0.0003984 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.027235 | west | Y | -0.031788 | -0.027234 | 0.0003984 | -0.027544 | 0.0003984 | west | N | 0.0003984 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.027235 | west | Y | -0.031788 | -0.027234 | 0.0003984 | -0.027544 | 0.0003984 | west | N | 0.0003984 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.027235 | west | Y | -0.031788 | -0.027234 | 0.0003984 | -0.027544 | 0.0003984 | west | N | 0.0003984 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.027235 | west | Y | -0.031788 | -0.027234 | 0.0003984 | -0.027544 | 0.0003984 | west | N | 0.0003984 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.027235 | west | Y | -0.031788 | -0.027234 | 0.0003984 | -0.027544 | 0.0003984 | west | N | 0.0003984 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.027843 | west | Y | -0.032396 | -0.027842 | -0.0002096 | -0.028152 | 0.0002096 | west | N | 0.0002096 | 0
11057 | CHAMPION | 1 | 126.5 | -0.027843 | west | Y | -0.032396 | -0.027842 | -0.0002096 | -0.028152 | 0.0002096 | west | N | 0.0002096 | 0
11058 | PYRON_1G | 1 | 249 | -0.027843 | west | Y | -0.032396 | -0.027842 | -0.0002096 | -0.028152 | 0.0002096 | west | N | 0.0002096 | 0
11059 | INADALE_ | 1 | 197 | -0.027843 | west | Y | -0.032396 | -0.027842 | -0.0002096 | -0.028152 | 0.0002096 | west | N | 0.0002096 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.027408 | west | Y | -0.031961 | -0.027407 | 0.0002254 | -0.027717 | 0.0002254 | west | N | 0.0002254 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.027408 | west | Y | -0.031961 | -0.027407 | 0.0002254 | -0.027717 | 0.0002254 | west | N | 0.0002254 | 0
11147 | NOTREES_ | 1 | 149 | -0.027311 | west | Y | -0.031864 | -0.02731 | 0.0003224 | -0.02762 | 0.0003224 | west | N | 0.0003224 | 0
11309 | BULLCREK | 1 | 180 | -0.029234 | west | Y | -0.033787 | -0.029233 | -0.0016006 | -0.029543 | 0.0016006 | west | N | 0.0016006 | 0
11310 | BULLCREK | 1 | 180 | -0.029234 | west | Y | -0.033787 | -0.029233 | -0.0016006 | -0.029543 | 0.0016006 | west | N | 0.0016006 | 0
11320 | COYOTE_1 | 1 | 225 | -0.029156 | west | Y | -0.033709 | -0.029155 | -0.0015226 | -0.029465 | 0.0015226 | west | N | 0.0015226 | 0
11415 | LORAINE_ | 1 | 125 | -0.027625 | west | Y | -0.032178 | -0.027624 | 8.4024e-06 | -0.027934 | 8.4024e-06 | west | N | 8.4024e-06 | 0
11416 | LORAINE_ | 1 | 125 | -0.027625 | west | Y | -0.032178 | -0.027624 | 8.4024e-06 | -0.027934 | 8.4024e-06 | west | N | 8.4024e-06 | 0
11691 | KMICHICT | 1 | 140 | 0.000484 | north | N | -0.0040692 | 0.0004852 | 0.028117 | 0.0001745 | 0.0001745 | houston | Y | 0.0040692 | 0
11692 | KMICHICT | 2 | 141 | 0.000484 | north | N | -0.0040692 | 0.0004852 | 0.028117 | 0.0001745 | 0.0001745 | houston | Y | 0.0040692 | 0
11693 | KMICHIST | 3 | 309 | 0.000484 | north | N | -0.0040692 | 0.0004852 | 0.028117 | 0.0001745 | 0.0001745 | houston | Y | 0.0040692 | 0
11694 | KMICHICT | 4 | 143 | 0.000484 | north | N | -0.0040692 | 0.0004852 | 0.028117 | 0.0001745 | 0.0001745 | houston | Y | 0.0040692 | 0
11695 | KMICHICT | 5 | 144 | 0.000484 | north | N | -0.0040692 | 0.0004852 | 0.028117 | 0.0001745 | 0.0001745 | houston | Y | 0.0040692 | 0
11696 | KMICHIST | 6 | 310 | 0.000484 | north | N | -0.0040692 | 0.0004852 | 0.028117 | 0.0001745 | 0.0001745 | houston | Y | 0.0040692 | 0
12322 | ENNSTRAC | 1 | 196 | 0.001318 | north | Y | -0.0032352 | 0.0013192 | 0.028951 | 0.0010085 | 0.0010085 | houston | Y | 0.0032352 | 0.43644
12323 | ENNSTRAC | 2 | 111 | 0.001318 | north | Y | -0.0032352 | 0.0013192 | 0.028951 | 0.0010085 | 0.0010085 | houston | Y | 0.0032352 | 0.24716
12357 | RNRTPL_1 | 1 | 0 | 0.00027 | north | N | -0.0042832 | 0.0002712 | 0.027903 | -3.9498e-05 | 3.9498e-05 | houston | Y | 0.0042832 | 0
12411 | FPLEFR1A | 1 | 161 | 0.000348 | north | Y | -0.0042052 | 0.0003492 | 0.027981 | 3.8502e-05 | 3.8502e-05 | houston | Y | 0.0042052 | 0.67084
12412 | FPLEFR1B | 2 | 164 | 0.000348 | north | Y | -0.0042052 | 0.0003492 | 0.027981 | 3.8502e-05 | 3.8502e-05 | houston | Y | 0.0042052 | 0.68334
12413 | FPLEFR1C | 3 | 164 | 0.000348 | north | Y | -0.0042052 | 0.0003492 | 0.027981 | 3.8502e-05 | 3.8502e-05 | houston | Y | 0.0042052 | 0.68334
12414 | FPLEFR1S | 4 | 414 | 0.000348 | north | Y | -0.0042052 | 0.0003492 | 0.027981 | 3.8502e-05 | 3.8502e-05 | houston | Y | 0.0042052 | 1.725
12421 | FPLEFR2A | 1 | 162 | 0.000348 | north | Y | -0.0042052 | 0.0003492 | 0.027981 | 3.8502e-05 | 3.8502e-05 | houston | Y | 0.0042052 | 0.67501
12422 | FPLEFR2B | 2 | 161 | 0.000348 | north | Y | -0.0042052 | 0.0003492 | 0.027981 | 3.8502e-05 | 3.8502e-05 | houston | Y | 0.0042052 | 0.67084
12423 | FPLEFR2C | 3 | 163 | 0.000348 | north | Y | -0.0042052 | 0.0003492 | 0.027981 | 3.8502e-05 | 3.8502e-05 | houston | Y | 0.0042052 | 0.67917
12424 | FPLEFR2S | 4 | 409 | 0.000348 | north | Y | -0.0042052 | 0.0003492 | 0.027981 | 3.8502e-05 | 3.8502e-05 | houston | Y | 0.0042052 | 1.7042
12440 | PARKD_1S | 1 | 0 | 0.000357 | north | N | -0.0041962 | 0.0003582 | 0.02799 | 4.7502e-05 | 4.7502e-05 | houston | Y | 0.0041962 | 0
12449 | PARKD_2S | 1 | 0 | 0.000357 | north | N | -0.0041962 | 0.0003582 | 0.02799 | 4.7502e-05 | 4.7502e-05 | houston | Y | 0.0041962 | 0
13116 | TGATEWAY | 1 | 148 | 0.000419 | north | N | -0.0041342 | 0.0004202 | 0.028052 | 0.0001095 | 0.0001095 | houston | Y | 0.0041342 | 0
13117 | TGATEWAY | 2 | 130 | 0.000419 | north | N | -0.0041342 | 0.0004202 | 0.028052 | 0.0001095 | 0.0001095 | houston | Y | 0.0041342 | 0
13118 | TGATEWAY | 3 | 145 | 0.000419 | north | N | -0.0041342 | 0.0004202 | 0.028052 | 0.0001095 | 0.0001095 | houston | Y | 0.0041342 | 0
13119 | TGATEWAY | 4 | 399 | 0.000419 | north | N | -0.0041342 | 0.0004202 | 0.028052 | 0.0001095 | 0.0001095 | houston | Y | 0.0041342 | 0
13131 | CALFREST | 1 | 150.7 | 0.000454 | north | Y | -0.0040992 | 0.0004552 | 0.028087 | 0.0001445 | 0.0001445 | houston | Y | 0.0040992 | 0.59597
13132 | CALFREST | 2 | 151 | 0.000454 | north | Y | -0.0040992 | 0.0004552 | 0.028087 | 0.0001445 | 0.0001445 | houston | Y | 0.0040992 | 0.59716
13133 | CALFREST | 3 | 177.4 | 0.000454 | north | Y | -0.0040992 | 0.0004552 | 0.028087 | 0.0001445 | 0.0001445 | houston | Y | 0.0040992 | 0.70157
13134 | CALFREST | 4 | 151.5 | 0.000464 | north | Y | -0.0040892 | 0.0004652 | 0.028097 | 0.0001545 | 0.0001545 | houston | Y | 0.0040892 | 0.59611
13135 | CALFREST | 5 | 152.3 | 0.000464 | north | Y | -0.0040892 | 0.0004652 | 0.028097 | 0.0001545 | 0.0001545 | houston | Y | 0.0040892 | 0.59926
13136 | CALFREST | 6 | 177.5 | 0.000464 | north | Y | -0.0040892 | 0.0004652 | 0.028097 | 0.0001545 | 0.0001545 | houston | Y | 0.0040892 | 0.69841
13432 | SANDOW_5 | 5 | 581 | 0.000637 | south | Y | -0.0039162 | 0.0006382 | 0.02827 | 0.0003275 | 0.0003275 | houston | Y | 0.0006382 | 0.18051
13691 | OAKGROVE | 1 | 855 | 0.000499 | north | Y | -0.0040542 | 0.0005002 | 0.028132 | 0.0001895 | 0.0001895 | houston | Y | 0.0040542 | 3.3043
13692 | OAKGROVE | 2 | 855 | 0.000499 | north | Y | -0.0040542 | 0.0005002 | 0.028132 | 0.0001895 | 0.0001895 | houston | Y | 0.0040542 | 3.3043
32798 | BRYN_TAM | 1 | 32 | 0.000492 | north | N | -0.0040612 | 0.0004932 | 0.028125 | 0.0001825 | 0.0001825 | houston | Y | 0.0040612 | 0
32883 | BRYN_DNS | 1 | 48 | 0.000502 | north | Y | -0.0040512 | 0.0005032 | 0.028135 | 0.0001925 | 0.0001925 | houston | Y | 0.0040512 | 0.18522
32884 | BRYN_DNS | 1 | 46 | 0.000502 | north | Y | -0.0040512 | 0.0005032 | 0.028135 | 0.0001925 | 0.0001925 | houston | Y | 0.0040512 | 0.1775
32886 | BRYN_ATK | MB | 12 | 0.000492 | north | Y | -0.0040612 | 0.0004932 | 0.028125 | 0.0001825 | 0.0001825 | houston | Y | 0.0040612 | 0
32887 | BRYN_ATK | MB | 51 | 0.000492 | north | Y | -0.0040612 | 0.0004932 | 0.028125 | 0.0001825 | 0.0001825 | houston | Y | 0.0040612 | 0
32888 | BRYN_ATK | 1 | 17 | 0.000492 | north | Y | -0.0040612 | 0.0004932 | 0.028125 | 0.0001825 | 0.0001825 | houston | Y | 0.0040612 | 0.065938
32890 | BRYN_ATK | MB | 22 | 0.000492 | north | Y | -0.0040612 | 0.0004932 | 0.028125 | 0.0001825 | 0.0001825 | houston | Y | 0.0040612 | 0
32891 | BRYN_ATK | MB | 25 | 0.000492 | north | Y | -0.0040612 | 0.0004932 | 0.028125 | 0.0001825 | 0.0001825 | houston | Y | 0.0040612 | 0
32892 | BRYN_DNS | 1 | 105 | 0.000502 | north | Y | -0.0040512 | 0.0005032 | 0.028135 | 0.0001925 | 0.0001925 | houston | Y | 0.0040512 | 0.40516
36998 | RDCNYNG1 | 1 | 84 | -0.031312 | west | Y | -0.035865 | -0.031311 | -0.0036786 | -0.031621 | 0.0036786 | west | N | 0.0036786 | 0
38332 | WDWRDU2 | 1 | 80 | -0.025242 | west | Y | -0.029795 | -0.025241 | 0.0023914 | -0.025551 | 0.0023914 | west | N | 0.0023914 | 0
38437 | TNSRBNMS | 1 | 150 | -0.025225 | west | Y | -0.029778 | -0.025224 | 0.0024084 | -0.025534 | 0.0024084 | west | N | 0.0024084 | 0
38438 | TNSRBNMS | 1 | 150 | -0.025225 | west | Y | -0.029778 | -0.025224 | 0.0024084 | -0.025534 | 0.0024084 | west | N | 0.0024084 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38600 | TNBP_CGN | 5 | 53 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38614 | TNBPAMCG | 4 | 96 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38615 | TNBPAMCG | 1 | 244 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38690 | TNBP_CGN | 3 | 40 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
39470 | TNDOWCGN | 1 | 32 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
39480 | TNDOWCGN | 1 | 30 | 0.000305 | houston | N | -0.0042482 | 0.0003062 | 0.027938 | -4.4978e-06 | 4.4978e-06 | houston | N | 4.4978e-06 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.000268 | houston | N | -0.0042852 | 0.0002692 | 0.027901 | -4.1498e-05 | 4.1498e-05 | houston | N | 4.1498e-05 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.000268 | houston | N | -0.0042852 | 0.0002692 | 0.027901 | -4.1498e-05 | 4.1498e-05 | houston | N | 4.1498e-05 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.000268 | houston | N | -0.0042852 | 0.0002692 | 0.027901 | -4.1498e-05 | 4.1498e-05 | houston | N | 4.1498e-05 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.000268 | houston | N | -0.0042852 | 0.0002692 | 0.027901 | -4.1498e-05 | 4.1498e-05 | houston | N | 4.1498e-05 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.000499 | north | Y | -0.0040542 | 0.0005002 | 0.028132 | 0.0001895 | 0.0001895 | houston | Y | 0.0040542 | 0.5886
39970 | TNTNPONE | 1 | 153 | 0.000499 | north | Y | -0.0040542 | 0.0005002 | 0.028132 | 0.0001895 | 0.0001895 | houston | Y | 0.0040542 | 0.5913
48500 | APD_GT1_ | 1 | 136 | 0.000327 | houston | N | -0.0042262 | 0.0003282 | 0.02796 | 1.7502e-05 | 1.7502e-05 | houston | N | 1.7502e-05 | 0
48510 | AK_GT1__ | 1 | 33 | 0.000293 | houston | N | -0.0042602 | 0.0002942 | 0.027926 | -1.6498e-05 | 1.6498e-05 | houston | N | 1.6498e-05 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.000326 | houston | Y | -0.0042272 | 0.0003272 | 0.027959 | 1.6502e-05 | 1.6502e-05 | houston | N | 1.6502e-05 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.000326 | houston | Y | -0.0042272 | 0.0003272 | 0.027959 | 1.6502e-05 | 1.6502e-05 | houston | N | 1.6502e-05 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.000326 | houston | Y | -0.0042272 | 0.0003272 | 0.027959 | 1.6502e-05 | 1.6502e-05 | houston | N | 1.6502e-05 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.000326 | houston | Y | -0.0042272 | 0.0003272 | 0.027959 | 1.6502e-05 | 1.6502e-05 | houston | N | 1.6502e-05 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.00026 | houston | N | -0.0042932 | 0.0002612 | 0.027893 | -4.9498e-05 | 4.9498e-05 | houston | N | 4.9498e-05 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.00026 | houston | N | -0.0042932 | 0.0002612 | 0.027893 | -4.9498e-05 | 4.9498e-05 | houston | N | 4.9498e-05 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.000293 | houston | N | -0.0042602 | 0.0002942 | 0.027926 | -1.6498e-05 | 1.6498e-05 | houston | N | 1.6498e-05 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.000293 | houston | N | -0.0042602 | 0.0002942 | 0.027926 | -1.6498e-05 | 1.6498e-05 | houston | N | 1.6498e-05 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.000293 | houston | N | -0.0042602 | 0.0002942 | 0.027926 | -1.6498e-05 | 1.6498e-05 | houston | N | 1.6498e-05 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.000318 | houston | N | -0.0042352 | 0.0003192 | 0.027951 | 8.5022e-06 | 8.5022e-06 | houston | N | 8.5022e-06 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.000318 | houston | N | -0.0042352 | 0.0003192 | 0.027951 | 8.5022e-06 | 8.5022e-06 | houston | N | 8.5022e-06 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.000318 | houston | N | -0.0042352 | 0.0003192 | 0.027951 | 8.5022e-06 | 8.5022e-06 | houston | N | 8.5022e-06 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.000318 | houston | N | -0.0042352 | 0.0003192 | 0.027951 | 8.5022e-06 | 8.5022e-06 | houston | N | 8.5022e-06 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.000317 | houston | N | -0.0042362 | 0.0003182 | 0.02795 | 7.5022e-06 | 7.5022e-06 | houston | N | 7.5022e-06 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.000317 | houston | N | -0.0042362 | 0.0003182 | 0.02795 | 7.5022e-06 | 7.5022e-06 | houston | N | 7.5022e-06 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.000317 | houston | N | -0.0042362 | 0.0003182 | 0.02795 | 7.5022e-06 | 7.5022e-06 | houston | N | 7.5022e-06 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.000317 | houston | N | -0.0042362 | 0.0003182 | 0.02795 | 7.5022e-06 | 7.5022e-06 | houston | N | 7.5022e-06 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.000317 | houston | N | -0.0042362 | 0.0003182 | 0.02795 | 7.5022e-06 | 7.5022e-06 | houston | N | 7.5022e-06 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.000333 | houston | Y | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.000333 | houston | Y | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.000333 | houston | Y | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.000333 | houston | Y | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.000347 | houston | N | -0.0042062 | 0.0003482 | 0.02798 | 3.7502e-05 | 3.7502e-05 | houston | N | 3.7502e-05 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.000327 | houston | N | -0.0042262 | 0.0003282 | 0.02796 | 1.7502e-05 | 1.7502e-05 | houston | N | 1.7502e-05 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.000327 | houston | N | -0.0042262 | 0.0003282 | 0.02796 | 1.7502e-05 | 1.7502e-05 | houston | N | 1.7502e-05 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.000335 | houston | N | -0.0042182 | 0.0003362 | 0.027968 | 2.5502e-05 | 2.5502e-05 | houston | N | 2.5502e-05 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.000335 | houston | N | -0.0042182 | 0.0003362 | 0.027968 | 2.5502e-05 | 2.5502e-05 | houston | N | 2.5502e-05 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.000335 | houston | N | -0.0042182 | 0.0003362 | 0.027968 | 2.5502e-05 | 2.5502e-05 | houston | N | 2.5502e-05 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.000335 | houston | N | -0.0042182 | 0.0003362 | 0.027968 | 2.5502e-05 | 2.5502e-05 | houston | N | 2.5502e-05 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.000322 | houston | N | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.000322 | houston | N | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.000322 | houston | N | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.000322 | houston | N | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.000322 | houston | N | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48651 | EP_1_2 | 1 | 5 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48651 | EP_1_2 | 2 | 21 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.00044 | north | N | -0.0041132 | 0.0004412 | 0.028073 | 0.0001305 | 0.0001305 | houston | Y | 0.0041132 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.00044 | north | N | -0.0041132 | 0.0004412 | 0.028073 | 0.0001305 | 0.0001305 | houston | Y | 0.0041132 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.00044 | north | N | -0.0041132 | 0.0004412 | 0.028073 | 0.0001305 | 0.0001305 | houston | Y | 0.0041132 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.00044 | north | N | -0.0041132 | 0.0004412 | 0.028073 | 0.0001305 | 0.0001305 | houston | Y | 0.0041132 | 0
48690 | GBY_GN5_ | 5 | 398 | 0.000336 | houston | Y | -0.0042172 | 0.0003372 | 0.027969 | 2.6502e-05 | 2.6502e-05 | houston | N | 2.6502e-05 | 0
48691 | GBY_7374 | A | 46 | 0.000322 | houston | Y | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48691 | GBY_7374 | B | 46 | 0.000322 | houston | Y | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48692 | GBY_8182 | C | 46 | 0.000322 | houston | Y | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48692 | GBY_8182 | D | 55 | 0.000322 | houston | Y | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48693 | GBY_8384 | E | 55 | 0.000322 | houston | Y | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48693 | GBY_8384 | F | 54 | 0.000322 | houston | Y | -0.0042312 | 0.0003232 | 0.027955 | 1.2502e-05 | 1.2502e-05 | houston | N | 1.2502e-05 | 0
48721 | LEG_1___ | 1 | 827 | 0.000515 | north | Y | -0.0040382 | 0.0005162 | 0.028148 | 0.0002055 | 0.0002055 | houston | Y | 0.0040382 | 3.1697
48722 | LEG_2___ | 2 | 819 | 0.000515 | north | Y | -0.0040382 | 0.0005162 | 0.028148 | 0.0002055 | 0.0002055 | houston | Y | 0.0040382 | 3.139
48730 | MNS_GT | 1 | 46.1 | 0.000289 | houston | N | -0.0042642 | 0.0002902 | 0.027922 | -2.0498e-05 | 2.0498e-05 | houston | N | 2.0498e-05 | 0
48731 | CBE_GT1 | 1 | 76 | 0.000217 | houston | Y | -0.0043362 | 0.0002182 | 0.02785 | -9.2498e-05 | 9.2498e-05 | houston | N | 9.2498e-05 | 0
48732 | CBE_GT2 | 1 | 76 | 0.000217 | houston | Y | -0.0043362 | 0.0002182 | 0.02785 | -9.2498e-05 | 9.2498e-05 | houston | N | 9.2498e-05 | 0
48733 | CBE_ST12 | 1 | 105 | 0.000217 | houston | Y | -0.0043362 | 0.0002182 | 0.02785 | -9.2498e-05 | 9.2498e-05 | houston | N | 9.2498e-05 | 0
48734 | CBE_GT3 | 1 | 74 | 0.000217 | houston | Y | -0.0043362 | 0.0002182 | 0.02785 | -9.2498e-05 | 9.2498e-05 | houston | N | 9.2498e-05 | 0
48735 | CBE_GT4 | 1 | 74 | 0.000217 | houston | Y | -0.0043362 | 0.0002182 | 0.02785 | -9.2498e-05 | 9.2498e-05 | houston | N | 9.2498e-05 | 0
48736 | CBE_ST34 | 1 | 102 | 0.000217 | houston | Y | -0.0043362 | 0.0002182 | 0.02785 | -9.2498e-05 | 9.2498e-05 | houston | N | 9.2498e-05 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48761 | PR_GT1__ | 1 | 35 | 0.000323 | houston | N | -0.0042302 | 0.0003242 | 0.027956 | 1.3502e-05 | 1.3502e-05 | houston | N | 1.3502e-05 | 0
48772 | PHR_GN2_ | MB | 459 | 0.000313 | houston | Y | -0.0042402 | 0.0003142 | 0.027946 | 3.5022e-06 | 3.5022e-06 | houston | N | 3.5022e-06 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.000347 | houston | N | -0.0042062 | 0.0003482 | 0.02798 | 3.7502e-05 | 3.7502e-05 | houston | N | 3.7502e-05 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.000347 | houston | N | -0.0042062 | 0.0003482 | 0.02798 | 3.7502e-05 | 3.7502e-05 | houston | N | 3.7502e-05 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.000347 | houston | N | -0.0042062 | 0.0003482 | 0.02798 | 3.7502e-05 | 3.7502e-05 | houston | N | 3.7502e-05 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.000347 | houston | N | -0.0042062 | 0.0003482 | 0.02798 | 3.7502e-05 | 3.7502e-05 | houston | N | 3.7502e-05 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.000333 | houston | N | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
48820 | SHELLG1_ | 1 | 71 | 0.000325 | houston | N | -0.0042282 | 0.0003262 | 0.027958 | 1.5502e-05 | 1.5502e-05 | houston | N | 1.5502e-05 | 0
48821 | SHELLG2 | 2 | 72 | 0.000325 | houston | N | -0.0042282 | 0.0003262 | 0.027958 | 1.5502e-05 | 1.5502e-05 | houston | N | 1.5502e-05 | 0
48822 | SHELLG3_ | 1 | 39 | 0.000325 | houston | N | -0.0042282 | 0.0003262 | 0.027958 | 1.5502e-05 | 1.5502e-05 | houston | N | 1.5502e-05 | 0
48822 | SHELLG3_ | 2 | 30 | 0.000325 | houston | N | -0.0042282 | 0.0003262 | 0.027958 | 1.5502e-05 | 1.5502e-05 | houston | N | 1.5502e-05 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.000321 | houston | N | -0.0042322 | 0.0003222 | 0.027954 | 1.1502e-05 | 1.1502e-05 | houston | N | 1.1502e-05 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.000321 | houston | N | -0.0042322 | 0.0003222 | 0.027954 | 1.1502e-05 | 1.1502e-05 | houston | N | 1.1502e-05 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.000324 | houston | N | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.000323 | houston | Y | -0.0042302 | 0.0003242 | 0.027956 | 1.3502e-05 | 1.3502e-05 | houston | N | 1.3502e-05 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.000323 | houston | Y | -0.0042302 | 0.0003242 | 0.027956 | 1.3502e-05 | 1.3502e-05 | houston | N | 1.3502e-05 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.000324 | houston | Y | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.000324 | houston | Y | -0.0042292 | 0.0003252 | 0.027957 | 1.4502e-05 | 1.4502e-05 | houston | N | 1.4502e-05 | 0
48855 | SRB_GT21 | B2 | 12 | 0.000323 | houston | Y | -0.0042302 | 0.0003242 | 0.027956 | 1.3502e-05 | 1.3502e-05 | houston | N | 1.3502e-05 | 0
48855 | SRB_GT21 | MB | 18 | 0.000323 | houston | Y | -0.0042302 | 0.0003242 | 0.027956 | 1.3502e-05 | 1.3502e-05 | houston | N | 1.3502e-05 | 0
48865 | TECO_GT1 | 1 | 50 | 0.000311 | houston | Y | -0.0042422 | 0.0003122 | 0.027944 | 1.5022e-06 | 1.5022e-06 | houston | N | 1.5022e-06 | 0
48873 | THW_ST3_ | 3 | 104 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48874 | THW_ST4_ | 4 | 104 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48875 | THW_3132 | A | 54 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48875 | THW_3132 | B | 53 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48877 | THW_3334 | C | 54 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48877 | THW_3334 | D | 57 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48879 | THW_4142 | E | 54 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48879 | THW_4142 | F | 54 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48881 | THW_4344 | G | 58 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48881 | THW_4344 | H | 58 | 0.00033 | houston | Y | -0.0042232 | 0.0003312 | 0.027963 | 2.0502e-05 | 2.0502e-05 | houston | N | 2.0502e-05 | 0
48883 | THW_GT1_ | B2 | 12 | 0.000332 | houston | Y | -0.0042212 | 0.0003332 | 0.027965 | 2.2502e-05 | 2.2502e-05 | houston | N | 2.2502e-05 | 0
48885 | THW_5152 | A | 56 | 0.000337 | houston | Y | -0.0042162 | 0.0003382 | 0.02797 | 2.7502e-05 | 2.7502e-05 | houston | N | 2.7502e-05 | 0
48885 | THW_5152 | B | 59 | 0.000337 | houston | Y | -0.0042162 | 0.0003382 | 0.02797 | 2.7502e-05 | 2.7502e-05 | houston | N | 2.7502e-05 | 0
48886 | THW_5354 | C | 56 | 0.000337 | houston | Y | -0.0042162 | 0.0003382 | 0.02797 | 2.7502e-05 | 2.7502e-05 | houston | N | 2.7502e-05 | 0
48886 | THW_5354 | D | 56 | 0.000337 | houston | Y | -0.0042162 | 0.0003382 | 0.02797 | 2.7502e-05 | 2.7502e-05 | houston | N | 2.7502e-05 | 0
48887 | THW_5556 | E | 59 | 0.000337 | houston | Y | -0.0042162 | 0.0003382 | 0.02797 | 2.7502e-05 | 2.7502e-05 | houston | N | 2.7502e-05 | 0
48887 | THW_5556 | F | 56 | 0.000337 | houston | Y | -0.0042162 | 0.0003382 | 0.02797 | 2.7502e-05 | 2.7502e-05 | houston | N | 2.7502e-05 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.000216 | houston | Y | -0.0043372 | 0.0002172 | 0.027849 | -9.3498e-05 | 9.3498e-05 | houston | N | 9.3498e-05 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.000298 | houston | Y | -0.0042552 | 0.0002992 | 0.027931 | -1.1498e-05 | 1.1498e-05 | houston | N | 1.1498e-05 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.000298 | houston | Y | -0.0042552 | 0.0002992 | 0.027931 | -1.1498e-05 | 1.1498e-05 | houston | N | 1.1498e-05 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.000298 | houston | Y | -0.0042552 | 0.0002992 | 0.027931 | -1.1498e-05 | 1.1498e-05 | houston | N | 1.1498e-05 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.000298 | houston | Y | -0.0042552 | 0.0002992 | 0.027931 | -1.1498e-05 | 1.1498e-05 | houston | N | 1.1498e-05 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.000298 | houston | N | -0.0042552 | 0.0002992 | 0.027931 | -1.1498e-05 | 1.1498e-05 | houston | N | 1.1498e-05 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.000293 | houston | Y | -0.0042602 | 0.0002942 | 0.027926 | -1.6498e-05 | 1.6498e-05 | houston | N | 1.6498e-05 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.000293 | houston | Y | -0.0042602 | 0.0002942 | 0.027926 | -1.6498e-05 | 1.6498e-05 | houston | N | 1.6498e-05 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.000293 | houston | Y | -0.0042602 | 0.0002942 | 0.027926 | -1.6498e-05 | 1.6498e-05 | houston | N | 1.6498e-05 | 0
48929 | WAPGT21_ | B1 | 13 | 0.000298 | houston | Y | -0.0042552 | 0.0002992 | 0.027931 | -1.1498e-05 | 1.1498e-05 | houston | N | 1.1498e-05 | 0
48940 | WARVUE_G | G1 | 12 | 0.000333 | houston | Y | -0.0042202 | 0.0003342 | 0.027966 | 2.3502e-05 | 2.3502e-05 | houston | N | 2.3502e-05 | 0
49803 | EXN_15GT | 1 | 34 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49826 | EXN938GT | 5 | 45.9 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49828 | EXN941GT | 10 | 17.7 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49829 | EXN942GT | 11 | 20.4 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49830 | EXN943GT | 12 | 19.9 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49831 | EXN944GT | 13 | 35 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49832 | EXN945GT | 9 | 18 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49837 | EXN_GT | 4 | 85.4 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49838 | EXN_14GT | 14 | 148 | 0.000331 | houston | N | -0.0042222 | 0.0003322 | 0.027964 | 2.1502e-05 | 2.1502e-05 | houston | N | 2.1502e-05 | 0
49851 | DOW17000 | 37 | 62 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49858 | DOW38100 | 31 | 71.4 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49859 | DOW38200 | 33 | 45 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49860 | DOW38300 | 32 | 101 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49862 | DOW39100 | 36 | 86 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49863 | DOW39200 | 35 | 88 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49865 | DOW41000 | 41 | 50 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49866 | DOW42000 | 42 | 18 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49869 | DOW49000 | 45 | 94 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49870 | DOW61000 | 61 | 70 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49871 | DOW62000 | 62 | 63 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49872 | DOW63000 | 63 | 72 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49873 | DOW64000 | 64 | 64.8 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49876 | DOW65000 | 65 | 101 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49877 | DOW66000 | 66 | 97 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49878 | DOW67000 | 67 | 103 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49882 | DOW81000 | 81 | 76 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49884 | DOW82000 | 82 | 80 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49885 | DOW83000 | 83 | 80 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
49886 | DOW84000 | 84 | 171 | 0.000252 | houston | N | -0.0043012 | 0.0002532 | 0.027885 | -5.7498e-05 | 5.7498e-05 | houston | N | 5.7498e-05 | 0
58909 | PEARSALL | 1 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58909 | PEARSALL | 2 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58909 | PEARSALL | 3 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58909 | PEARSALL | 4 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58909 | PEARSALL | 5 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58909 | PEARSALL | 6 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58919 | PEARSALL | 1 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58919 | PEARSALL | 2 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58919 | PEARSALL | 3 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58919 | PEARSALL | 4 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58919 | PEARSALL | 5 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58919 | PEARSALL | 6 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58929 | PEARSALL | 1 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58929 | PEARSALL | 2 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58929 | PEARSALL | 3 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58929 | PEARSALL | 4 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58929 | PEARSALL | 5 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58929 | PEARSALL | 6 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58949 | PEARSALL | 1 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58949 | PEARSALL | 2 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58949 | PEARSALL | 3 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58949 | PEARSALL | 4 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58949 | PEARSALL | 5 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
58949 | PEARSALL | 6 | 8.4 | -0.001256 | south | Y | -0.0058092 | -0.0012548 | 0.026377 | -0.0015655 | 0.0012548 | south | N | 0.0012548 | 0
60000 | DSKY2 | 1 | 76.5 | -0.024446 | west | Y | -0.028999 | -0.024445 | 0.0031874 | -0.024755 | 0.0031874 | west | N | 0.0031874 | 0
60003 | KING_NE1 | 1 | 80 | -0.025268 | west | Y | -0.029821 | -0.025267 | 0.0023654 | -0.025577 | 0.0023654 | west | N | 0.0023654 | 0
60005 | KING_SE1 | 1 | 40 | -0.025268 | west | Y | -0.029821 | -0.025267 | 0.0023654 | -0.025577 | 0.0023654 | west | N | 0.0023654 | 0
60007 | KING_SW1 | 1 | 80 | -0.025384 | west | Y | -0.029937 | -0.025383 | 0.0022494 | -0.025693 | 0.0022494 | west | N | 0.0022494 | 0
60016 | WOODWRD1 | 1 | 80 | -0.025246 | west | Y | -0.029799 | -0.025245 | 0.0023874 | -0.025555 | 0.0023874 | west | N | 0.0023874 | 0
60017 | ORNNWP1 | 1 | 80 | -0.024626 | west | Y | -0.029179 | -0.024625 | 0.0030074 | -0.024935 | 0.0030074 | west | N | 0.0030074 | 0
60018 | DSKY1 | 1 | 84 | -0.024423 | west | Y | -0.028976 | -0.024422 | 0.0032104 | -0.024732 | 0.0032104 | west | N | 0.0032104 | 0
60019 | KING_NW1 | 1 | 80 | -0.025384 | west | Y | -0.029937 | -0.025383 | 0.0022494 | -0.025693 | 0.0022494 | west | N | 0.0022494 | 0
60057 | CALLAHAN | 1 | 114 | -0.000197 | south | Y | -0.0047502 | -0.0001958 | 0.027436 | -0.0005065 | 0.0001958 | south | N | 0.0001958 | 0
60058 | BUFF_GAP | 1 | 120 | -0.026269 | west | Y | -0.030822 | -0.026268 | 0.0013644 | -0.026578 | 0.0013644 | west | N | 0.0013644 | 0
60060 | CIRELLO | 1 | 233 | -0.026269 | west | Y | -0.030822 | -0.026268 | 0.0013644 | -0.026578 | 0.0013644 | west | N | 0.0013644 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.026269 | west | Y | -0.030822 | -0.026268 | 0.0013644 | -0.026578 | 0.0013644 | west | N | 0.0013644 | 0
60066 | H_HOLLOW | 1 | 222 | -0.000197 | south | Y | -0.0047502 | -0.0001958 | 0.027436 | -0.0005065 | 0.0001958 | south | N | 0.0001958 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.000197 | south | Y | -0.0047502 | -0.0001958 | 0.027436 | -0.0005065 | 0.0001958 | south | N | 0.0001958 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.000197 | south | Y | -0.0047502 | -0.0001958 | 0.027436 | -0.0005065 | 0.0001958 | south | N | 0.0001958 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.000197 | south | Y | -0.0047502 | -0.0001958 | 0.027436 | -0.0005065 | 0.0001958 | south | N | 0.0001958 | 0
60074 | HORSH5 | 1 | 100 | -0.000197 | south | Y | -0.0047502 | -0.0001958 | 0.027436 | -0.0005065 | 0.0001958 | south | N | 0.0001958 | 0
60081 | WHRLWIND | 1 | 60 | -0.038454 | west | Y | -0.043007 | -0.038453 | -0.010821 | -0.038763 | 0.010821 | west | N | 0.010821 | 0
60201 | RIO DRCS | F | 0 | -0.007191 | south | N | -0.011744 | -0.0071898 | 0.020442 | -0.0075005 | 0.0071898 | south | N | 0.0071898 | 0
60202 | FRIEND_R | F | 0 | -0.021242 | west | N | -0.025795 | -0.021241 | 0.0063914 | -0.021551 | 0.0063914 | west | N | 0.0063914 | 0
60203 | PRES0A | BT | 4.8 | -0.025887 | west | N | -0.03044 | -0.025886 | 0.0017464 | -0.026196 | 0.0017464 | west | N | 0.0017464 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.027787 | west | Y | -0.03234 | -0.027786 | -0.0001536 | -0.028096 | 0.0001536 | west | N | 0.0001536 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.027787 | west | Y | -0.03234 | -0.027786 | -0.0001536 | -0.028096 | 0.0001536 | west | N | 0.0001536 | 0
71057 | L_SWEETW | W1 | 135 | -0.027787 | west | Y | -0.03234 | -0.027786 | -0.0001536 | -0.028096 | 0.0001536 | west | N | 0.0001536 | 0
71059 | L_SWEETW | W1 | 119 | -0.027787 | west | Y | -0.03234 | -0.027786 | -0.0001536 | -0.028096 | 0.0001536 | west | N | 0.0001536 | 0
71060 | L_SWEETW | W1 | 105 | -0.027787 | west | Y | -0.03234 | -0.027786 | -0.0001536 | -0.028096 | 0.0001536 | west | N | 0.0001536 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.027787 | west | Y | -0.03234 | -0.027786 | -0.0001536 | -0.028096 | 0.0001536 | west | N | 0.0001536 | 0
76031 | L_GASCCR | W1 | 150 | -0.025403 | west | Y | -0.029956 | -0.025402 | 0.0022304 | -0.025712 | 0.0022304 | west | N | 0.0022304 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.025003 | west | Y | -0.029556 | -0.025002 | 0.0026304 | -0.025312 | 0.0026304 | west | N | 0.0026304 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.025003 | west | Y | -0.029556 | -0.025002 | 0.0026304 | -0.025312 | 0.0026304 | west | N | 0.0026304 | 0
76096 | L_CAPRSI | W1 | 186 | -0.025003 | west | Y | -0.029556 | -0.025002 | 0.0026304 | -0.025312 | 0.0026304 | west | N | 0.0026304 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.025003 | west | Y | -0.029556 | -0.025002 | 0.0026304 | -0.025312 | 0.0026304 | west | N | 0.0026304 | 0
80003 | MILHWYS | F | 0 | -0.000137 | south | N | -0.0046902 | -0.0001358 | 0.027496 | -0.0004465 | 0.0001358 | south | N | 0.0001358 | 0
80010 | EPLVT1 | F | 0 | -0.004763 | south | N | -0.0093162 | -0.0047618 | 0.02287 | -0.0050725 | 0.0047618 | south | N | 0.0047618 | 0
80012 | LAR | F | 0 | -0.000725 | south | N | -0.0052782 | -0.0007238 | 0.026908 | -0.0010345 | 0.0007238 | south | N | 0.0007238 | 0
80051 | FORPVCM0 | 8 | 28 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
80052 | FOR69CG0 | 9 | 43.6 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
80053 | FOR69CG0 | 10 | 74 | 1.3e-05 | south | N | -0.0045402 | 1.4196e-05 | 0.027646 | -0.0002965 | 1.4196e-05 | south | N | 1.4196e-05 | 0
80080 | GWINDT11 | 1 | 94 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80080 | GWINDT11 | 2 | 41 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80080 | GWINDT11 | 3 | 38 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80080 | GWINDT11 | 4 | 19 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80081 | GWINDT21 | 1 | 94 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80081 | GWINDT21 | 2 | 36 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80081 | GWINDT21 | 3 | 43 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80081 | GWINDT21 | 4 | 22 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80137 | CSDR89 | 8 | 39 | -1.6e-05 | south | N | -0.0045692 | -1.4804e-05 | 0.027617 | -0.0003255 | 1.4804e-05 | south | N | 1.4804e-05 | 0
80137 | CSDR89 | 9 | 15 | -1.6e-05 | south | N | -0.0045692 | -1.4804e-05 | 0.027617 | -0.0003255 | 1.4804e-05 | south | N | 1.4804e-05 | 0
80138 | CSDR7 | 7 | 7 | -1.6e-05 | south | N | -0.0045692 | -1.4804e-05 | 0.027617 | -0.0003255 | 1.4804e-05 | south | N | 1.4804e-05 | 0
80139 | CSDR56 | 5 | 15 | -1.6e-05 | south | N | -0.0045692 | -1.4804e-05 | 0.027617 | -0.0003255 | 1.4804e-05 | south | N | 1.4804e-05 | 0
80139 | CSDR56 | 6 | 39 | -1.6e-05 | south | N | -0.0045692 | -1.4804e-05 | 0.027617 | -0.0003255 | 1.4804e-05 | south | N | 1.4804e-05 | 0
80140 | CSDR11 | 11 | 39 | -1.6e-05 | south | N | -0.0045692 | -1.4804e-05 | 0.027617 | -0.0003255 | 1.4804e-05 | south | N | 1.4804e-05 | 0
80180 | PNSCALT1 | 1 | 148 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80180 | PNSCALT1 | 2 | 50 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80181 | PNSCALT2 | 1 | 55 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80181 | PNSCALT2 | 2 | 50 | -0.00013 | south | Y | -0.0046832 | -0.0001288 | 0.027503 | -0.0004395 | 0.0001288 | south | N | 0.0001288 | 0
80223 | REYSHR G | 1 | 12 | -9.4e-05 | south | N | -0.0046472 | -9.2804e-05 | 0.027539 | -0.0004035 | 9.2804e-05 | south | N | 9.2804e-05 | 0
80224 | VISTRONG | 1 | 15 | -2.1e-05 | south | N | -0.0045742 | -1.9804e-05 | 0.027612 | -0.0003305 | 1.9804e-05 | south | N | 1.9804e-05 | 0
80225 | VISTRONG | 2 | 23 | -2.1e-05 | south | N | -0.0045742 | -1.9804e-05 | 0.027612 | -0.0003305 | 1.9804e-05 | south | N | 1.9804e-05 | 0
80226 | ALCOA G | 1 | 48 | 7e-06 | south | N | -0.0045462 | 8.1955e-06 | 0.02764 | -0.0003025 | 8.1955e-06 | south | N | 8.1955e-06 | 0
80227 | AIRCO G | 1 | 8 | -2.1e-05 | south | N | -0.0045742 | -1.9804e-05 | 0.027612 | -0.0003305 | 1.9804e-05 | south | N | 1.9804e-05 | 0
80261 | NBEC81A | 1 | 180 | -0.000108 | south | Y | -0.0046612 | -0.0001068 | 0.027525 | -0.0004175 | 0.0001068 | south | N | 0.0001068 | 0
80262 | NBEC91A | 1 | 180 | -0.000108 | south | Y | -0.0046612 | -0.0001068 | 0.027525 | -0.0004175 | 0.0001068 | south | N | 0.0001068 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.00011 | south | Y | -0.0046632 | -0.0001088 | 0.027523 | -0.0004195 | 0.0001088 | south | N | 0.0001088 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.00011 | south | Y | -0.0046632 | -0.0001088 | 0.027523 | -0.0004195 | 0.0001088 | south | N | 0.0001088 | 0
80265 | LARECU40 | 4 | 100 | -0.000724 | south | Y | -0.0052772 | -0.0007228 | 0.026909 | -0.0010335 | 0.0007228 | south | N | 0.0007228 | 0
80266 | LARECU50 | 5 | 100 | -0.000724 | south | Y | -0.0052772 | -0.0007228 | 0.026909 | -0.0010335 | 0.0007228 | south | N | 0.0007228 | 0
80291 | PAPALOTE | 1 | 25 | -0.0001 | south | Y | -0.0046532 | -9.8804e-05 | 0.027533 | -0.0004095 | 9.8804e-05 | south | N | 9.8804e-05 | 0
80291 | PAPALOTE | 2 | 25 | -0.0001 | south | Y | -0.0046532 | -9.8804e-05 | 0.027533 | -0.0004095 | 9.8804e-05 | south | N | 9.8804e-05 | 0
80291 | PAPALOTE | 3 | 25 | -0.0001 | south | Y | -0.0046532 | -9.8804e-05 | 0.027533 | -0.0004095 | 9.8804e-05 | south | N | 9.8804e-05 | 0
80291 | PAPALOTE | 4 | 16 | -0.0001 | south | Y | -0.0046532 | -9.8804e-05 | 0.027533 | -0.0004095 | 9.8804e-05 | south | N | 9.8804e-05 | 0
80294 | PAPALOTE | 5 | 25 | -0.0001 | south | Y | -0.0046532 | -9.8804e-05 | 0.027533 | -0.0004095 | 9.8804e-05 | south | N | 9.8804e-05 | 0
80294 | PAPALOTE | 6 | 25 | -0.0001 | south | Y | -0.0046532 | -9.8804e-05 | 0.027533 | -0.0004095 | 9.8804e-05 | south | N | 9.8804e-05 | 0
80294 | PAPALOTE | 7 | 25 | -0.0001 | south | Y | -0.0046532 | -9.8804e-05 | 0.027533 | -0.0004095 | 9.8804e-05 | south | N | 9.8804e-05 | 0
80294 | PAPALOTE | 8 | 15 | -0.0001 | south | Y | -0.0046532 | -9.8804e-05 | 0.027533 | -0.0004095 | 9.8804e-05 | south | N | 9.8804e-05 | 0
86104 | CID-138 | EQ | 0 | -0.000724 | south | N | -0.0052772 | -0.0007228 | 0.026909 | -0.0010335 | 0.0007228 | south | N | 0.0007228 | 0
86105 | CID-230 | EQ | 500 | -0.000724 | south | N | -0.0052772 | -0.0007228 | 0.026909 | -0.0010335 | 0.0007228 | south | N | 0.0007228 | 0
86106 | CUF-230 | EQ | 500 | -0.000724 | south | N | -0.0052772 | -0.0007228 | 0.026909 | -0.0010335 | 0.0007228 | south | N | 0.0007228 | 0
86107 | CUF-138 | EQ | 0 | -0.000724 | south | N | -0.0052772 | -0.0007228 | 0.026909 | -0.0010335 | 0.0007228 | south | N | 0.0007228 | 0
88198 | BEEVILLE | F | 0 | -0.00019 | south | N | -0.0047432 | -0.0001888 | 0.027443 | -0.0004995 | 0.0001888 | south | N | 0.0001888 | 0
88253 | HAMILTON | F | 0 | -0.007137 | south | N | -0.01169 | -0.0071358 | 0.020496 | -0.0074465 | 0.0071358 | south | N | 0.0071358 | 0
88299 | ZAPATA | F | 0 | -0.000533 | south | N | -0.0050862 | -0.0005318 | 0.0271 | -0.0008425 | 0.0005318 | south | N | 0.0005318 | 0
88508 | FALFURRI | F | 0 | -0.000218 | south | N | -0.0047712 | -0.0002168 | 0.027415 | -0.0005275 | 0.0002168 | south | N | 0.0002168 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1596 GRAHAMSW - 1601 GRAHAME_ C: 37980 TNWICKET- 38000 TNPYOTE C: 38000 TNPYOTE_ - 38020 TNWORSHA C: 38020 TNWORSHA - 38040 TNH20__ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.44854 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 53.8244 | 120 | 0.47617 | 57.1404 | 120 | 57.1404
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.12102 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4523 | 0 | 0.14865 | 0 | 120 | 57.1404
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.12102 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4523 | 0 | 0.14865 | 0 | 120 | 57.1404
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.1074 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.8403 | 73 | 0.13503 | 9.8575 | 193 | 66.9979 | Weighted Shift Factors
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.1074 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.7807 | 119 | 0.13503 | 16.069 | 312 | 83.0669 | North | 0.0045532
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.1074 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.0172 | 205 | 0.13503 | 27.682 | 517 | 110.7489 | West | -0.027633
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.1074 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.9549 | 102 | 0.13503 | 13.7735 |  |  |  | 0.032186
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.1074 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.3105 | 96 | 0.13503 | 12.9633
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.095506 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7191 | 18 | 0.12314 | 2.2165 |  |  | Line Rating | 290.5
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.095506 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7191 | 18 | 0.12314 | 2.2165 |  |  | Conc Gen | 517
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.095506 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 3.6292 | 38 | 0.12314 | 4.6793 |  |  | Weighted Imp. | 110.7489
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.04712 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5706 | 288 | 0.074753 | 21.5288 |  |  | PTDF | 0.21421
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.04712 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9266 | 147 | 0.074753 | 10.9887
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.04712 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9266 | 147 | 0.074753 | 10.9887 |  |  | Concentration | 6.6555
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.013082 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.4717 | 112.5 | 0.040715 | 4.5804
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.85022 | 70 | 0.039779 | 2.7845
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.83807 | 69 | 0.039779 | 2.7447
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.83807 | 69 | 0.039779 | 2.7447
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.82593 | 68 | 0.039779 | 2.705
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.009589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.611 | 168 | 0.037222 | 6.2533
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.009589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.86301 | 90 | 0.037222 | 3.35
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.00853 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.5118 | 60 | 0.036163 | 2.1698
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.007906 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.11859 | 0 | 0.035539 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.007906 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.11859 | 0 | 0.035539 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.006602 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034235 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.006602 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034235 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.006602 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034235 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.004311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64665 | 150 | 0.031944 | 4.7916
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.004311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.34488 | 80 | 0.031944 | 2.5555
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.002962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75531 | 255 | 0.030595 | 7.8017
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.002962 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.44134 | 149 | 0.030595 | 4.5586
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.002962 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.45319 | 153 | 0.030595 | 4.681
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.001393 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029026 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.001393 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029026 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.001318 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.25833 | 196 | 0.028951 | 5.6744
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.001318 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.1463 | 111 | 0.028951 | 3.2136
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.001299 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.05196 | 0 | 0.028932 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.001299 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.05196 | 0 | 0.028932 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.001265 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028898 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.001265 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.99555 | 787 | 0.028898 | 22.7427
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.001027 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.06162 | 60 | 0.02866 | 1.7196
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.001027 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.064701 | 63 | 0.02866 | 1.8056
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.000979 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.16643 | 170 | 0.028612 | 4.864
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.000979 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.50908 | 520 | 0.028612 | 14.8782
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.000971 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.2175 | 224 | 0.028604 | 6.4073
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.000909 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.39542 | 435 | 0.028542 | 12.4157
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.000817 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.32271 | 395 | 0.02845 | 11.2377
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.000817 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.3554 | 435 | 0.02845 | 12.3757
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13216 | 224 | 0.028223 | 6.3219
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13334 | 226 | 0.028223 | 6.3784
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12508 | 212 | 0.028223 | 5.9833
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12449 | 211 | 0.028223 | 5.955
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.000518 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.03885 | 0 | 0.028151 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.000518 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.041233 | 0 | 0.028151 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.000518 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.045791 | 0 | 0.028151 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.000515 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.4259 | 827 | 0.028148 | 23.2783
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.000515 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.42179 | 819 | 0.028148 | 23.0531
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.000502 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.024096 | 48 | 0.028135 | 1.3505
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.000502 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.023092 | 46 | 0.028135 | 1.2942
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.000502 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.05271 | 105 | 0.028135 | 2.9542
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.42664 | 855 | 0.028132 | 24.0528
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.42664 | 855 | 0.028132 | 24.0528
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.075998 | 152.3 | 0.028132 | 4.2845
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.076347 | 153 | 0.028132 | 4.3042
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.000492 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.015744 | 0 | 0.028125 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028125 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028125 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.000492 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.008364 | 17 | 0.028125 | 0.47812
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028125 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028125 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.000484 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.17908 | 370 | 0.028117 | 10.4033
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.06776 | 0 | 0.028117 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.068244 | 0 | 0.028117 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.14956 | 0 | 0.028117 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.069212 | 0 | 0.028117 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.069696 | 0 | 0.028117 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.15004 | 0 | 0.028117 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.000467 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.2872 | 615 | 0.0281 | 17.2814
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.000467 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.27413 | 587 | 0.0281 | 16.4947
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.000464 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.070296 | 151.5 | 0.028097 | 4.2567
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.000464 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.070667 | 152.3 | 0.028097 | 4.2792
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.000464 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.08236 | 177.5 | 0.028097 | 4.9872
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.000459 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.21252 | 463 | 0.028092 | 13.0066
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.07328 | 160 | 0.028091 | 4.4945
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.071448 | 156 | 0.028091 | 4.3822
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.089768 | 196 | 0.028091 | 5.5058
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.071448 | 156 | 0.028091 | 4.3822
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.071906 | 157 | 0.028091 | 4.4103
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.090684 | 198 | 0.028091 | 5.562
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.000454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.068418 | 150.7 | 0.028087 | 4.2327
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.000454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.068554 | 151 | 0.028087 | 4.2411
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.000454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.08054 | 177.4 | 0.028087 | 4.9826
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.000445 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028078 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.067848 | 0 | 0.028073 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.06864 | 0 | 0.028073 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.06864 | 0 | 0.028073 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.1672 | 0 | 0.028073 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.000436 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.079352 | 182 | 0.028069 | 5.1085
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.000436 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.21102 | 484 | 0.028069 | 13.5854
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.000428 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.050504 | 118 | 0.028061 | 3.3112
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.000428 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.04922 | 115 | 0.028061 | 3.227
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.000428 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.23797 | 556 | 0.028061 | 15.6019
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.000424 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.0212 | 50 | 0.028057 | 1.4028
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.000424 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.028057 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.062012 | 0 | 0.028052 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.05447 | 0 | 0.028052 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.060755 | 0 | 0.028052 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.16718 | 0 | 0.028052 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.000411 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32264 | 785 | 0.028044 | 22.0145
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.000411 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32675 | 795 | 0.028044 | 22.2949
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.000411 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32058 | 780 | 0.028044 | 21.8743
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000357 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.02799 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000357 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.02799 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.000353 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.13696 | 388 | 0.027986 | 10.8585
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.000353 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.1818 | 515 | 0.027986 | 14.4127
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.056028 | 161 | 0.027981 | 4.5049
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.057072 | 164 | 0.027981 | 4.5889
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.057072 | 164 | 0.027981 | 4.5889
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.14407 | 414 | 0.027981 | 11.5841
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.056376 | 162 | 0.027981 | 4.5329
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.056028 | 161 | 0.027981 | 4.5049
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.056724 | 163 | 0.027981 | 4.5609
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.14233 | 409 | 0.027981 | 11.4442
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.000346 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.19307 | 558 | 0.027979 | 15.6122
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.000346 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.20033 | 579 | 0.027979 | 16.1998
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.000346 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.27957 | 808 | 0.027979 | 22.607
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.000341 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.01364 | 40 | 0.027974 | 1.119
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.000336 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.00672 | 20 | 0.027969 | 0.55938
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.000336 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.0084 | 25 | 0.027969 | 0.69922
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.000336 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.013776 | 41 | 0.027969 | 1.1467
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.000328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.025912 | 79 | 0.027961 | 2.2089
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.000328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.034768 | 106 | 0.027961 | 2.9639
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.000328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.047888 | 146 | 0.027961 | 4.0823
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.000328 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.024928 | 76 | 0.027961 | 2.125
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.00027 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.027903 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.000151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.032676 | 216.4 | 0.027784 | 6.0124
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.000151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.032631 | 216.1 | 0.027784 | 6.0041
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 3.4e-05 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.027667 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.027633 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.027633 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.0197 | 100 | 0.027436 | 2.7436
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.000931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.20231 | 217.3 | 0.026702 | 5.8023
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.000931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.19085 | 205 | 0.026702 | 5.4739
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.000931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.2536 | 272.4 | 0.026702 | 7.2736
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.00101 | north | 3 | N | N | Nnorth | Nnorth | 1 | -1.1686 | 0 | 0.026623 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.00101 | north | 3 | N | N | Nnorth | Nnorth | 1 | -1.1696 | 0 | 0.026623 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.007191 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.020442 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.01584 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2314 | 204 | 0.011793 | 2.4058
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.01584 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1838 | 201 | 0.011793 | 2.3704
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.01584 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8333 | 242 | 0.011793 | 2.8539
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.01821 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7315 | 150 | 0.0094229 | 1.4134
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.021242 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0063909 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.024423 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0515 | 84 | 0.0032099 | 0.26963
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.024446 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8701 | 76.5 | 0.0031869 | 0.2438
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.024626 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9701 | 80 | 0.0030069 | 0.24055
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8128 | 112.5 | 0.0026299 | 0.29587
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7379 | 149.5 | 0.0026299 | 0.39317
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.6506 | 186 | 0.0026299 | 0.48916
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3631 | 214.5 | 0.0026299 | 0.56412
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.025094 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2534 | 169.5 | 0.0025389 | 0.43035
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.025225 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7837 | 150 | 0.0024079 | 0.36119
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.025225 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7837 | 150 | 0.0024079 | 0.36119
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.025242 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0194 | 80 | 0.0023909 | 0.19127
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.025246 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0197 | 80 | 0.0023869 | 0.19095
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.025268 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8951 | 75 | 0.0023649 | 0.17737
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.025268 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0214 | 80 | 0.0023649 | 0.18919
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.025268 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.0107 | 40 | 0.0023649 | 0.094597
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.025384 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0307 | 80 | 0.0022489 | 0.17991
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.025384 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0307 | 80 | 0.0022489 | 0.17991
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.025403 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8104 | 150 | 0.0022299 | 0.33449
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.025887 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.12426 | 0 | 0.0017459 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.026269 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.1523 | 120 | 0.0013639 | 0.16367
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.026269 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.1207 | 233 | 0.0013639 | 0.31779
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.026269 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.471 | 170.2 | 0.0013639 | 0.23214
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.7855 | 66 | 0.00057992 | 0.038275
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.7584 | 65 | 0.00057992 | 0.037695
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8126 | 67 | 0.00057992 | 0.038855
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8126 | 67 | 0.00057992 | 0.038855
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8126 | 67 | 0.00057992 | 0.038855
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.027053 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00057992 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.027053 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00057992 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.027128 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.94948 | 35 | 0.00050492 | 0.017672
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.027128 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.81384 | 30 | 0.00050492 | 0.015148
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.6703 | 208.2 | 0.00039792 | 0.082847
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.8701 | 142.1 | 0.00039792 | 0.056544
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.6059 | 132.4 | 0.00039792 | 0.052684
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.704 | 136 | 0.00039792 | 0.054117
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.0035 | 147 | 0.00039792 | 0.058494
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.7194 | 210 | 0.00039792 | 0.083563
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.9065 | 70 | 0.00039692 | 0.027784
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.9065 | 70 | 0.00039692 | 0.027784
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5275 | 92.8 | 0.00039692 | 0.036834
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.1789 | 80 | 0.00039692 | 0.031753
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.1789 | 80 | 0.00039692 | 0.031753
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.1321 | 115 | 0.00039692 | 0.045646
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.027273 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.18 | 6.6 | 0.00035992 | 0.0023755
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.027273 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.93546 | 34.3 | 0.00035992 | 0.012345
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.027311 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0693 | 149 | 0.00032192 | 0.047966
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.027389 | west | 8 | N | N | Nwest | Nwest | 1 | -1.9172 | 0 | 0.00024392 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.027389 | west | 8 | N | N | Nwest | Nwest | 1 | -2.0104 | 0 | 0.00024392 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.027389 | west | 8 | N | N | Nwest | Nwest | 1 | -1.9282 | 0 | 0.00024392 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1112 | 150 | 0.00022492 | 0.033738
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.0298 | 220 | 0.00022492 | 0.049482
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.4816 | 200 | 0.00022492 | 0.044984
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.341 | 121.9 | 0.00022492 | 0.027418
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.027625 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4531 | 125 | 7.9184e-06 | 0.00098981
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.027625 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4531 | 125 | 7.9184e-06 | 0.00098981
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.02767 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7808 | 100.5 | -3.7082e-05 | -0.0037267
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.027687 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.6058 | 58 | -5.4082e-05 | -0.0031367
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.027771 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.9485 | 214.2 | -0.00013808 | -0.029577
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.042 | 37.5 | -0.00015408 | -0.0057781
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9871 | 107.5 | -0.00015408 | -0.016564
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7512 | 135 | -0.00015408 | -0.020801
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.3067 | 119 | -0.00015408 | -0.018336
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9176 | 105 | -0.00015408 | -0.016179
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2369 | 80.5 | -0.00015408 | -0.012404
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.8192 | 209 | -0.00021008 | -0.043907
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5221 | 126.5 | -0.00021008 | -0.026575
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9329 | 249 | -0.00021008 | -0.05231
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.4851 | 197 | -0.00021008 | -0.041386
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.028011 | west | 8 | N | N | Nwest | Nwest | 1 | -0.72268 | 0 | -0.00037808 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8666 | 66 | -0.00064908 | -0.042839
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.9515 | 69 | -0.00064908 | -0.044787
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.9515 | 69 | -0.00064908 | -0.044787
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8949 | 67 | -0.00064908 | -0.043488
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8949 | 67 | -0.00064908 | -0.043488
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8383 | 65 | -0.00064908 | -0.04219
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.028429 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4115 | 120 | -0.00079608 | -0.09553
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.028584 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4301 | 120 | -0.00095108 | -0.11413
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.028914 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.5656 | 400 | -0.0012811 | -0.51243
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.028916 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.8242 | 236 | -0.0012831 | -0.30281
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.029156 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.5601 | 225 | -0.0015231 | -0.34269
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.029234 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2621 | 180 | -0.0016011 | -0.28819
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.029234 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2621 | 180 | -0.0016011 | -0.28819
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.029284 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.8319 | 165 | -0.0016511 | -0.27243
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.029354 | west | 4 | Y | N | Ywest | Nwest | 1 | -19.0713 | 649.7 | -0.0017211 | -1.1182
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.029654 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4481 | 150 | -0.0020211 | -0.30316
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.029654 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9951 | 101 | -0.0020211 | -0.20413
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.029694 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8707 | 63 | -0.0020611 | -0.12985
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.030131 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2485 | 141 | -0.0024981 | -0.35223
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.030131 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6157 | 120 | -0.0024981 | -0.29977
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.03019 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9888 | 99 | -0.0025571 | -0.25315
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.03019 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8416 | 61 | -0.0025571 | -0.15598
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.03019 | west | 7 | N | N | Nwest | Nwest | 1 | -0.75475 | 0 | -0.0025571 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.03019 | west | 7 | N | N | Nwest | Nwest | 1 | -1.3797 | 0 | -0.0025571 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.03019 | west | 7 | N | N | Nwest | Nwest | 1 | -1.3797 | 0 | -0.0025571 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.03045 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.1447 | 366 | -0.0028171 | -1.0311
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6302 | 84 | -0.0036791 | -0.30904
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.000637 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.36245 | 569 | -0.0039162 | -2.2283
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.000637 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.3701 | 581 | -0.0039162 | -2.2753
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.060031 | 0 | -0.0042062 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.054132 | 0 | -0.0042062 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.053438 | 0 | -0.0042062 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.053438 | 0 | -0.0042062 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.056214 | 0 | -0.0042062 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.018872 | 56 | -0.0042162 | -0.23611
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.019883 | 59 | -0.0042162 | -0.24876
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.018872 | 56 | -0.0042162 | -0.23611
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.018872 | 56 | -0.0042162 | -0.23611
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.019883 | 59 | -0.0042162 | -0.24876
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.018872 | 56 | -0.0042162 | -0.23611
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.000336 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.13373 | 398 | -0.0042172 | -1.6785
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.054538 | 0 | -0.0042182 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.054069 | 0 | -0.0042182 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.053232 | 0 | -0.0042182 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.090182 | 0 | -0.0042182 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.000333 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 0.24742 | 743 | -0.0042202 | -3.1356
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.000333 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.003996 | 12 | -0.0042202 | -0.050643
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021645 | 0 | -0.0042202 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021978 | 0 | -0.0042202 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02331 | 0 | -0.0042202 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020979 | 0 | -0.0042202 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020646 | 0 | -0.0042202 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.034632 | 0 | -0.0042202 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.019647 | 0 | -0.0042202 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.001665 | 0 | -0.0042202 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.006993 | 0 | -0.0042202 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.000333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.057276 | 172 | -0.0042202 | -0.72588
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.000333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.057276 | 172 | -0.0042202 | -0.72588
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.000333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.057276 | 172 | -0.0042202 | -0.72588
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.000333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.052281 | 0 | -0.0042202 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.000332 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.052456 | 158 | -0.0042212 | -0.66695
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.000332 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.05312 | 160 | -0.0042212 | -0.67539
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.000332 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0581 | 175 | -0.0042212 | -0.73871
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.000332 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.003984 | 12 | -0.0042212 | -0.050655
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.011254 | 0 | -0.0042222 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.011486 | 0 | -0.0042222 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.010824 | 0 | -0.0042222 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.015193 | 0 | -0.0042222 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0058587 | 0 | -0.0042222 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0067524 | 0 | -0.0042222 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0065869 | 0 | -0.0042222 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.011585 | 0 | -0.0042222 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.005958 | 0 | -0.0042222 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.028267 | 0 | -0.0042222 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.048988 | 0 | -0.0042222 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.03432 | 104 | -0.0042232 | -0.43921
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.03432 | 104 | -0.0042232 | -0.43921
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01782 | 54 | -0.0042232 | -0.22805
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01749 | 53 | -0.0042232 | -0.22383
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01782 | 54 | -0.0042232 | -0.22805
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01881 | 57 | -0.0042232 | -0.24072
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01782 | 54 | -0.0042232 | -0.22805
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01782 | 54 | -0.0042232 | -0.22805
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01914 | 58 | -0.0042232 | -0.24495
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01914 | 58 | -0.0042232 | -0.24495
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.00033 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 0.24255 | 735 | -0.0042232 | -3.1041
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.000327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.044472 | 0 | -0.0042262 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.056571 | 0 | -0.0042262 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.000327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.044145 | 0 | -0.0042262 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.013692 | 42 | -0.0042272 | -0.17754
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.013692 | 42 | -0.0042272 | -0.17754
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.012388 | 38 | -0.0042272 | -0.16063
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.012388 | 38 | -0.0042272 | -0.16063
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.023075 | 0 | -0.0042282 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0234 | 0 | -0.0042282 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.012675 | 0 | -0.0042282 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.00975 | 0 | -0.0042282 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.048276 | 0 | -0.0042292 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021092 | 0 | -0.0042292 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.000324 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.05832 | 0 | -0.0042292 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.000324 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.051386 | 0 | -0.0042292 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.000324 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.050868 | 0 | -0.0042292 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.000324 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.073872 | 228 | -0.0042292 | -0.96426
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020736 | 0 | -0.0042292 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020477 | 0 | -0.0042292 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.026762 | 0 | -0.0042292 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.023846 | 0 | -0.0042292 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0052488 | 0 | -0.0042292 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.000324 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.069012 | 213 | -0.0042292 | -0.90082
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.000323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.011305 | 0 | -0.0042302 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.000323 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.053295 | 165 | -0.0042302 | -0.69798
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.000323 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.054587 | 169 | -0.0042302 | -0.71491
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.000323 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.003876 | 12 | -0.0042302 | -0.050763
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.000323 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0042302 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.014812 | 46 | -0.0042312 | -0.19464
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.014812 | 46 | -0.0042312 | -0.19464
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.014812 | 46 | -0.0042312 | -0.19464
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.01771 | 55 | -0.0042312 | -0.23272
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.01771 | 55 | -0.0042312 | -0.23272
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.017388 | 54 | -0.0042312 | -0.22849
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.05255 | 0 | -0.0042312 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.050586 | 0 | -0.0042312 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.050715 | 0 | -0.0042312 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.050554 | 0 | -0.0042312 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.086618 | 0 | -0.0042312 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.000321 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.025038 | 0 | -0.0042322 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.000321 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02568 | 0 | -0.0042322 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02067 | 0 | -0.0042352 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.01908 | 0 | -0.0042352 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02067 | 0 | -0.0042352 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02067 | 0 | -0.0042352 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.028847 | 0 | -0.0042362 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.027769 | 0 | -0.0042362 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.027579 | 0 | -0.0042362 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.017277 | 0 | -0.0042362 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0038674 | 0 | -0.0042362 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.000313 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0042402 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.000311 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01555 | 50 | -0.0042422 | -0.21211
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01302 | 42 | -0.0042432 | -0.17821
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01364 | 44 | -0.0042432 | -0.1867
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01364 | 44 | -0.0042432 | -0.1867
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01457 | 47 | -0.0042432 | -0.19943
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.000307 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.040524 | 132 | -0.0042462 | -0.5605
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.000307 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.041138 | 134 | -0.0042462 | -0.56899
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.000307 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.099161 | 323 | -0.0042462 | -1.3715
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021594 | 0 | -0.0042482 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020344 | 0 | -0.0042482 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.016165 | 0 | -0.0042482 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.046726 | 0 | -0.0042482 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.046817 | 0 | -0.0042482 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.046451 | 0 | -0.0042482 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02928 | 0 | -0.0042482 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.07442 | 0 | -0.0042482 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0122 | 0 | -0.0042482 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.00976 | 0 | -0.0042482 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.00915 | 0 | -0.0042482 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.030592 | 0 | -0.0042482 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.028334 | 0 | -0.0042482 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.031323 | 0 | -0.0042482 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.03111 | 0 | -0.0042482 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.000299 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.045597 | 152.5 | -0.0042542 | -0.64877
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.000299 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0447 | 149.5 | -0.0042542 | -0.636
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.000299 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.069547 | 232.6 | -0.0042542 | -0.98953
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.000298 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.047978 | 161 | -0.0042552 | -0.68509
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.000298 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.049468 | 166 | -0.0042552 | -0.70637
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.000298 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.073904 | 248 | -0.0042552 | -1.0553
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.000298 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 0.16271 | 546 | -0.0042552 | -2.3233
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.000298 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 0.19161 | 0 | -0.0042552 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.000298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.003874 | 13 | -0.0042552 | -0.055318
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.000293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.047759 | 0 | -0.0042602 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.000293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.047759 | 0 | -0.0042602 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.000293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.071785 | 0 | -0.0042602 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.000293 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 0.19074 | 651 | -0.0042602 | -2.7734
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.000293 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 0.16525 | 564 | -0.0042602 | -2.4028
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.000293 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 0.1758 | 600 | -0.0042602 | -2.5561
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.000293 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.009669 | 0 | -0.0042602 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.000289 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.08959 | 310 | -0.0042642 | -1.3219
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.000289 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11936 | 413 | -0.0042642 | -1.7611
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.000289 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.013323 | 0 | -0.0042642 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.000286 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.16702 | 584 | -0.0042672 | -2.4921
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.000286 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.17017 | 595 | -0.0042672 | -2.539
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.000285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.12341 | 433 | -0.0042682 | -1.8481
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0141 | 50 | -0.0042712 | -0.21356
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0141 | 50 | -0.0042712 | -0.21356
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0141 | 50 | -0.0042712 | -0.21356
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0141 | 50 | -0.0042712 | -0.21356
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.013475 | 49 | -0.0042782 | -0.20963
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01265 | 46 | -0.0042782 | -0.1968
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01265 | 46 | -0.0042782 | -0.1968
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012925 | 47 | -0.0042782 | -0.20108
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.000275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.04235 | 154 | -0.0042782 | -0.65884
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.000275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0407 | 148 | -0.0042782 | -0.63318
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0132 | 48 | -0.0042782 | -0.20535
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0132 | 48 | -0.0042782 | -0.20535
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.000272 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002176 | 0 | -0.0042812 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.000272 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002176 | 0 | -0.0042812 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.029748 | 0 | -0.0042852 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.029748 | 0 | -0.0042852 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.031892 | 0 | -0.0042852 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.029346 | 0 | -0.0042852 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.00026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01846 | 0 | -0.0042932 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.00026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0026 | 0 | -0.0042932 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.015624 | 0 | -0.0043012 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.017993 | 0 | -0.0043012 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01134 | 0 | -0.0043012 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.025452 | 0 | -0.0043012 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021672 | 0 | -0.0043012 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.022176 | 0 | -0.0043012 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0126 | 0 | -0.0043012 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.004536 | 0 | -0.0043012 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.023688 | 0 | -0.0043012 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01764 | 0 | -0.0043012 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.015876 | 0 | -0.0043012 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.018144 | 0 | -0.0043012 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01633 | 0 | -0.0043012 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.025452 | 0 | -0.0043012 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.024444 | 0 | -0.0043012 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.025956 | 0 | -0.0043012 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.019152 | 0 | -0.0043012 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02016 | 0 | -0.0043012 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02016 | 0 | -0.0043012 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.043092 | 0 | -0.0043012 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.016492 | 76 | -0.0043362 | -0.32955
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.016492 | 76 | -0.0043362 | -0.32955
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.022785 | 105 | -0.0043362 | -0.4553
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.016058 | 74 | -0.0043362 | -0.32088
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.016058 | 74 | -0.0043362 | -0.32088
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.022134 | 102 | -0.0043362 | -0.44229
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.000216 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.014256 | 66 | -0.0043372 | -0.28626
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.000205 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 0.27326 | 0 | -0.0043482 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.000205 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 0.27224 | 0 | -0.0043482 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 9.5e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.003325 | 0 | -0.0044582 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 9.5e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00323 | 0 | -0.0044582 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 9.5e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.003325 | 0 | -0.0044582 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.013434 | 223.9 | -0.0044932 | -1.006
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0135 | 225 | -0.0044932 | -1.011
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.013476 | 224.6 | -0.0044932 | -1.0092
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.013602 | 226.7 | -0.0044932 | -1.0186
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 5.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0001368 | 0 | -0.0044962 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 5.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0001368 | 0 | -0.0044962 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 3.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.000222 | 0 | -0.0045162 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 2.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.000336 | 0 | -0.0045252 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 2.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 6.48e-05 | 0 | -0.0045262 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 2.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 6.48e-05 | 0 | -0.0045262 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 2.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 7.56e-05 | 0 | -0.0045262 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.002982 | 142 | -0.0045322 | -0.64357
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.003045 | 145 | -0.0045322 | -0.65717
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.003171 | 151 | -0.0045322 | -0.68436
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.00609 | 290 | -0.0045322 | -1.3143
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001027 | 0 | -0.0045402 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001053 | 0 | -0.0045402 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001027 | 0 | -0.0045402 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00104 | 0 | -0.0045402 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0010192 | 0 | -0.0045402 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000325 | 0 | -0.0045402 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000598 | 0 | -0.0045402 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000364 | 0 | -0.0045402 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0005668 | 0 | -0.0045402 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000962 | 0 | -0.0045402 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 7e-06 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000336 | 0 | -0.0045462 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0045532 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0045532 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000448 | 0 | -0.0045692 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000112 | 0 | -0.0045692 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000624 | 0 | -0.0045692 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00024 | 0 | -0.0045692 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000112 | 0 | -0.0045692 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00024 | 0 | -0.0045692 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000624 | 0 | -0.0045692 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000624 | 0 | -0.0045692 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -1.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.2e-05 | 0 | -0.0045712 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.002646 | 147 | -0.0045712 | -0.67197
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.002484 | 138 | -0.0045712 | -0.63083
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.00252 | 140 | -0.0045712 | -0.63997
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.002646 | 147 | -0.0045712 | -0.67197
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.003276 | 182 | -0.0045712 | -0.83196
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.003564 | 198 | -0.0045712 | -0.9051
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -2.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000315 | 0 | -0.0045742 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -2.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000483 | 0 | -0.0045742 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -2.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000168 | 0 | -0.0045742 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -2.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.001898 | 0 | -0.0045792 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -3.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.004464 | 144 | -0.0045842 | -0.66013
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -3.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.005828 | 188 | -0.0045842 | -0.86183
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0020511 | 47.7 | -0.0045962 | -0.21924
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0016039 | 37.3 | -0.0045962 | -0.17144
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.001978 | 46 | -0.0045962 | -0.21143
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.002064 | 48 | -0.0045962 | -0.22062
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -6.3e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.001386 | 22 | -0.0046162 | -0.10156
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -6.3e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.000693 | 11 | -0.0046162 | -0.050778
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -6.3e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.000693 | 11 | -0.0046162 | -0.050778
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -9e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.05661 | 629 | -0.0046432 | -2.9206
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.014852 | 0 | -0.0046472 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.014382 | 0 | -0.0046472 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.0094 | 0 | -0.0046472 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.01363 | 0 | -0.0046472 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.013818 | 0 | -0.0046472 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.011938 | 0 | -0.0046472 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -9.4e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.001128 | 0 | -0.0046472 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -9.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.05187 | 546 | -0.0046482 | -2.5379
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -9.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.07125 | 750 | -0.0046482 | -3.4862
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 25 | -0.0046532 | -0.11633
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 25 | -0.0046532 | -0.11633
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 25 | -0.0046532 | -0.11633
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0016 | 16 | -0.0046532 | -0.074451
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 25 | -0.0046532 | -0.11633
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 25 | -0.0046532 | -0.11633
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 25 | -0.0046532 | -0.11633
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0015 | 15 | -0.0046532 | -0.069798
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000106 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01643 | 155 | -0.0046592 | -0.72218
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.000106 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01802 | 170 | -0.0046592 | -0.79207
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000106 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01643 | 155 | -0.0046592 | -0.72218
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.000108 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01944 | 180 | -0.0046612 | -0.83902
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.000108 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.036288 | 336 | -0.0046612 | -1.5662
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.000108 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01944 | 180 | -0.0046612 | -0.83902
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.000108 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.016016 | 0 | -0.0046612 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.000108 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.016049 | 0 | -0.0046612 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.000108 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.016524 | 0 | -0.0046612 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.00011 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.03674 | 334 | -0.0046632 | -1.5575
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.00011 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.0374 | 340 | -0.0046632 | -1.5855
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.00011 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0198 | 180 | -0.0046632 | -0.83938
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.00011 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0198 | 180 | -0.0046632 | -0.83938
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.000112 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0046652 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.000112 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0046652 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.000112 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0046652 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.000112 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.004256 | 0 | -0.0046652 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.000112 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0028 | 0 | -0.0046652 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.000112 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0028 | 0 | -0.0046652 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.000114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.004332 | 0 | -0.0046672 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.000122 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.003538 | 0 | -0.0046752 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.01222 | 94 | -0.0046832 | -0.44022
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00533 | 41 | -0.0046832 | -0.19201
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00494 | 38 | -0.0046832 | -0.17796
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00247 | 19 | -0.0046832 | -0.088981
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.01222 | 94 | -0.0046832 | -0.44022
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00468 | 36 | -0.0046832 | -0.1686
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00559 | 43 | -0.0046832 | -0.20138
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00286 | 22 | -0.0046832 | -0.10303
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.01924 | 148 | -0.0046832 | -0.69312
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0065 | 50 | -0.0046832 | -0.23416
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00715 | 55 | -0.0046832 | -0.25758
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0065 | 50 | -0.0046832 | -0.23416
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.000137 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0046902 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.000137 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.005206 | 38 | -0.0046902 | -0.17823
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.000137 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.0026441 | 19.3 | -0.0046902 | -0.090521
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.000137 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.002055 | 15 | -0.0046902 | -0.070353
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.000137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.006439 | 47 | -0.0046902 | -0.22044
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.000143 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.060632 | 424 | -0.0046962 | -1.9912
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.000143 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.060775 | 425 | -0.0046962 | -1.9959
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.000151 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.062212 | 412 | -0.0047042 | -1.9381
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.000151 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.0604 | 400 | -0.0047042 | -1.8817
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.000152 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.031768 | 209 | -0.0047052 | -0.98339
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.000152 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.032832 | 216 | -0.0047052 | -1.0163
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.006992 | 46 | -0.0047052 | -0.21644
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.007144 | 47 | -0.0047052 | -0.22114
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.006992 | 46 | -0.0047052 | -0.21644
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.006992 | 46 | -0.0047052 | -0.21644
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.000154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.022176 | 144 | -0.0047072 | -0.67784
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.000154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.022176 | 144 | -0.0047072 | -0.67784
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.000154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.026334 | 171 | -0.0047072 | -0.80493
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.000155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.032085 | 207 | -0.0047082 | -0.9746
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.000155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.033589 | 216.7 | -0.0047082 | -1.0203
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.000155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.03751 | 242 | -0.0047082 | -1.1394
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.000166 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.067562 | 407 | -0.0047192 | -1.9207
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.000184 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.026956 | 146.5 | -0.0047372 | -0.694
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.000184 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.027214 | 147.9 | -0.0047372 | -0.70063
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.000184 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.031832 | 173 | -0.0047372 | -0.81954
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.00019 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.07524 | 396 | -0.0047432 | -1.8783
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.00019 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0047432 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.022458 | 114 | -0.0047502 | -0.54152
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.043734 | 222 | -0.0047502 | -1.0545
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.036248 | 184 | -0.0047502 | -0.87404
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.044128 | 224 | -0.0047502 | -1.064
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.022655 | 115 | -0.0047502 | -0.54627
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.00021 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.01218 | 58 | -0.0047632 | -0.27627
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.00021 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.01869 | 89 | -0.0047632 | -0.42393
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00924 | 44 | -0.0047632 | -0.20958
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00924 | 44 | -0.0047632 | -0.20958
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00903 | 43 | -0.0047632 | -0.20482
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00945 | 45 | -0.0047632 | -0.21434
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.000218 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0047712 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.000335 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00603 | 0 | -0.0048882 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.000335 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00603 | 0 | -0.0048882 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.000363 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004356 | 0 | -0.0049162 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.000363 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.003993 | 0 | -0.0049162 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.000363 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004356 | 0 | -0.0049162 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.000381 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.006858 | 0 | -0.0049342 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.000381 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.006858 | 0 | -0.0049342 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.000381 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.005715 | 0 | -0.0049342 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000458 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012824 | 0 | -0.0050112 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000458 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.013282 | 0 | -0.0050112 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.000525 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.22155 | 422 | -0.0050782 | -2.143
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.000533 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0050862 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.000724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0724 | 100 | -0.0052772 | -0.52772
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.000724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0724 | 100 | -0.0052772 | -0.52772
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000724 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052772 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000724 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052772 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000724 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052772 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000724 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052772 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.000725 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052782 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.000743 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010179 | 0 | -0.0052962 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.001073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.025752 | 24 | -0.0056262 | -0.13503
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.001073 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.025752 | 24 | -0.0056262 | -0.13503
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.001073 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.024679 | 23 | -0.0056262 | -0.1294
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.68792 | 20 | -0.0067631 | -0.13526
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.68792 | 20 | -0.0067631 | -0.13526
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.68792 | 20 | -0.0067631 | -0.13526
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.58473 | 17 | -0.0067631 | -0.11497
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.036236 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.4354 | 150 | -0.0086031 | -1.2905
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.004763 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0093162 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.005211 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.031266 | 0 | -0.0097642 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.038454 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3072 | 60 | -0.010821 | -0.64926
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.007137 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.23552 | 0 | -0.01169 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.007137 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17843 | 0 | -0.01169 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.007137 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.01169 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.1301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -31.4835 | 242 | -0.10246 | -24.7963

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1596 GRAHAMSW - 1601 GRAHAME_ C: 37980 TNWICKET- 38000 TNPYOTE C: 38000 TNPYOTE_ - 38020 TNWORSHA C: 38020 TNWORSHA - 38040 TNH20__ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.1301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -31.4835 | 242 | -0.10246 | -24.7963 | 242 | 24.7963
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.007137 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.23552 | 0 | -0.01169 | 0 | 242 | 24.7963
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.007137 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17843 | 0 | -0.01169 | 0 | 242 | 24.7963
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.007137 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.01169 | 0 | 242 | 24.7963 | Weighted Shift Factors
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.038454 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3072 | 0 | -0.010821 | 0 | 242 | 24.7963 | North | 0.0045532
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.005211 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.031266 | 0 | -0.0097642 | 0 | 242 | 24.7963 | West | -0.027633
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.004763 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0093162 | 0 | 242 | 24.7963 |  | 0.032186
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.036236 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.4354 | 0 | -0.0086031 | 0 | 242 | 24.7963
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.68792 | 20 | -0.0067631 | -0.13526 | 262 | 24.9316 | Line Rating | 290.5
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.68792 | 20 | -0.0067631 | -0.13526 | 282 | 25.0668 | Conc Gen | 568.6
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.68792 | 20 | -0.0067631 | -0.13526 | 302 | 25.2021 | Weighted Imp. | 26.7583
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.034396 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.58473 | 17 | -0.0067631 | -0.11497 | 319 | 25.3171 | PTDF | 0.04706
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 327.4 | 25.3659
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 335.8 | 25.4147 | Concentration | 1.4621
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 344.2 | 25.4635
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 352.6 | 25.5123
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 361 | 25.5611
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 369.4 | 25.6098
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 377.8 | 25.6586
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 386.2 | 25.7074
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 394.6 | 25.7562
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 403 | 25.805
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 411.4 | 25.8538
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 419.8 | 25.9026
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 428.2 | 25.9514
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 436.6 | 26.0002
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 445 | 26.049
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 453.4 | 26.0978
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 461.8 | 26.1466
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 470.2 | 26.1954
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 478.6 | 26.2442
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 487 | 26.293
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 495.4 | 26.3418
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 503.8 | 26.3906
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 512.2 | 26.4394
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.001256 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.01055 | 8.4 | -0.0058092 | -0.048797 | 520.6 | 26.4882
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.001073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.025752 | 24 | -0.0056262 | -0.13503 | 544.6 | 26.6232
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.001073 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.025752 | 24 | -0.0056262 | -0.13503 | 568.6 | 26.7583
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.001073 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.024679 | 23 | -0.0056262 | -0.1294
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.000743 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010179 | 0 | -0.0052962 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.000725 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052782 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.000724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0724 | 100 | -0.0052772 | -0.52772
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.000724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0724 | 100 | -0.0052772 | -0.52772
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000724 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052772 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000724 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052772 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.000724 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052772 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.000724 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0052772 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.000533 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0050862 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.000525 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.22155 | 422 | -0.0050782 | -2.143
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000458 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012824 | 0 | -0.0050112 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000458 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.013282 | 0 | -0.0050112 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.000381 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.006858 | 0 | -0.0049342 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.000381 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.006858 | 0 | -0.0049342 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.000381 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.005715 | 0 | -0.0049342 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.000363 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004356 | 0 | -0.0049162 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.000363 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.003993 | 0 | -0.0049162 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.000363 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004356 | 0 | -0.0049162 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.000335 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00603 | 0 | -0.0048882 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.000335 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00603 | 0 | -0.0048882 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.000218 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0047712 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.00021 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.01218 | 58 | -0.0047632 | -0.27627
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.00021 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.01869 | 89 | -0.0047632 | -0.42393
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00924 | 44 | -0.0047632 | -0.20958
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00924 | 44 | -0.0047632 | -0.20958
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00903 | 43 | -0.0047632 | -0.20482
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.00021 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00945 | 45 | -0.0047632 | -0.21434
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.022458 | 0 | -0.0047502 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.043734 | 0 | -0.0047502 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.036248 | 0 | -0.0047502 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.044128 | 0 | -0.0047502 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.022655 | 0 | -0.0047502 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.00019 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0047432 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.00019 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.07524 | 0 | -0.0047432 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.000184 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.026956 | 146.5 | -0.0047372 | -0.694
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.000184 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.027214 | 147.9 | -0.0047372 | -0.70063
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.000184 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.031832 | 173 | -0.0047372 | -0.81954
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.000166 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.067562 | 407 | -0.0047192 | -1.9207
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.000155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.032085 | 207 | -0.0047082 | -0.9746
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.000155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.033589 | 216.7 | -0.0047082 | -1.0203
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.000155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.03751 | 242 | -0.0047082 | -1.1394
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.000154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.022176 | 144 | -0.0047072 | -0.67784
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.000154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.022176 | 144 | -0.0047072 | -0.67784
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.000154 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.026334 | 171 | -0.0047072 | -0.80493
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.000152 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.031768 | 209 | -0.0047052 | -0.98339
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.000152 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.032832 | 216 | -0.0047052 | -1.0163
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.006992 | 46 | -0.0047052 | -0.21644
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.007144 | 47 | -0.0047052 | -0.22114
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.006992 | 46 | -0.0047052 | -0.21644
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.000152 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.006992 | 46 | -0.0047052 | -0.21644
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.000151 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.062212 | 412 | -0.0047042 | -1.9381
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.000151 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.0604 | 400 | -0.0047042 | -1.8817
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.000143 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.060632 | 0 | -0.0046962 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.000143 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.060775 | 0 | -0.0046962 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.000137 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.005206 | 38 | -0.0046902 | -0.17823
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.000137 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.0026441 | 19.3 | -0.0046902 | -0.090521
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.000137 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.002055 | 15 | -0.0046902 | -0.070353
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.000137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.006439 | 47 | -0.0046902 | -0.22044
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.000137 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0046902 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.01222 | 0 | -0.0046832 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00533 | 0 | -0.0046832 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00494 | 0 | -0.0046832 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00247 | 0 | -0.0046832 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.01222 | 0 | -0.0046832 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00468 | 0 | -0.0046832 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00559 | 0 | -0.0046832 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00286 | 0 | -0.0046832 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.01924 | 0 | -0.0046832 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0065 | 0 | -0.0046832 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.00715 | 0 | -0.0046832 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.00013 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0065 | 0 | -0.0046832 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.000122 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.003538 | 0 | -0.0046752 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.000114 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.004332 | 0 | -0.0046672 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.000112 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0028 | 0 | -0.0046652 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.000112 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0028 | 0 | -0.0046652 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.000112 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.004256 | 0 | -0.0046652 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.000112 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0046652 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.000112 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0046652 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.000112 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0046652 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.00011 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.03674 | 334 | -0.0046632 | -1.5575
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.00011 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.0374 | 340 | -0.0046632 | -1.5855
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.00011 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0198 | 180 | -0.0046632 | -0.83938
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.00011 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0198 | 180 | -0.0046632 | -0.83938
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.000108 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.016016 | 0 | -0.0046612 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.000108 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.016049 | 0 | -0.0046612 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.000108 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.016524 | 0 | -0.0046612 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.000108 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.036288 | 336 | -0.0046612 | -1.5662
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.000108 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01944 | 180 | -0.0046612 | -0.83902
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.000108 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01944 | 180 | -0.0046612 | -0.83902
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000106 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01643 | 155 | -0.0046592 | -0.72218
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.000106 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01802 | 170 | -0.0046592 | -0.79207
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000106 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01643 | 155 | -0.0046592 | -0.72218
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 0 | -0.0046532 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 0 | -0.0046532 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 0 | -0.0046532 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0016 | 0 | -0.0046532 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 0 | -0.0046532 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 0 | -0.0046532 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0025 | 0 | -0.0046532 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.0001 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0015 | 0 | -0.0046532 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -9.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.05187 | 0 | -0.0046482 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -9.5e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.07125 | 0 | -0.0046482 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.014852 | 0 | -0.0046472 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.014382 | 0 | -0.0046472 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.0094 | 0 | -0.0046472 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.01363 | 0 | -0.0046472 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.013818 | 0 | -0.0046472 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -9.4e-05 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.011938 | 0 | -0.0046472 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -9.4e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.001128 | 0 | -0.0046472 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -9e-05 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.05661 | 0 | -0.0046432 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -6.3e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.001386 | 22 | -0.0046162 | -0.10156
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -6.3e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.000693 | 11 | -0.0046162 | -0.050778
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -6.3e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.000693 | 11 | -0.0046162 | -0.050778
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0020511 | 47.7 | -0.0045962 | -0.21924
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0016039 | 37.3 | -0.0045962 | -0.17144
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.001978 | 46 | -0.0045962 | -0.21143
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -4.3e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.002064 | 48 | -0.0045962 | -0.22062
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -3.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.004464 | 144 | -0.0045842 | -0.66013
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -3.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.005828 | 188 | -0.0045842 | -0.86183
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -2.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.001898 | 0 | -0.0045792 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -2.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000168 | 0 | -0.0045742 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -2.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000315 | 0 | -0.0045742 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -2.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000483 | 0 | -0.0045742 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.002646 | 147 | -0.0045712 | -0.67197
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.002484 | 138 | -0.0045712 | -0.63083
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.00252 | 140 | -0.0045712 | -0.63997
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.002646 | 147 | -0.0045712 | -0.67197
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.003276 | 182 | -0.0045712 | -0.83196
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -1.8e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.003564 | 198 | -0.0045712 | -0.9051
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -1.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.2e-05 | 0 | -0.0045712 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000448 | 0 | -0.0045692 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000112 | 0 | -0.0045692 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000624 | 0 | -0.0045692 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00024 | 0 | -0.0045692 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000112 | 0 | -0.0045692 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00024 | 0 | -0.0045692 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000624 | 0 | -0.0045692 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -1.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.000624 | 0 | -0.0045692 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045532 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0045532 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0045532 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 7e-06 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000336 | 0 | -0.0045462 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001027 | 0 | -0.0045402 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001053 | 0 | -0.0045402 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001027 | 0 | -0.0045402 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00104 | 0 | -0.0045402 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0010192 | 0 | -0.0045402 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000325 | 0 | -0.0045402 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000598 | 0 | -0.0045402 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000364 | 0 | -0.0045402 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0005668 | 0 | -0.0045402 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 1.3e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.000962 | 0 | -0.0045402 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.002982 | 142 | -0.0045322 | -0.64357
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.003045 | 145 | -0.0045322 | -0.65717
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.003171 | 151 | -0.0045322 | -0.68436
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 2.1e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.00609 | 290 | -0.0045322 | -1.3143
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 2.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 6.48e-05 | 0 | -0.0045262 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 2.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 6.48e-05 | 0 | -0.0045262 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 2.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 7.56e-05 | 0 | -0.0045262 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 2.8e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.000336 | 0 | -0.0045252 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 3.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.000222 | 0 | -0.0045162 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 5.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0001368 | 0 | -0.0044962 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 5.7e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0001368 | 0 | -0.0044962 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.013434 | 223.9 | -0.0044932 | -1.006
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0135 | 225 | -0.0044932 | -1.011
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.013476 | 224.6 | -0.0044932 | -1.0092
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 6e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.013602 | 226.7 | -0.0044932 | -1.0186
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 9.5e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.003325 | 0 | -0.0044582 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 9.5e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00323 | 0 | -0.0044582 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 9.5e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.003325 | 0 | -0.0044582 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.000205 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 0.27326 | 0 | -0.0043482 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.000205 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 0.27224 | 0 | -0.0043482 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.000216 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.014256 | 66 | -0.0043372 | -0.28626
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.016492 | 76 | -0.0043362 | -0.32955
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.016492 | 76 | -0.0043362 | -0.32955
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.022785 | 105 | -0.0043362 | -0.4553
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.016058 | 74 | -0.0043362 | -0.32088
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.016058 | 74 | -0.0043362 | -0.32088
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.000217 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.022134 | 102 | -0.0043362 | -0.44229
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.015624 | 0 | -0.0043012 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.017993 | 0 | -0.0043012 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01134 | 0 | -0.0043012 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.025452 | 0 | -0.0043012 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021672 | 0 | -0.0043012 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.022176 | 0 | -0.0043012 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0126 | 0 | -0.0043012 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.004536 | 0 | -0.0043012 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.023688 | 0 | -0.0043012 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01764 | 0 | -0.0043012 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.015876 | 0 | -0.0043012 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.018144 | 0 | -0.0043012 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01633 | 0 | -0.0043012 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.025452 | 0 | -0.0043012 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.024444 | 0 | -0.0043012 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.025956 | 0 | -0.0043012 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.019152 | 0 | -0.0043012 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02016 | 0 | -0.0043012 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02016 | 0 | -0.0043012 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.000252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.043092 | 0 | -0.0043012 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.00026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.01846 | 0 | -0.0042932 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.00026 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0026 | 0 | -0.0042932 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.029748 | 0 | -0.0042852 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.029748 | 0 | -0.0042852 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.031892 | 0 | -0.0042852 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.000268 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.029346 | 0 | -0.0042852 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.000272 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002176 | 0 | -0.0042812 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.000272 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002176 | 0 | -0.0042812 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.013475 | 49 | -0.0042782 | -0.20963
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01265 | 46 | -0.0042782 | -0.1968
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01265 | 46 | -0.0042782 | -0.1968
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.012925 | 47 | -0.0042782 | -0.20108
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.000275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.04235 | 154 | -0.0042782 | -0.65884
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.000275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0407 | 148 | -0.0042782 | -0.63318
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0132 | 48 | -0.0042782 | -0.20535
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.000275 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0132 | 48 | -0.0042782 | -0.20535
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0141 | 50 | -0.0042712 | -0.21356
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0141 | 50 | -0.0042712 | -0.21356
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0141 | 50 | -0.0042712 | -0.21356
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.000282 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.0141 | 50 | -0.0042712 | -0.21356
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.000285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.12341 | 0 | -0.0042682 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.000286 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.16702 | 0 | -0.0042672 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.000286 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.17017 | 0 | -0.0042672 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.000289 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.013323 | 0 | -0.0042642 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.000289 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.08959 | 310 | -0.0042642 | -1.3219
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.000289 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11936 | 413 | -0.0042642 | -1.7611
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.000293 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.009669 | 0 | -0.0042602 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.000293 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 0.19074 | 0 | -0.0042602 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.000293 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 0.16525 | 0 | -0.0042602 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.000293 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 0.1758 | 0 | -0.0042602 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.000293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.047759 | 0 | -0.0042602 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.000293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.047759 | 0 | -0.0042602 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.000293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.071785 | 0 | -0.0042602 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.000298 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.047978 | 161 | -0.0042552 | -0.68509
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.000298 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.049468 | 166 | -0.0042552 | -0.70637
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.000298 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.073904 | 248 | -0.0042552 | -1.0553
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.000298 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 0.16271 | 546 | -0.0042552 | -2.3233
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.000298 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 0.19161 | 0 | -0.0042552 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.000298 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.003874 | 13 | -0.0042552 | -0.055318
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.000299 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.045597 | 152.5 | -0.0042542 | -0.64877
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.000299 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0447 | 149.5 | -0.0042542 | -0.636
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.000299 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.069547 | 232.6 | -0.0042542 | -0.98953
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.030592 | 0 | -0.0042482 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.028334 | 0 | -0.0042482 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.031323 | 0 | -0.0042482 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.03111 | 0 | -0.0042482 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.00976 | 0 | -0.0042482 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.00915 | 0 | -0.0042482 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021594 | 0 | -0.0042482 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020344 | 0 | -0.0042482 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.016165 | 0 | -0.0042482 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.046726 | 0 | -0.0042482 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.046817 | 0 | -0.0042482 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.046451 | 0 | -0.0042482 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02928 | 0 | -0.0042482 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.000305 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.07442 | 0 | -0.0042482 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.000305 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0122 | 0 | -0.0042482 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.000307 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.040524 | 132 | -0.0042462 | -0.5605
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.000307 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.041138 | 134 | -0.0042462 | -0.56899
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.000307 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.099161 | 323 | -0.0042462 | -1.3715
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01302 | 42 | -0.0042432 | -0.17821
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01364 | 44 | -0.0042432 | -0.1867
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01364 | 44 | -0.0042432 | -0.1867
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00031 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.01457 | 47 | -0.0042432 | -0.19943
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.000311 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01555 | 50 | -0.0042422 | -0.21211
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.000313 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0042402 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.028847 | 0 | -0.0042362 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.027769 | 0 | -0.0042362 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.027579 | 0 | -0.0042362 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.017277 | 0 | -0.0042362 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.000317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0038674 | 0 | -0.0042362 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02067 | 0 | -0.0042352 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.01908 | 0 | -0.0042352 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02067 | 0 | -0.0042352 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.000318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02067 | 0 | -0.0042352 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.000321 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.025038 | 0 | -0.0042322 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.000321 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.02568 | 0 | -0.0042322 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.05255 | 0 | -0.0042312 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.050586 | 0 | -0.0042312 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.050715 | 0 | -0.0042312 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.050554 | 0 | -0.0042312 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.000322 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.086618 | 0 | -0.0042312 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.014812 | 46 | -0.0042312 | -0.19464
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.014812 | 46 | -0.0042312 | -0.19464
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.014812 | 46 | -0.0042312 | -0.19464
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.01771 | 55 | -0.0042312 | -0.23272
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.01771 | 55 | -0.0042312 | -0.23272
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.000322 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.017388 | 54 | -0.0042312 | -0.22849
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.000323 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.003876 | 12 | -0.0042302 | -0.050763
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.000323 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0042302 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.000323 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.054587 | 169 | -0.0042302 | -0.71491
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.000323 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.053295 | 165 | -0.0042302 | -0.69798
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.000323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.011305 | 0 | -0.0042302 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.000324 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.069012 | 213 | -0.0042292 | -0.90082
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0052488 | 0 | -0.0042292 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020736 | 0 | -0.0042292 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020477 | 0 | -0.0042292 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.026762 | 0 | -0.0042292 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.023846 | 0 | -0.0042292 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.000324 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.073872 | 228 | -0.0042292 | -0.96426
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.000324 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.05832 | 0 | -0.0042292 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.000324 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.051386 | 0 | -0.0042292 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.000324 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.050868 | 0 | -0.0042292 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.048276 | 0 | -0.0042292 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.000324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021092 | 0 | -0.0042292 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.023075 | 0 | -0.0042282 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0234 | 0 | -0.0042282 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.012675 | 0 | -0.0042282 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.000325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.00975 | 0 | -0.0042282 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.013692 | 42 | -0.0042272 | -0.17754
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.013692 | 42 | -0.0042272 | -0.17754
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.012388 | 38 | -0.0042272 | -0.16063
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.012388 | 38 | -0.0042272 | -0.16063
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.056571 | 0 | -0.0042262 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.000327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.044145 | 0 | -0.0042262 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.000327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.044472 | 0 | -0.0042262 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.00033 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 0.24255 | 735 | -0.0042232 | -3.1041
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.03432 | 104 | -0.0042232 | -0.43921
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.03432 | 104 | -0.0042232 | -0.43921
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01782 | 54 | -0.0042232 | -0.22805
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01749 | 53 | -0.0042232 | -0.22383
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01782 | 54 | -0.0042232 | -0.22805
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01881 | 57 | -0.0042232 | -0.24072
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01782 | 54 | -0.0042232 | -0.22805
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01782 | 54 | -0.0042232 | -0.22805
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01914 | 58 | -0.0042232 | -0.24495
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.00033 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.01914 | 58 | -0.0042232 | -0.24495
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.011254 | 0 | -0.0042222 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.011486 | 0 | -0.0042222 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.010824 | 0 | -0.0042222 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.015193 | 0 | -0.0042222 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0058587 | 0 | -0.0042222 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0067524 | 0 | -0.0042222 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0065869 | 0 | -0.0042222 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.011585 | 0 | -0.0042222 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.005958 | 0 | -0.0042222 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.028267 | 0 | -0.0042222 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.000331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.048988 | 0 | -0.0042222 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.000332 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.003984 | 12 | -0.0042212 | -0.050655
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.000332 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.052456 | 158 | -0.0042212 | -0.66695
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.000332 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.05312 | 160 | -0.0042212 | -0.67539
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.000332 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0581 | 175 | -0.0042212 | -0.73871
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.000333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.052281 | 0 | -0.0042202 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.000333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.057276 | 172 | -0.0042202 | -0.72588
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.000333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.057276 | 172 | -0.0042202 | -0.72588
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.000333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.057276 | 172 | -0.0042202 | -0.72588
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.001665 | 0 | -0.0042202 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.006993 | 0 | -0.0042202 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021645 | 0 | -0.0042202 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.021978 | 0 | -0.0042202 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02331 | 0 | -0.0042202 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020979 | 0 | -0.0042202 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.020646 | 0 | -0.0042202 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.034632 | 0 | -0.0042202 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.000333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.019647 | 0 | -0.0042202 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.000333 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.003996 | 0 | -0.0042202 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.000333 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 0.24742 | 743 | -0.0042202 | -3.1356
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.054538 | 0 | -0.0042182 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.054069 | 0 | -0.0042182 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.053232 | 0 | -0.0042182 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.090182 | 0 | -0.0042182 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.000336 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.13373 | 398 | -0.0042172 | -1.6785
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.018872 | 56 | -0.0042162 | -0.23611
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.019883 | 59 | -0.0042162 | -0.24876
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.018872 | 56 | -0.0042162 | -0.23611
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.018872 | 56 | -0.0042162 | -0.23611
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.019883 | 59 | -0.0042162 | -0.24876
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.000337 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.018872 | 56 | -0.0042162 | -0.23611
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.060031 | 0 | -0.0042062 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.054132 | 0 | -0.0042062 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.053438 | 0 | -0.0042062 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.000347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.053438 | 0 | -0.0042062 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.056214 | 0 | -0.0042062 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.000637 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.36245 | 0 | -0.0039162 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.000637 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.3701 | 0 | -0.0039162 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6302 | 0 | -0.0036791 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.03045 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.1447 | 366 | -0.0028171 | -1.0311
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.03019 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9888 | 0 | -0.0025571 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.03019 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8416 | 0 | -0.0025571 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.03019 | west | 7 | N | N | Nwest | Nwest | 1 | -0.75475 | 0 | -0.0025571 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.03019 | west | 7 | N | N | Nwest | Nwest | 1 | -1.3797 | 0 | -0.0025571 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.03019 | west | 7 | N | N | Nwest | Nwest | 1 | -1.3797 | 0 | -0.0025571 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.030131 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2485 | 0 | -0.0024981 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.030131 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6157 | 0 | -0.0024981 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.029694 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8707 | 0 | -0.0020611 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.029654 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4481 | 0 | -0.0020211 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.029654 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9951 | 0 | -0.0020211 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.029354 | west | 4 | Y | N | Ywest | Nwest | 1 | -19.0713 | 0 | -0.0017211 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.029284 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.8319 | 0 | -0.0016511 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.029234 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2621 | 0 | -0.0016011 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.029234 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2621 | 0 | -0.0016011 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.029156 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.5601 | 0 | -0.0015231 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.028916 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.8242 | 0 | -0.0012831 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.028914 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.5656 | 0 | -0.0012811 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.028584 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4301 | 0 | -0.00095108 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.028429 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4115 | 0 | -0.00079608 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8666 | 66 | -0.00064908 | -0.042839
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.9515 | 69 | -0.00064908 | -0.044787
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.9515 | 69 | -0.00064908 | -0.044787
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8949 | 67 | -0.00064908 | -0.043488
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8949 | 67 | -0.00064908 | -0.043488
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.028282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8383 | 65 | -0.00064908 | -0.04219
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.028011 | west | 8 | N | N | Nwest | Nwest | 1 | -0.72268 | 0 | -0.00037808 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.8192 | 0 | -0.00021008 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5221 | 0 | -0.00021008 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9329 | 0 | -0.00021008 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.027843 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.4851 | 0 | -0.00021008 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.042 | 0 | -0.00015408 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9871 | 0 | -0.00015408 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7512 | 0 | -0.00015408 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.3067 | 0 | -0.00015408 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9176 | 0 | -0.00015408 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.027787 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2369 | 0 | -0.00015408 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.027771 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.9485 | 0 | -0.00013808 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.027687 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.6058 | 0 | -5.4082e-05 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.02767 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7808 | 0 | -3.7082e-05 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.027625 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4531 | 0 | 7.9184e-06 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.027625 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4531 | 0 | 7.9184e-06 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1112 | 0 | 0.00022492 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.0298 | 0 | 0.00022492 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.4816 | 0 | 0.00022492 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.027408 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.341 | 0 | 0.00022492 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.027389 | west | 8 | N | N | Nwest | Nwest | 1 | -1.9172 | 0 | 0.00024392 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.027389 | west | 8 | N | N | Nwest | Nwest | 1 | -2.0104 | 0 | 0.00024392 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.027389 | west | 8 | N | N | Nwest | Nwest | 1 | -1.9282 | 0 | 0.00024392 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.027311 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0693 | 0 | 0.00032192 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.027273 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.18 | 0 | 0.00035992 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.027273 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.93546 | 0 | 0.00035992 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.9065 | 70 | 0.00039692 | 0.027784
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.9065 | 70 | 0.00039692 | 0.027784
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5275 | 92.8 | 0.00039692 | 0.036834
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.1789 | 80 | 0.00039692 | 0.031753
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.1789 | 80 | 0.00039692 | 0.031753
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.027236 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.1321 | 115 | 0.00039692 | 0.045646
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.6703 | 208.2 | 0.00039792 | 0.082847
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.8701 | 142.1 | 0.00039792 | 0.056544
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.6059 | 132.4 | 0.00039792 | 0.052684
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.704 | 136 | 0.00039792 | 0.054117
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.0035 | 147 | 0.00039792 | 0.058494
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.027235 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.7194 | 210 | 0.00039792 | 0.083563
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.027128 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.94948 | 0 | 0.00050492 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.027128 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.81384 | 0 | 0.00050492 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.7855 | 66 | 0.00057992 | 0.038275
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.7584 | 65 | 0.00057992 | 0.037695
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8126 | 67 | 0.00057992 | 0.038855
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8126 | 67 | 0.00057992 | 0.038855
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.027053 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.8126 | 67 | 0.00057992 | 0.038855
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.027053 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00057992 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.027053 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00057992 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.026269 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.1523 | 0 | 0.0013639 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.026269 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.1207 | 0 | 0.0013639 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.026269 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.471 | 0 | 0.0013639 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.025887 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.12426 | 0 | 0.0017459 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.025403 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8104 | 0 | 0.0022299 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.025384 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0307 | 0 | 0.0022489 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.025384 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0307 | 0 | 0.0022489 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.025268 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8951 | 0 | 0.0023649 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.025268 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0214 | 0 | 0.0023649 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.025268 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.0107 | 0 | 0.0023649 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.025246 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0197 | 0 | 0.0023869 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.025242 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0194 | 0 | 0.0023909 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.025225 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7837 | 0 | 0.0024079 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.025225 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7837 | 0 | 0.0024079 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.025094 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2534 | 0 | 0.0025389 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8128 | 0 | 0.0026299 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7379 | 0 | 0.0026299 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.6506 | 0 | 0.0026299 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.025003 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3631 | 0 | 0.0026299 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.024626 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9701 | 0 | 0.0030069 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.024446 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8701 | 0 | 0.0031869 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.024423 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0515 | 0 | 0.0032099 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.021242 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0063909 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.01821 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7315 | 0 | 0.0094229 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.01584 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2314 | 204 | 0.011793 | 2.4058
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.01584 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1838 | 201 | 0.011793 | 2.3704
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.01584 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8333 | 242 | 0.011793 | 2.8539
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.007191 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.020442 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.00101 | north | 3 | N | N | Nnorth | Nnorth | 1 | -1.1686 | 0 | 0.026623 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.00101 | north | 3 | N | N | Nnorth | Nnorth | 1 | -1.1696 | 0 | 0.026623 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.000931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.20231 | 217.3 | 0.026702 | 5.8023
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.000931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.19085 | 205 | 0.026702 | 5.4739
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.000931 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.2536 | 272.4 | 0.026702 | 7.2736
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.000197 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.0197 | 0 | 0.027436 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.027633 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.027633 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 3.4e-05 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.027667 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.000151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.032676 | 216.4 | 0.027784 | 6.0124
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.000151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.032631 | 216.1 | 0.027784 | 6.0041
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.00027 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.027903 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.000328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.025912 | 79 | 0.027961 | 2.2089
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.000328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.034768 | 106 | 0.027961 | 2.9639
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.000328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.047888 | 146 | 0.027961 | 4.0823
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.000328 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.024928 | 76 | 0.027961 | 2.125
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.000336 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.00672 | 20 | 0.027969 | 0.55938
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.000336 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.0084 | 25 | 0.027969 | 0.69922
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.000336 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.013776 | 41 | 0.027969 | 1.1467
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.000341 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.01364 | 40 | 0.027974 | 1.119
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.000346 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.19307 | 0 | 0.027979 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.000346 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.20033 | 0 | 0.027979 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.000346 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.27957 | 0 | 0.027979 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.056028 | 161 | 0.027981 | 4.5049
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.057072 | 164 | 0.027981 | 4.5889
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.057072 | 164 | 0.027981 | 4.5889
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.14407 | 414 | 0.027981 | 11.5841
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.056376 | 162 | 0.027981 | 4.5329
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.056028 | 161 | 0.027981 | 4.5049
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.056724 | 163 | 0.027981 | 4.5609
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.000348 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.14233 | 409 | 0.027981 | 11.4442
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.000353 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.13696 | 388 | 0.027986 | 10.8585
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.000353 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.1818 | 515 | 0.027986 | 14.4127
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000357 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.02799 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000357 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.02799 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.000411 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32264 | 0 | 0.028044 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.000411 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32675 | 0 | 0.028044 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.000411 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.32058 | 0 | 0.028044 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.062012 | 0 | 0.028052 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.05447 | 0 | 0.028052 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.060755 | 0 | 0.028052 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.000419 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.16718 | 0 | 0.028052 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.000424 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.028057 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.000424 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.0212 | 0 | 0.028057 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.000428 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.050504 | 118 | 0.028061 | 3.3112
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.000428 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.04922 | 115 | 0.028061 | 3.227
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.000428 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.23797 | 556 | 0.028061 | 15.6019
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.000436 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.079352 | 182 | 0.028069 | 5.1085
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.000436 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.21102 | 484 | 0.028069 | 13.5854
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.067848 | 0 | 0.028073 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.06864 | 0 | 0.028073 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.06864 | 0 | 0.028073 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.00044 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.1672 | 0 | 0.028073 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.000445 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028078 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.000454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.068418 | 150.7 | 0.028087 | 4.2327
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.000454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.068554 | 151 | 0.028087 | 4.2411
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.000454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.08054 | 177.4 | 0.028087 | 4.9826
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.07328 | 160 | 0.028091 | 4.4945
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.071448 | 156 | 0.028091 | 4.3822
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.089768 | 196 | 0.028091 | 5.5058
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.071448 | 156 | 0.028091 | 4.3822
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.071906 | 157 | 0.028091 | 4.4103
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.000458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.090684 | 198 | 0.028091 | 5.562
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.000459 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.21252 | 0 | 0.028092 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.000464 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.070296 | 151.5 | 0.028097 | 4.2567
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.000464 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.070667 | 152.3 | 0.028097 | 4.2792
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.000464 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.08236 | 177.5 | 0.028097 | 4.9872
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.000467 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.2872 | 0 | 0.0281 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.000467 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.27413 | 0 | 0.0281 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.000484 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.17908 | 370 | 0.028117 | 10.4033
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.06776 | 0 | 0.028117 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.068244 | 0 | 0.028117 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.14956 | 0 | 0.028117 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.069212 | 0 | 0.028117 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.069696 | 0 | 0.028117 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.000484 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.15004 | 0 | 0.028117 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028125 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028125 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.000492 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.008364 | 17 | 0.028125 | 0.47812
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028125 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.000492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028125 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.000492 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.015744 | 0 | 0.028125 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.42664 | 0 | 0.028132 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.42664 | 0 | 0.028132 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.075998 | 0 | 0.028132 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.000499 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.076347 | 0 | 0.028132 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.000502 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.024096 | 48 | 0.028135 | 1.3505
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.000502 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.023092 | 46 | 0.028135 | 1.2942
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.000502 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.05271 | 105 | 0.028135 | 2.9542
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.000515 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.4259 | 0 | 0.028148 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.000515 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.42179 | 0 | 0.028148 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.000518 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.03885 | 0 | 0.028151 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.000518 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.041233 | 0 | 0.028151 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.000518 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.045791 | 0 | 0.028151 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13216 | 224 | 0.028223 | 6.3219
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13334 | 226 | 0.028223 | 6.3784
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12508 | 212 | 0.028223 | 5.9833
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.00059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12449 | 211 | 0.028223 | 5.955
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.000817 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.32271 | 395 | 0.02845 | 11.2377
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.000817 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.3554 | 435 | 0.02845 | 12.3757
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.000909 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.39542 | 435 | 0.028542 | 12.4157
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.000971 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.2175 | 224 | 0.028604 | 6.4073
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.000979 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.16643 | 170 | 0.028612 | 4.864
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.000979 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.50908 | 520 | 0.028612 | 14.8782
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.001027 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.06162 | 60 | 0.02866 | 1.7196
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.001027 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.064701 | 63 | 0.02866 | 1.8056
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.001265 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.028898 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.001265 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.99555 | 787 | 0.028898 | 22.7427
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.001299 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.05196 | 0 | 0.028932 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.001299 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.05196 | 0 | 0.028932 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.001318 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.25833 | 196 | 0.028951 | 5.6744
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.001318 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.1463 | 111 | 0.028951 | 3.2136
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.001393 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029026 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.001393 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029026 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.002962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75531 | 255 | 0.030595 | 7.8017
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.002962 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.44134 | 149 | 0.030595 | 4.5586
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.002962 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.45319 | 153 | 0.030595 | 4.681
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.004311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64665 | 150 | 0.031944 | 4.7916
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.004311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.34488 | 80 | 0.031944 | 2.5555
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.006602 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034235 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.006602 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034235 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.006602 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034235 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.007906 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.11859 | 0 | 0.035539 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.007906 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.11859 | 0 | 0.035539 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.00853 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.5118 | 0 | 0.036163 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.009589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.611 | 168 | 0.037222 | 6.2533
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.009589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.86301 | 90 | 0.037222 | 3.35
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.85022 | 70 | 0.039779 | 2.7845
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.83807 | 69 | 0.039779 | 2.7447
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.83807 | 69 | 0.039779 | 2.7447
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.012146 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.82593 | 68 | 0.039779 | 2.705
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.013082 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.4717 | 0 | 0.040715 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.04712 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5706 | 288 | 0.074753 | 21.5288
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.04712 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9266 | 147 | 0.074753 | 10.9887
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.04712 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9266 | 147 | 0.074753 | 10.9887
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.095506 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7191 | 18 | 0.12314 | 2.2165
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.095506 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7191 | 18 | 0.12314 | 2.2165
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.095506 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 3.6292 | 38 | 0.12314 | 4.6793
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.1074 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.8403 | 73 | 0.13503 | 9.8575
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.1074 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.7807 | 119 | 0.13503 | 16.069
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.1074 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.0172 | 205 | 0.13503 | 27.682
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.1074 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.9549 | 102 | 0.13503 | 13.7735
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.1074 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.3105 | 96 | 0.13503 | 12.9633
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.12102 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4523 | 0 | 0.14865 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.12102 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4523 | 0 | 0.14865 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.44854 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 53.8244 | 0 | 0.47617 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 314
| 25 | 314
| 30 | 314
| 35 | 314
| 40 | 314
| 45 | 314
| 50 | 314
| 55 | 314
| 60 | 313
| 65 | 307
| 70 | 300
| 75 | 294
| 80 | 287
| 85 | 280
| 90 | 272
| 95 | 265
| 100 | 257
| 105 | 249
| 110 | 241
| 115 | 233
| Max | 314
| Min | 233
| Avg | 290.5