Proposed Protocol Language Revision

2.1	Definitions

Interval Data Recorder Meter Optional Removal Threshold

The kW (kVA) level at which an Interval Data Recorder meter may be removed as set forth in Section 18.6.6, Interval Data Recorder Meter Optional Removal Threshold.

Interval Data Recorder Meter Mandatory Installation Requirements

The kW (kVA) level at which the installation of an Interval Data Recorder meter is required for settlement purposes as set forth in Protocols Section 18.6.1, Interval Data Recorder Meter Mandatory Installation Requirements.

18.6	Installation and Use of Interval Data Recorder Meters

18.6.1	Interval Data Recorder Meter Mandatory Installation Requirements

(1)	IDR meters are required and shall be installed and utilized for settlement of Premises having either:

a.	A peak Demand greater than 700 kW (or 700 kVA), or

b.	Service provided at transmission voltage (above 60 kV).

For the IDR meter installation process, refer to the Retail Market Guide Section 7.13.2.2, Mandatory IDR Installation Process.

(2)	A Competitive Retailer (CR), upon a Customer’s request or with a Customer’s authorization, may have an IDR installed and used for settlement purposes at any associated Premise outside the IDR Mandatory Installation Threshold.  Except as stated in item (4) of this Section, IDRs in place or installed after September 1, 1999 shall be used for settlement.  Once an IDR is installed on a Premise and used for settlement purposes, the given Premise shall continue to be settled with its interval data, except as stated in Sections 18.6.7, Interval Data Recorder Optional Removal Threshold.  If a Customer or CR requests installation of an IDR meter, the same Customer may not request removal of the IDR meter for a period of 12  consecutive months following such installation.

(3)	All Non-Metered Loads such as street lighting, regardless of the aggregation level, shall not be required to install IDRs under the IDR Mandatory Installation Threshold.  These Loads shall be settled using Load Profiles.

(4)	For Premises not subject to the IDR Mandatory Installation Threshold in item (1) of this Section:

(a)	IDRs installed at the request of ERCOT, a Transmission and/or Distribution Service Provider (TDSP), a municipal, or a cooperative for Load research, rate/tariff design calculation, coincident Demand calculation, or Load Profiling purposes shall be exempt from the requirement to use an IDR for settlement purposes; or

(b)	IDRs previously used specifically for separating Non Opt-In Entity (NOIE) Load from competitive Load shall be exempt from the requirement to use an IDR for retail Customer settlement purposes, provided that the IDR meter has been removed within 120 consecutive days after the NOIE has fully implemented Customer Choice.  IDR meters used for NOIE separation that do not meet the IDR Mandatory Installation Threshold shall not be used for retail Customer settlement purposes.

(5)	For IDR installation procedures reference Section 10.2.2, TDSP Metered Entities.

(6)	TDSPs responsible for any Load transfer schemes between ERCOT and non -ERCOT Regions shall install IDR metering capable of measuring the Load served during the period the Load transfer is implemented.

18.6.2	Interval Data Recorder Administration Issues

ERCOT shall produce a report informing the appropriate Market Participants of Premises that have become subject to the provisions of item (1) of Section 18.6.1, Interval Data Recorder Installation and Use in Settlement, IDR Mandatory Installation Threshold.  ERCOT shall put in place a system to track Market Participants’ timely adherence to this requirement.  This report shall be posted to Market Information System (MIS).

18.6.3	Adherence to Interval Data Recorder Requirements

Municipal Entities and Electric Cooperative Entities that opt-in to Customer Choice must install IDR meters at all Premises subject to the IDR Mandatory Installation Threshold for metering prior to the effective date of their participation in the testing and integration requirements of ERCOT systems for Customer Choice.

18.6.4	Technical Requirements

Regardless of data retrieval method, interval data shall be provided on a schedule that supports the requirements of final settlement (typical monthly billing cycle).

Interval data that is provided for settlement shall be consistent with the ERCOT defined Settlement Interval.

IDRs used for settlement shall meet technical metering requirements defined in the Load Profiling Guide.

18.6.5	Peak Demand Determination for Non-Interval Data Recorder Premises

For the purpose of determining the peak Demand level for the IDR Mandatory Installation Threshold in Section 18.6.1, Interval Data Recorder Installation and Use in Settlement, the Demand will be determined in accordance with Public Utility Commission of Texas (PUCT) rulemaking or through a consensus process with ERCOT and Market Participants.  In the absence of a clear definition of peak Demand in the Price-to-Beat rulemaking, the following application shall be used in determining the peak Demand level for IDR Mandatory Installation Threshold in Section 18.6.1:

(1)	A Premise (Electric Service Identifier (ESI ID)) has a peak Demand greater than the applicable level in Section 18.6.1 when measured in any two billing months of the most recent 12 month period.  CRs may dispute an IDR assignment through the ERCOT settlement dispute process, described in Section 9.5, Settlement and Billing Dispute Process.

ERCOT shall be responsible for receiving and storing Demand information necessary for determining mandatory IDR installations.

18.6.6	Interval Data Recorder Meter Optional Removal Threshold

The CR, upon a Customer’s request or with a Customer’s authorization, may request, in accordance with PUCT rules and regulations, removal of an IDR meter at the Customer’s Premise unless an IDR meter is required by Section 18.6.1, Interval Data Recorder Meter Mandatory Installation Requirements.

The IDR Meter Optional Removal Threshold for a Premise is established as follows:

(1)	Removal shall be allowed under the following conditions:

- Where the Demand at the Premise has not exceeded the IDR Meter Optional Removal Threshold of one hundred and fifty (150) kW (kVA) during the most recent twelve (12) consecutive months, or

- Where an Advanced Meter can be provisioned, an IDR meter may be replaced with an Advanced Meter,

unless the existing Customer requested or authorized installation of an IDR meter pursuant to item (2) of Section 18.6.1, in which case the existing Customer may not request removal of the IDR meter for a period of twelve (12) consecutive months following such installation.

(2)	For a new Customer move-in, where the request is communicated to the CR within 120 consecutive days of the move-in provided the new Customer’s Demand at the Premise has remained below the IDR Mandatory Installation Threshold between the move-in date and the date the request is received, and that meter readings covering at least 45 consecutive days of usage at the Premise have been registered for the new Customer.

Once an IDR has been removed at a Premise by request, an IDR may not be reinstalled at that Premise for a period of 12 consecutive months following such removal, unless a change in Customer(s) has taken place at that Premise during the 12 month period or unless the IDR Mandatory Installation Threshold pursuant to item (1) of Section 18.6.1, has been met.  Removal or re-installation of an IDR is subject to applicable tariff charges.