## test results
CRE test for: |  | 3402 LAKE_CRK 3405 THOUSE__ | [5 empty] | FAIL
Line Rating: |  | 1239.6
Direction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3402 LAKE_CRK 3405 THOUSE__
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.13305
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.14606
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.15283
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.081382
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3402 LAKE_CRK 3405 THOUSE__
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.17496
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.14405
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.1534
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.080133
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3402 LAKE_CRK 3405 THOUSE__
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.2771
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.020349
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.21318
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.29946
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.064679
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.23296
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | 0.32102 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.32102 | -0.2771
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.20929
[6 empty] | Concentration |  | 0.65195 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.17477
[6 empty] | Concentration |  | 0.54443 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 620.5745
| Percent of line rating => | [6 empty] | 50.06% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.3106
[7 empty] | B1(N-S) | -0.038777 | -0.40193 | -0.36315 | -0.038777
[7 empty] | B2 (N-W) | -0.043283 | -0.016614 | 0.026669 | -0.043283
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.060232 | -0.21915 | -0.27938 | 0.060232
[7 empty] | B4 (S-W) | -0.0028709 | 0.38958 | 0.39245 | -0.0028709
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.10228 | 0.18705 | 0.084765 | 0.10228
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.10352 | -0.20179 | -0.30531 | 0.10352
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | -9.217%
Deployment Error Percent | [6 empty] | B2 | -10.29%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 14.32%
[7 empty] | B4 | -0.6824%
[7 empty] | B5 | 24.31%
[7 empty] | B6 | 24.61%
[7 empty] | Max Abs Error | 24.61% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | S-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3402 LAKE_CRK 3405 THOUSE__ C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 3405 - 3409 and 3405 - 3412 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3402 LAKE_CRK 3405 THOUSE__ C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 3405 - 3409 and 3405 - 3412
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.33041 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -84.2545
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.33041 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -49.2311
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.23445 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -3.5168
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.23445 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -3.5168
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.33041 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -50.5527
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.2506 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -37.59
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.2506 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -20.048
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.1758 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -12.8334
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.1758 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -20.9202
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.1758 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -36.039
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.1758 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -17.9316
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.1758 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -16.8768
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.16976 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -2.0372
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.16976 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -2.0372
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.18963 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -31.8578
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.18963 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -17.0667
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.17279 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -3.1102
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.17279 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -3.1102
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.17279 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -6.5661
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.16913 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -48.7103
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.16913 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -24.8626
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.16913 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -24.8626
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.16358 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -18.4023
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.14654 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -5.8618
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.1467 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -11.589
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.1467 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -15.5498
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.1467 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -21.4176
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.1467 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -11.1489
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.16159 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -9.6952
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.16159 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -10.18
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.14571 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -2.9141
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.14571 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -3.6427
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.14571 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -5.974
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.039436 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 18.2589
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -9.9492
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -9.7984
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -10.0999
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -10.0999
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -10.0999
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.15074 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -17.1849
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.15074 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -77.6337
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -10.2347
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -10.6999
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -10.6999
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -10.3898
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -10.3898
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -10.0796
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.15443 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -10.8102
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.15443 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -11.3352
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.15443 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -10.8719
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -23.2167
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -34.0512
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.15532 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -15.3763
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.15532 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -9.4743
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.15528 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -21.8946
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.15532 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -3.8829
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.15532 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -7.0979
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.15532 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -7.0979
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.15528 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -18.6337
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.15335 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -3.9565
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.153 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -15.3767
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.15407 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -18.4879
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.15298 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -8.8727
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.15327 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -32.8306
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.15599 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -23.3989
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.15171 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -1.0013
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.15171 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -5.2035
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.15599 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -15.7553
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.15412 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -18.4942
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.16609 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -60.7871
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.16635 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -40.256
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.1606 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -64.2384
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.1606 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -37.9025
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.16192 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -26.7166
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.16884 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -34.4442
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.16884 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -33.9376
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.16884 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -40.8602
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -3.3161
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -3.3161
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -3.3161
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -2.8187
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.16992 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -20.3909
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.17416 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -10.4494
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.14775 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -11.0812
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.14775 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -11.7608
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.14775 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -13.061
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -23.7261
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -23.1329
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -29.0644
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -23.1329
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -23.2812
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -29.361
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.14991 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -25.484
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.14991 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -77.9511
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.14888 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -55.0867
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.14733 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -82.2074
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.14733 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -85.3012
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.14733 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -119.0386
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.17095 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -19.146
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.17095 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -17.0946
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.17095 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -64.6176
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.17946 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -38.9962
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.17946 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -36.7889
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.17946 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -48.8844
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.17921 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -137.9879
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -12.6645
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -12.4835
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -12.4835
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -12.3026
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.179 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -207.1065
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.179 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -207.2855
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -44.3585
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -44.7546
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.19562 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -42.3311
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.19562 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -42.2724
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -41.9821
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -41.7841
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.17721 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -69.9976
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.17558 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -76.376
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.17721 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -77.0859
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.15435 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -21.3002
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.15692 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -18.5169
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.15692 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -18.0461
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.15692 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -87.2492
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.14605 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -56.6678
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.14605 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -75.2163
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.11696 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -91.8175
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.11696 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -92.9872
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.11696 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -91.2327
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.10854 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -19.7543
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.10854 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -52.5334
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.12113 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -27.1338
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.11016 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -5.508
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.11044 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -4.6385
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.068161 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -41.919
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.068161 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -40.0105
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.48927 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -262.7391
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.48927 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -385.0571
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.23116 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 17.3368
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.23116 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 51.3171
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.1944 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 110.6119
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.14099 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 29.4675
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.14099 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 30.4545
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.14085 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 57.3255
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 6.4857
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 6.6267
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 6.4857
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 6.4857
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.14119 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 59.8658
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.14119 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 60.007
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.1401 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 8.1259
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.1401 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 12.469
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 6.1644
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 6.1644
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 6.0243
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 6.3045
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.14109 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 58.1278
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.14109 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 56.4348
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.14078 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 76.867
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.14078 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 105.5865
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.14165 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 8.6407
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.14165 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 13.4568
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.14165 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 21.3893
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.14109 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 21.8697
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.14109 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 23.9861
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.14109 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 21.8697
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.12567 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 2.7647
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.12567 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 1.3823
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.12567 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 1.3823
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 6.0294
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 4.7148
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 5.8145
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 6.0673
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.12726 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 1.5271
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.12726 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 1.3998
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.12566 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 3.016
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.12566 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 3.016
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.12566 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 2.8903
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.13585 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 53.7954
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.10412 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 138.788
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.10412 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 138.2674
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.12765 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 4.8507
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.12765 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 2.4636
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.12765 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 1.9147
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.12765 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 5.9995
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.13875 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -10.4062
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.15699 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -23.548
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.15082 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -25.5642
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.088265 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -13.2398
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.15519 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -9.7768
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.1627 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -105.7062
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.15079 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -6.0317
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.15079 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -6.0317
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.14128 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 59.618
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.16541 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 21.8343
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.16541 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 22.1651
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.16541 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 53.4278
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.16693 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 26.3743
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.16693 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 26.7082
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.16693 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 29.2121
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.15506 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 90.5539
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.15506 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 92.2595
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.15496 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 67.0977
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 33.8288
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 33.995
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 33.9346
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 34.2519
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.16871 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 1.3497
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.16871 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 1.3497
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.13705 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 2.4668
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.13705 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 2.4668
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.13705 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 2.0557
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.13539 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 1.8548
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.14763 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 2.6574
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.14763 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 2.6574
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.16205 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 5.6716
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.16205 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 5.5096
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.16205 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 5.6716
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.14231 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 3.9846
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.14231 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 4.1269
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.15085 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -5.2799
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.15085 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -4.5256
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 7.7984
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 7.7984
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 7.7984
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 7.7984
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.15279 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.91673
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.14788 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.35491
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.14788 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.35491
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.14788 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.41406
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.14629 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.58517
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.14697 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.35272
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.14697 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.35272
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 21.1962
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 19.8985
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 20.1869
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 21.1962
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 26.2429
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 28.55
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.1673 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 25.5139
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.1673 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 25.0119
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.1673 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 38.9149
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 20.9532
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 21.3959
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 22.2813
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 42.7918
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.053117 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 1.7529
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.053117 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 1.3279
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.12726 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 1.5271
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.12666 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 9.2464
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 9.6818
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 9.927
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 3.4909
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.87273
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 9.6818
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 9.8044
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 9.6083
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 3.0639
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 5.6375
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.13015 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 81.8662
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.12738 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 18.3424
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.12738 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 23.9471
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.14156 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 1.6988
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.075942 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.45565
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.12712 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 42.7113
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.12725 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 42.5025
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.12725 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 43.266
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.12732 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 4.8383
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.12726 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 3.1816
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.12726 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 3.1816
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.12733 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 4.8386
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.12759 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 3.7003
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.12712 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 18.8525
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.12712 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 18.8906
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.12712 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 19.45
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 19.9892
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 19.3566
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 12.6514
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 18.3445
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 18.5976
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 16.0673
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.1276 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 18.6937
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.1276 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 18.8723
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.1276 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 22.0751
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.12767 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 26.4267
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.12767 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 27.665
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.12767 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 30.8949
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.12766 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 18.3835
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.12766 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 18.3835
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.12766 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 21.8304
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.16942 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 52.5202
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.16942 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 69.9705
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 7.1736
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 7.5152
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 7.5152
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 8.0276
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 8.2379
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 7.7335
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 7.7335
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 7.9016
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.16812 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 25.8905
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.16812 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 24.8818
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 8.0698
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 8.0698
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -10.7032
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -10.7032
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -14.1894
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -12.2322
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -12.2322
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -17.5838
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -31.83
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -21.7245
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -20.2416
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -20.792
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -22.4737
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -32.1052
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -32.7478
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -19.821
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -39.0153
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -30.8675
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -30.9556
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -18.8674
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.15122 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -22.5321
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.15446 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -27.8037
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.15446 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -27.8037
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.15435 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -34.729
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -19.4883
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -19.4883
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -20.8436
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -20.9925
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -46.0048
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -21.2903
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -21.4392
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -46.1537
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.15069 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -29.5347
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.15069 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -16.7263
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.15366 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -22.6474
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -23.0694
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -23.0694
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -58.2361
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -22.7881
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -22.6474
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -22.9287
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -57.5328
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.14834 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.14834 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -16.8206
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -14.7749
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -16.4797
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -45.3475
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.076294 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -11.4975
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.076294 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -11.5204
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.076294 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -13.5346
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.07728 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -11.7079
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.07728 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -11.7697
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.07728 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -13.7172
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.1944 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 112.9447
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 13.4312
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 13.4312
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.044289 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 1.4172
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.046435 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 2.2289
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.046435 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 2.136
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.5306
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 2.2551
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.044217 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.75169
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.97277
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 1.1054
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.046435 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 4.8757
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.15563 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -13.0726
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.13853 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -11.0826
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.13842 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -20.7631
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.13842 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -20.7631
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 5.8277
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 5.4902
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 4.3625
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 12.6102
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 12.6349
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 12.5361
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 7.902
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 20.0841
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 3.2925
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 8.2574
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 7.6482
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 8.455
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 8.3974
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.082326 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 2.6344
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.082326 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 2.4698
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 10.1087
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 10.1087
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 10.8372
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 9.9721
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 2.3925
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 2.4035
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.076978 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 10.469
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.085229 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 2.8126
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 3.2316
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 3.2316
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 2.9239
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 2.9239
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.092458 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 6.5645
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.092458 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.92458
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.085783 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 13.9826
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.085783 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 13.9826
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.085783 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 21.0168
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 5.1329
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 4.7381
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 5.1329
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 5.1329
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.077669 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 11.5727
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.077669 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 5.0563
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 7.2218
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 6.9519
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 6.9043
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 4.3251
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.96819
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.07531 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 55.9553
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.075973 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 55.8402
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.07511 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 12.9189
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.07511 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 12.9189
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.07511 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 12.9189
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 12.3581
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.076846 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 13.2944
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.076846 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 10.3742
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 12.1517
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 12.0472
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 11.8606
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 20.0936
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 4.968
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 4.9059
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 6.4118
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 5.7132
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 12.7356
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 12.2596
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 12.2908
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 12.2518
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 20.992
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.075346 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.37673
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.075346 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 1.5823
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 7.0099
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 7.0918
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 7.0918
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 17.2748
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.074482 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 29.6438
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 3.6061
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 3.6061
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 3.6061
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 4.3116
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 4.3116
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 4.2332
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.00797 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 6.5912
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.00797 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 6.5274
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.085988 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 3.964
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 7.8994
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 7.8994
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 10.9137
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 7.6916
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 7.6916
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 10.6019
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.077613 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 13.9703
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.077613 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 12.3094
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.077613 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 12.1852
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.077878 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 2.7257
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.080358 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 36.8843
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 4.8973
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 4.9726
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 5.274
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 4.7466
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 4.6713
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 7.8357
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 4.4452
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 11.1437
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 11.0008
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 11.0008
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.071434 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 11.5723
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.075191 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 11.805
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 5.493
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 5.5704
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 3.0173
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 2.321
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.078241 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 6.1028
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.078241 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 6.2593
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.077628 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 1.2576
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.077679 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 12.817
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.077693 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 13.1301
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.077632 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 16.5356
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.077619 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 17.6971
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.077703 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.93244
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.077703 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 1.3987
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.081226 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 4.0613
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 7.9272
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 7.9272
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 4.116
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 4.0398
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 4.116
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 4.3447
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 4.116
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 4.116
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 4.4209
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 4.4209
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.075613 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.90736
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 4.1551
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 4.3777
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 4.1551
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 4.1551
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 4.3777
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 4.1551
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.10153 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 6.7011
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.085037 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 13.691
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.085037 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 14.1161
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.085037 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 21.0892
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.085037 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 46.4302
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.085037 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 54.6788
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.085826 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 55.8727
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.085826 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 48.4059
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.085826 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 51.4956
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.085037 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 1.1055
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.075329 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.90395
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 2.5776
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 2.6307
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 2.4791
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 3.4798
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 1.3419
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 1.5466
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 1.5087
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 2.6534
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 1.3646
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 6.4743
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 11.2202
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 5.842
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 6.7277
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 4.2402
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 9.5168
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 8.1034
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 8.2919
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 4.7113
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 1.6961
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 8.8572
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 6.5958
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 5.9362
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 6.7843
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 6.1058
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 9.5168
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 9.1399
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 9.7053
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 7.1612
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 7.5381
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 7.5381
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 16.1126
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 1.0387
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.1333 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -10.1972
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.13875 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -11.0999
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.13875 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -5.55
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.13963 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -11.1701
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.13856 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -11.0846
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.13404 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -10.7231
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.13256 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -11.1351
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.13963 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -11.1701
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 16.4304
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.15434 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -18.5204
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.15434 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -35.9605
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.15434 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -26.2682
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 31.996
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 26.5192
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 32.2842
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 16.5745
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 14.4126
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.1586 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -9.5157
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.052633 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.10898 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.14288 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.68582
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -5.8698
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -16.8269
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -21.1314
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -18.627
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -16.4355
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -12.6006
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.15299 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -22.9492
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -17.1618
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -22.8061
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -28.3741
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -32.7218
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.12765 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.081251 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.12747 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 3.4315
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 5.3434
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 9.0691
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 11.9989
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 5.2336
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 4.8506
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 2.4253
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 11.9989
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 4.5953
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 5.4889
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 2.8083
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 4.8624
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 1.8701
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.87273
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 1.8701
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 4.8624
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 4.8624
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 18.8919
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 6.3824
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 7.0206
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 6.3824
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.12651 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 1.5182
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.12539 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 1.8808
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.12539 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 2.8839
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.12306 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 5.907
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.12491 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.99925
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.12713 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 22.8843
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.12712 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 22.8811
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.12725 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 22.9055
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.12725 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 22.9055
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.12748 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 12.748
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.12748 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 12.748
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 3.1687
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 3.1687
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 3.1687
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 2.028
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 3.1687
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 3.1687
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 3.1687
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 1.9012
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.12748 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.12748 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 63.74
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.12748 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 63.74
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.12748 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.13042 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.053117 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.12693 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.12823 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:3402 LAKE_CRK 3405 THOUSE__ C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 3405 - 3409 and 3405 - 3412 | [7 empty] | 620.5745
Number of Bus | Name of Bus | ID | Max MW | L:3402 LAKE_CRK 3405 THOUSE__ C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 3405 - 3409 and 3405 - 3412 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.33041 | north | Y | -0.19736 | -0.47647 | -0.17758 | -0.41179 | 0.17758 | west | Y | 0.19736 | 5.045
239 | BOSQUESW | 1 | 149 | -0.33041 | north | Y | -0.19736 | -0.47647 | -0.17758 | -0.41179 | 0.17758 | west | Y | 0.19736 | 2.9479
244 | WHITNYDM | 1 | 15 | -0.23445 | north | N | -0.10141 | -0.38052 | -0.081625 | -0.31584 | 0.081625 | west | Y | 0.10141 | 0
245 | WHITNYDM | 2 | 15 | -0.23445 | north | N | -0.10141 | -0.38052 | -0.081625 | -0.31584 | 0.081625 | west | Y | 0.10141 | 0
247 | BOSQUESW | 2 | 153 | -0.33041 | north | Y | -0.19736 | -0.47647 | -0.17758 | -0.41179 | 0.17758 | west | Y | 0.19736 | 3.027
251 | BOSQUESW | 2 | 150 | -0.2506 | north | Y | -0.11755 | -0.39666 | -0.09777 | -0.33198 | 0.09777 | west | Y | 0.11755 | 2.9676
253 | BOSQUESW | 2 | 80 | -0.2506 | north | Y | -0.11755 | -0.39666 | -0.09777 | -0.33198 | 0.09777 | west | Y | 0.11755 | 1.5827
332 | RWMILLER | 1 | 73 | -0.1758 | north | Y | -0.042754 | -0.32186 | -0.02297 | -0.25718 | 0.02297 | west | Y | 0.042754 | 1.4443
333 | RWMILLER | 2 | 119 | -0.1758 | north | Y | -0.042754 | -0.32186 | -0.02297 | -0.25718 | 0.02297 | west | Y | 0.042754 | 2.3543
334 | RWMILLER | 3 | 205 | -0.1758 | north | Y | -0.042754 | -0.32186 | -0.02297 | -0.25718 | 0.02297 | west | Y | 0.042754 | 4.0558
335 | RWMILLER | 4 | 102 | -0.1758 | north | Y | -0.042754 | -0.32186 | -0.02297 | -0.25718 | 0.02297 | west | Y | 0.042754 | 2.018
336 | RWMILLER | 5 | 96 | -0.1758 | north | Y | -0.042754 | -0.32186 | -0.02297 | -0.25718 | 0.02297 | west | Y | 0.042754 | 1.8993
344 | MRSSHPRD | 1 | 12 | -0.16976 | north | N | -0.036717 | -0.31582 | -0.016933 | -0.25114 | 0.016933 | west | Y | 0.036717 | 0
345 | MRSSHPRD | 2 | 12 | -0.16976 | north | N | -0.036717 | -0.31582 | -0.016933 | -0.25114 | 0.016933 | west | Y | 0.036717 | 0
366 | JNSNCNTY | 1 | 168 | -0.18963 | north | Y | -0.056584 | -0.33569 | -0.0368 | -0.27101 | 0.0368 | west | Y | 0.056584 | 3.3238
367 | JNSNCNTY | 2 | 90 | -0.18963 | north | Y | -0.056584 | -0.33569 | -0.0368 | -0.27101 | 0.0368 | west | Y | 0.056584 | 1.7806
503 | NTHTEXAS | 1 | 18 | -0.17279 | north | Y | -0.039745 | -0.31885 | -0.019961 | -0.25417 | 0.019961 | west | Y | 0.039745 | 0.35612
504 | NTHTEXAS | 2 | 18 | -0.17279 | north | Y | -0.039745 | -0.31885 | -0.019961 | -0.25417 | 0.019961 | west | Y | 0.039745 | 0.35612
505 | NTHTEXAS | 3 | 38 | -0.17279 | north | Y | -0.039745 | -0.31885 | -0.019961 | -0.25417 | 0.019961 | west | Y | 0.039745 | 0.7518
580 | JCKCNTY8 | 1 | 288 | -0.16913 | north | Y | -0.036087 | -0.31519 | -0.016303 | -0.25051 | 0.016303 | west | Y | 0.036087 | 5.6979
581 | JCKCNTY8 | 2 | 147 | -0.16913 | north | Y | -0.036087 | -0.31519 | -0.016303 | -0.25051 | 0.016303 | west | Y | 0.036087 | 2.9083
582 | JCKCNTY8 | 3 | 147 | -0.16913 | north | Y | -0.036087 | -0.31519 | -0.016303 | -0.25051 | 0.016303 | west | Y | 0.036087 | 2.9083
728 | WOLFRIDG | 1 | 112.5 | -0.16358 | north | Y | -0.03053 | -0.30964 | -0.010746 | -0.24496 | 0.010746 | west | Y | 0.03053 | 2.2257
837 | NEWMAN_G | 1 | 40 | -0.14654 | north | Y | -0.013498 | -0.2926 | 0.0062864 | -0.22793 | 0.0062864 | west | Y | 0.013498 | 0.28846
842 | OLINGER_ | 1 | 79 | -0.1467 | north | Y | -0.01365 | -0.29276 | 0.0061344 | -0.22808 | 0.0061344 | west | Y | 0.01365 | 0.59373
843 | OLINGER_ | 1 | 106 | -0.1467 | north | Y | -0.01365 | -0.29276 | 0.0061344 | -0.22808 | 0.0061344 | west | Y | 0.01365 | 0.79665
844 | OLINGER_ | 1 | 146 | -0.1467 | north | Y | -0.01365 | -0.29276 | 0.0061344 | -0.22808 | 0.0061344 | west | Y | 0.01365 | 1.0973
845 | OLINGER_ | 1 | 76 | -0.1467 | north | Y | -0.01365 | -0.29276 | 0.0061344 | -0.22808 | 0.0061344 | west | Y | 0.01365 | 0.57118
923 | SPENCER_ | 1 | 60 | -0.16159 | north | Y | -0.028541 | -0.30765 | -0.0087566 | -0.24297 | 0.0087566 | west | Y | 0.028541 | 1.1871
924 | SPENCER_ | 1 | 63 | -0.16159 | north | Y | -0.028541 | -0.30765 | -0.0087566 | -0.24297 | 0.0087566 | west | Y | 0.028541 | 1.2464
948 | STEAM1 | 1 | 20 | -0.14571 | north | Y | -0.012659 | -0.29177 | 0.0071254 | -0.22709 | 0.0071254 | west | Y | 0.012659 | 0.11067
949 | STEAM2 | 1 | 25 | -0.14571 | north | Y | -0.012661 | -0.29177 | 0.0071234 | -0.22709 | 0.0071234 | west | Y | 0.012661 | 0.13844
950 | STEAM3 | 1 | 41 | -0.14571 | north | Y | -0.012661 | -0.29177 | 0.0071234 | -0.22709 | 0.0071234 | west | Y | 0.012661 | 0.22704
990 | GIBN_CRE | 1 | 463 | 0.039436 | north | Y | 0.17248 | -0.10662 | 0.19227 | -0.041946 | 0.041946 | houston | Y | 0.17248 | 60.4382
1002 | PBCTAGE_ | A | 66 | -0.15074 | west | Y | -0.017699 | -0.29681 | 0.0020854 | -0.23213 | 0.0020854 | west | N | 0.0020854 | 0
1003 | PBCTBGE_ | B | 65 | -0.15074 | west | Y | -0.017699 | -0.29681 | 0.0020854 | -0.23213 | 0.0020854 | west | N | 0.0020854 | 0
1004 | PBCTCGE_ | C | 67 | -0.15074 | west | Y | -0.017699 | -0.29681 | 0.0020854 | -0.23213 | 0.0020854 | west | N | 0.0020854 | 0
1005 | PBCTDGE_ | D | 67 | -0.15074 | west | Y | -0.017699 | -0.29681 | 0.0020854 | -0.23213 | 0.0020854 | west | N | 0.0020854 | 0
1006 | PBCTEGE_ | E | 67 | -0.15074 | west | Y | -0.017699 | -0.29681 | 0.0020854 | -0.23213 | 0.0020854 | west | N | 0.0020854 | 0
1007 | PB5GEN_6 | MB | 114 | -0.15074 | west | Y | -0.017699 | -0.29681 | 0.0020854 | -0.23213 | 0.0020854 | west | N | 0.0020854 | 0
1008 | PB6GEN_7 | MB | 515 | -0.15074 | west | Y | -0.017699 | -0.29681 | 0.0020854 | -0.23213 | 0.0020854 | west | N | 0.0020854 | 0
1039 | MRGNAG_1 | A | 66 | -0.15507 | west | Y | -0.022025 | -0.30113 | -0.0022406 | -0.23645 | 0.0022406 | west | N | 0.0022406 | 0
1040 | MRGNBG_2 | B | 69 | -0.15507 | west | Y | -0.022025 | -0.30113 | -0.0022406 | -0.23645 | 0.0022406 | west | N | 0.0022406 | 0
1041 | MRGNCG_3 | C | 69 | -0.15507 | west | Y | -0.022025 | -0.30113 | -0.0022406 | -0.23645 | 0.0022406 | west | N | 0.0022406 | 0
1042 | MRGNDG_4 | D | 67 | -0.15507 | west | Y | -0.022025 | -0.30113 | -0.0022406 | -0.23645 | 0.0022406 | west | N | 0.0022406 | 0
1043 | MRGNEG_5 | E | 67 | -0.15507 | west | Y | -0.022025 | -0.30113 | -0.0022406 | -0.23645 | 0.0022406 | west | N | 0.0022406 | 0
1044 | MRGNFG_6 | F | 65 | -0.15507 | west | Y | -0.022025 | -0.30113 | -0.0022406 | -0.23645 | 0.0022406 | west | N | 0.0022406 | 0
1045 | CALENG1G | 1 | 70 | -0.15443 | west | N | -0.021385 | -0.30049 | -0.0016006 | -0.23581 | 0.0016006 | west | N | 0.0016006 | 0
1046 | CALENG2G | 2 | 73.4 | -0.15443 | west | N | -0.021385 | -0.30049 | -0.0016006 | -0.23581 | 0.0016006 | west | N | 0.0016006 | 0
1047 | CALENG3G | 3 | 70.4 | -0.15443 | west | N | -0.021385 | -0.30049 | -0.0016006 | -0.23581 | 0.0016006 | west | N | 0.0016006 | 0
1058 | LONGSHOR | 1 | 150 | -0.15478 | west | Y | -0.021732 | -0.30084 | -0.0019476 | -0.23616 | 0.0019476 | west | N | 0.0019476 | 0
1058 | LONGSHOR | 2 | 220 | -0.15478 | west | Y | -0.021732 | -0.30084 | -0.0019476 | -0.23616 | 0.0019476 | west | N | 0.0019476 | 0
1061 | CIELOGEN | 1 | 99 | -0.15532 | west | Y | -0.02227 | -0.30138 | -0.0024856 | -0.2367 | 0.0024856 | west | N | 0.0024856 | 0
1062 | CIELOGEN | 1 | 61 | -0.15532 | west | Y | -0.02227 | -0.30138 | -0.0024856 | -0.2367 | 0.0024856 | west | N | 0.0024856 | 0
1068 | SCURRYCW | 1 | 141 | -0.15528 | west | Y | -0.022235 | -0.30134 | -0.0024506 | -0.23666 | 0.0024506 | west | N | 0.0024506 | 0
1069 | KINDERMG | 1 | 25 | -0.15532 | west | N | -0.02227 | -0.30138 | -0.0024856 | -0.2367 | 0.0024856 | west | N | 0.0024856 | 0
1070 | KINDERMG | 1 | 45.7 | -0.15532 | west | N | -0.02227 | -0.30138 | -0.0024856 | -0.2367 | 0.0024856 | west | N | 0.0024856 | 0
1071 | KINDERMG | 1 | 45.7 | -0.15532 | west | N | -0.02227 | -0.30138 | -0.0024856 | -0.2367 | 0.0024856 | west | N | 0.0024856 | 0
1073 | SCURRYCW | 2 | 120 | -0.15528 | west | Y | -0.022235 | -0.30134 | -0.0024506 | -0.23666 | 0.0024506 | west | N | 0.0024506 | 0
1320 | BSP 1 | 1 | 25.8 | -0.15335 | west | N | -0.020307 | -0.29941 | -0.00052263 | -0.23473 | 0.00052263 | west | N | 0.00052263 | 0
1326 | STANTONW | 1 | 100.5 | -0.153 | west | Y | -0.019956 | -0.29906 | -0.00017163 | -0.23438 | 0.00017163 | west | N | 0.00017163 | 0
1327 | WILDHRSE | 1 | 120 | -0.15407 | west | Y | -0.02102 | -0.30013 | -0.0012356 | -0.23545 | 0.0012356 | west | N | 0.0012356 | 0
1328 | OCOTILLO | 1 | 58 | -0.15298 | west | Y | -0.019932 | -0.29904 | -0.00014763 | -0.23436 | 0.00014763 | west | N | 0.00014763 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.15327 | west | Y | -0.020225 | -0.29933 | -0.00044063 | -0.23465 | 0.00044063 | west | N | 0.00044063 | 0
1343 | TRENTIPP | 1 | 150 | -0.15599 | west | Y | -0.022947 | -0.30205 | -0.0031626 | -0.23737 | 0.0031626 | west | N | 0.0031626 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.15171 | west | Y | -0.01866 | -0.29777 | 0.0011244 | -0.23309 | 0.0011244 | west | N | 0.0011244 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.15171 | west | Y | -0.01866 | -0.29777 | 0.0011244 | -0.23309 | 0.0011244 | west | N | 0.0011244 | 0
1354 | AEPWIND_ | 1 | 101 | -0.15599 | west | Y | -0.022947 | -0.30205 | -0.0031626 | -0.23737 | 0.0031626 | west | N | 0.0031626 | 0
1360 | GUNSIGHT | 1 | 120 | -0.15412 | west | Y | -0.021072 | -0.30018 | -0.0012876 | -0.2355 | 0.0012876 | west | N | 0.0012876 | 0
1432 | GRHAMSES | 2 | 366 | -0.16609 | north | Y | -0.033039 | -0.31215 | -0.013255 | -0.24747 | 0.013255 | west | Y | 0.033039 | 7.2411
1433 | GRHAMSES | 1 | 242 | -0.16635 | north | Y | -0.033301 | -0.31241 | -0.013517 | -0.24773 | 0.013517 | west | Y | 0.033301 | 4.7878
1437 | MESQUITW | 1 | 400 | -0.1606 | west | Y | -0.02755 | -0.30666 | -0.0077656 | -0.24198 | 0.0077656 | west | N | 0.0077656 | 0
1438 | MESQUITW | 1 | 236 | -0.1606 | west | Y | -0.027558 | -0.30666 | -0.0077736 | -0.24199 | 0.0077736 | west | N | 0.0077736 | 0
1442 | COKFIELD | 1 | 165 | -0.16192 | west | Y | -0.028873 | -0.30798 | -0.0090886 | -0.2433 | 0.0090886 | west | N | 0.0090886 | 0
1453 | WCPWRCO_ | 1 | 204 | -0.16884 | north | Y | -0.035798 | -0.3149 | -0.016014 | -0.25023 | 0.016014 | west | Y | 0.035798 | 4.036
1454 | WCPWRCO_ | 2 | 201 | -0.16884 | north | Y | -0.035798 | -0.3149 | -0.016014 | -0.25023 | 0.016014 | west | Y | 0.035798 | 3.9766
1455 | WCPWRCO_ | 3 | 242 | -0.16884 | north | Y | -0.035798 | -0.3149 | -0.016014 | -0.25023 | 0.016014 | west | Y | 0.035798 | 4.7878
1479 | WFCOGEN_ | 1 | 20 | -0.16581 | west | Y | -0.03276 | -0.31187 | -0.012976 | -0.24719 | 0.012976 | west | N | 0.012976 | 0
1479 | WFCOGEN_ | 2 | 20 | -0.16581 | west | Y | -0.03276 | -0.31187 | -0.012976 | -0.24719 | 0.012976 | west | N | 0.012976 | 0
1482 | WFCOGEN_ | 1 | 20 | -0.16581 | west | Y | -0.03276 | -0.31187 | -0.012976 | -0.24719 | 0.012976 | west | N | 0.012976 | 0
1482 | WFCOGEN_ | 2 | 17 | -0.16581 | west | Y | -0.03276 | -0.31187 | -0.012976 | -0.24719 | 0.012976 | west | N | 0.012976 | 0
1600 | BARTNWND | 1 | 120 | -0.16992 | north | Y | -0.036878 | -0.31598 | -0.017094 | -0.25131 | 0.017094 | west | Y | 0.036878 | 2.3741
1643 | SLSTR1PP | 1 | 60 | -0.17416 | north | Y | -0.04111 | -0.32022 | -0.021326 | -0.25554 | 0.021326 | west | Y | 0.04111 | 1.1871
1675 | PEC_1G | 1 | 75 | -0.14775 | north | N | -0.014703 | -0.29381 | 0.0050814 | -0.22913 | 0.0050814 | west | Y | 0.014703 | 0
1676 | PEC_2G | 2 | 79.6 | -0.14775 | north | N | -0.014703 | -0.29381 | 0.0050814 | -0.22913 | 0.0050814 | west | Y | 0.014703 | 0
1677 | PEC_3G | 3 | 88.4 | -0.14775 | north | N | -0.014703 | -0.29381 | 0.0050814 | -0.22913 | 0.0050814 | west | Y | 0.014703 | 0
1678 | LAMARPWR | 1 | 160 | -0.14829 | north | Y | -0.015242 | -0.29435 | 0.0045424 | -0.22967 | 0.0045424 | west | Y | 0.015242 | 1.7119
1679 | LAMARPWR | 2 | 156 | -0.14829 | north | Y | -0.015242 | -0.29435 | 0.0045424 | -0.22967 | 0.0045424 | west | Y | 0.015242 | 1.6691
1680 | LAMARPWR | 3 | 196 | -0.14829 | north | Y | -0.015242 | -0.29435 | 0.0045424 | -0.22967 | 0.0045424 | west | Y | 0.015242 | 2.0971
1681 | LAMARPWR | 4 | 156 | -0.14829 | north | Y | -0.015242 | -0.29435 | 0.0045424 | -0.22967 | 0.0045424 | west | Y | 0.015242 | 1.6691
1682 | LAMARPWR | 5 | 157 | -0.14829 | north | Y | -0.015242 | -0.29435 | 0.0045424 | -0.22967 | 0.0045424 | west | Y | 0.015242 | 1.6798
1683 | LAMARPWR | 6 | 198 | -0.14829 | north | Y | -0.015242 | -0.29435 | 0.0045424 | -0.22967 | 0.0045424 | west | Y | 0.015242 | 2.1185
1687 | VALLEY_1 | 1 | 170 | -0.14991 | north | Y | -0.01686 | -0.29597 | 0.0029244 | -0.23129 | 0.0029244 | west | Y | 0.01686 | 2.369
1688 | VALLEY_2 | 2 | 520 | -0.14991 | north | Y | -0.01686 | -0.29597 | 0.0029244 | -0.23129 | 0.0029244 | west | Y | 0.01686 | 7.2465
1689 | VALLEY_3 | 3 | 370 | -0.14888 | north | Y | -0.015837 | -0.29494 | 0.0039474 | -0.23026 | 0.0039474 | west | Y | 0.015837 | 4.3991
1701 | MOSES_1G | 1 | 558 | -0.14733 | north | Y | -0.014279 | -0.29339 | 0.0055054 | -0.22871 | 0.0055054 | west | Y | 0.014279 | 4.8956
1702 | MOSES_2G | 2 | 579 | -0.14733 | north | Y | -0.014279 | -0.29339 | 0.0055054 | -0.22871 | 0.0055054 | west | Y | 0.014279 | 5.0799
1703 | MOSES_3G | 3 | 808 | -0.14733 | north | Y | -0.014279 | -0.29339 | 0.0055054 | -0.22871 | 0.0055054 | west | Y | 0.014279 | 7.089
1861 | EAGLEMNT | MB | 112 | -0.17095 | north | Y | -0.0379 | -0.31701 | -0.018116 | -0.25233 | 0.018116 | west | Y | 0.0379 | 0
1862 | EAGLEMNT | MB | 100 | -0.17095 | north | Y | -0.0379 | -0.31701 | -0.018116 | -0.25233 | 0.018116 | west | Y | 0.0379 | 0
1863 | EAGLEMNT | MB | 378 | -0.17095 | north | Y | -0.0379 | -0.31701 | -0.018116 | -0.25233 | 0.018116 | west | Y | 0.0379 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.17946 | north | Y | -0.046412 | -0.32552 | -0.026628 | -0.26084 | 0.026628 | west | Y | 0.046412 | 4.2991
1878 | WLFHOLW_ | 2 | 205 | -0.17946 | north | Y | -0.046412 | -0.32552 | -0.026628 | -0.26084 | 0.026628 | west | Y | 0.046412 | 4.0558
1879 | WLFHOLW_ | 3 | 272.4 | -0.17946 | north | Y | -0.046412 | -0.32552 | -0.026628 | -0.26084 | 0.026628 | west | Y | 0.046412 | 5.3892
1889 | DECRDOVA | MB | 770 | -0.17921 | north | Y | -0.046159 | -0.32527 | -0.026375 | -0.26059 | 0.026375 | west | Y | 0.046159 | 0
1892 | DECRDOVA | A | 70 | -0.18092 | north | Y | -0.047875 | -0.32698 | -0.028091 | -0.2623 | 0.028091 | west | Y | 0.047875 | 1.3849
1893 | DECRDOVA | B | 69 | -0.18092 | north | Y | -0.047875 | -0.32698 | -0.028091 | -0.2623 | 0.028091 | west | Y | 0.047875 | 1.3651
1894 | DECRDOVA | C | 69 | -0.18092 | north | Y | -0.047875 | -0.32698 | -0.028091 | -0.2623 | 0.028091 | west | Y | 0.047875 | 1.3651
1895 | DECRDOVA | D | 68 | -0.18092 | north | Y | -0.047875 | -0.32698 | -0.028091 | -0.2623 | 0.028091 | west | Y | 0.047875 | 1.3453
1898 | COMCHEPK | 1 | 1157 | -0.179 | north | N | -0.045957 | -0.32506 | -0.026173 | -0.26038 | 0.026173 | west | Y | 0.045957 | 0
1899 | COMCHEPK | 2 | 1158 | -0.179 | north | N | -0.045957 | -0.32506 | -0.026173 | -0.26038 | 0.026173 | west | Y | 0.045957 | 0
1937 | MDLTHELP | 5 | 224 | -0.19803 | north | Y | -0.064983 | -0.34409 | -0.045199 | -0.27941 | 0.045199 | west | Y | 0.064983 | 4.4317
1938 | MDLTHELP | 6 | 226 | -0.19803 | north | Y | -0.064983 | -0.34409 | -0.045199 | -0.27941 | 0.045199 | west | Y | 0.064983 | 4.4713
1941 | MDLTHELP | 1 | 216.4 | -0.19562 | north | Y | -0.062569 | -0.34168 | -0.042785 | -0.277 | 0.042785 | west | Y | 0.062569 | 4.2813
1942 | MDLTHELP | 2 | 216.1 | -0.19562 | north | Y | -0.062569 | -0.34168 | -0.042785 | -0.277 | 0.042785 | west | Y | 0.062569 | 4.2754
1943 | MDLTHELP | 3 | 212 | -0.19803 | north | Y | -0.064983 | -0.34409 | -0.045199 | -0.27941 | 0.045199 | west | Y | 0.064983 | 4.1943
1944 | MDLTHELP | 4 | 211 | -0.19803 | north | Y | -0.064983 | -0.34409 | -0.045199 | -0.27941 | 0.045199 | west | Y | 0.064983 | 4.1745
1947 | HANDLEY_ | 3 | 395 | -0.17721 | north | Y | -0.044163 | -0.32327 | -0.024379 | -0.25859 | 0.024379 | west | Y | 0.044163 | 7.8148
1948 | HANDLEY_ | 4 | 435 | -0.17558 | north | Y | -0.042531 | -0.32164 | -0.022747 | -0.25696 | 0.022747 | west | Y | 0.042531 | 8.6062
1949 | HANDLEY_ | 5 | 435 | -0.17721 | north | Y | -0.044163 | -0.32327 | -0.024379 | -0.25859 | 0.024379 | west | Y | 0.044163 | 8.6062
2371 | COLLIN_1 | MB | 138 | -0.15435 | north | Y | -0.021303 | -0.30041 | -0.0015186 | -0.23573 | 0.0015186 | west | Y | 0.021303 | 0
2413 | MTCK6_G | 6 | 118 | -0.15692 | north | Y | -0.023877 | -0.30298 | -0.0040926 | -0.2383 | 0.0040926 | west | Y | 0.023877 | 2.3345
2414 | MTCK7_G | 7 | 115 | -0.15692 | north | Y | -0.023877 | -0.30298 | -0.0040926 | -0.2383 | 0.0040926 | west | Y | 0.023877 | 2.2752
2417 | MTCK8_G | 8 | 556 | -0.15692 | north | Y | -0.023877 | -0.30298 | -0.0040926 | -0.2383 | 0.0040926 | west | Y | 0.023877 | 11.0001
2451 | LKHB1_G | 1 | 388 | -0.14605 | north | Y | -0.013005 | -0.29211 | 0.0067794 | -0.22743 | 0.0067794 | west | Y | 0.013005 | 2.4155
2452 | LKHB2_G | 2 | 515 | -0.14605 | north | Y | -0.013005 | -0.29211 | 0.0067794 | -0.22743 | 0.0067794 | west | Y | 0.013005 | 3.2062
3097 | MARTLAKE | 1 | 785 | -0.11696 | north | Y | 0.016081 | -0.26303 | 0.035865 | -0.19835 | 0.016081 | North | N | 0.016081 | 0
3098 | MARTLAKE | 2 | 795 | -0.11696 | north | Y | 0.016081 | -0.26303 | 0.035865 | -0.19835 | 0.016081 | North | N | 0.016081 | 0
3099 | MARTLAKE | 3 | 780 | -0.11696 | north | Y | 0.016081 | -0.26303 | 0.035865 | -0.19835 | 0.016081 | North | N | 0.016081 | 0
3107 | STRYKER_ | 1 | 182 | -0.10854 | north | Y | 0.024506 | -0.2546 | 0.04429 | -0.18992 | 0.024506 | North | N | 0.024506 | 0
3108 | STRYKER_ | 2 | 484 | -0.10854 | north | Y | 0.024506 | -0.2546 | 0.04429 | -0.18992 | 0.024506 | North | N | 0.024506 | 0
3126 | TRINIDAD | 1 | 224 | -0.12113 | north | Y | 0.011913 | -0.26719 | 0.031697 | -0.20251 | 0.011913 | North | N | 0.011913 | 0
3309 | ASPN_G | 1 | 50 | -0.11016 | north | Y | 0.022887 | -0.25622 | 0.042671 | -0.19154 | 0.022887 | North | N | 0.022887 | 0
3348 | CHAMPION | MB | 42 | -0.11044 | north | N | 0.022605 | -0.2565 | 0.042389 | -0.19182 | 0.022605 | North | N | 0.022605 | 0
3381 | BBRN_1G | 1 | 615 | -0.068161 | north | Y | 0.064885 | -0.21422 | 0.084669 | -0.14954 | 0.064885 | North | N | 0.064885 | 0
3382 | BBRN_2G | 2 | 587 | -0.068161 | north | Y | 0.064885 | -0.21422 | 0.084669 | -0.14954 | 0.064885 | North | N | 0.064885 | 0
3403 | THOUSE_1 | MB | 537 | -0.48927 | north | Y | -0.35623 | -0.63533 | -0.33644 | -0.57065 | 0.33644 | west | Y | 0.35623 | 0
3404 | THOUSE_2 | 2 | 787 | -0.48927 | north | Y | -0.35623 | -0.63533 | -0.33644 | -0.57065 | 0.33644 | west | Y | 0.35623 | 15.5702
3416 | LAKE_CRK | MB | 75 | 0.23116 | north | Y | 0.3642 | 0.085097 | 0.38399 | 0.14978 | 0.085097 | south | Y | 0.3642 | 0
3417 | LAKE_CRK | MB | 222 | 0.23116 | north | Y | 0.3642 | 0.085097 | 0.38399 | 0.14978 | 0.085097 | south | Y | 0.3642 | 0
3432 | SANDOW_4 | 4 | 569 | 0.1944 | south | Y | 0.32744 | 0.048336 | 0.34723 | 0.11302 | 0.048336 | south | N | 0.048336 | 0
5026 | BRAUNIG_ | 1 | 209 | 0.14099 | south | Y | 0.27404 | -0.0050676 | 0.29382 | 0.059611 | 0.0050676 | south | N | 0.0050676 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.14099 | south | Y | 0.27404 | -0.0050676 | 0.29382 | 0.059611 | 0.0050676 | south | N | 0.0050676 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.14085 | south | Y | 0.2739 | -0.0052116 | 0.29368 | 0.059467 | 0.0052116 | south | N | 0.0052116 | 0
5031 | BRA_VHBC | 1 | 46 | 0.14099 | south | Y | 0.27404 | -0.0050676 | 0.29382 | 0.059611 | 0.0050676 | south | N | 0.0050676 | 0
5032 | BRA_VHBC | 2 | 47 | 0.14099 | south | Y | 0.27404 | -0.0050676 | 0.29382 | 0.059611 | 0.0050676 | south | N | 0.0050676 | 0
5033 | BRA_VHBC | 3 | 46 | 0.14099 | south | Y | 0.27404 | -0.0050676 | 0.29382 | 0.059611 | 0.0050676 | south | N | 0.0050676 | 0
5034 | BRA_VHBC | 4 | 46 | 0.14099 | south | Y | 0.27404 | -0.0050676 | 0.29382 | 0.059611 | 0.0050676 | south | N | 0.0050676 | 0
5111 | CALAVER_ | 1 | 424 | 0.14119 | south | Y | 0.27424 | -0.0048676 | 0.29402 | 0.059811 | 0.0048676 | south | N | 0.0048676 | 0
5112 | CALAVER_ | 2 | 425 | 0.14119 | south | Y | 0.27424 | -0.0048676 | 0.29402 | 0.059811 | 0.0048676 | south | N | 0.0048676 | 0
5264 | LEON_LCP | 3 | 58 | 0.1401 | south | Y | 0.27315 | -0.0059596 | 0.29293 | 0.058719 | 0.0059596 | south | N | 0.0059596 | 0
5265 | LEON_LCP | 4 | 89 | 0.1401 | south | Y | 0.27315 | -0.0059596 | 0.29293 | 0.058719 | 0.0059596 | south | N | 0.0059596 | 0
5266 | LEON_LCP | 1 | 44 | 0.1401 | south | Y | 0.27315 | -0.0059596 | 0.29293 | 0.058719 | 0.0059596 | south | N | 0.0059596 | 0
5267 | LEON_LCP | 2 | 44 | 0.1401 | south | Y | 0.27315 | -0.0059596 | 0.29293 | 0.058719 | 0.0059596 | south | N | 0.0059596 | 0
5268 | LEON_LCP | 3 | 43 | 0.1401 | south | Y | 0.27315 | -0.0059596 | 0.29293 | 0.058719 | 0.0059596 | south | N | 0.0059596 | 0
5269 | LEON_LCP | 4 | 45 | 0.1401 | south | Y | 0.27315 | -0.0059596 | 0.29293 | 0.058719 | 0.0059596 | south | N | 0.0059596 | 0
5396 | CALAVER_ | 1 | 412 | 0.14109 | south | Y | 0.27413 | -0.0049736 | 0.29392 | 0.059705 | 0.0049736 | south | N | 0.0049736 | 0
5397 | CALAVER_ | 2 | 400 | 0.14109 | south | Y | 0.27413 | -0.0049736 | 0.29392 | 0.059705 | 0.0049736 | south | N | 0.0049736 | 0
5401 | CALAVER_ | 1 | 546 | 0.14078 | south | Y | 0.27383 | -0.0052786 | 0.29361 | 0.0594 | 0.0052786 | south | N | 0.0052786 | 0
5402 | CALAVER_ | 2 | 750 | 0.14078 | south | Y | 0.27383 | -0.0052786 | 0.29361 | 0.0594 | 0.0052786 | south | N | 0.0052786 | 0
5436 | TUTTL_WB | MB | 61 | 0.14165 | south | Y | 0.2747 | -0.0044096 | 0.29448 | 0.060269 | 0.0044096 | south | N | 0.0044096 | 0
5438 | TUTTL_WB | MB | 95 | 0.14165 | south | Y | 0.2747 | -0.0044096 | 0.29448 | 0.060269 | 0.0044096 | south | N | 0.0044096 | 0
5439 | TUTTL_WB | MB | 151 | 0.14165 | south | Y | 0.2747 | -0.0044096 | 0.29448 | 0.060269 | 0.0044096 | south | N | 0.0044096 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.14109 | south | Y | 0.27414 | -0.0049656 | 0.29393 | 0.059713 | 0.0049656 | south | N | 0.0049656 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.14109 | south | Y | 0.27414 | -0.0049656 | 0.29393 | 0.059713 | 0.0049656 | south | N | 0.0049656 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.14109 | south | Y | 0.27414 | -0.0049656 | 0.29393 | 0.059713 | 0.0049656 | south | N | 0.0049656 | 0
5503 | RAYBURNG | 1 | 22 | 0.12567 | south | Y | 0.25871 | -0.020393 | 0.2785 | 0.044286 | 0.020393 | south | N | 0.020393 | 0
5505 | RAYBURNG | 1 | 11 | 0.12567 | south | Y | 0.25871 | -0.020393 | 0.2785 | 0.044286 | 0.020393 | south | N | 0.020393 | 0
5506 | RAYBURNG | 1 | 11 | 0.12567 | south | Y | 0.25871 | -0.020393 | 0.2785 | 0.044286 | 0.020393 | south | N | 0.020393 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.1264 | south | Y | 0.25945 | -0.019658 | 0.27923 | 0.045021 | 0.019658 | south | N | 0.019658 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.1264 | south | Y | 0.25945 | -0.019658 | 0.27923 | 0.045021 | 0.019658 | south | N | 0.019658 | 0
5511 | RAYBURNC | 1 | 46 | 0.1264 | south | Y | 0.25945 | -0.019658 | 0.27923 | 0.045021 | 0.019658 | south | N | 0.019658 | 0
5512 | RAYBURNC | 1 | 48 | 0.1264 | south | Y | 0.25945 | -0.019658 | 0.27923 | 0.045021 | 0.019658 | south | N | 0.019658 | 0
5728 | FALCONHY | 2 | 12 | 0.12726 | south | N | 0.2603 | -0.018803 | 0.28009 | 0.045876 | 0.018803 | south | N | 0.018803 | 0
5729 | FALCONHY | 3 | 11 | 0.12726 | south | N | 0.2603 | -0.018803 | 0.28009 | 0.045876 | 0.018803 | south | N | 0.018803 | 0
5890 | PEARSALL | 1 | 24 | 0.12566 | south | Y | 0.25871 | -0.020396 | 0.2785 | 0.044283 | 0.020396 | south | N | 0.020396 | 0
5891 | PEARSALL | 1 | 24 | 0.12566 | south | Y | 0.25871 | -0.020396 | 0.2785 | 0.044283 | 0.020396 | south | N | 0.020396 | 0
5892 | PEARSALL | 1 | 23 | 0.12566 | south | Y | 0.25871 | -0.020396 | 0.2785 | 0.044283 | 0.020396 | south | N | 0.020396 | 0
5903 | SANMIGUE | 1 | 396 | 0.13585 | south | Y | 0.26889 | -0.010214 | 0.28868 | 0.054465 | 0.010214 | south | N | 0.010214 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.10412 | houston | N | 0.23716 | -0.041944 | 0.25695 | 0.022735 | 0.022735 | houston | N | 0.022735 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.10412 | houston | N | 0.23716 | -0.041944 | 0.25695 | 0.022735 | 0.022735 | houston | N | 0.022735 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.13305 | 0
5932 | SI_RAY9 | 9 | 38 | 0.12765 | south | Y | 0.2607 | -0.018412 | 0.28048 | 0.046267 | 0.018412 | south | N | 0.018412 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.12765 | south | Y | 0.2607 | -0.018412 | 0.28048 | 0.046267 | 0.018412 | south | N | 0.018412 | 0
5934 | SI_RAY5 | 5 | 15 | 0.12765 | south | Y | 0.2607 | -0.018412 | 0.28048 | 0.046267 | 0.018412 | south | N | 0.018412 | 0
5935 | SI_RAY10 | 10 | 47 | 0.12765 | south | Y | 0.2607 | -0.018412 | 0.28048 | 0.046267 | 0.018412 | south | N | 0.018412 | 0
6016 | SWMESA | 1 | 75 | -0.13875 | west | Y | -0.0057029 | -0.28481 | 0.014081 | -0.22013 | 0.0057029 | North | Y | 0.014081 | 0.62838
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.15283 | 0
6144 | MCADOO1A | 1 | 150 | -0.15699 | west | Y | -0.023941 | -0.30305 | -0.0041566 | -0.23837 | 0.0041566 | west | N | 0.0041566 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.15082 | west | Y | -0.017775 | -0.29688 | 0.0020094 | -0.2322 | 0.0020094 | west | N | 0.0020094 | 0
6476 | LANGFORD | 1 | 150 | -0.088265 | west | Y | 0.044781 | -0.23433 | 0.064565 | -0.16965 | 0.044781 | North | Y | 0.064565 | 2.9676
6637 | SNYDERW1 | 1 | 63 | -0.15519 | west | Y | -0.022141 | -0.30125 | -0.0023566 | -0.23657 | 0.0023566 | west | N | 0.0023566 | 0
6752 | OKLA0A | 1 | 649.7 | -0.1627 | west | Y | -0.029654 | -0.30876 | -0.0098696 | -0.24408 | 0.0098696 | west | N | 0.0098696 | 0
6948 | DENISNDM | 1 | 40 | -0.15079 | north | N | -0.017746 | -0.29685 | 0.0020384 | -0.23217 | 0.0020384 | west | Y | 0.017746 | 0
6948 | DENISNDM | 2 | 40 | -0.15079 | north | N | -0.017746 | -0.29685 | 0.0020384 | -0.23217 | 0.0020384 | west | Y | 0.017746 | 0
7000 | L_FERGUS | 1 | 422 | 0.14128 | south | Y | 0.27432 | -0.0047856 | 0.29411 | 0.059893 | 0.0047856 | south | N | 0.0047856 | 0
7004 | L_SIMGID | 1 | 132 | 0.16541 | south | Y | 0.29846 | 0.01935 | 0.31824 | 0.084029 | 0.01935 | south | N | 0.01935 | 0
7005 | L_SIMGID | 2 | 134 | 0.16541 | south | Y | 0.29846 | 0.01935 | 0.31824 | 0.084029 | 0.01935 | south | N | 0.01935 | 0
7006 | L_SIMGID | 3 | 323 | 0.16541 | south | Y | 0.29846 | 0.01935 | 0.31824 | 0.084029 | 0.01935 | south | N | 0.01935 | 0
7007 | L_LOSTPI | 1 | 158 | 0.16693 | south | Y | 0.29997 | 0.020865 | 0.31976 | 0.085544 | 0.020865 | south | N | 0.020865 | 0
7008 | L_LOSTPI | 2 | 160 | 0.16693 | south | Y | 0.29997 | 0.020865 | 0.31976 | 0.085544 | 0.020865 | south | N | 0.020865 | 0
7009 | L_LOSTPI | 3 | 175 | 0.16693 | south | Y | 0.29997 | 0.020865 | 0.31976 | 0.085544 | 0.020865 | south | N | 0.020865 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.15506 | south | Y | 0.2881 | 0.0089974 | 0.30789 | 0.073676 | 0.0089974 | south | N | 0.0089974 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.15506 | south | Y | 0.2881 | 0.0089974 | 0.30789 | 0.073676 | 0.0089974 | south | N | 0.0089974 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.15496 | south | Y | 0.28801 | 0.0088994 | 0.30779 | 0.073578 | 0.0088994 | south | N | 0.0088994 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.15109 | south | Y | 0.28414 | 0.0050284 | 0.30392 | 0.069707 | 0.0050284 | south | N | 0.0050284 | 0
7015 | L_HAYSEN | 2 | 225 | 0.15109 | south | Y | 0.28414 | 0.0050284 | 0.30392 | 0.069707 | 0.0050284 | south | N | 0.0050284 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.15109 | south | Y | 0.28414 | 0.0050284 | 0.30392 | 0.069707 | 0.0050284 | south | N | 0.0050284 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.15109 | south | Y | 0.28414 | 0.0050284 | 0.30392 | 0.069707 | 0.0050284 | south | N | 0.0050284 | 0
7020 | L_AUSTPL | 1 | 8 | 0.16871 | south | N | 0.30176 | 0.02265 | 0.32154 | 0.087329 | 0.02265 | south | N | 0.02265 | 0
7020 | L_AUSTPL | 2 | 8 | 0.16871 | south | N | 0.30176 | 0.02265 | 0.32154 | 0.087329 | 0.02265 | south | N | 0.02265 | 0
7022 | L_BUCHAN | 1 | 18 | 0.13705 | south | N | 0.27009 | -0.0090156 | 0.28988 | 0.055663 | 0.0090156 | south | N | 0.0090156 | 0
7023 | L_BUCHAN | 2 | 18 | 0.13705 | south | N | 0.27009 | -0.0090156 | 0.28988 | 0.055663 | 0.0090156 | south | N | 0.0090156 | 0
7024 | L_BUCHAN | 3 | 15 | 0.13705 | south | N | 0.27009 | -0.0090156 | 0.28988 | 0.055663 | 0.0090156 | south | N | 0.0090156 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.13539 | south | N | 0.26843 | -0.010674 | 0.28822 | 0.054005 | 0.010674 | south | N | 0.010674 | 0
7028 | L_MARBFA | 1 | 18 | 0.14763 | south | N | 0.28068 | 0.0015714 | 0.30046 | 0.06625 | 0.0015714 | south | N | 0.0015714 | 0
7029 | L_MARBFA | 2 | 18 | 0.14763 | south | N | 0.28068 | 0.0015714 | 0.30046 | 0.06625 | 0.0015714 | south | N | 0.0015714 | 0
7031 | L_MARSFO | 1 | 35 | 0.16205 | south | N | 0.29509 | 0.015986 | 0.31488 | 0.080665 | 0.015986 | south | N | 0.015986 | 0
7032 | L_MARSFO | 2 | 34 | 0.16205 | south | N | 0.29509 | 0.015986 | 0.31488 | 0.080665 | 0.015986 | south | N | 0.015986 | 0
7033 | L_MARSFO | 3 | 35 | 0.16205 | south | N | 0.29509 | 0.015986 | 0.31488 | 0.080665 | 0.015986 | south | N | 0.015986 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.14231 | south | N | 0.27535 | -0.0037546 | 0.29514 | 0.060924 | 0.0037546 | south | N | 0.0037546 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.14231 | south | N | 0.27535 | -0.0037546 | 0.29514 | 0.060924 | 0.0037546 | south | N | 0.0037546 | 0
7038 | L_DELAWA | 1 | 35 | -0.15085 | west | Y | -0.017807 | -0.29691 | 0.0019774 | -0.23223 | 0.0019774 | west | N | 0.0019774 | 0
7038 | L_DELAWA | 2 | 30 | -0.15085 | west | Y | -0.017807 | -0.29691 | 0.0019774 | -0.23223 | 0.0019774 | west | N | 0.0019774 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.15597 | south | Y | 0.28902 | 0.0099084 | 0.3088 | 0.074587 | 0.0099084 | south | N | 0.0099084 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.15597 | south | Y | 0.28902 | 0.0099084 | 0.3088 | 0.074587 | 0.0099084 | south | N | 0.0099084 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.15597 | south | Y | 0.28902 | 0.0099084 | 0.3088 | 0.074587 | 0.0099084 | south | N | 0.0099084 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.15597 | south | Y | 0.28902 | 0.0099084 | 0.3088 | 0.074587 | 0.0099084 | south | N | 0.0099084 | 0
7487 | L_CANYHY | 1 | 6 | 0.15279 | south | N | 0.28584 | 0.0067284 | 0.30562 | 0.071407 | 0.0067284 | south | N | 0.0067284 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.14788 | south | N | 0.28093 | 0.0018194 | 0.30071 | 0.066498 | 0.0018194 | south | N | 0.0018194 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.14788 | south | N | 0.28093 | 0.0018194 | 0.30071 | 0.066498 | 0.0018194 | south | N | 0.0018194 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.14788 | south | N | 0.28093 | 0.0018194 | 0.30071 | 0.066498 | 0.0018194 | south | N | 0.0018194 | 0
7609 | L_SCHUMA | 1 | 4 | 0.14629 | south | N | 0.27934 | 0.00023137 | 0.29912 | 0.06491 | 0.00023137 | south | N | 0.00023137 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.14697 | south | N | 0.28001 | 0.00090737 | 0.2998 | 0.065586 | 0.00090737 | south | N | 0.00090737 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.14697 | south | N | 0.28001 | 0.00090737 | 0.2998 | 0.065586 | 0.00090737 | south | N | 0.00090737 | 0
7800 | L_GUADGE | 1 | 147 | 0.14419 | south | Y | 0.27724 | -0.0018686 | 0.29702 | 0.06281 | 0.0018686 | south | N | 0.0018686 | 0
7801 | L_GUADGE | 2 | 138 | 0.14419 | south | Y | 0.27724 | -0.0018686 | 0.29702 | 0.06281 | 0.0018686 | south | N | 0.0018686 | 0
7802 | L_GUADGE | 3 | 140 | 0.14419 | south | Y | 0.27724 | -0.0018686 | 0.29702 | 0.06281 | 0.0018686 | south | N | 0.0018686 | 0
7803 | L_GUADGE | 4 | 147 | 0.14419 | south | Y | 0.27724 | -0.0018686 | 0.29702 | 0.06281 | 0.0018686 | south | N | 0.0018686 | 0
7804 | L_GUADGE | 5 | 182 | 0.14419 | south | Y | 0.27724 | -0.0018686 | 0.29702 | 0.06281 | 0.0018686 | south | N | 0.0018686 | 0
7805 | L_GUADGE | 6 | 198 | 0.14419 | south | Y | 0.27724 | -0.0018686 | 0.29702 | 0.06281 | 0.0018686 | south | N | 0.0018686 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.1673 | south | Y | 0.30035 | 0.021243 | 0.32013 | 0.085922 | 0.021243 | south | N | 0.021243 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.1673 | south | Y | 0.30035 | 0.021243 | 0.32013 | 0.085922 | 0.021243 | south | N | 0.021243 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.1673 | south | Y | 0.30035 | 0.021243 | 0.32013 | 0.085922 | 0.021243 | south | N | 0.021243 | 0
7810 | L_RIONOG | 1 | 142 | 0.14756 | south | Y | 0.2806 | 0.0014974 | 0.30039 | 0.066176 | 0.0014974 | south | N | 0.0014974 | 0
7811 | L_RIONOG | 2 | 145 | 0.14756 | south | Y | 0.2806 | 0.0014974 | 0.30039 | 0.066176 | 0.0014974 | south | N | 0.0014974 | 0
7812 | L_RIONOG | 3 | 151 | 0.14756 | south | Y | 0.2806 | 0.0014974 | 0.30039 | 0.066176 | 0.0014974 | south | N | 0.0014974 | 0
7813 | L_RIONOG | 4 | 290 | 0.14756 | south | Y | 0.2806 | 0.0014974 | 0.30039 | 0.066176 | 0.0014974 | south | N | 0.0014974 | 0
8032 | AMISTADH | 1 | 33 | 0.053117 | south | N | 0.18616 | -0.092944 | 0.20595 | -0.028265 | 0.028265 | houston | Y | 0.092944 | 0
8033 | AMISTADH | 2 | 25 | 0.053117 | south | N | 0.18616 | -0.092944 | 0.20595 | -0.028265 | 0.028265 | houston | Y | 0.092944 | 0
8048 | FALCONHY | 1 | 12 | 0.12726 | south | N | 0.2603 | -0.018803 | 0.28009 | 0.045876 | 0.018803 | south | N | 0.018803 | 0
8066 | DUP1V#1 | 1 | 73 | 0.12666 | south | N | 0.25971 | -0.019398 | 0.27949 | 0.045281 | 0.019398 | south | N | 0.019398 | 0
8134 | FOR69CG0 | 1 | 79 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
8138 | FOR69CG0 | 2 | 81 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.14606 | 0
8147 | UCAR #2 | 10 | 28 | 0.12468 | south | N | 0.25772 | -0.021385 | 0.27751 | 0.043294 | 0.021385 | south | N | 0.021385 | 0
8148 | UCAR #1 | 2 | 7 | 0.12468 | south | N | 0.25772 | -0.021385 | 0.27751 | 0.043294 | 0.021385 | south | N | 0.021385 | 0
8153 | FOR69CG0 | 3 | 79 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
8154 | FOR69CG0 | 4 | 80 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
8156 | FOR69CG0 | 6 | 25 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
8157 | FOR69CG0 | 7 | 46 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
8161 | COLETOU1 | 1 | 629 | 0.13015 | south | Y | 0.2632 | -0.015908 | 0.28298 | 0.048771 | 0.015908 | south | N | 0.015908 | 0
8173 | VICEC51A | 5 | 144 | 0.12738 | south | Y | 0.26042 | -0.018683 | 0.28021 | 0.045996 | 0.018683 | south | N | 0.018683 | 0
8174 | VICEC61A | 6 | 188 | 0.12738 | south | Y | 0.26042 | -0.018683 | 0.28021 | 0.045996 | 0.018683 | south | N | 0.018683 | 0
8189 | CUERO 2 | 1 | 12 | 0.14156 | south | N | 0.27461 | -0.0044966 | 0.29439 | 0.060182 | 0.0044966 | south | N | 0.0044966 | 0
8262 | ELPS | 1 | 6 | 0.075942 | south | N | 0.20899 | -0.070119 | 0.22877 | -0.00544 | 0.00544 | houston | Y | 0.070119 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.14606 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.14606 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.14606 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.14606 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.14606 | 0
8442 | NBEC71A | 1 | 336 | 0.12712 | south | Y | 0.26016 | -0.018944 | 0.27995 | 0.045735 | 0.018944 | south | N | 0.018944 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.14606 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | 0.13305 | -0.14606 | 0.15283 | -0.081382 | 0.081382 | houston | Y | 0.14606 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.12725 | south | Y | 0.2603 | -0.018808 | 0.28008 | 0.045871 | 0.018808 | south | N | 0.018808 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.12725 | south | Y | 0.2603 | -0.018808 | 0.28008 | 0.045871 | 0.018808 | south | N | 0.018808 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.12732 | south | N | 0.26037 | -0.018737 | 0.28015 | 0.045942 | 0.018737 | south | N | 0.018737 | 0
8506 | VAL #1 | 1 | 25 | 0.12726 | south | N | 0.26031 | -0.018796 | 0.2801 | 0.045883 | 0.018796 | south | N | 0.018796 | 0
8507 | VAL #2 | 2 | 25 | 0.12726 | south | N | 0.26031 | -0.018796 | 0.2801 | 0.045883 | 0.018796 | south | N | 0.018796 | 0
8511 | OXY_CC0A | 1 | 38 | 0.12733 | south | N | 0.26038 | -0.018729 | 0.28016 | 0.04595 | 0.018729 | south | N | 0.018729 | 0
8517 | CELANEBI | 1 | 29 | 0.12759 | south | N | 0.26064 | -0.018466 | 0.28043 | 0.046213 | 0.018466 | south | N | 0.018466 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.12712 | south | N | 0.26017 | -0.018937 | 0.27995 | 0.045742 | 0.018937 | south | N | 0.018937 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.12712 | south | N | 0.26017 | -0.018937 | 0.27995 | 0.045742 | 0.018937 | south | N | 0.018937 | 0
8562 | CNOPST1 | 3 | 153 | 0.12712 | south | N | 0.26017 | -0.018937 | 0.27995 | 0.045742 | 0.018937 | south | N | 0.018937 | 0
8926 | LGE_GT10 | 1 | 158 | 0.12651 | south | N | 0.25956 | -0.019547 | 0.27934 | 0.045132 | 0.019547 | south | N | 0.019547 | 0
8927 | LGE_GT20 | 2 | 153 | 0.12651 | south | N | 0.25956 | -0.019547 | 0.27934 | 0.045132 | 0.019547 | south | N | 0.019547 | 0
8928 | LGE_STG0 | 3 | 100 | 0.12651 | south | N | 0.25956 | -0.019547 | 0.27934 | 0.045132 | 0.019547 | south | N | 0.019547 | 0
8930 | ICPGN10A | 1 | 145 | 0.12651 | south | N | 0.25956 | -0.019547 | 0.27934 | 0.045132 | 0.019547 | south | N | 0.019547 | 0
8931 | ICPGN20A | 2 | 147 | 0.12651 | south | N | 0.25956 | -0.019547 | 0.27934 | 0.045132 | 0.019547 | south | N | 0.019547 | 0
8932 | ICPGN30A | 3 | 127 | 0.12651 | south | N | 0.25956 | -0.019547 | 0.27934 | 0.045132 | 0.019547 | south | N | 0.019547 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.1276 | south | Y | 0.26065 | -0.018459 | 0.28043 | 0.04622 | 0.018459 | south | N | 0.018459 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.1276 | south | Y | 0.26065 | -0.018459 | 0.28043 | 0.04622 | 0.018459 | south | N | 0.018459 | 0
8935 | FGNTS201 | 3 | 173 | 0.1276 | south | Y | 0.26065 | -0.018459 | 0.28043 | 0.04622 | 0.018459 | south | N | 0.018459 | 0
8936 | MVGN#1 | 1 | 207 | 0.12767 | south | Y | 0.26071 | -0.018396 | 0.2805 | 0.046283 | 0.018396 | south | N | 0.018396 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.12767 | south | Y | 0.26071 | -0.018396 | 0.2805 | 0.046283 | 0.018396 | south | N | 0.018396 | 0
8938 | MVGN#3 | 3 | 242 | 0.12767 | south | Y | 0.26071 | -0.018396 | 0.2805 | 0.046283 | 0.018396 | south | N | 0.018396 | 0
8981 | HECN1 | 1 | 144 | 0.12766 | south | Y | 0.26071 | -0.018398 | 0.28049 | 0.046281 | 0.018398 | south | N | 0.018398 | 0
8982 | HECN2 | 2 | 144 | 0.12766 | south | Y | 0.26071 | -0.018398 | 0.28049 | 0.046281 | 0.018398 | south | N | 0.018398 | 0
8983 | HECN3 | 3 | 171 | 0.12766 | south | Y | 0.26071 | -0.018398 | 0.28049 | 0.046281 | 0.018398 | south | N | 0.018398 | 0
9000 | DECKR_G1 | 1 | 310 | 0.16942 | south | Y | 0.30247 | 0.023359 | 0.32225 | 0.088038 | 0.023359 | south | N | 0.023359 | 0
9001 | DECKR_G2 | 2 | 413 | 0.16942 | south | Y | 0.30247 | 0.023359 | 0.32225 | 0.088038 | 0.023359 | south | N | 0.023359 | 0
9002 | DECKR_G3 | 3 | 42 | 0.1708 | south | Y | 0.30385 | 0.02474 | 0.32363 | 0.089419 | 0.02474 | south | N | 0.02474 | 0
9003 | DECKR_G4 | 4 | 44 | 0.1708 | south | Y | 0.30385 | 0.02474 | 0.32363 | 0.089419 | 0.02474 | south | N | 0.02474 | 0
9004 | DECKR_G5 | 5 | 44 | 0.1708 | south | Y | 0.30385 | 0.02474 | 0.32363 | 0.089419 | 0.02474 | south | N | 0.02474 | 0
9005 | DECKR_G6 | 6 | 47 | 0.1708 | south | Y | 0.30385 | 0.02474 | 0.32363 | 0.089419 | 0.02474 | south | N | 0.02474 | 0
9016 | SANDH_G1 | 1 | 49 | 0.16812 | south | Y | 0.30117 | 0.022059 | 0.32095 | 0.086738 | 0.022059 | south | N | 0.022059 | 0
9017 | SANDH_G2 | 2 | 46 | 0.16812 | south | Y | 0.30117 | 0.022059 | 0.32095 | 0.086738 | 0.022059 | south | N | 0.022059 | 0
9018 | SANDH_G3 | 3 | 46 | 0.16812 | south | Y | 0.30117 | 0.022059 | 0.32095 | 0.086738 | 0.022059 | south | N | 0.022059 | 0
9019 | SANDH_G4 | 4 | 47 | 0.16812 | south | Y | 0.30117 | 0.022059 | 0.32095 | 0.086738 | 0.022059 | south | N | 0.022059 | 0
9020 | SANDHG5A | 5A | 154 | 0.16812 | south | Y | 0.30117 | 0.022059 | 0.32095 | 0.086738 | 0.022059 | south | N | 0.022059 | 0
9021 | SANDHG5C | 5C | 148 | 0.16812 | south | Y | 0.30117 | 0.022059 | 0.32095 | 0.086738 | 0.022059 | south | N | 0.022059 | 0
9022 | SANDH_G6 | 6 | 48 | 0.16812 | south | Y | 0.30117 | 0.022059 | 0.32095 | 0.086738 | 0.022059 | south | N | 0.022059 | 0
9023 | SANDH_G7 | 7 | 48 | 0.16812 | south | Y | 0.30117 | 0.022059 | 0.32095 | 0.086738 | 0.022059 | south | N | 0.022059 | 0
11001 | NAV1CT | 1 | 70 | -0.1529 | west | Y | -0.019857 | -0.29896 | -7.2628e-05 | -0.23428 | 7.2628e-05 | west | N | 7.2628e-05 | 0
11009 | NAV2CT | 1 | 70 | -0.1529 | west | Y | -0.019857 | -0.29896 | -7.2628e-05 | -0.23428 | 7.2628e-05 | west | N | 7.2628e-05 | 0
11011 | NAV3ST | 1 | 92.8 | -0.1529 | west | Y | -0.019857 | -0.29896 | -7.2628e-05 | -0.23428 | 7.2628e-05 | west | N | 7.2628e-05 | 0
11012 | NAV4CT | 1 | 80 | -0.1529 | west | Y | -0.019857 | -0.29896 | -7.2628e-05 | -0.23428 | 7.2628e-05 | west | N | 7.2628e-05 | 0
11013 | NAV5CT | 1 | 80 | -0.1529 | west | Y | -0.019857 | -0.29896 | -7.2628e-05 | -0.23428 | 7.2628e-05 | west | N | 7.2628e-05 | 0
11014 | NAV6ST | 1 | 115 | -0.1529 | west | Y | -0.019857 | -0.29896 | -7.2628e-05 | -0.23428 | 7.2628e-05 | west | N | 7.2628e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.15288 | west | Y | -0.019836 | -0.29894 | -5.1628e-05 | -0.23426 | 5.1628e-05 | west | N | 5.1628e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.15288 | west | Y | -0.019836 | -0.29894 | -5.1628e-05 | -0.23426 | 5.1628e-05 | west | N | 5.1628e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.15288 | west | Y | -0.019836 | -0.29894 | -5.1628e-05 | -0.23426 | 5.1628e-05 | west | N | 5.1628e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.15288 | west | Y | -0.019836 | -0.29894 | -5.1628e-05 | -0.23426 | 5.1628e-05 | west | N | 5.1628e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.15288 | west | Y | -0.019836 | -0.29894 | -5.1628e-05 | -0.23426 | 5.1628e-05 | west | N | 5.1628e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.15288 | west | Y | -0.019836 | -0.29894 | -5.1628e-05 | -0.23426 | 5.1628e-05 | west | N | 5.1628e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.15669 | west | Y | -0.023642 | -0.30275 | -0.0038576 | -0.23807 | 0.0038576 | west | N | 0.0038576 | 0
11057 | CHAMPION | 1 | 126.5 | -0.15669 | west | Y | -0.023642 | -0.30275 | -0.0038576 | -0.23807 | 0.0038576 | west | N | 0.0038576 | 0
11058 | PYRON_1G | 1 | 249 | -0.15669 | west | Y | -0.023642 | -0.30275 | -0.0038576 | -0.23807 | 0.0038576 | west | N | 0.0038576 | 0
11059 | INADALE_ | 1 | 197 | -0.15669 | west | Y | -0.023642 | -0.30275 | -0.0038576 | -0.23807 | 0.0038576 | west | N | 0.0038576 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.15478 | west | Y | -0.021732 | -0.30084 | -0.0019476 | -0.23616 | 0.0019476 | west | N | 0.0019476 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.15478 | west | Y | -0.021732 | -0.30084 | -0.0019476 | -0.23616 | 0.0019476 | west | N | 0.0019476 | 0
11147 | NOTREES_ | 1 | 149 | -0.15122 | west | Y | -0.018176 | -0.29728 | 0.0016084 | -0.2326 | 0.0016084 | west | N | 0.0016084 | 0
11309 | BULLCREK | 1 | 180 | -0.15446 | west | Y | -0.021419 | -0.30053 | -0.0016346 | -0.23585 | 0.0016346 | west | N | 0.0016346 | 0
11310 | BULLCREK | 1 | 180 | -0.15446 | west | Y | -0.021419 | -0.30053 | -0.0016346 | -0.23585 | 0.0016346 | west | N | 0.0016346 | 0
11320 | COYOTE_1 | 1 | 225 | -0.15435 | west | Y | -0.021305 | -0.30041 | -0.0015206 | -0.23573 | 0.0015206 | west | N | 0.0015206 | 0
11415 | LORAINE_ | 1 | 125 | -0.15591 | west | Y | -0.02286 | -0.30197 | -0.0030756 | -0.23729 | 0.0030756 | west | N | 0.0030756 | 0
11416 | LORAINE_ | 1 | 125 | -0.15591 | west | Y | -0.02286 | -0.30197 | -0.0030756 | -0.23729 | 0.0030756 | west | N | 0.0030756 | 0
11691 | KMICHICT | 1 | 140 | -0.14888 | north | N | -0.015837 | -0.29494 | 0.0039474 | -0.23026 | 0.0039474 | west | Y | 0.015837 | 0
11692 | KMICHICT | 2 | 141 | -0.14888 | north | N | -0.015837 | -0.29494 | 0.0039474 | -0.23026 | 0.0039474 | west | Y | 0.015837 | 0
11693 | KMICHIST | 3 | 309 | -0.14888 | north | N | -0.015837 | -0.29494 | 0.0039474 | -0.23026 | 0.0039474 | west | Y | 0.015837 | 0
11694 | KMICHICT | 4 | 143 | -0.14888 | north | N | -0.015837 | -0.29494 | 0.0039474 | -0.23026 | 0.0039474 | west | Y | 0.015837 | 0
11695 | KMICHICT | 5 | 144 | -0.14888 | north | N | -0.015837 | -0.29494 | 0.0039474 | -0.23026 | 0.0039474 | west | Y | 0.015837 | 0
11696 | KMICHIST | 6 | 310 | -0.14888 | north | N | -0.015837 | -0.29494 | 0.0039474 | -0.23026 | 0.0039474 | west | Y | 0.015837 | 0
12322 | ENNSTRAC | 1 | 196 | -0.15069 | north | Y | -0.017641 | -0.29675 | 0.0021434 | -0.23207 | 0.0021434 | west | Y | 0.017641 | 3.0375
12323 | ENNSTRAC | 2 | 111 | -0.15069 | north | Y | -0.017641 | -0.29675 | 0.0021434 | -0.23207 | 0.0021434 | west | Y | 0.017641 | 1.7202
12357 | RNRTPL_1 | 1 | 0 | -0.15366 | north | N | -0.020613 | -0.29972 | -0.00082863 | -0.23504 | 0.00082863 | west | Y | 0.020613 | 0
12411 | FPLEFR1A | 1 | 161 | -0.14067 | north | Y | -0.0076209 | -0.28673 | 0.012163 | -0.22205 | 0.0076209 | North | N | 0.0076209 | 0
12412 | FPLEFR1B | 2 | 164 | -0.14067 | north | Y | -0.0076209 | -0.28673 | 0.012163 | -0.22205 | 0.0076209 | North | N | 0.0076209 | 0
12413 | FPLEFR1C | 3 | 164 | -0.14067 | north | Y | -0.0076209 | -0.28673 | 0.012163 | -0.22205 | 0.0076209 | North | N | 0.0076209 | 0
12414 | FPLEFR1S | 4 | 414 | -0.14067 | north | Y | -0.0076209 | -0.28673 | 0.012163 | -0.22205 | 0.0076209 | North | N | 0.0076209 | 0
12421 | FPLEFR2A | 1 | 162 | -0.14067 | north | Y | -0.0076209 | -0.28673 | 0.012163 | -0.22205 | 0.0076209 | North | N | 0.0076209 | 0
12422 | FPLEFR2B | 2 | 161 | -0.14067 | north | Y | -0.0076209 | -0.28673 | 0.012163 | -0.22205 | 0.0076209 | North | N | 0.0076209 | 0
12423 | FPLEFR2C | 3 | 163 | -0.14067 | north | Y | -0.0076209 | -0.28673 | 0.012163 | -0.22205 | 0.0076209 | North | N | 0.0076209 | 0
12424 | FPLEFR2S | 4 | 409 | -0.14067 | north | Y | -0.0076209 | -0.28673 | 0.012163 | -0.22205 | 0.0076209 | North | N | 0.0076209 | 0
12440 | PARKD_1S | 1 | 0 | -0.14834 | north | N | -0.015295 | -0.2944 | 0.0044894 | -0.22972 | 0.0044894 | west | Y | 0.015295 | 0
12449 | PARKD_2S | 1 | 0 | -0.14834 | north | N | -0.015295 | -0.2944 | 0.0044894 | -0.22972 | 0.0044894 | west | Y | 0.015295 | 0
13116 | TGATEWAY | 1 | 148 | -0.11365 | north | N | 0.019393 | -0.25971 | 0.039177 | -0.19503 | 0.019393 | North | N | 0.019393 | 0
13117 | TGATEWAY | 2 | 130 | -0.11365 | north | N | 0.019393 | -0.25971 | 0.039177 | -0.19503 | 0.019393 | North | N | 0.019393 | 0
13118 | TGATEWAY | 3 | 145 | -0.11365 | north | N | 0.019393 | -0.25971 | 0.039177 | -0.19503 | 0.019393 | North | N | 0.019393 | 0
13119 | TGATEWAY | 4 | 399 | -0.11365 | north | N | 0.019393 | -0.25971 | 0.039177 | -0.19503 | 0.019393 | North | N | 0.019393 | 0
13131 | CALFREST | 1 | 150.7 | -0.076294 | north | Y | 0.056752 | -0.22235 | 0.076536 | -0.15768 | 0.056752 | North | N | 0.056752 | 0
13132 | CALFREST | 2 | 151 | -0.076294 | north | Y | 0.056752 | -0.22235 | 0.076536 | -0.15768 | 0.056752 | North | N | 0.056752 | 0
13133 | CALFREST | 3 | 177.4 | -0.076294 | north | Y | 0.056752 | -0.22235 | 0.076536 | -0.15768 | 0.056752 | North | N | 0.056752 | 0
13134 | CALFREST | 4 | 151.5 | -0.07728 | north | Y | 0.055766 | -0.22334 | 0.07555 | -0.15866 | 0.055766 | North | N | 0.055766 | 0
13135 | CALFREST | 5 | 152.3 | -0.07728 | north | Y | 0.055766 | -0.22334 | 0.07555 | -0.15866 | 0.055766 | North | N | 0.055766 | 0
13136 | CALFREST | 6 | 177.5 | -0.07728 | north | Y | 0.055766 | -0.22334 | 0.07555 | -0.15866 | 0.055766 | North | N | 0.055766 | 0
13432 | SANDOW_5 | 5 | 581 | 0.1944 | south | Y | 0.32744 | 0.048336 | 0.34723 | 0.11302 | 0.048336 | south | N | 0.048336 | 0
13691 | OAKGROVE | 1 | 855 | 0.015709 | north | Y | 0.14876 | -0.13035 | 0.16854 | -0.065673 | 0.065673 | houston | Y | 0.14876 | 71.0352
13692 | OAKGROVE | 2 | 855 | 0.015709 | north | Y | 0.14876 | -0.13035 | 0.16854 | -0.065673 | 0.065673 | houston | Y | 0.14876 | 71.0352
32798 | BRYN_TAM | 1 | 32 | 0.044289 | north | N | 0.17734 | -0.10177 | 0.19712 | -0.037093 | 0.037093 | houston | Y | 0.17734 | 0
32883 | BRYN_DNS | 1 | 48 | 0.046435 | north | Y | 0.17948 | -0.099626 | 0.19927 | -0.034947 | 0.034947 | houston | Y | 0.17948 | 6.9376
32884 | BRYN_DNS | 1 | 46 | 0.046435 | north | Y | 0.17948 | -0.099626 | 0.19927 | -0.034947 | 0.034947 | houston | Y | 0.17948 | 6.6486
32886 | BRYN_ATK | MB | 12 | 0.044217 | north | Y | 0.17726 | -0.10184 | 0.19705 | -0.037165 | 0.037165 | houston | Y | 0.17726 | 0
32887 | BRYN_ATK | MB | 51 | 0.044217 | north | Y | 0.17726 | -0.10184 | 0.19705 | -0.037165 | 0.037165 | houston | Y | 0.17726 | 0
32888 | BRYN_ATK | 1 | 17 | 0.044217 | north | Y | 0.17726 | -0.10184 | 0.19705 | -0.037165 | 0.037165 | houston | Y | 0.17726 | 2.3817
32890 | BRYN_ATK | MB | 22 | 0.044217 | north | Y | 0.17726 | -0.10184 | 0.19705 | -0.037165 | 0.037165 | houston | Y | 0.17726 | 0
32891 | BRYN_ATK | MB | 25 | 0.044217 | north | Y | 0.17726 | -0.10184 | 0.19705 | -0.037165 | 0.037165 | houston | Y | 0.17726 | 0
32892 | BRYN_DNS | 1 | 105 | 0.046435 | north | Y | 0.17948 | -0.099626 | 0.19927 | -0.034947 | 0.034947 | houston | Y | 0.17948 | 15.1761
36998 | RDCNYNG1 | 1 | 84 | -0.15563 | west | Y | -0.02258 | -0.30169 | -0.0027956 | -0.23701 | 0.0027956 | west | N | 0.0027956 | 0
38332 | WDWRDU2 | 1 | 80 | -0.13853 | west | Y | -0.0054869 | -0.28459 | 0.014297 | -0.21991 | 0.0054869 | North | Y | 0.014297 | 0.70484
38437 | TNSRBNMS | 1 | 150 | -0.13842 | west | Y | -0.0053749 | -0.28448 | 0.014409 | -0.2198 | 0.0053749 | North | Y | 0.014409 | 1.3552
38438 | TNSRBNMS | 1 | 150 | -0.13842 | west | Y | -0.0053749 | -0.28448 | 0.014409 | -0.2198 | 0.0053749 | North | Y | 0.014409 | 1.3552
38580 | TNBP_CGN | 1 | 70.8 | 0.082312 | houston | N | 0.21536 | -0.063749 | 0.23514 | 0.00093003 | 0.00093003 | houston | N | 0.00093003 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.082312 | houston | N | 0.21536 | -0.063749 | 0.23514 | 0.00093003 | 0.00093003 | houston | N | 0.00093003 | 0
38600 | TNBP_CGN | 5 | 53 | 0.082312 | houston | N | 0.21536 | -0.063749 | 0.23514 | 0.00093003 | 0.00093003 | houston | N | 0.00093003 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.082312 | houston | N | 0.21536 | -0.063749 | 0.23514 | 0.00093003 | 0.00093003 | houston | N | 0.00093003 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.082312 | houston | N | 0.21536 | -0.063749 | 0.23514 | 0.00093003 | 0.00093003 | houston | N | 0.00093003 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.082312 | houston | N | 0.21536 | -0.063749 | 0.23514 | 0.00093003 | 0.00093003 | houston | N | 0.00093003 | 0
38614 | TNBPAMCG | 4 | 96 | 0.082312 | houston | N | 0.21536 | -0.063749 | 0.23514 | 0.00093003 | 0.00093003 | houston | N | 0.00093003 | 0
38615 | TNBPAMCG | 1 | 244 | 0.082312 | houston | N | 0.21536 | -0.063749 | 0.23514 | 0.00093003 | 0.00093003 | houston | N | 0.00093003 | 0
38690 | TNBP_CGN | 3 | 40 | 0.082312 | houston | N | 0.21536 | -0.063749 | 0.23514 | 0.00093003 | 0.00093003 | houston | N | 0.00093003 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.082327 | houston | N | 0.21537 | -0.063734 | 0.23516 | 0.00094503 | 0.00094503 | houston | N | 0.00094503 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.082327 | houston | N | 0.21537 | -0.063734 | 0.23516 | 0.00094503 | 0.00094503 | houston | N | 0.00094503 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.082327 | houston | N | 0.21537 | -0.063734 | 0.23516 | 0.00094503 | 0.00094503 | houston | N | 0.00094503 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.082327 | houston | N | 0.21537 | -0.063734 | 0.23516 | 0.00094503 | 0.00094503 | houston | N | 0.00094503 | 0
39470 | TNDOWCGN | 1 | 32 | 0.082326 | houston | N | 0.21537 | -0.063735 | 0.23516 | 0.00094403 | 0.00094403 | houston | N | 0.00094403 | 0
39480 | TNDOWCGN | 1 | 30 | 0.082326 | houston | N | 0.21537 | -0.063735 | 0.23516 | 0.00094403 | 0.00094403 | houston | N | 0.00094403 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.091069 | houston | N | 0.22412 | -0.054992 | 0.2439 | 0.009687 | 0.009687 | houston | N | 0.009687 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.091069 | houston | N | 0.22412 | -0.054992 | 0.2439 | 0.009687 | 0.009687 | houston | N | 0.009687 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.091069 | houston | N | 0.22412 | -0.054992 | 0.2439 | 0.009687 | 0.009687 | houston | N | 0.009687 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.091069 | houston | N | 0.22412 | -0.054992 | 0.2439 | 0.009687 | 0.009687 | houston | N | 0.009687 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.015709 | north | Y | 0.14876 | -0.13035 | 0.16854 | -0.065673 | 0.065673 | houston | Y | 0.14876 | 12.6534
39970 | TNTNPONE | 1 | 153 | 0.015709 | north | Y | 0.14876 | -0.13035 | 0.16854 | -0.065673 | 0.065673 | houston | Y | 0.14876 | 12.7116
48500 | APD_GT1_ | 1 | 136 | 0.076978 | houston | N | 0.21002 | -0.069083 | 0.22981 | -0.004404 | 0.004404 | houston | N | 0.004404 | 0
48510 | AK_GT1__ | 1 | 33 | 0.085229 | houston | N | 0.21828 | -0.060832 | 0.23806 | 0.003847 | 0.003847 | houston | N | 0.003847 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.076944 | houston | Y | 0.20999 | -0.069117 | 0.22977 | -0.004438 | 0.004438 | houston | N | 0.004438 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.076944 | houston | Y | 0.20999 | -0.069117 | 0.22977 | -0.004438 | 0.004438 | houston | N | 0.004438 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.076944 | houston | Y | 0.20999 | -0.069117 | 0.22977 | -0.004438 | 0.004438 | houston | N | 0.004438 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.076944 | houston | Y | 0.20999 | -0.069117 | 0.22977 | -0.004438 | 0.004438 | houston | N | 0.004438 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.092458 | houston | N | 0.2255 | -0.053603 | 0.24529 | 0.011076 | 0.011076 | houston | N | 0.011076 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.092458 | houston | N | 0.2255 | -0.053603 | 0.24529 | 0.011076 | 0.011076 | houston | N | 0.011076 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.085783 | houston | N | 0.21883 | -0.060278 | 0.23861 | 0.004401 | 0.004401 | houston | N | 0.004401 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.085783 | houston | N | 0.21883 | -0.060278 | 0.23861 | 0.004401 | 0.004401 | houston | N | 0.004401 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.085783 | houston | N | 0.21883 | -0.060278 | 0.23861 | 0.004401 | 0.004401 | houston | N | 0.004401 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.078968 | houston | N | 0.21201 | -0.067093 | 0.2318 | -0.002414 | 0.002414 | houston | N | 0.002414 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.078968 | houston | N | 0.21201 | -0.067093 | 0.2318 | -0.002414 | 0.002414 | houston | N | 0.002414 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.078968 | houston | N | 0.21201 | -0.067093 | 0.2318 | -0.002414 | 0.002414 | houston | N | 0.002414 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.078968 | houston | N | 0.21201 | -0.067093 | 0.2318 | -0.002414 | 0.002414 | houston | N | 0.002414 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.077669 | houston | N | 0.21072 | -0.068392 | 0.2305 | -0.003713 | 0.003713 | houston | N | 0.003713 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.077669 | houston | N | 0.21072 | -0.068392 | 0.2305 | -0.003713 | 0.003713 | houston | N | 0.003713 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.07936 | houston | N | 0.21241 | -0.066701 | 0.23219 | -0.002022 | 0.002022 | houston | N | 0.002022 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.07936 | houston | N | 0.21241 | -0.066701 | 0.23219 | -0.002022 | 0.002022 | houston | N | 0.002022 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.07936 | houston | N | 0.21241 | -0.066701 | 0.23219 | -0.002022 | 0.002022 | houston | N | 0.002022 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.07936 | houston | N | 0.21241 | -0.066701 | 0.23219 | -0.002022 | 0.002022 | houston | N | 0.002022 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.07936 | houston | N | 0.21241 | -0.066701 | 0.23219 | -0.002022 | 0.002022 | houston | N | 0.002022 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.07531 | houston | Y | 0.20836 | -0.070751 | 0.22814 | -0.006072 | 0.006072 | houston | N | 0.006072 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.075973 | houston | Y | 0.20902 | -0.070088 | 0.2288 | -0.005409 | 0.005409 | houston | N | 0.005409 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.07511 | houston | Y | 0.20816 | -0.070951 | 0.22794 | -0.006272 | 0.006272 | houston | N | 0.006272 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.07511 | houston | Y | 0.20816 | -0.070951 | 0.22794 | -0.006272 | 0.006272 | houston | N | 0.006272 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.07511 | houston | Y | 0.20816 | -0.070951 | 0.22794 | -0.006272 | 0.006272 | houston | N | 0.006272 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.071434 | houston | N | 0.20448 | -0.074627 | 0.22426 | -0.009948 | 0.009948 | houston | N | 0.009948 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.076846 | houston | N | 0.20989 | -0.069215 | 0.22968 | -0.004536 | 0.004536 | houston | N | 0.004536 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.076846 | houston | N | 0.20989 | -0.069215 | 0.22968 | -0.004536 | 0.004536 | houston | N | 0.004536 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.074642 | houston | N | 0.20769 | -0.071419 | 0.22747 | -0.00674 | 0.00674 | houston | N | 0.00674 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.074642 | houston | N | 0.20769 | -0.071419 | 0.22747 | -0.00674 | 0.00674 | houston | N | 0.00674 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.074642 | houston | N | 0.20769 | -0.071419 | 0.22747 | -0.00674 | 0.00674 | houston | N | 0.00674 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.074642 | houston | N | 0.20769 | -0.071419 | 0.22747 | -0.00674 | 0.00674 | houston | N | 0.00674 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.077625 | houston | N | 0.21067 | -0.068436 | 0.23046 | -0.003757 | 0.003757 | houston | N | 0.003757 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.077625 | houston | N | 0.21067 | -0.068436 | 0.23046 | -0.003757 | 0.003757 | houston | N | 0.003757 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.077625 | houston | N | 0.21067 | -0.068436 | 0.23046 | -0.003757 | 0.003757 | houston | N | 0.003757 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.077625 | houston | N | 0.21067 | -0.068436 | 0.23046 | -0.003757 | 0.003757 | houston | N | 0.003757 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.078037 | houston | N | 0.21108 | -0.068024 | 0.23087 | -0.003345 | 0.003345 | houston | N | 0.003345 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.078037 | houston | N | 0.21108 | -0.068024 | 0.23087 | -0.003345 | 0.003345 | houston | N | 0.003345 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.078037 | houston | N | 0.21108 | -0.068024 | 0.23087 | -0.003345 | 0.003345 | houston | N | 0.003345 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.078037 | houston | N | 0.21108 | -0.068024 | 0.23087 | -0.003345 | 0.003345 | houston | N | 0.003345 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.078037 | houston | N | 0.21108 | -0.068024 | 0.23087 | -0.003345 | 0.003345 | houston | N | 0.003345 | 0
48651 | EP_1_2 | 1 | 5 | 0.075346 | houston | N | 0.20839 | -0.070715 | 0.22818 | -0.006036 | 0.006036 | houston | N | 0.006036 | 0
48651 | EP_1_2 | 2 | 21 | 0.075346 | houston | N | 0.20839 | -0.070715 | 0.22818 | -0.006036 | 0.006036 | houston | N | 0.006036 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.04546 | north | N | 0.17851 | -0.1006 | 0.19829 | -0.035922 | 0.035922 | houston | Y | 0.17851 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.04546 | north | N | 0.17851 | -0.1006 | 0.19829 | -0.035922 | 0.035922 | houston | Y | 0.17851 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.04546 | north | N | 0.17851 | -0.1006 | 0.19829 | -0.035922 | 0.035922 | houston | Y | 0.17851 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.04546 | north | N | 0.17851 | -0.1006 | 0.19829 | -0.035922 | 0.035922 | houston | Y | 0.17851 | 0
48690 | GBY_GN5_ | 5 | 398 | 0.074482 | houston | Y | 0.20753 | -0.071579 | 0.22731 | -0.0069 | 0.0069 | houston | N | 0.0069 | 0
48691 | GBY_7374 | A | 46 | 0.078393 | houston | Y | 0.21144 | -0.067668 | 0.23122 | -0.002989 | 0.002989 | houston | N | 0.002989 | 0
48691 | GBY_7374 | B | 46 | 0.078393 | houston | Y | 0.21144 | -0.067668 | 0.23122 | -0.002989 | 0.002989 | houston | N | 0.002989 | 0
48692 | GBY_8182 | C | 46 | 0.078393 | houston | Y | 0.21144 | -0.067668 | 0.23122 | -0.002989 | 0.002989 | houston | N | 0.002989 | 0
48692 | GBY_8182 | D | 55 | 0.078393 | houston | Y | 0.21144 | -0.067668 | 0.23122 | -0.002989 | 0.002989 | houston | N | 0.002989 | 0
48693 | GBY_8384 | E | 55 | 0.078393 | houston | Y | 0.21144 | -0.067668 | 0.23122 | -0.002989 | 0.002989 | houston | N | 0.002989 | 0
48693 | GBY_8384 | F | 54 | 0.078393 | houston | Y | 0.21144 | -0.067668 | 0.23122 | -0.002989 | 0.002989 | houston | N | 0.002989 | 0
48721 | LEG_1___ | 1 | 827 | 0.00797 | north | Y | 0.14102 | -0.13809 | 0.1608 | -0.073412 | 0.073412 | houston | Y | 0.14102 | 55.9086
48722 | LEG_2___ | 2 | 819 | 0.00797 | north | Y | 0.14102 | -0.13809 | 0.1608 | -0.073412 | 0.073412 | houston | Y | 0.14102 | 55.3678
48730 | MNS_GT | 1 | 46.1 | 0.085988 | houston | N | 0.21903 | -0.060073 | 0.23882 | 0.004606 | 0.004606 | houston | N | 0.004606 | 0
48731 | CBE_GT1 | 1 | 76 | 0.10394 | houston | Y | 0.23699 | -0.042121 | 0.25677 | 0.022558 | 0.022558 | houston | N | 0.022558 | 0
48732 | CBE_GT2 | 1 | 76 | 0.10394 | houston | Y | 0.23699 | -0.042121 | 0.25677 | 0.022558 | 0.022558 | houston | N | 0.022558 | 0
48733 | CBE_ST12 | 1 | 105 | 0.10394 | houston | Y | 0.23699 | -0.042121 | 0.25677 | 0.022558 | 0.022558 | houston | N | 0.022558 | 0
48734 | CBE_GT3 | 1 | 74 | 0.10394 | houston | Y | 0.23699 | -0.042121 | 0.25677 | 0.022558 | 0.022558 | houston | N | 0.022558 | 0
48735 | CBE_GT4 | 1 | 74 | 0.10394 | houston | Y | 0.23699 | -0.042121 | 0.25677 | 0.022558 | 0.022558 | houston | N | 0.022558 | 0
48736 | CBE_ST34 | 1 | 102 | 0.10394 | houston | Y | 0.23699 | -0.042121 | 0.25677 | 0.022558 | 0.022558 | houston | N | 0.022558 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.077613 | houston | N | 0.21066 | -0.068448 | 0.23044 | -0.003769 | 0.003769 | houston | N | 0.003769 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.077613 | houston | N | 0.21066 | -0.068448 | 0.23044 | -0.003769 | 0.003769 | houston | N | 0.003769 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.077613 | houston | N | 0.21066 | -0.068448 | 0.23044 | -0.003769 | 0.003769 | houston | N | 0.003769 | 0
48761 | PR_GT1__ | 1 | 35 | 0.077878 | houston | N | 0.21092 | -0.068183 | 0.23071 | -0.003504 | 0.003504 | houston | N | 0.003504 | 0
48772 | PHR_GN2_ | MB | 459 | 0.080358 | houston | Y | 0.2134 | -0.065703 | 0.23319 | -0.001024 | 0.001024 | houston | N | 0.001024 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.075343 | houston | N | 0.20839 | -0.070718 | 0.22817 | -0.006039 | 0.006039 | houston | N | 0.006039 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.075343 | houston | N | 0.20839 | -0.070718 | 0.22817 | -0.006039 | 0.006039 | houston | N | 0.006039 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.075343 | houston | N | 0.20839 | -0.070718 | 0.22817 | -0.006039 | 0.006039 | houston | N | 0.006039 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.075343 | houston | N | 0.20839 | -0.070718 | 0.22817 | -0.006039 | 0.006039 | houston | N | 0.006039 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.075343 | houston | N | 0.20839 | -0.070718 | 0.22817 | -0.006039 | 0.006039 | houston | N | 0.006039 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.075343 | houston | N | 0.20839 | -0.070718 | 0.22817 | -0.006039 | 0.006039 | houston | N | 0.006039 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.075343 | houston | N | 0.20839 | -0.070718 | 0.22817 | -0.006039 | 0.006039 | houston | N | 0.006039 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.071434 | houston | N | 0.20448 | -0.074627 | 0.22426 | -0.009948 | 0.009948 | houston | N | 0.009948 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.071434 | houston | N | 0.20448 | -0.074627 | 0.22426 | -0.009948 | 0.009948 | houston | N | 0.009948 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.071434 | houston | N | 0.20448 | -0.074627 | 0.22426 | -0.009948 | 0.009948 | houston | N | 0.009948 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.071434 | houston | N | 0.20448 | -0.074627 | 0.22426 | -0.009948 | 0.009948 | houston | N | 0.009948 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.075191 | houston | N | 0.20824 | -0.07087 | 0.22802 | -0.006191 | 0.006191 | houston | N | 0.006191 | 0
48820 | SHELLG1_ | 1 | 71 | 0.077366 | houston | N | 0.21041 | -0.068695 | 0.2302 | -0.004016 | 0.004016 | houston | N | 0.004016 | 0
48821 | SHELLG2 | 2 | 72 | 0.077366 | houston | N | 0.21041 | -0.068695 | 0.2302 | -0.004016 | 0.004016 | houston | N | 0.004016 | 0
48822 | SHELLG3_ | 1 | 39 | 0.077366 | houston | N | 0.21041 | -0.068695 | 0.2302 | -0.004016 | 0.004016 | houston | N | 0.004016 | 0
48822 | SHELLG3_ | 2 | 30 | 0.077366 | houston | N | 0.21041 | -0.068695 | 0.2302 | -0.004016 | 0.004016 | houston | N | 0.004016 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.078241 | houston | N | 0.21129 | -0.06782 | 0.23107 | -0.003141 | 0.003141 | houston | N | 0.003141 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.078241 | houston | N | 0.21129 | -0.06782 | 0.23107 | -0.003141 | 0.003141 | houston | N | 0.003141 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.077628 | houston | N | 0.21067 | -0.068433 | 0.23046 | -0.003754 | 0.003754 | houston | N | 0.003754 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.077679 | houston | Y | 0.21073 | -0.068382 | 0.23051 | -0.003703 | 0.003703 | houston | N | 0.003703 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.077693 | houston | Y | 0.21074 | -0.068368 | 0.23052 | -0.003689 | 0.003689 | houston | N | 0.003689 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.077632 | houston | Y | 0.21068 | -0.068429 | 0.23046 | -0.00375 | 0.00375 | houston | N | 0.00375 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.077619 | houston | Y | 0.21067 | -0.068442 | 0.23045 | -0.003763 | 0.003763 | houston | N | 0.003763 | 0
48855 | SRB_GT21 | B2 | 12 | 0.077703 | houston | Y | 0.21075 | -0.068358 | 0.23053 | -0.003679 | 0.003679 | houston | N | 0.003679 | 0
48855 | SRB_GT21 | MB | 18 | 0.077703 | houston | Y | 0.21075 | -0.068358 | 0.23053 | -0.003679 | 0.003679 | houston | N | 0.003679 | 0
48865 | TECO_GT1 | 1 | 50 | 0.081226 | houston | Y | 0.21427 | -0.064835 | 0.23406 | -0.00015597 | 0.00015597 | houston | N | 0.00015597 | 0
48873 | THW_ST3_ | 3 | 104 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48874 | THW_ST4_ | 4 | 104 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48875 | THW_3132 | A | 54 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48875 | THW_3132 | B | 53 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48877 | THW_3334 | C | 54 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48877 | THW_3334 | D | 57 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48879 | THW_4142 | E | 54 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48879 | THW_4142 | F | 54 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48881 | THW_4344 | G | 58 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48881 | THW_4344 | H | 58 | 0.076223 | houston | Y | 0.20927 | -0.069838 | 0.22905 | -0.005159 | 0.005159 | houston | N | 0.005159 | 0
48883 | THW_GT1_ | B2 | 12 | 0.075613 | houston | Y | 0.20866 | -0.070448 | 0.22844 | -0.005769 | 0.005769 | houston | N | 0.005769 | 0
48885 | THW_5152 | A | 56 | 0.074198 | houston | Y | 0.20724 | -0.071863 | 0.22703 | -0.007184 | 0.007184 | houston | N | 0.007184 | 0
48885 | THW_5152 | B | 59 | 0.074198 | houston | Y | 0.20724 | -0.071863 | 0.22703 | -0.007184 | 0.007184 | houston | N | 0.007184 | 0
48886 | THW_5354 | C | 56 | 0.074198 | houston | Y | 0.20724 | -0.071863 | 0.22703 | -0.007184 | 0.007184 | houston | N | 0.007184 | 0
48886 | THW_5354 | D | 56 | 0.074198 | houston | Y | 0.20724 | -0.071863 | 0.22703 | -0.007184 | 0.007184 | houston | N | 0.007184 | 0
48887 | THW_5556 | E | 59 | 0.074198 | houston | Y | 0.20724 | -0.071863 | 0.22703 | -0.007184 | 0.007184 | houston | N | 0.007184 | 0
48887 | THW_5556 | F | 56 | 0.074198 | houston | Y | 0.20724 | -0.071863 | 0.22703 | -0.007184 | 0.007184 | houston | N | 0.007184 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.10153 | houston | Y | 0.23458 | -0.044529 | 0.25436 | 0.02015 | 0.02015 | houston | N | 0.02015 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.085037 | houston | Y | 0.21808 | -0.061024 | 0.23787 | 0.003655 | 0.003655 | houston | N | 0.003655 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.085037 | houston | Y | 0.21808 | -0.061024 | 0.23787 | 0.003655 | 0.003655 | houston | N | 0.003655 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.085037 | houston | Y | 0.21808 | -0.061024 | 0.23787 | 0.003655 | 0.003655 | houston | N | 0.003655 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.085037 | houston | Y | 0.21808 | -0.061024 | 0.23787 | 0.003655 | 0.003655 | houston | N | 0.003655 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.085037 | houston | N | 0.21808 | -0.061024 | 0.23787 | 0.003655 | 0.003655 | houston | N | 0.003655 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.085826 | houston | Y | 0.21887 | -0.060235 | 0.23866 | 0.004444 | 0.004444 | houston | N | 0.004444 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.085826 | houston | Y | 0.21887 | -0.060235 | 0.23866 | 0.004444 | 0.004444 | houston | N | 0.004444 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.085826 | houston | Y | 0.21887 | -0.060235 | 0.23866 | 0.004444 | 0.004444 | houston | N | 0.004444 | 0
48929 | WAPGT21_ | B1 | 13 | 0.085037 | houston | Y | 0.21808 | -0.061024 | 0.23787 | 0.003655 | 0.003655 | houston | N | 0.003655 | 0
48940 | WARVUE_G | G1 | 12 | 0.075329 | houston | Y | 0.20838 | -0.070732 | 0.22816 | -0.006053 | 0.006053 | houston | N | 0.006053 | 0
49803 | EXN_15GT | 1 | 34 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49826 | EXN938GT | 5 | 45.9 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49828 | EXN941GT | 10 | 17.7 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49829 | EXN942GT | 11 | 20.4 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49830 | EXN943GT | 12 | 19.9 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49831 | EXN944GT | 13 | 35 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49832 | EXN945GT | 9 | 18 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49837 | EXN_GT | 4 | 85.4 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49838 | EXN_14GT | 14 | 148 | 0.075812 | houston | N | 0.20886 | -0.070249 | 0.22864 | -0.00557 | 0.00557 | houston | N | 0.00557 | 0
49851 | DOW17000 | 37 | 62 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49858 | DOW38100 | 31 | 71.4 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49859 | DOW38200 | 33 | 45 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49860 | DOW38300 | 32 | 101 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49862 | DOW39100 | 36 | 86 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49863 | DOW39200 | 35 | 88 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49865 | DOW41000 | 41 | 50 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49866 | DOW42000 | 42 | 18 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49869 | DOW49000 | 45 | 94 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49870 | DOW61000 | 61 | 70 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49871 | DOW62000 | 62 | 63 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49872 | DOW63000 | 63 | 72 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49873 | DOW64000 | 64 | 64.8 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49876 | DOW65000 | 65 | 101 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49877 | DOW66000 | 66 | 97 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49878 | DOW67000 | 67 | 103 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49882 | DOW81000 | 81 | 76 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49884 | DOW82000 | 82 | 80 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49885 | DOW83000 | 83 | 80 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
49886 | DOW84000 | 84 | 171 | 0.094226 | houston | N | 0.22727 | -0.051835 | 0.24706 | 0.012844 | 0.012844 | houston | N | 0.012844 | 0
58909 | PEARSALL | 1 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58909 | PEARSALL | 2 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58909 | PEARSALL | 3 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58909 | PEARSALL | 4 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58909 | PEARSALL | 5 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58909 | PEARSALL | 6 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58919 | PEARSALL | 1 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58919 | PEARSALL | 2 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58919 | PEARSALL | 3 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58919 | PEARSALL | 4 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58919 | PEARSALL | 5 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58919 | PEARSALL | 6 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58929 | PEARSALL | 1 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58929 | PEARSALL | 2 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58929 | PEARSALL | 3 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58929 | PEARSALL | 4 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58929 | PEARSALL | 5 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58929 | PEARSALL | 6 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58949 | PEARSALL | 1 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58949 | PEARSALL | 2 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58949 | PEARSALL | 3 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58949 | PEARSALL | 4 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58949 | PEARSALL | 5 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
58949 | PEARSALL | 6 | 8.4 | 0.12365 | south | Y | 0.2567 | -0.022411 | 0.27648 | 0.042268 | 0.022411 | south | N | 0.022411 | 0
60000 | DSKY2 | 1 | 76.5 | -0.1333 | west | Y | -0.00025092 | -0.27936 | 0.019533 | -0.21468 | 0.00025092 | North | Y | 0.019533 | 1.4751
60003 | KING_NE1 | 1 | 80 | -0.13875 | west | Y | -0.0057029 | -0.28481 | 0.014081 | -0.22013 | 0.0057029 | North | Y | 0.014081 | 0.67028
60005 | KING_SE1 | 1 | 40 | -0.13875 | west | Y | -0.0057029 | -0.28481 | 0.014081 | -0.22013 | 0.0057029 | North | Y | 0.014081 | 0.33514
60007 | KING_SW1 | 1 | 80 | -0.13963 | west | Y | -0.0065799 | -0.28569 | 0.013204 | -0.22101 | 0.0065799 | North | Y | 0.013204 | 0.52996
60016 | WOODWRD1 | 1 | 80 | -0.13856 | west | Y | -0.0055119 | -0.28462 | 0.014272 | -0.21994 | 0.0055119 | North | Y | 0.014272 | 0.70084
60017 | ORNNWP1 | 1 | 80 | -0.13404 | west | Y | -0.00099292 | -0.2801 | 0.018791 | -0.21542 | 0.00099292 | North | Y | 0.018791 | 1.4239
60018 | DSKY1 | 1 | 84 | -0.13256 | west | Y | 0.00048508 | -0.27862 | 0.020269 | -0.21394 | 0.00048508 | North | Y | 0.020269 | 1.6619
60019 | KING_NW1 | 1 | 80 | -0.13963 | west | Y | -0.0065799 | -0.28569 | 0.013204 | -0.22101 | 0.0065799 | North | Y | 0.013204 | 0.52996
60057 | CALLAHAN | 1 | 114 | 0.14413 | south | Y | 0.27717 | -0.0019346 | 0.29696 | 0.062744 | 0.0019346 | south | N | 0.0019346 | 0
60058 | BUFF_GAP | 1 | 120 | -0.15434 | west | Y | -0.021291 | -0.3004 | -0.0015066 | -0.23572 | 0.0015066 | west | N | 0.0015066 | 0
60060 | CIRELLO | 1 | 233 | -0.15434 | west | Y | -0.021291 | -0.3004 | -0.0015066 | -0.23572 | 0.0015066 | west | N | 0.0015066 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.15434 | west | Y | -0.021291 | -0.3004 | -0.0015066 | -0.23572 | 0.0015066 | west | N | 0.0015066 | 0
60066 | H_HOLLOW | 1 | 222 | 0.14413 | south | Y | 0.27717 | -0.0019346 | 0.29696 | 0.062744 | 0.0019346 | south | N | 0.0019346 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.14413 | south | Y | 0.27717 | -0.0019346 | 0.29696 | 0.062744 | 0.0019346 | south | N | 0.0019346 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.14413 | south | Y | 0.27717 | -0.0019346 | 0.29696 | 0.062744 | 0.0019346 | south | N | 0.0019346 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.14413 | south | Y | 0.27717 | -0.0019346 | 0.29696 | 0.062744 | 0.0019346 | south | N | 0.0019346 | 0
60074 | HORSH5 | 1 | 100 | 0.14413 | south | Y | 0.27717 | -0.0019346 | 0.29696 | 0.062744 | 0.0019346 | south | N | 0.0019346 | 0
60081 | WHRLWIND | 1 | 60 | -0.1586 | west | Y | -0.025549 | -0.30466 | -0.0057646 | -0.23998 | 0.0057646 | west | N | 0.0057646 | 0
60201 | RIO DRCS | F | 0 | 0.052633 | south | N | 0.18568 | -0.093428 | 0.20546 | -0.028749 | 0.028749 | houston | Y | 0.093428 | 0
60202 | FRIEND_R | F | 0 | -0.10898 | west | N | 0.024061 | -0.25505 | 0.043845 | -0.19037 | 0.024061 | North | Y | 0.043845 | 0
60203 | PRES0A | BT | 4.8 | -0.14288 | west | N | -0.0098339 | -0.28894 | 0.0099504 | -0.22426 | 0.0098339 | North | Y | 0.0099504 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.15653 | west | Y | -0.023483 | -0.30259 | -0.0036986 | -0.23791 | 0.0036986 | west | N | 0.0036986 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.15653 | west | Y | -0.023483 | -0.30259 | -0.0036986 | -0.23791 | 0.0036986 | west | N | 0.0036986 | 0
71057 | L_SWEETW | W1 | 135 | -0.15653 | west | Y | -0.023483 | -0.30259 | -0.0036986 | -0.23791 | 0.0036986 | west | N | 0.0036986 | 0
71059 | L_SWEETW | W1 | 119 | -0.15653 | west | Y | -0.023483 | -0.30259 | -0.0036986 | -0.23791 | 0.0036986 | west | N | 0.0036986 | 0
71060 | L_SWEETW | W1 | 105 | -0.15653 | west | Y | -0.023483 | -0.30259 | -0.0036986 | -0.23791 | 0.0036986 | west | N | 0.0036986 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.15653 | west | Y | -0.023483 | -0.30259 | -0.0036986 | -0.23791 | 0.0036986 | west | N | 0.0036986 | 0
76031 | L_GASCCR | W1 | 150 | -0.15299 | west | Y | -0.019949 | -0.29906 | -0.00016463 | -0.23438 | 0.00016463 | west | N | 0.00016463 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.15255 | west | Y | -0.019503 | -0.29861 | 0.00028137 | -0.23393 | 0.00028137 | west | N | 0.00028137 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.15255 | west | Y | -0.019503 | -0.29861 | 0.00028137 | -0.23393 | 0.00028137 | west | N | 0.00028137 | 0
76096 | L_CAPRSI | W1 | 186 | -0.15255 | west | Y | -0.019503 | -0.29861 | 0.00028137 | -0.23393 | 0.00028137 | west | N | 0.00028137 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.15255 | west | Y | -0.019503 | -0.29861 | 0.00028137 | -0.23393 | 0.00028137 | west | N | 0.00028137 | 0
80003 | MILHWYS | F | 0 | 0.12765 | south | N | 0.2607 | -0.018412 | 0.28048 | 0.046267 | 0.018412 | south | N | 0.018412 | 0
80010 | EPLVT1 | F | 0 | 0.081251 | south | N | 0.2143 | -0.06481 | 0.23408 | -0.00013097 | 0.00013097 | houston | Y | 0.06481 | 0
80012 | LAR | F | 0 | 0.12747 | south | N | 0.26052 | -0.018589 | 0.2803 | 0.04609 | 0.018589 | south | N | 0.018589 | 0
80051 | FORPVCM0 | 8 | 28 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
80053 | FOR69CG0 | 10 | 74 | 0.12255 | south | N | 0.2556 | -0.023506 | 0.27539 | 0.041173 | 0.023506 | south | N | 0.023506 | 0
80080 | GWINDT11 | 1 | 94 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80080 | GWINDT11 | 2 | 41 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80080 | GWINDT11 | 3 | 38 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80080 | GWINDT11 | 4 | 19 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80081 | GWINDT21 | 1 | 94 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80081 | GWINDT21 | 2 | 36 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80081 | GWINDT21 | 3 | 43 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80081 | GWINDT21 | 4 | 22 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80137 | CSDR89 | 8 | 39 | 0.12468 | south | N | 0.25772 | -0.021385 | 0.27751 | 0.043294 | 0.021385 | south | N | 0.021385 | 0
80137 | CSDR89 | 9 | 15 | 0.12468 | south | N | 0.25772 | -0.021385 | 0.27751 | 0.043294 | 0.021385 | south | N | 0.021385 | 0
80138 | CSDR7 | 7 | 7 | 0.12468 | south | N | 0.25772 | -0.021385 | 0.27751 | 0.043294 | 0.021385 | south | N | 0.021385 | 0
80139 | CSDR56 | 5 | 15 | 0.12468 | south | N | 0.25772 | -0.021385 | 0.27751 | 0.043294 | 0.021385 | south | N | 0.021385 | 0
80139 | CSDR56 | 6 | 39 | 0.12468 | south | N | 0.25772 | -0.021385 | 0.27751 | 0.043294 | 0.021385 | south | N | 0.021385 | 0
80140 | CSDR11 | 11 | 39 | 0.12468 | south | N | 0.25772 | -0.021384 | 0.27751 | 0.043295 | 0.021384 | south | N | 0.021384 | 0
80180 | PNSCALT1 | 1 | 148 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80180 | PNSCALT1 | 2 | 50 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80181 | PNSCALT2 | 1 | 55 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80181 | PNSCALT2 | 2 | 50 | 0.12765 | south | Y | 0.26069 | -0.018413 | 0.28048 | 0.046266 | 0.018413 | south | N | 0.018413 | 0
80223 | REYSHR G | 1 | 12 | 0.12651 | south | N | 0.25956 | -0.019547 | 0.27934 | 0.045132 | 0.019547 | south | N | 0.019547 | 0
80224 | VISTRONG | 1 | 15 | 0.12539 | south | N | 0.25843 | -0.020675 | 0.27822 | 0.044004 | 0.020675 | south | N | 0.020675 | 0
80225 | VISTRONG | 2 | 23 | 0.12539 | south | N | 0.25843 | -0.020675 | 0.27822 | 0.044004 | 0.020675 | south | N | 0.020675 | 0
80226 | ALCOA G | 1 | 48 | 0.12306 | south | N | 0.25611 | -0.022999 | 0.27589 | 0.04168 | 0.022999 | south | N | 0.022999 | 0
80227 | AIRCO G | 1 | 8 | 0.12491 | south | N | 0.25795 | -0.021155 | 0.27774 | 0.043524 | 0.021155 | south | N | 0.021155 | 0
80261 | NBEC81A | 1 | 180 | 0.12713 | south | Y | 0.26018 | -0.018926 | 0.27997 | 0.045753 | 0.018926 | south | N | 0.018926 | 0
80262 | NBEC91A | 1 | 180 | 0.12712 | south | Y | 0.26016 | -0.018944 | 0.27995 | 0.045735 | 0.018944 | south | N | 0.018944 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.12725 | south | Y | 0.2603 | -0.018808 | 0.28008 | 0.045871 | 0.018808 | south | N | 0.018808 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.12725 | south | Y | 0.2603 | -0.018808 | 0.28008 | 0.045871 | 0.018808 | south | N | 0.018808 | 0
80265 | LARECU40 | 4 | 100 | 0.12748 | south | Y | 0.26053 | -0.018581 | 0.28031 | 0.046098 | 0.018581 | south | N | 0.018581 | 0
80266 | LARECU50 | 5 | 100 | 0.12748 | south | Y | 0.26053 | -0.018581 | 0.28031 | 0.046098 | 0.018581 | south | N | 0.018581 | 0
80291 | PAPALOTE | 1 | 25 | 0.12675 | south | Y | 0.25979 | -0.019313 | 0.27958 | 0.045366 | 0.019313 | south | N | 0.019313 | 0
80291 | PAPALOTE | 2 | 25 | 0.12675 | south | Y | 0.25979 | -0.019313 | 0.27958 | 0.045366 | 0.019313 | south | N | 0.019313 | 0
80291 | PAPALOTE | 3 | 25 | 0.12675 | south | Y | 0.25979 | -0.019313 | 0.27958 | 0.045366 | 0.019313 | south | N | 0.019313 | 0
80291 | PAPALOTE | 4 | 16 | 0.12675 | south | Y | 0.25979 | -0.019313 | 0.27958 | 0.045366 | 0.019313 | south | N | 0.019313 | 0
80294 | PAPALOTE | 5 | 25 | 0.12675 | south | Y | 0.25979 | -0.019313 | 0.27958 | 0.045366 | 0.019313 | south | N | 0.019313 | 0
80294 | PAPALOTE | 6 | 25 | 0.12675 | south | Y | 0.25979 | -0.019313 | 0.27958 | 0.045366 | 0.019313 | south | N | 0.019313 | 0
80294 | PAPALOTE | 7 | 25 | 0.12675 | south | Y | 0.25979 | -0.019313 | 0.27958 | 0.045366 | 0.019313 | south | N | 0.019313 | 0
80294 | PAPALOTE | 8 | 15 | 0.12675 | south | Y | 0.25979 | -0.019313 | 0.27958 | 0.045366 | 0.019313 | south | N | 0.019313 | 0
86104 | CID-138 | EQ | 0 | 0.12748 | south | N | 0.26053 | -0.018581 | 0.28031 | 0.046098 | 0.018581 | south | N | 0.018581 | 0
86105 | CID-230 | EQ | 500 | 0.12748 | south | N | 0.26053 | -0.018581 | 0.28031 | 0.046098 | 0.018581 | south | N | 0.018581 | 0
86106 | CUF-230 | EQ | 500 | 0.12748 | south | N | 0.26053 | -0.018581 | 0.28031 | 0.046098 | 0.018581 | south | N | 0.018581 | 0
86107 | CUF-138 | EQ | 0 | 0.12748 | south | N | 0.26053 | -0.018581 | 0.28031 | 0.046098 | 0.018581 | south | N | 0.018581 | 0
88198 | BEEVILLE | F | 0 | 0.13042 | south | N | 0.26347 | -0.015639 | 0.28325 | 0.04904 | 0.015639 | south | N | 0.015639 | 0
88253 | HAMILTON | F | 0 | 0.053117 | south | N | 0.18616 | -0.092944 | 0.20595 | -0.028265 | 0.028265 | houston | Y | 0.092944 | 0
88299 | ZAPATA | F | 0 | 0.12693 | south | N | 0.25998 | -0.019132 | 0.27976 | 0.045547 | 0.019132 | south | N | 0.019132 | 0
88508 | FALFURRI | F | 0 | 0.12823 | south | N | 0.26127 | -0.017835 | 0.28106 | 0.046844 | 0.017835 | south | N | 0.017835 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3402 LAKE_CRK 3405 THOUSE__ C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 3405 - 3409 and 3405 - 3412 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.23116 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.40611 | 0 | 0 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.23116 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.40611 | 0 | 0 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 14.4126 | 100 | 0.31908 | 31.9082 | 100 | 31.9082
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.052633 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.22759 | 0 | 100 | 31.9082 | Weighted Shift Factors
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.046435 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.2289 | 48 | 0.22139 | 10.6268 | 148 | 42.535 | South | 0.14606
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.046435 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.136 | 46 | 0.22139 | 10.184 | 194 | 52.719 | North | -0.17496
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.046435 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8757 | 105 | 0.22139 | 23.2461 | 299 | 75.9651 |  | 0.32102
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0099 | 0 | 0.22042 | 0 | 299 | 75.9651
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0918 | 0 | 0.22042 | 0 | 299 | 75.9651 | Line Rating | 1239.6
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0918 | 0 | 0.22042 | 0 | 299 | 75.9651 | Conc Gen | 1634
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.2748 | 0 | 0.22042 | 0 | 299 | 75.9651 | Weighted Imp. | 341.9734
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.044289 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.4172 | 0 | 0.21925 | 0 | 299 | 75.9651 | PTDF | 0.20929
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21917 | 0 | 299 | 75.9651
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21917 | 0 | 299 | 75.9651 | Concentration | 0.65195
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.044217 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.75169 | 17 | 0.21917 | 3.7259 | 316 | 79.691
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21917 | 0 | 316 | 79.691
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21917 | 0 | 316 | 79.691
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.039436 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 18.2589 | 463 | 0.21439 | 99.2636 | 779 | 178.9546
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.4312 | 855 | 0.19067 | 163.0188 | 1634 | 341.9734
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.4312 | 855 | 0.19067 | 163.0188
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.3925 | 152.3 | 0.19067 | 29.0383
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4035 | 153 | 0.19067 | 29.1718
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.00797 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.5912 | 827 | 0.18293 | 151.28
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.00797 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.5274 | 819 | 0.18293 | 149.8166
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17496 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17496 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.068161 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -41.919 | 615 | 0.1068 | 65.6791
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.068161 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -40.0105 | 587 | 0.1068 | 62.6888
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.076294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.4975 | 150.7 | 0.098662 | 14.8684
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.076294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.5204 | 151 | 0.098662 | 14.898
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.076294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -13.5346 | 177.4 | 0.098662 | 17.5027
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.07728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.7079 | 151.5 | 0.097676 | 14.7979
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.07728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.7697 | 152.3 | 0.097676 | 14.8761
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.07728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -13.7172 | 177.5 | 0.097676 | 17.3375
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.088265 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.2398 | 150 | 0.086691 | 13.0037
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.10854 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -19.7543 | 182 | 0.066416 | 12.0878
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.10854 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -52.5334 | 484 | 0.066416 | 32.1455
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.10898 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.065971 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.11016 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -5.508 | 50 | 0.064797 | 3.2399
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.11044 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.064515 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | 1 | -16.8206 | 0 | 0.061303 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | 1 | -14.7749 | 0 | 0.061303 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | 1 | -16.4797 | 0 | 0.061303 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | 1 | -45.3475 | 0 | 0.061303 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.11696 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -91.8175 | 785 | 0.057991 | 45.5231
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.11696 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -92.9872 | 795 | 0.057991 | 46.103
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.11696 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -91.2327 | 780 | 0.057991 | 45.2332
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.12113 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -27.1338 | 224 | 0.053823 | 12.0564
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.1944 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 110.6119 | 569 | 0.048336 | 27.5034
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.1944 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 112.9447 | 581 | 0.048336 | 28.0834
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.13256 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1351 | 84 | 0.042395 | 3.5612
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.1333 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.1972 | 76.5 | 0.041659 | 3.1869
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13404 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.7231 | 80 | 0.040917 | 3.2734
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.13842 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7631 | 150 | 0.036535 | 5.4803
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.13842 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7631 | 150 | 0.036535 | 5.4803
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.13853 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.0826 | 80 | 0.036423 | 2.9139
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13856 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.0846 | 80 | 0.036398 | 2.9119
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.13875 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.4062 | 75 | 0.036207 | 2.7155
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13875 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.0999 | 80 | 0.036207 | 2.8966
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.13875 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.55 | 40 | 0.036207 | 1.4483
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13963 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1701 | 80 | 0.03533 | 2.8264
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13963 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1701 | 80 | 0.03533 | 2.8264
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.6474 | 161 | 0.034289 | 5.5206
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.0694 | 164 | 0.034289 | 5.6234
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.0694 | 164 | 0.034289 | 5.6234
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -58.2361 | 414 | 0.034289 | 14.1957
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.7881 | 162 | 0.034289 | 5.5549
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.6474 | 161 | 0.034289 | 5.5206
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.9287 | 163 | 0.034289 | 5.5891
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -57.5328 | 409 | 0.034289 | 14.0243
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.14288 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.68582 | 0 | 0.032076 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.14571 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.9141 | 20 | 0.029251 | 0.58502
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.14571 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.6427 | 25 | 0.029249 | 0.73123
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.14571 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.974 | 41 | 0.029249 | 1.1992
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.14605 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -56.6678 | 388 | 0.028905 | 11.2152
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.14605 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -75.2163 | 515 | 0.028905 | 14.8862
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.14654 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.8618 | 40 | 0.028412 | 1.1365
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.1467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -11.589 | 79 | 0.02826 | 2.2326
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.1467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -15.5498 | 106 | 0.02826 | 2.9956
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.1467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -21.4176 | 146 | 0.02826 | 4.126
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.1467 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -11.1489 | 76 | 0.02826 | 2.1478
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.14733 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -82.2074 | 558 | 0.027631 | 15.4182
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.14733 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -85.3012 | 579 | 0.027631 | 15.9985
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.14733 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -119.0386 | 808 | 0.027631 | 22.326
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.14775 | north | 8 | N | N | Nnorth | Nnorth | 1 | -11.0812 | 0 | 0.027207 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.14775 | north | 8 | N | N | Nnorth | Nnorth | 1 | -11.7608 | 0 | 0.027207 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.14775 | north | 8 | N | N | Nnorth | Nnorth | 1 | -13.061 | 0 | 0.027207 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.7261 | 160 | 0.026668 | 4.2669
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.1329 | 156 | 0.026668 | 4.1602
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.0644 | 196 | 0.026668 | 5.227
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.1329 | 156 | 0.026668 | 4.1602
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.2812 | 157 | 0.026668 | 4.1869
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.361 | 198 | 0.026668 | 5.2803
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.14834 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.026615 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.14834 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.026615 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.14888 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -55.0867 | 370 | 0.026073 | 9.6471
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -20.8436 | 0 | 0.026073 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -20.9925 | 0 | 0.026073 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -46.0048 | 0 | 0.026073 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -21.2903 | 0 | 0.026073 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -21.4392 | 0 | 0.026073 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -46.1537 | 0 | 0.026073 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.14991 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -25.484 | 170 | 0.02505 | 4.2585
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.14991 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -77.9511 | 520 | 0.02505 | 13.0261
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.1736 | 42 | 0.02474 | 1.0391
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.5152 | 44 | 0.02474 | 1.0886
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.5152 | 44 | 0.02474 | 1.0886
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.0276 | 47 | 0.02474 | 1.1628
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.15069 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.5347 | 196 | 0.024269 | 4.7568
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.15069 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -16.7263 | 111 | 0.024269 | 2.6939
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -9.9492 | 66 | 0.024211 | 1.5979
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -9.7984 | 65 | 0.024211 | 1.5737
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.0999 | 67 | 0.024211 | 1.6222
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.0999 | 67 | 0.024211 | 1.6222
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.0999 | 67 | 0.024211 | 1.6222
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.15074 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.024211 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.15074 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.024211 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.15079 | north | 5 | N | N | Nnorth | Nnorth | 1 | -6.0317 | 0 | 0.024164 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.15079 | north | 5 | N | N | Nnorth | Nnorth | 1 | -6.0317 | 0 | 0.024164 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.15082 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.5642 | 169.5 | 0.024135 | 4.0909
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.15085 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2799 | 35 | 0.024103 | 0.84361
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.15085 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5256 | 30 | 0.024103 | 0.7231
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.15122 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.5321 | 149 | 0.023734 | 3.5364
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.16942 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 52.5202 | 310 | 0.023359 | 7.2414
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.16942 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 69.9705 | 413 | 0.023359 | 9.6474
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.15171 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.0013 | 6.6 | 0.02325 | 0.15345
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.15171 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2035 | 34.3 | 0.02325 | 0.79748
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.16871 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3497 | 0 | 0.02265 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.16871 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3497 | 0 | 0.02265 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.1618 | 112.5 | 0.022407 | 2.5208
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.8061 | 149.5 | 0.022407 | 3.3499
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.3741 | 186 | 0.022407 | 4.1677
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.7218 | 214.5 | 0.022407 | 4.8063
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -31.83 | 208.2 | 0.022074 | 4.5959
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -21.7245 | 142.1 | 0.022074 | 3.1367
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -20.2416 | 132.4 | 0.022074 | 2.9226
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -20.792 | 136 | 0.022074 | 3.0021
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.4737 | 147 | 0.022074 | 3.2449
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -32.1052 | 210 | 0.022074 | 4.6356
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.2379 | 49 | 0.022059 | 1.0809
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7335 | 46 | 0.022059 | 1.0147
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7335 | 46 | 0.022059 | 1.0147
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.9016 | 47 | 0.022059 | 1.0368
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.16812 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 25.8905 | 154 | 0.022059 | 3.3971
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.16812 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.8818 | 148 | 0.022059 | 3.2648
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.0698 | 48 | 0.022059 | 1.0588
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.0698 | 48 | 0.022059 | 1.0588
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.7032 | 70 | 0.022053 | 1.5437
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.7032 | 70 | 0.022053 | 1.5437
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -14.1894 | 92.8 | 0.022053 | 2.0465
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -12.2322 | 80 | 0.022053 | 1.7643
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -12.2322 | 80 | 0.022053 | 1.7643
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -17.5838 | 115 | 0.022053 | 2.5361
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.15298 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8727 | 58 | 0.021978 | 1.2747
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.15299 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.9492 | 150 | 0.021961 | 3.2942
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.153 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.3767 | 100.5 | 0.021954 | 2.2064
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.15327 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.8306 | 214.2 | 0.021685 | 4.645
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.15335 | west | 8 | N | N | Nwest | Nwest | 1 | -3.9565 | 0 | 0.021603 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.15366 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.021297 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.1673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 25.5139 | 152.5 | 0.021243 | 3.2396
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.1673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 25.0119 | 149.5 | 0.021243 | 3.1759
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.1673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 38.9149 | 232.6 | 0.021243 | 4.9412
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.15407 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.4879 | 120 | 0.02089 | 2.5068
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.16693 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.3743 | 158 | 0.020865 | 3.2967
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.16693 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.7082 | 160 | 0.020865 | 3.3385
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.16693 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 29.2121 | 175 | 0.020865 | 3.6514
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.15412 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.4942 | 120 | 0.020838 | 2.5006
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.15434 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.5204 | 120 | 0.020619 | 2.4743
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.15434 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.9605 | 233 | 0.020619 | 4.8043
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.15434 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.2682 | 170.2 | 0.020619 | 3.5094
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.15435 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.020607 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.15435 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.729 | 225 | 0.020605 | 4.6362
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.15443 | west | 8 | N | N | Nwest | Nwest | 1 | -10.8102 | 0 | 0.020525 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.15443 | west | 8 | N | N | Nwest | Nwest | 1 | -11.3352 | 0 | 0.020525 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.15443 | west | 8 | N | N | Nwest | Nwest | 1 | -10.8719 | 0 | 0.020525 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.15446 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.8037 | 180 | 0.020491 | 3.6884
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.15446 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.8037 | 180 | 0.020491 | 3.6884
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.2167 | 150 | 0.020178 | 3.0267
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.0512 | 220 | 0.020178 | 4.4392
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.9556 | 200 | 0.020178 | 4.0356
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.8674 | 121.9 | 0.020178 | 2.4597
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.2347 | 66 | 0.019885 | 1.3124
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.6999 | 69 | 0.019885 | 1.3721
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.6999 | 69 | 0.019885 | 1.3721
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.3898 | 67 | 0.019885 | 1.3323
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.3898 | 67 | 0.019885 | 1.3323
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.0796 | 65 | 0.019885 | 1.2925
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.15519 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.7768 | 63 | 0.019769 | 1.2455
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.15528 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.8946 | 141 | 0.019675 | 2.7742
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.15528 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.6337 | 120 | 0.019675 | 2.361
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.15532 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.3763 | 99 | 0.01964 | 1.9444
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.15532 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.4743 | 61 | 0.01964 | 1.1981
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.15532 | west | 7 | N | N | Nwest | Nwest | 1 | -3.8829 | 0 | 0.01964 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.15532 | west | 7 | N | N | Nwest | Nwest | 1 | -7.0979 | 0 | 0.01964 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.15532 | west | 7 | N | N | Nwest | Nwest | 1 | -7.0979 | 0 | 0.01964 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.16541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 21.8343 | 132 | 0.01935 | 2.5542
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.16541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 22.1651 | 134 | 0.01935 | 2.5929
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.16541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 53.4278 | 323 | 0.01935 | 6.2502
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.15563 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.0726 | 84 | 0.01933 | 1.6237
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.4883 | 125 | 0.01905 | 2.3813
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.4883 | 125 | 0.01905 | 2.3813
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.15599 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.3989 | 150 | 0.018963 | 2.8445
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.15599 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.7553 | 101 | 0.018963 | 1.9153
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.8698 | 37.5 | 0.018427 | 0.69102
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.8269 | 107.5 | 0.018427 | 1.9809
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.1314 | 135 | 0.018427 | 2.4877
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.627 | 119 | 0.018427 | 2.1928
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.4355 | 105 | 0.018427 | 1.9349
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.6006 | 80.5 | 0.018427 | 1.4834
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.7478 | 209 | 0.018268 | 3.8181
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.821 | 126.5 | 0.018268 | 2.3109
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 1 | -39.0153 | 249 | 0.018268 | 4.5488
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.8675 | 197 | 0.018268 | 3.5988
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.15692 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -18.5169 | 118 | 0.018033 | 2.1279
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.15692 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -18.0461 | 115 | 0.018033 | 2.0738
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.15692 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -87.2492 | 556 | 0.018033 | 10.0265
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.15699 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.548 | 150 | 0.017969 | 2.6954
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.1586 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.5157 | 60 | 0.016361 | 0.98167
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.16205 | south | 5 | N | N | Nsouth | Nsouth | -1 | 5.6716 | 0 | 0.015986 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.16205 | south | 5 | N | N | Nsouth | Nsouth | -1 | 5.5096 | 0 | 0.015986 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.16205 | south | 5 | N | N | Nsouth | Nsouth | -1 | 5.6716 | 0 | 0.015986 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.1606 | west | 6 | Y | N | Ywest | Nwest | 1 | -64.2384 | 400 | 0.01436 | 5.7441
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.1606 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.9025 | 236 | 0.014352 | 3.3871
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.16159 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -9.6952 | 60 | 0.013369 | 0.80215
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.16159 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -10.18 | 63 | 0.013369 | 0.84226
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.16192 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.7166 | 165 | 0.013037 | 2.1511
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.1627 | west | 4 | Y | N | Ywest | Nwest | 1 | -105.7062 | 649.7 | 0.012256 | 7.9629
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.16358 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -18.4023 | 112.5 | 0.01138 | 1.2803
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7984 | 50 | 0.0099084 | 0.49542
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7984 | 50 | 0.0099084 | 0.49542
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7984 | 50 | 0.0099084 | 0.49542
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7984 | 50 | 0.0099084 | 0.49542
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.3161 | 20 | 0.0091502 | 0.183
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.3161 | 20 | 0.0091502 | 0.183
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.3161 | 20 | 0.0091502 | 0.183
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.8187 | 17 | 0.0091502 | 0.15555
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.15506 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 90.5539 | 584 | 0.0089974 | 5.2545
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.15506 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 92.2595 | 595 | 0.0089974 | 5.3534
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.15496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 67.0977 | 433 | 0.0088994 | 3.8534
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.16609 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -60.7871 | 366 | 0.0088712 | 3.2469
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.16635 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -40.256 | 242 | 0.0086092 | 2.0834
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.15279 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.91673 | 0 | 0.0067284 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.16884 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -34.4442 | 204 | 0.0061122 | 1.2469
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.16884 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -33.9376 | 201 | 0.0061122 | 1.2286
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.16884 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -40.8602 | 242 | 0.0061122 | 1.4792
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.16913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -48.7103 | 288 | 0.0058232 | 1.6771
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.16913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -24.8626 | 147 | 0.0058232 | 0.85601
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.16913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -24.8626 | 147 | 0.0058232 | 0.85601
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.16976 | north | 5 | N | N | Nnorth | Nnorth | 1 | -2.0372 | 0 | 0.0051932 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.16976 | north | 5 | N | N | Nnorth | Nnorth | 1 | -2.0372 | 0 | 0.0051932 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.16992 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -20.3909 | 120 | 0.0050322 | 0.60387
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 33.8288 | 223.9 | 0.0050284 | 1.1259
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 33.995 | 225 | 0.0050284 | 1.1314
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 33.9346 | 224.6 | 0.0050284 | 1.1294
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 34.2519 | 226.7 | 0.0050284 | 1.1399
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.17095 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0040102 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.17095 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0040102 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.17095 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0040102 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.17279 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -3.1102 | 18 | 0.0021652 | 0.038974
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.17279 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -3.1102 | 18 | 0.0021652 | 0.038974
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.17279 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -6.5661 | 38 | 0.0021652 | 0.082278
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.14788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35491 | 0 | 0.0018194 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.14788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35491 | 0 | 0.0018194 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.14788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41406 | 0 | 0.0018194 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.14763 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.6574 | 0 | 0.0015714 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.14763 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.6574 | 0 | 0.0015714 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 20.9532 | 142 | 0.0014974 | 0.21263
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.3959 | 145 | 0.0014974 | 0.21712
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.2813 | 151 | 0.0014974 | 0.2261
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 42.7918 | 290 | 0.0014974 | 0.43424
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.14697 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35272 | 0 | 0.00090737 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.14697 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35272 | 0 | 0.00090737 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.17416 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -10.4494 | 60 | 0.00080022 | 0.048013
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.14629 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.58517 | 0 | 0.00023137 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.17558 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -76.376 | 435 | -0.00062078 | -0.27004
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.1758 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -12.8334 | 73 | -0.00084378 | -0.061596
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.1758 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -20.9202 | 119 | -0.00084378 | -0.10041
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.1758 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -36.039 | 205 | -0.00084378 | -0.17297
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.1758 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -17.9316 | 102 | -0.00084378 | -0.086065
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.1758 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -16.8768 | 96 | -0.00084378 | -0.081003
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.1962 | 147 | -0.0018686 | -0.27469
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.8985 | 138 | -0.0018686 | -0.25787
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 20.1869 | 140 | -0.0018686 | -0.26161
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.1962 | 147 | -0.0018686 | -0.27469
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.2429 | 182 | -0.0018686 | -0.34009
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 28.55 | 198 | -0.0018686 | -0.36999
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 16.4304 | 114 | -0.0019346 | -0.22055
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 31.996 | 222 | -0.0019346 | -0.42949
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 26.5192 | 184 | -0.0019346 | -0.35597
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 32.2842 | 224 | -0.0019346 | -0.43336
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 16.5745 | 115 | -0.0019346 | -0.22248
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.17721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -69.9976 | 395 | -0.0022528 | -0.88985
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.17721 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -77.0859 | 435 | -0.0022528 | -0.97996
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.14231 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.9846 | 0 | -0.0037546 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.14231 | south | 5 | N | N | Nsouth | Nsouth | -1 | 4.1269 | 0 | -0.0037546 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.179 | north | 3 | N | N | Nnorth | Nnorth | 1 | -207.1065 | 0 | -0.0040468 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.179 | north | 3 | N | N | Nnorth | Nnorth | 1 | -207.2855 | 0 | -0.0040468 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.17921 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0042488 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.14165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0044096 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.14165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0044096 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.14165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0044096 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.14156 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.6988 | 0 | -0.0044966 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.17946 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -38.9962 | 217.3 | -0.0045018 | -0.97824
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.17946 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -36.7889 | 205 | -0.0045018 | -0.92286
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.17946 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -48.8844 | 272.4 | -0.0045018 | -1.2263
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.14128 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 59.618 | 422 | -0.0047856 | -2.0195
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.14119 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 59.8658 | 424 | -0.0048676 | -2.0639
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.14119 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 60.007 | 425 | -0.0048676 | -2.0687
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.14109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.8697 | 155 | -0.0049656 | -0.76967
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.14109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 23.9861 | 170 | -0.0049656 | -0.84416
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.14109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.8697 | 155 | -0.0049656 | -0.76967
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.14109 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 58.1278 | 412 | -0.0049736 | -2.0491
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.14109 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 56.4348 | 400 | -0.0049736 | -1.9895
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.14099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 29.4675 | 209 | -0.0050676 | -1.0591
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.14099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 30.4545 | 216 | -0.0050676 | -1.0946
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.4857 | 46 | -0.0050676 | -0.23311
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.6267 | 47 | -0.0050676 | -0.23818
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.4857 | 46 | -0.0050676 | -0.23311
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.4857 | 46 | -0.0050676 | -0.23311
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.14085 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 57.3255 | 407 | -0.0052116 | -2.1211
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.14078 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 76.867 | 546 | -0.0052786 | -2.8821
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.14078 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 105.5865 | 750 | -0.0052786 | -3.959
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.1401 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.1259 | 58 | -0.0059596 | -0.34566
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.1401 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.469 | 89 | -0.0059596 | -0.53041
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.1644 | 44 | -0.0059596 | -0.26222
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.1644 | 44 | -0.0059596 | -0.26222
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.0243 | 43 | -0.0059596 | -0.25626
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.3045 | 45 | -0.0059596 | -0.26818
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.6645 | 70 | -0.0059648 | -0.41753
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.4835 | 69 | -0.0059648 | -0.41157
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.4835 | 69 | -0.0059648 | -0.41157
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.3026 | 68 | -0.0059648 | -0.4056
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.13705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.4668 | 0 | -0.0090156 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.13705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.4668 | 0 | -0.0090156 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.13705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.0557 | 0 | -0.0090156 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.13585 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 53.7954 | 396 | -0.010214 | -4.0446
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.13539 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8548 | 0 | -0.010674 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.18963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -31.8578 | 168 | -0.014674 | -2.4652
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.18963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -17.0667 | 90 | -0.014674 | -1.3206
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.13042 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015639 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.13015 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 81.8662 | 629 | -0.015908 | -10.0059
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.12823 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.017835 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.12767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.4267 | 207 | -0.018396 | -3.8079
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.12767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 27.665 | 216.7 | -0.018396 | -3.9863
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.12767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 30.8949 | 242 | -0.018396 | -4.4517
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.12766 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.3835 | 144 | -0.018398 | -2.6493
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.12766 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.3835 | 144 | -0.018398 | -2.6493
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.12766 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.8304 | 171 | -0.018398 | -3.146
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.12765 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018412 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.12765 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.8507 | 38 | -0.018412 | -0.69964
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.12765 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.4636 | 19.3 | -0.018412 | -0.35534
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.12765 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.9147 | 15 | -0.018412 | -0.27617
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.12765 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.9995 | 47 | -0.018412 | -0.86535
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.9989 | 94 | -0.018413 | -1.7308
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 5.2336 | 41 | -0.018413 | -0.75492
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.8506 | 38 | -0.018413 | -0.69968
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.4253 | 19 | -0.018413 | -0.34984
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.9989 | 94 | -0.018413 | -1.7308
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.5953 | 36 | -0.018413 | -0.66285
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 5.4889 | 43 | -0.018413 | -0.79174
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.8083 | 22 | -0.018413 | -0.40508
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 18.8919 | 148 | -0.018413 | -2.7251
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.3824 | 50 | -0.018413 | -0.92063
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.0206 | 55 | -0.018413 | -1.0127
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.3824 | 50 | -0.018413 | -0.92063
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.1276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.6937 | 146.5 | -0.018459 | -2.7042
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.1276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.8723 | 147.9 | -0.018459 | -2.73
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.1276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.0751 | 173 | -0.018459 | -3.1933
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.12759 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.7003 | 0 | -0.018466 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.12748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 12.748 | 100 | -0.018581 | -1.8581
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.12748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 12.748 | 100 | -0.018581 | -1.8581
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.12748 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018581 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.12748 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018581 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.12748 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018581 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.12748 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018581 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.12747 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018589 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.12738 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.3424 | 144 | -0.018683 | -2.6903
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.12738 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 23.9471 | 188 | -0.018683 | -3.5123
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.12733 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8386 | 0 | -0.018729 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.12732 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8383 | 0 | -0.018737 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.12726 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.1816 | 0 | -0.018796 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.12726 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.1816 | 0 | -0.018796 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.12726 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.5271 | 0 | -0.018803 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.12726 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3998 | 0 | -0.018803 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.12726 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.5271 | 0 | -0.018803 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.12725 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 42.5025 | 334 | -0.018808 | -6.2817
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.12725 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 43.266 | 340 | -0.018808 | -6.3946
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.12725 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.9055 | 180 | -0.018808 | -3.3854
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.12725 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.9055 | 180 | -0.018808 | -3.3854
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.12713 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.8843 | 180 | -0.018926 | -3.4066
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.12712 | south | 8 | N | N | Nsouth | Nsouth | -1 | 18.8525 | 0 | -0.018937 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.12712 | south | 8 | N | N | Nsouth | Nsouth | -1 | 18.8906 | 0 | -0.018937 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.12712 | south | 8 | N | N | Nsouth | Nsouth | -1 | 19.45 | 0 | -0.018937 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.12712 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 42.7113 | 336 | -0.018944 | -6.3651
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.12712 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.8811 | 180 | -0.018944 | -3.4099
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.12693 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.019132 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 25 | -0.019313 | -0.48282
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 25 | -0.019313 | -0.48282
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 25 | -0.019313 | -0.48282
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.028 | 16 | -0.019313 | -0.309
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 25 | -0.019313 | -0.48282
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 25 | -0.019313 | -0.48282
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 25 | -0.019313 | -0.48282
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.9012 | 15 | -0.019313 | -0.28969
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.12666 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.2464 | 0 | -0.019398 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 19.9892 | 0 | -0.019547 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 19.3566 | 0 | -0.019547 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.6514 | 0 | -0.019547 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 18.3445 | 0 | -0.019547 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 18.5976 | 0 | -0.019547 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 16.0673 | 0 | -0.019547 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.12651 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5182 | 0 | -0.019547 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0294 | 47.7 | -0.019658 | -0.93767
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7148 | 37.3 | -0.019658 | -0.73323
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.8145 | 46 | -0.019658 | -0.90425
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0673 | 48 | -0.019658 | -0.94357
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.12567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.7647 | 22 | -0.020393 | -0.44864
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.12567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.3823 | 11 | -0.020393 | -0.22432
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.12567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.3823 | 11 | -0.020393 | -0.22432
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.12566 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.016 | 24 | -0.020396 | -0.4895
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.12566 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 3.016 | 24 | -0.020396 | -0.4895
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.12566 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 2.8903 | 23 | -0.020396 | -0.4691
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.19562 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -42.3311 | 216.4 | -0.020659 | -4.4706
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.19562 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -42.2724 | 216.1 | -0.020659 | -4.4644
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.12539 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8808 | 0 | -0.020675 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.12539 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.8839 | 0 | -0.020675 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.12491 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.99925 | 0 | -0.021155 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8624 | 0 | -0.021384 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.4909 | 0 | -0.021385 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87273 | 0 | -0.021385 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8624 | 0 | -0.021385 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8701 | 0 | -0.021385 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87273 | 0 | -0.021385 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8701 | 0 | -0.021385 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8624 | 0 | -0.021385 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.12306 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.907 | 0 | -0.022999 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -44.3585 | 224 | -0.023073 | -5.1683
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -44.7546 | 226 | -0.023073 | -5.2144
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -41.9821 | 212 | -0.023073 | -4.8914
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -41.7841 | 211 | -0.023073 | -4.8684
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.6818 | 0 | -0.023506 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.927 | 0 | -0.023506 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.6818 | 0 | -0.023506 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.8044 | 0 | -0.023506 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.6083 | 0 | -0.023506 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0639 | 0 | -0.023506 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.6375 | 0 | -0.023506 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.4315 | 0 | -0.023506 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.3434 | 0 | -0.023506 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.0691 | 0 | -0.023506 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.10412 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 138.788 | 0 | -0.041944 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.10412 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 138.2674 | 0 | -0.041944 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.8994 | 76 | -0.042121 | -3.2012
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.8994 | 76 | -0.042121 | -3.2012
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 10.9137 | 105 | -0.042121 | -4.4227
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.6916 | 74 | -0.042121 | -3.1169
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.6916 | 74 | -0.042121 | -3.1169
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 10.6019 | 102 | -0.042121 | -4.2963
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.10153 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 6.7011 | 66 | -0.044529 | -2.9389
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.842 | 0 | -0.051835 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.7277 | 0 | -0.051835 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.2402 | 0 | -0.051835 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.5168 | 0 | -0.051835 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.1034 | 0 | -0.051835 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.2919 | 0 | -0.051835 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.7113 | 0 | -0.051835 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6961 | 0 | -0.051835 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.8572 | 0 | -0.051835 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.5958 | 0 | -0.051835 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.9362 | 0 | -0.051835 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.7843 | 0 | -0.051835 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.1058 | 0 | -0.051835 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.5168 | 0 | -0.051835 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.1399 | 0 | -0.051835 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.7053 | 0 | -0.051835 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.1612 | 0 | -0.051835 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.5381 | 0 | -0.051835 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.5381 | 0 | -0.051835 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 16.1126 | 0 | -0.051835 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.092458 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.5645 | 0 | -0.053603 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.092458 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.92458 | 0 | -0.053603 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.1087 | 0 | -0.054992 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.1087 | 0 | -0.054992 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.8372 | 0 | -0.054992 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.9721 | 0 | -0.054992 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.23445 | north | 5 | N | N | Nnorth | Nnorth | 1 | -3.5168 | 0 | -0.059499 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.23445 | north | 5 | N | N | Nnorth | Nnorth | 1 | -3.5168 | 0 | -0.059499 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.085988 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.964 | 0 | -0.060073 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.085826 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 55.8727 | 651 | -0.060235 | -39.2127
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.085826 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 48.4059 | 564 | -0.060235 | -33.9723
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.085826 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 51.4956 | 600 | -0.060235 | -36.1408
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.085783 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 13.9826 | 0 | -0.060278 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.085783 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 13.9826 | 0 | -0.060278 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.085783 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 21.0168 | 0 | -0.060278 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.085229 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.8126 | 0 | -0.060832 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.085037 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 13.691 | 161 | -0.061024 | -9.8248
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.085037 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 14.1161 | 166 | -0.061024 | -10.1299
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.085037 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 21.0892 | 248 | -0.061024 | -15.1339
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.085037 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 46.4302 | 546 | -0.061024 | -33.3189
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.085037 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 54.6788 | 0 | -0.061024 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.085037 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.1055 | 13 | -0.061024 | -0.79331
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 8.2574 | 0 | -0.063734 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 7.6482 | 0 | -0.063734 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 8.455 | 0 | -0.063734 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 8.3974 | 0 | -0.063734 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.082326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6344 | 0 | -0.063735 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.082326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4698 | 0 | -0.063735 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.8277 | 0 | -0.063749 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.4902 | 0 | -0.063749 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.3625 | 0 | -0.063749 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.6102 | 0 | -0.063749 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.6349 | 0 | -0.063749 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.5361 | 0 | -0.063749 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 7.902 | 0 | -0.063749 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 20.0841 | 0 | -0.063749 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.2925 | 0 | -0.063749 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.081251 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.06481 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.081226 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.0613 | 50 | -0.064835 | -3.2417
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.080358 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.065703 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.2218 | 0 | -0.066701 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.9519 | 0 | -0.066701 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.9043 | 0 | -0.066701 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.3251 | 0 | -0.066701 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96819 | 0 | -0.066701 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.1329 | 0 | -0.067093 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.7381 | 0 | -0.067093 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.1329 | 0 | -0.067093 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.1329 | 0 | -0.067093 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.6061 | 46 | -0.067668 | -3.1127
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.6061 | 46 | -0.067668 | -3.1127
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.6061 | 46 | -0.067668 | -3.1127
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.3116 | 55 | -0.067668 | -3.7217
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.3116 | 55 | -0.067668 | -3.7217
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.2332 | 54 | -0.067668 | -3.6541
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.078241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.1028 | 0 | -0.06782 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.078241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.2593 | 0 | -0.06782 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.7356 | 0 | -0.068024 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.2596 | 0 | -0.068024 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.2908 | 0 | -0.068024 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.2518 | 0 | -0.068024 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 20.992 | 0 | -0.068024 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.077878 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.7257 | 0 | -0.068183 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.077703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.93244 | 12 | -0.068358 | -0.82029
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.077703 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.068358 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.077693 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 13.1301 | 169 | -0.068368 | -11.5541
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.077679 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 12.817 | 165 | -0.068382 | -11.283
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.077669 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.5727 | 0 | -0.068392 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.077669 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.0563 | 0 | -0.068392 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.077632 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 16.5356 | 213 | -0.068429 | -14.5753
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.077628 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2576 | 0 | -0.068433 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.968 | 0 | -0.068436 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.9059 | 0 | -0.068436 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.4118 | 0 | -0.068436 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.7132 | 0 | -0.068436 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.077619 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 17.6971 | 228 | -0.068442 | -15.6047
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.077613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 13.9703 | 0 | -0.068448 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.077613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.3094 | 0 | -0.068448 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.077613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.1852 | 0 | -0.068448 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.493 | 0 | -0.068695 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.5704 | 0 | -0.068695 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.0173 | 0 | -0.068695 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.321 | 0 | -0.068695 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.076978 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.469 | 0 | -0.069083 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.2316 | 42 | -0.069117 | -2.9029
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.2316 | 42 | -0.069117 | -2.9029
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.9239 | 38 | -0.069117 | -2.6264
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.9239 | 38 | -0.069117 | -2.6264
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.076846 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.2944 | 0 | -0.069215 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.076846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.3742 | 0 | -0.069215 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9272 | 104 | -0.069838 | -7.2631
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9272 | 104 | -0.069838 | -7.2631
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.116 | 54 | -0.069838 | -3.7712
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.0398 | 53 | -0.069838 | -3.7014
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.116 | 54 | -0.069838 | -3.7712
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.3447 | 57 | -0.069838 | -3.9807
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.116 | 54 | -0.069838 | -3.7712
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.116 | 54 | -0.069838 | -3.7712
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.4209 | 58 | -0.069838 | -4.0506
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.4209 | 58 | -0.069838 | -4.0506
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.075973 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 55.8402 | 735 | -0.070088 | -51.5144
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.075942 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.45565 | 0 | -0.070119 | 0
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.5776 | 0 | -0.070249 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6307 | 0 | -0.070249 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4791 | 0 | -0.070249 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.4798 | 0 | -0.070249 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3419 | 0 | -0.070249 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5466 | 0 | -0.070249 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5087 | 0 | -0.070249 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6534 | 0 | -0.070249 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3646 | 0 | -0.070249 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.4743 | 0 | -0.070249 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.2202 | 0 | -0.070249 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.075613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.90736 | 12 | -0.070448 | -0.84537
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.075346 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37673 | 0 | -0.070715 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.075346 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5823 | 0 | -0.070715 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.8973 | 0 | -0.070718 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.9726 | 0 | -0.070718 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.274 | 0 | -0.070718 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.7466 | 0 | -0.070718 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.6713 | 0 | -0.070718 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.8357 | 0 | -0.070718 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.4452 | 0 | -0.070718 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.075329 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.90395 | 12 | -0.070732 | -0.84878
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.07531 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 55.9553 | 743 | -0.070751 | -52.5677
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.075191 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.805 | 0 | -0.07087 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.07511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 12.9189 | 172 | -0.070951 | -12.2035
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.07511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 12.9189 | 172 | -0.070951 | -12.2035
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.07511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 12.9189 | 172 | -0.070951 | -12.2035
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.1517 | 0 | -0.071419 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.0472 | 0 | -0.071419 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.8606 | 0 | -0.071419 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 20.0936 | 0 | -0.071419 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.074482 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 29.6438 | 398 | -0.071579 | -28.4883
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.1551 | 56 | -0.071863 | -4.0243
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.3777 | 59 | -0.071863 | -4.2399
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.1551 | 56 | -0.071863 | -4.0243
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.1551 | 56 | -0.071863 | -4.0243
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.3777 | 59 | -0.071863 | -4.2399
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.1551 | 56 | -0.071863 | -4.0243
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.3581 | 0 | -0.074627 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.1437 | 0 | -0.074627 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.0008 | 0 | -0.074627 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.0008 | 0 | -0.074627 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.071434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.5723 | 0 | -0.074627 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.2506 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -37.59 | 150 | -0.075644 | -11.3466
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.2506 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -20.048 | 80 | -0.075644 | -6.0515
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.053117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.7529 | 0 | -0.092944 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.053117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3279 | 0 | -0.092944 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.053117 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.092944 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14606 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14606 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.33041 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -84.2545 | 255 | -0.15545 | -39.6407
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.33041 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -49.2311 | 149 | -0.15545 | -23.1626
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.33041 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -50.5527 | 153 | -0.15545 | -23.7844
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.48927 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.31432 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.48927 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -385.0571 | 787 | -0.31432 | -247.3665

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3402 LAKE_CRK 3405 THOUSE__ C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 3405 - 3409 and 3405 - 3412 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.48927 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.31432 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.48927 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -385.0571 | 787 | -0.31432 | -247.3665 | 787 | 247.3665
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.33041 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -84.2545 | 255 | -0.15545 | -39.6407 | 1042 | 287.0072
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.33041 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -49.2311 | 149 | -0.15545 | -23.1626 | 1191 | 310.1698 | Weighted Shift Factors
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.33041 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -50.5527 | 153 | -0.15545 | -23.7844 | 1344 | 333.9543 | South | 0.14606
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0 | 1344 | 333.9543 | North | -0.17496
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0 | 1344 | 333.9543 |  | 0.32102
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0 | 1344 | 333.9543
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0 | 1344 | 333.9543 | Line Rating | 1239.6
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0 | 1344 | 333.9543 | Conc Gen | 2314
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0 | 1344 | 333.9543 | Weighted Imp. | 404.4177
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14606 | 0 | 1344 | 333.9543 | PTDF | 0.17477
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14606 | 0 | 1344 | 333.9543
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.053117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.7529 | 0 | -0.092944 | 0 | 1344 | 333.9543 | Concentration | 0.54443
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.053117 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3279 | 0 | -0.092944 | 0 | 1344 | 333.9543
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.053117 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.092944 | 0 | 1344 | 333.9543
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.2506 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -37.59 | 150 | -0.075644 | -11.3466 | 1494 | 345.3008
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.2506 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -20.048 | 80 | -0.075644 | -6.0515 | 1574 | 351.3523
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.3581 | 0 | -0.074627 | 0 | 1574 | 351.3523
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.1437 | 0 | -0.074627 | 0 | 1574 | 351.3523
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.0008 | 0 | -0.074627 | 0 | 1574 | 351.3523
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.071434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.0008 | 0 | -0.074627 | 0 | 1574 | 351.3523
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.071434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.5723 | 0 | -0.074627 | 0 | 1574 | 351.3523
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.1551 | 56 | -0.071863 | -4.0243 | 1630 | 355.3767
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.3777 | 59 | -0.071863 | -4.2399 | 1689 | 359.6165
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.1551 | 56 | -0.071863 | -4.0243 | 1745 | 363.6409
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.1551 | 56 | -0.071863 | -4.0243 | 1801 | 367.6652
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.3777 | 59 | -0.071863 | -4.2399 | 1860 | 371.9051
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.074198 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.1551 | 56 | -0.071863 | -4.0243 | 1916 | 375.9294
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.074482 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 29.6438 | 398 | -0.071579 | -28.4883 | 2314 | 404.4177
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.1517 | 0 | -0.071419 | 0 | 2314 | 404.4177
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.0472 | 0 | -0.071419 | 0 | 2314 | 404.4177
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.8606 | 0 | -0.071419 | 0 | 2314 | 404.4177
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.074642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 20.0936 | 0 | -0.071419 | 0 | 2314 | 404.4177
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.07511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 12.9189 | 172 | -0.070951 | -12.2035
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.07511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 12.9189 | 172 | -0.070951 | -12.2035
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.07511 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 12.9189 | 172 | -0.070951 | -12.2035
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.075191 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.805 | 0 | -0.07087 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.07531 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 55.9553 | 743 | -0.070751 | -52.5677
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.075329 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.90395 | 0 | -0.070732 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.8973 | 0 | -0.070718 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.9726 | 0 | -0.070718 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.274 | 0 | -0.070718 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.7466 | 0 | -0.070718 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.6713 | 0 | -0.070718 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.8357 | 0 | -0.070718 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.075343 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.4452 | 0 | -0.070718 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.075346 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37673 | 0 | -0.070715 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.075346 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5823 | 0 | -0.070715 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.075613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.90736 | 12 | -0.070448 | -0.84537
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.5776 | 0 | -0.070249 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6307 | 0 | -0.070249 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4791 | 0 | -0.070249 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.4798 | 0 | -0.070249 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3419 | 0 | -0.070249 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5466 | 0 | -0.070249 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5087 | 0 | -0.070249 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6534 | 0 | -0.070249 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3646 | 0 | -0.070249 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.4743 | 0 | -0.070249 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.075812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.2202 | 0 | -0.070249 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.075942 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.45565 | 0 | -0.070119 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.075973 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 55.8402 | 735 | -0.070088 | -51.5144
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9272 | 104 | -0.069838 | -7.2631
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9272 | 104 | -0.069838 | -7.2631
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.116 | 54 | -0.069838 | -3.7712
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.0398 | 53 | -0.069838 | -3.7014
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.116 | 54 | -0.069838 | -3.7712
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.3447 | 57 | -0.069838 | -3.9807
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.116 | 54 | -0.069838 | -3.7712
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.116 | 54 | -0.069838 | -3.7712
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.4209 | 58 | -0.069838 | -4.0506
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.076223 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.4209 | 58 | -0.069838 | -4.0506
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.076846 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.2944 | 0 | -0.069215 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.076846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.3742 | 0 | -0.069215 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.2316 | 42 | -0.069117 | -2.9029
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.2316 | 42 | -0.069117 | -2.9029
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.9239 | 38 | -0.069117 | -2.6264
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.076944 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.9239 | 38 | -0.069117 | -2.6264
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.076978 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.469 | 0 | -0.069083 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.493 | 0 | -0.068695 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.5704 | 0 | -0.068695 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.0173 | 0 | -0.068695 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.077366 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.321 | 0 | -0.068695 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.077613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 13.9703 | 0 | -0.068448 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.077613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.3094 | 0 | -0.068448 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.077613 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.1852 | 0 | -0.068448 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.077619 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 17.6971 | 228 | -0.068442 | -15.6047
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.968 | 0 | -0.068436 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.9059 | 0 | -0.068436 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.4118 | 0 | -0.068436 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.077625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.7132 | 0 | -0.068436 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.077628 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2576 | 0 | -0.068433 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.077632 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 16.5356 | 213 | -0.068429 | -14.5753
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.077669 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.5727 | 0 | -0.068392 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.077669 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.0563 | 0 | -0.068392 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.077679 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 12.817 | 165 | -0.068382 | -11.283
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.077693 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 13.1301 | 169 | -0.068368 | -11.5541
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.077703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.93244 | 12 | -0.068358 | -0.82029
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.077703 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.068358 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.077878 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.7257 | 0 | -0.068183 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.7356 | 0 | -0.068024 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.2596 | 0 | -0.068024 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.2908 | 0 | -0.068024 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.2518 | 0 | -0.068024 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.078037 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 20.992 | 0 | -0.068024 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.078241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.1028 | 0 | -0.06782 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.078241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.2593 | 0 | -0.06782 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.6061 | 46 | -0.067668 | -3.1127
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.6061 | 46 | -0.067668 | -3.1127
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 3.6061 | 46 | -0.067668 | -3.1127
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.3116 | 55 | -0.067668 | -3.7217
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.3116 | 55 | -0.067668 | -3.7217
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.078393 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 4.2332 | 54 | -0.067668 | -3.6541
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.1329 | 0 | -0.067093 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.7381 | 0 | -0.067093 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.1329 | 0 | -0.067093 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.078968 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 5.1329 | 0 | -0.067093 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.2218 | 0 | -0.066701 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.9519 | 0 | -0.066701 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.9043 | 0 | -0.066701 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.3251 | 0 | -0.066701 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.07936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96819 | 0 | -0.066701 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.080358 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.065703 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.081226 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 4.0613 | 50 | -0.064835 | -3.2417
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.081251 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.06481 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.8277 | 0 | -0.063749 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.4902 | 0 | -0.063749 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.3625 | 0 | -0.063749 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.6102 | 0 | -0.063749 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.6349 | 0 | -0.063749 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.5361 | 0 | -0.063749 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 7.902 | 0 | -0.063749 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.082312 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 20.0841 | 0 | -0.063749 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.082312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.2925 | 0 | -0.063749 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.082326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6344 | 0 | -0.063735 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.082326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4698 | 0 | -0.063735 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 8.2574 | 0 | -0.063734 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 7.6482 | 0 | -0.063734 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 8.455 | 0 | -0.063734 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.082327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 8.3974 | 0 | -0.063734 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.085037 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 13.691 | 161 | -0.061024 | -9.8248
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.085037 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 14.1161 | 166 | -0.061024 | -10.1299
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.085037 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 21.0892 | 248 | -0.061024 | -15.1339
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.085037 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 46.4302 | 546 | -0.061024 | -33.3189
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.085037 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 54.6788 | 0 | -0.061024 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.085037 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.1055 | 13 | -0.061024 | -0.79331
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.085229 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.8126 | 0 | -0.060832 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.085783 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 13.9826 | 0 | -0.060278 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.085783 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 13.9826 | 0 | -0.060278 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.085783 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 21.0168 | 0 | -0.060278 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.085826 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 55.8727 | 0 | -0.060235 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.085826 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 48.4059 | 0 | -0.060235 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.085826 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 51.4956 | 0 | -0.060235 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.085988 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.964 | 0 | -0.060073 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.23445 | north | 5 | N | N | Nnorth | Nnorth | 1 | -3.5168 | 0 | -0.059499 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.23445 | north | 5 | N | N | Nnorth | Nnorth | 1 | -3.5168 | 0 | -0.059499 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.1087 | 0 | -0.054992 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.1087 | 0 | -0.054992 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 10.8372 | 0 | -0.054992 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.091069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.9721 | 0 | -0.054992 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.092458 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.5645 | 0 | -0.053603 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.092458 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.92458 | 0 | -0.053603 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.842 | 0 | -0.051835 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.7277 | 0 | -0.051835 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.2402 | 0 | -0.051835 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.5168 | 0 | -0.051835 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.1034 | 0 | -0.051835 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.2919 | 0 | -0.051835 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.7113 | 0 | -0.051835 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6961 | 0 | -0.051835 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.8572 | 0 | -0.051835 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.5958 | 0 | -0.051835 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.9362 | 0 | -0.051835 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.7843 | 0 | -0.051835 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.1058 | 0 | -0.051835 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.5168 | 0 | -0.051835 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.1399 | 0 | -0.051835 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.7053 | 0 | -0.051835 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.1612 | 0 | -0.051835 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.5381 | 0 | -0.051835 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.5381 | 0 | -0.051835 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.094226 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 16.1126 | 0 | -0.051835 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.10153 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 6.7011 | 66 | -0.044529 | -2.9389
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.8994 | 76 | -0.042121 | -3.2012
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.8994 | 76 | -0.042121 | -3.2012
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 10.9137 | 105 | -0.042121 | -4.4227
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.6916 | 74 | -0.042121 | -3.1169
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.6916 | 74 | -0.042121 | -3.1169
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.10394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 10.6019 | 102 | -0.042121 | -4.2963
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.10412 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 138.788 | 0 | -0.041944 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.10412 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 138.2674 | 0 | -0.041944 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.6818 | 0 | -0.023506 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.927 | 0 | -0.023506 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.6818 | 0 | -0.023506 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.8044 | 0 | -0.023506 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.6083 | 0 | -0.023506 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0639 | 0 | -0.023506 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.6375 | 0 | -0.023506 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.4315 | 0 | -0.023506 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.3434 | 0 | -0.023506 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.12255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.0691 | 0 | -0.023506 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -44.3585 | 224 | -0.023073 | -5.1683
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -44.7546 | 226 | -0.023073 | -5.2144
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -41.9821 | 212 | -0.023073 | -4.8914
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.19803 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -41.7841 | 211 | -0.023073 | -4.8684
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.12306 | south | 7 | N | N | Nsouth | Nsouth | -1 | 5.907 | 0 | -0.022999 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.12365 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 1.0387 | 8.4 | -0.022411 | -0.18825
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.4909 | 0 | -0.021385 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87273 | 0 | -0.021385 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8624 | 0 | -0.021385 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8701 | 0 | -0.021385 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87273 | 0 | -0.021385 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8701 | 0 | -0.021385 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8624 | 0 | -0.021385 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.12468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8624 | 0 | -0.021384 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.12491 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.99925 | 0 | -0.021155 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.12539 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8808 | 0 | -0.020675 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.12539 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.8839 | 0 | -0.020675 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.19562 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -42.3311 | 216.4 | -0.020659 | -4.4706
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.19562 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -42.2724 | 216.1 | -0.020659 | -4.4644
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.12566 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.016 | 24 | -0.020396 | -0.4895
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.12566 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 3.016 | 24 | -0.020396 | -0.4895
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.12566 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 2.8903 | 23 | -0.020396 | -0.4691
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.12567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.7647 | 22 | -0.020393 | -0.44864
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.12567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.3823 | 11 | -0.020393 | -0.22432
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.12567 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.3823 | 11 | -0.020393 | -0.22432
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0294 | 47.7 | -0.019658 | -0.93767
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7148 | 37.3 | -0.019658 | -0.73323
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.8145 | 46 | -0.019658 | -0.90425
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.1264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0673 | 48 | -0.019658 | -0.94357
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 19.9892 | 0 | -0.019547 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 19.3566 | 0 | -0.019547 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.6514 | 0 | -0.019547 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 18.3445 | 0 | -0.019547 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 18.5976 | 0 | -0.019547 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.12651 | south | 8 | N | N | Nsouth | Nsouth | -1 | 16.0673 | 0 | -0.019547 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.12651 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5182 | 0 | -0.019547 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.12666 | south | 7 | N | N | Nsouth | Nsouth | -1 | 9.2464 | 0 | -0.019398 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 0 | -0.019313 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 0 | -0.019313 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 0 | -0.019313 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.028 | 0 | -0.019313 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 0 | -0.019313 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 0 | -0.019313 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1687 | 0 | -0.019313 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.12675 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.9012 | 0 | -0.019313 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.12693 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.019132 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.12712 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 42.7113 | 336 | -0.018944 | -6.3651
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.12712 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.8811 | 180 | -0.018944 | -3.4099
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.12712 | south | 8 | N | N | Nsouth | Nsouth | -1 | 18.8525 | 0 | -0.018937 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.12712 | south | 8 | N | N | Nsouth | Nsouth | -1 | 18.8906 | 0 | -0.018937 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.12712 | south | 8 | N | N | Nsouth | Nsouth | -1 | 19.45 | 0 | -0.018937 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.12713 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.8843 | 180 | -0.018926 | -3.4066
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.12725 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 42.5025 | 334 | -0.018808 | -6.2817
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.12725 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 43.266 | 340 | -0.018808 | -6.3946
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.12725 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.9055 | 180 | -0.018808 | -3.3854
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.12725 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.9055 | 180 | -0.018808 | -3.3854
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.12726 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.5271 | 0 | -0.018803 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.12726 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3998 | 0 | -0.018803 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.12726 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.5271 | 0 | -0.018803 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.12726 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.1816 | 0 | -0.018796 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.12726 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.1816 | 0 | -0.018796 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.12732 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8383 | 0 | -0.018737 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.12733 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.8386 | 0 | -0.018729 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.12738 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.3424 | 144 | -0.018683 | -2.6903
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.12738 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 23.9471 | 188 | -0.018683 | -3.5123
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.12747 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018589 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.12748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 12.748 | 100 | -0.018581 | -1.8581
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.12748 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 12.748 | 100 | -0.018581 | -1.8581
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.12748 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018581 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.12748 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018581 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.12748 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018581 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.12748 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018581 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.12759 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.7003 | 0 | -0.018466 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.1276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.6937 | 146.5 | -0.018459 | -2.7042
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.1276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.8723 | 147.9 | -0.018459 | -2.73
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.1276 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.0751 | 173 | -0.018459 | -3.1933
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.9989 | 0 | -0.018413 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 5.2336 | 0 | -0.018413 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.8506 | 0 | -0.018413 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.4253 | 0 | -0.018413 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.9989 | 0 | -0.018413 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.5953 | 0 | -0.018413 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 5.4889 | 0 | -0.018413 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.8083 | 0 | -0.018413 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 18.8919 | 0 | -0.018413 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.3824 | 0 | -0.018413 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.0206 | 0 | -0.018413 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.12765 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.3824 | 0 | -0.018413 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.12765 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.8507 | 38 | -0.018412 | -0.69964
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.12765 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.4636 | 19.3 | -0.018412 | -0.35534
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.12765 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.9147 | 15 | -0.018412 | -0.27617
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.12765 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.9995 | 47 | -0.018412 | -0.86535
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.12765 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.018412 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.12766 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.3835 | 144 | -0.018398 | -2.6493
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.12766 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.3835 | 144 | -0.018398 | -2.6493
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.12766 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.8304 | 171 | -0.018398 | -3.146
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.12767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.4267 | 207 | -0.018396 | -3.8079
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.12767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 27.665 | 216.7 | -0.018396 | -3.9863
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.12767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 30.8949 | 242 | -0.018396 | -4.4517
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.12823 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.017835 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.13015 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 81.8662 | 0 | -0.015908 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.13042 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.015639 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.18963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -31.8578 | 168 | -0.014674 | -2.4652
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.18963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -17.0667 | 90 | -0.014674 | -1.3206
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.13539 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8548 | 0 | -0.010674 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.13585 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 53.7954 | 0 | -0.010214 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.13705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.4668 | 0 | -0.0090156 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.13705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.4668 | 0 | -0.0090156 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.13705 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.0557 | 0 | -0.0090156 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.6645 | 70 | -0.0059648 | -0.41753
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.4835 | 69 | -0.0059648 | -0.41157
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.4835 | 69 | -0.0059648 | -0.41157
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.18092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.3026 | 68 | -0.0059648 | -0.4056
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.1401 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.1259 | 58 | -0.0059596 | -0.34566
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.1401 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.469 | 89 | -0.0059596 | -0.53041
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.1644 | 44 | -0.0059596 | -0.26222
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.1644 | 44 | -0.0059596 | -0.26222
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.0243 | 43 | -0.0059596 | -0.25626
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.1401 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.3045 | 45 | -0.0059596 | -0.26818
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.14078 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 76.867 | 0 | -0.0052786 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.14078 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 105.5865 | 0 | -0.0052786 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.14085 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 57.3255 | 407 | -0.0052116 | -2.1211
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.14099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 29.4675 | 209 | -0.0050676 | -1.0591
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.14099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 30.4545 | 216 | -0.0050676 | -1.0946
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.4857 | 46 | -0.0050676 | -0.23311
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.6267 | 47 | -0.0050676 | -0.23818
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.4857 | 46 | -0.0050676 | -0.23311
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.14099 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.4857 | 46 | -0.0050676 | -0.23311
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.14109 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 58.1278 | 412 | -0.0049736 | -2.0491
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.14109 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 56.4348 | 400 | -0.0049736 | -1.9895
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.14109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.8697 | 155 | -0.0049656 | -0.76967
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.14109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 23.9861 | 170 | -0.0049656 | -0.84416
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.14109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.8697 | 155 | -0.0049656 | -0.76967
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.14119 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 59.8658 | 0 | -0.0048676 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.14119 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 60.007 | 0 | -0.0048676 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.14128 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 59.618 | 422 | -0.0047856 | -2.0195
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.17946 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -38.9962 | 217.3 | -0.0045018 | -0.97824
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.17946 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -36.7889 | 205 | -0.0045018 | -0.92286
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.17946 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -48.8844 | 272.4 | -0.0045018 | -1.2263
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.14156 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.6988 | 0 | -0.0044966 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.14165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0044096 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.14165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0044096 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.14165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0044096 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.17921 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0042488 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.179 | north | 3 | N | N | Nnorth | Nnorth | 1 | -207.1065 | 0 | -0.0040468 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.179 | north | 3 | N | N | Nnorth | Nnorth | 1 | -207.2855 | 0 | -0.0040468 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.14231 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.9846 | 0 | -0.0037546 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.14231 | south | 5 | N | N | Nsouth | Nsouth | -1 | 4.1269 | 0 | -0.0037546 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.17721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -69.9976 | 395 | -0.0022528 | -0.88985
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.17721 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -77.0859 | 435 | -0.0022528 | -0.97996
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 16.4304 | 0 | -0.0019346 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 31.996 | 0 | -0.0019346 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 26.5192 | 0 | -0.0019346 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 32.2842 | 0 | -0.0019346 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 16.5745 | 0 | -0.0019346 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.1962 | 147 | -0.0018686 | -0.27469
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 19.8985 | 138 | -0.0018686 | -0.25787
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 20.1869 | 140 | -0.0018686 | -0.26161
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.1962 | 147 | -0.0018686 | -0.27469
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.2429 | 182 | -0.0018686 | -0.34009
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.14419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 28.55 | 198 | -0.0018686 | -0.36999
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.1758 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -12.8334 | 73 | -0.00084378 | -0.061596
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.1758 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -20.9202 | 119 | -0.00084378 | -0.10041
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.1758 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -36.039 | 205 | -0.00084378 | -0.17297
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.1758 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -17.9316 | 102 | -0.00084378 | -0.086065
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.1758 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -16.8768 | 96 | -0.00084378 | -0.081003
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.17558 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -76.376 | 435 | -0.00062078 | -0.27004
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.14629 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.58517 | 0 | 0.00023137 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.17416 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -10.4494 | 0 | 0.00080022 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.14697 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35272 | 0 | 0.00090737 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.14697 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35272 | 0 | 0.00090737 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 20.9532 | 142 | 0.0014974 | 0.21263
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 21.3959 | 145 | 0.0014974 | 0.21712
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 22.2813 | 151 | 0.0014974 | 0.2261
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.14756 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 42.7918 | 290 | 0.0014974 | 0.43424
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.14763 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.6574 | 0 | 0.0015714 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.14763 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.6574 | 0 | 0.0015714 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.14788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35491 | 0 | 0.0018194 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.14788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35491 | 0 | 0.0018194 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.14788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41406 | 0 | 0.0018194 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.17279 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -3.1102 | 18 | 0.0021652 | 0.038974
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.17279 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -3.1102 | 18 | 0.0021652 | 0.038974
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.17279 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -6.5661 | 38 | 0.0021652 | 0.082278
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.17095 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0040102 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.17095 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0040102 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.17095 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0040102 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 33.8288 | 223.9 | 0.0050284 | 1.1259
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 33.995 | 225 | 0.0050284 | 1.1314
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 33.9346 | 224.6 | 0.0050284 | 1.1294
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.15109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 34.2519 | 226.7 | 0.0050284 | 1.1399
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.16992 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -20.3909 | 0 | 0.0050322 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.16976 | north | 5 | N | N | Nnorth | Nnorth | 1 | -2.0372 | 0 | 0.0051932 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.16976 | north | 5 | N | N | Nnorth | Nnorth | 1 | -2.0372 | 0 | 0.0051932 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.16913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -48.7103 | 288 | 0.0058232 | 1.6771
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.16913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -24.8626 | 147 | 0.0058232 | 0.85601
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.16913 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -24.8626 | 147 | 0.0058232 | 0.85601
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.16884 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -34.4442 | 204 | 0.0061122 | 1.2469
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.16884 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -33.9376 | 201 | 0.0061122 | 1.2286
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.16884 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -40.8602 | 242 | 0.0061122 | 1.4792
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.15279 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.91673 | 0 | 0.0067284 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.16635 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -40.256 | 242 | 0.0086092 | 2.0834
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.16609 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -60.7871 | 366 | 0.0088712 | 3.2469
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.15496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 67.0977 | 0 | 0.0088994 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.15506 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 90.5539 | 0 | 0.0089974 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.15506 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 92.2595 | 0 | 0.0089974 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.3161 | 20 | 0.0091502 | 0.183
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.3161 | 20 | 0.0091502 | 0.183
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.3161 | 20 | 0.0091502 | 0.183
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.16581 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.8187 | 17 | 0.0091502 | 0.15555
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7984 | 50 | 0.0099084 | 0.49542
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7984 | 50 | 0.0099084 | 0.49542
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7984 | 50 | 0.0099084 | 0.49542
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.15597 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7984 | 50 | 0.0099084 | 0.49542
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.16358 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -18.4023 | 0 | 0.01138 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.1627 | west | 4 | Y | N | Ywest | Nwest | 1 | -105.7062 | 0 | 0.012256 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.16192 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.7166 | 0 | 0.013037 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.16159 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -9.6952 | 60 | 0.013369 | 0.80215
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.16159 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -10.18 | 63 | 0.013369 | 0.84226
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.1606 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.9025 | 0 | 0.014352 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.1606 | west | 6 | Y | N | Ywest | Nwest | 1 | -64.2384 | 0 | 0.01436 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.16205 | south | 5 | N | N | Nsouth | Nsouth | -1 | 5.6716 | 0 | 0.015986 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.16205 | south | 5 | N | N | Nsouth | Nsouth | -1 | 5.5096 | 0 | 0.015986 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.16205 | south | 5 | N | N | Nsouth | Nsouth | -1 | 5.6716 | 0 | 0.015986 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.1586 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.5157 | 0 | 0.016361 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.15699 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.548 | 0 | 0.017969 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.15692 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -18.5169 | 118 | 0.018033 | 2.1279
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.15692 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -18.0461 | 115 | 0.018033 | 2.0738
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.15692 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -87.2492 | 556 | 0.018033 | 10.0265
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.7478 | 0 | 0.018268 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.821 | 0 | 0.018268 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 1 | -39.0153 | 0 | 0.018268 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.15669 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.8675 | 0 | 0.018268 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.8698 | 0 | 0.018427 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.8269 | 0 | 0.018427 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.1314 | 0 | 0.018427 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.627 | 0 | 0.018427 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.4355 | 0 | 0.018427 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.15653 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.6006 | 0 | 0.018427 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.15599 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.3989 | 0 | 0.018963 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.15599 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.7553 | 0 | 0.018963 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.4883 | 0 | 0.01905 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.15591 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.4883 | 0 | 0.01905 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.15563 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.0726 | 0 | 0.01933 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.16541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 21.8343 | 132 | 0.01935 | 2.5542
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.16541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 22.1651 | 134 | 0.01935 | 2.5929
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.16541 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 53.4278 | 323 | 0.01935 | 6.2502
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.15532 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.3763 | 0 | 0.01964 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.15532 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.4743 | 0 | 0.01964 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.15532 | west | 7 | N | N | Nwest | Nwest | 1 | -3.8829 | 0 | 0.01964 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.15532 | west | 7 | N | N | Nwest | Nwest | 1 | -7.0979 | 0 | 0.01964 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.15532 | west | 7 | N | N | Nwest | Nwest | 1 | -7.0979 | 0 | 0.01964 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.15528 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.8946 | 0 | 0.019675 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.15528 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.6337 | 0 | 0.019675 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.15519 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.7768 | 0 | 0.019769 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.2347 | 66 | 0.019885 | 1.3124
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.6999 | 69 | 0.019885 | 1.3721
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.6999 | 69 | 0.019885 | 1.3721
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.3898 | 67 | 0.019885 | 1.3323
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.3898 | 67 | 0.019885 | 1.3323
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.15507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.0796 | 65 | 0.019885 | 1.2925
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.2167 | 0 | 0.020178 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.0512 | 0 | 0.020178 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.9556 | 0 | 0.020178 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.15478 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.8674 | 0 | 0.020178 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.15446 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.8037 | 0 | 0.020491 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.15446 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.8037 | 0 | 0.020491 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.15443 | west | 8 | N | N | Nwest | Nwest | 1 | -10.8102 | 0 | 0.020525 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.15443 | west | 8 | N | N | Nwest | Nwest | 1 | -11.3352 | 0 | 0.020525 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.15443 | west | 8 | N | N | Nwest | Nwest | 1 | -10.8719 | 0 | 0.020525 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.15435 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.729 | 0 | 0.020605 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.15435 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.020607 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.15434 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.5204 | 0 | 0.020619 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.15434 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.9605 | 0 | 0.020619 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.15434 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.2682 | 0 | 0.020619 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.15412 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.4942 | 0 | 0.020838 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.16693 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.3743 | 158 | 0.020865 | 3.2967
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.16693 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.7082 | 160 | 0.020865 | 3.3385
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.16693 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 29.2121 | 175 | 0.020865 | 3.6514
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.15407 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.4879 | 0 | 0.02089 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.1673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 25.5139 | 152.5 | 0.021243 | 3.2396
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.1673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 25.0119 | 149.5 | 0.021243 | 3.1759
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.1673 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 38.9149 | 232.6 | 0.021243 | 4.9412
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.15366 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.021297 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.15335 | west | 8 | N | N | Nwest | Nwest | 1 | -3.9565 | 0 | 0.021603 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.15327 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.8306 | 0 | 0.021685 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.153 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.3767 | 0 | 0.021954 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.15299 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.9492 | 0 | 0.021961 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.15298 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8727 | 0 | 0.021978 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.7032 | 70 | 0.022053 | 1.5437
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.7032 | 70 | 0.022053 | 1.5437
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -14.1894 | 92.8 | 0.022053 | 2.0465
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -12.2322 | 80 | 0.022053 | 1.7643
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -12.2322 | 80 | 0.022053 | 1.7643
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.1529 | west | 9 | Y | Y | Ywest | Ywest | 1 | -17.5838 | 115 | 0.022053 | 2.5361
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.2379 | 49 | 0.022059 | 1.0809
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7335 | 46 | 0.022059 | 1.0147
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.7335 | 46 | 0.022059 | 1.0147
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.9016 | 47 | 0.022059 | 1.0368
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.16812 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 25.8905 | 154 | 0.022059 | 3.3971
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.16812 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 24.8818 | 148 | 0.022059 | 3.2648
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.0698 | 48 | 0.022059 | 1.0588
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.16812 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.0698 | 48 | 0.022059 | 1.0588
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -31.83 | 208.2 | 0.022074 | 4.5959
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -21.7245 | 142.1 | 0.022074 | 3.1367
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -20.2416 | 132.4 | 0.022074 | 2.9226
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -20.792 | 136 | 0.022074 | 3.0021
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.4737 | 147 | 0.022074 | 3.2449
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.15288 | west | 9 | Y | Y | Ywest | Ywest | 1 | -32.1052 | 210 | 0.022074 | 4.6356
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.1618 | 0 | 0.022407 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.8061 | 0 | 0.022407 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.3741 | 0 | 0.022407 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.15255 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.7218 | 0 | 0.022407 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.16871 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3497 | 0 | 0.02265 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.16871 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3497 | 0 | 0.02265 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.15171 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.0013 | 0 | 0.02325 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.15171 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2035 | 0 | 0.02325 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.16942 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 52.5202 | 310 | 0.023359 | 7.2414
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.16942 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 69.9705 | 413 | 0.023359 | 9.6474
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.15122 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.5321 | 0 | 0.023734 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.15085 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2799 | 0 | 0.024103 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.15085 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5256 | 0 | 0.024103 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.15082 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.5642 | 0 | 0.024135 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.15079 | north | 5 | N | N | Nnorth | Nnorth | 1 | -6.0317 | 0 | 0.024164 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.15079 | north | 5 | N | N | Nnorth | Nnorth | 1 | -6.0317 | 0 | 0.024164 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -9.9492 | 66 | 0.024211 | 1.5979
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -9.7984 | 65 | 0.024211 | 1.5737
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.0999 | 67 | 0.024211 | 1.6222
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.0999 | 67 | 0.024211 | 1.6222
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.15074 | west | 13 | Y | Y | Ywest | Ywest | 1 | -10.0999 | 67 | 0.024211 | 1.6222
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.15074 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.024211 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.15074 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.024211 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.15069 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.5347 | 196 | 0.024269 | 4.7568
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.15069 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -16.7263 | 111 | 0.024269 | 2.6939
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.1736 | 42 | 0.02474 | 1.0391
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.5152 | 44 | 0.02474 | 1.0886
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 7.5152 | 44 | 0.02474 | 1.0886
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.1708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 8.0276 | 47 | 0.02474 | 1.1628
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.14991 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -25.484 | 170 | 0.02505 | 4.2585
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.14991 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -77.9511 | 520 | 0.02505 | 13.0261
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.14888 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -55.0867 | 370 | 0.026073 | 9.6471
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -20.8436 | 0 | 0.026073 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -20.9925 | 0 | 0.026073 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -46.0048 | 0 | 0.026073 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -21.2903 | 0 | 0.026073 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -21.4392 | 0 | 0.026073 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.14888 | north | 1 | N | N | Nnorth | Nnorth | 1 | -46.1537 | 0 | 0.026073 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.14834 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.026615 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.14834 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.026615 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.7261 | 160 | 0.026668 | 4.2669
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.1329 | 156 | 0.026668 | 4.1602
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.0644 | 196 | 0.026668 | 5.227
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.1329 | 156 | 0.026668 | 4.1602
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.2812 | 157 | 0.026668 | 4.1869
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.14829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.361 | 198 | 0.026668 | 5.2803
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.14775 | north | 8 | N | N | Nnorth | Nnorth | 1 | -11.0812 | 0 | 0.027207 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.14775 | north | 8 | N | N | Nnorth | Nnorth | 1 | -11.7608 | 0 | 0.027207 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.14775 | north | 8 | N | N | Nnorth | Nnorth | 1 | -13.061 | 0 | 0.027207 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.14733 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -82.2074 | 0 | 0.027631 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.14733 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -85.3012 | 0 | 0.027631 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.14733 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -119.0386 | 0 | 0.027631 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.1467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -11.589 | 79 | 0.02826 | 2.2326
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.1467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -15.5498 | 106 | 0.02826 | 2.9956
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.1467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -21.4176 | 146 | 0.02826 | 4.126
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.1467 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -11.1489 | 76 | 0.02826 | 2.1478
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.14654 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.8618 | 40 | 0.028412 | 1.1365
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.14605 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -56.6678 | 388 | 0.028905 | 11.2152
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.14605 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -75.2163 | 515 | 0.028905 | 14.8862
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.14571 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.6427 | 25 | 0.029249 | 0.73123
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.14571 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.974 | 41 | 0.029249 | 1.1992
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.14571 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.9141 | 20 | 0.029251 | 0.58502
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.14288 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.68582 | 0 | 0.032076 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.6474 | 161 | 0.034289 | 5.5206
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.0694 | 164 | 0.034289 | 5.6234
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -23.0694 | 164 | 0.034289 | 5.6234
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -58.2361 | 414 | 0.034289 | 14.1957
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.7881 | 162 | 0.034289 | 5.5549
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.6474 | 161 | 0.034289 | 5.5206
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.9287 | 163 | 0.034289 | 5.5891
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.14067 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -57.5328 | 409 | 0.034289 | 14.0243
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13963 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1701 | 0 | 0.03533 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13963 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1701 | 0 | 0.03533 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.13875 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.4062 | 0 | 0.036207 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13875 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.0999 | 0 | 0.036207 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.13875 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.55 | 0 | 0.036207 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13856 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.0846 | 0 | 0.036398 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.13853 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.0826 | 0 | 0.036423 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.13842 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7631 | 0 | 0.036535 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.13842 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7631 | 0 | 0.036535 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.13404 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.7231 | 0 | 0.040917 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.1333 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.1972 | 0 | 0.041659 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.13256 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1351 | 0 | 0.042395 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.1944 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 110.6119 | 0 | 0.048336 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.1944 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 112.9447 | 0 | 0.048336 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.12113 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -27.1338 | 224 | 0.053823 | 12.0564
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.11696 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -91.8175 | 0 | 0.057991 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.11696 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -92.9872 | 0 | 0.057991 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.11696 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -91.2327 | 0 | 0.057991 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | 1 | -16.8206 | 0 | 0.061303 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | 1 | -14.7749 | 0 | 0.061303 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | 1 | -16.4797 | 0 | 0.061303 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.11365 | north | 1 | N | N | Nnorth | Nnorth | 1 | -45.3475 | 0 | 0.061303 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.11044 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.064515 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.11016 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -5.508 | 0 | 0.064797 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.10898 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.065971 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.10854 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -19.7543 | 182 | 0.066416 | 12.0878
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.10854 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -52.5334 | 484 | 0.066416 | 32.1455
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.088265 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.2398 | 0 | 0.086691 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.07728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.7079 | 151.5 | 0.097676 | 14.7979
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.07728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.7697 | 152.3 | 0.097676 | 14.8761
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.07728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -13.7172 | 177.5 | 0.097676 | 17.3375
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.076294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.4975 | 150.7 | 0.098662 | 14.8684
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.076294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.5204 | 151 | 0.098662 | 14.898
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.076294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -13.5346 | 177.4 | 0.098662 | 17.5027
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.068161 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -41.919 | 0 | 0.1068 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.068161 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -40.0105 | 0 | 0.1068 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17496 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17496 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.00797 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.5912 | 0 | 0.18293 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.00797 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.5274 | 0 | 0.18293 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.4312 | 0 | 0.19067 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.4312 | 0 | 0.19067 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.3925 | 0 | 0.19067 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.015709 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4035 | 0 | 0.19067 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.039436 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 18.2589 | 0 | 0.21439 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21917 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21917 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.044217 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.75169 | 17 | 0.21917 | 3.7259
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21917 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.044217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.21917 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.044289 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.4172 | 0 | 0.21925 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0099 | 0 | 0.22042 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0918 | 0 | 0.22042 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0918 | 0 | 0.22042 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.04546 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.2748 | 0 | 0.22042 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.046435 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.2289 | 48 | 0.22139 | 10.6268
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.046435 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.136 | 46 | 0.22139 | 10.184
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.046435 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8757 | 105 | 0.22139 | 23.2461
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.052633 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.22759 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.14413 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 14.4126 | 0 | 0.31908 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.23116 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.40611 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.23116 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.40611 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1334
| 65 | 1307
| 70 | 1280
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| Max | 1340
| Min | 994
| Avg | 1239.6