## test results
CRE test for: |  | 3409 LAKE_CRK 3414 TEMP_SS_ctg1 | [5 empty] | PASS
Line Rating: |  | 1239.6
Direction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3409 LAKE_CRK 3414 TEMP_SS_ctg1
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.14174
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.19162
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.12679
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.039595
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3409 LAKE_CRK 3414 TEMP_SS_ctg1
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.15292
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.18809
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.1274
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.036687
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3409 LAKE_CRK 3414 TEMP_SS_ctg1
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.32983
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.014335
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.17843
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.31903
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.15203
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.16348
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | -0.34454 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.34454 | 0.32983
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.16711
[6 empty] | Concentration |  | -0.48502 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.052044
[6 empty] | Concentration |  | -0.15105 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 78.0168
| Percent of line rating => | [6 empty] | 6.294% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -1.2211
[7 empty] | B1(N-S) | 0.00082662 | -0.40193 | -0.40275 | 0.00082662
[7 empty] | B2 (N-W) | 0.00089091 | -0.016614 | -0.017505 | 0.00089091
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.0012797 | -0.21915 | -0.21787 | -0.0012797
[7 empty] | B4 (S-W) | 2.4593e-05 | 0.38958 | 0.38956 | 2.4593e-05
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.0014051 | 0.18705 | 0.18564 | 0.0014051
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0021702 | -0.20179 | -0.19962 | -0.0021702
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | 0.1965%
Deployment Error Percent | [6 empty] | B2 | 0.2118%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -0.3042%
[7 empty] | B4 | 0.005845%
[7 empty] | B5 | 0.334%
[7 empty] | B6 | -0.5158%
[7 empty] | Max Abs Error | 0.5158% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | S-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3409 LAKE_CRK 3414 TEMP_SS_ctg1 C:3405 THOUSE__3412 TEMP_PEC | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3409 LAKE_CRK 3414 TEMP_SS_ctg1 C:3405 THOUSE__3412 TEMP_PEC
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.19712 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 50.2669
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.19712 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 29.3716
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.16262 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.4393
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.16262 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.4393
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.19712 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 30.1601
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.16628 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 24.9425
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.16628 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 13.3026
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14563 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 10.6308
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14563 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 17.3297
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14563 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 29.8537
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14563 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 14.8541
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14563 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 13.9803
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.14443 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.7332
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.14443 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.7332
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.1541 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 25.8896
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.1541 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 13.8695
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.14747 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.6545
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.14747 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.6545
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.14747 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 5.604
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14775 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 42.5523
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14775 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 21.7194
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14775 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 21.7194
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.14766 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 16.6115
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 5.8882
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 11.6287
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 15.6031
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 21.4911
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.1472 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 11.1871
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14858 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 8.9145
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14858 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 9.3602
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14702 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.9404
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14702 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.6755
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14702 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 6.0278
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.055301 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 25.6044
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 8.2175
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 8.093
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.342
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.342
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.342
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12451 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 14.1938
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12451 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 64.1211
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 8.5211
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.9084
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.9084
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.6502
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.6502
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 8.392
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12846 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 8.992
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12846 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 9.4287
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12846 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 9.0434
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 19.3246
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 28.3428
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12936 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 12.8067
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12936 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 7.891
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 18.2347
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12936 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 3.234
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12936 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.9118
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12936 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.9118
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 15.5189
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.12718 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 3.2813
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.12689 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 12.7526
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.128 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 15.3604
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.12687 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 7.3586
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 27.243
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12976 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 19.4644
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12526 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.82675
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12526 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 4.2966
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12976 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 13.1061
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.12806 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 15.367
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.14245 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 52.136
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.1416 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 34.2672
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.1357 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 54.2784
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.13571 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 32.0266
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.13732 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 22.6585
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14633 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 29.8505
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14633 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 29.4115
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14633 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 35.4109
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.8506
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.8506
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.8506
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 2.423
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.14426 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 17.3117
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.13912 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 8.3474
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14722 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 11.0416
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14722 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 11.7188
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14722 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 13.0143
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 23.572
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.9827
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 28.8757
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.9827
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 23.13
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 29.1703
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14752 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 25.0782
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14752 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 76.7099
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14742 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 54.5458
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14718 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 82.1281
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14718 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 85.219
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14718 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 118.9239
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.15014 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 16.8158
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.15014 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 15.0141
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.15014 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 56.7533
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.15071 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 32.7482
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.15071 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 30.8945
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.15071 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 41.052
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.15118 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 116.4094
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 10.5383
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 10.3877
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 10.3877
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 10.2372
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.15004 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 173.6009
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.15004 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 173.751
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 35.8832
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 36.2036
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.16064 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 34.7621
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.16064 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 34.7139
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 33.9609
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 33.8007
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.15327 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 60.5436
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.15298 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 66.5476
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.15327 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 66.6746
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.14828 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 20.4631
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14982 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 17.6791
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14982 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 17.2296
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14982 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 83.3016
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14726 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 57.1373
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14726 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 75.8394
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.14148 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 111.0642
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.14148 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 112.479
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.14148 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 110.3567
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13933 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 25.3582
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13933 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 67.4362
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.14319 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 32.075
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.14009 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 7.0043
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.14013 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 5.8853
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.13309 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 81.8473
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.13309 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 78.1209
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.24375 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 130.8927
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.24375 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 191.8297
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.17421 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 13.0657
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.17421 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 38.6746
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.28628 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -162.895
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18271 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -38.1853
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18271 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -39.4643
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.18262 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -74.328
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -8.4044
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -8.5871
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -8.4044
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -8.4044
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.18305 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -77.6132
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.18305 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -77.7963
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.1816 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -10.5325
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.1816 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -16.162
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -7.9902
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -7.9902
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -7.8086
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -8.1718
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.18291 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -75.361
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.18291 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -73.166
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.18132 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -99.0002
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.18132 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -135.9892
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.18358 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -11.1983
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.18358 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -17.4399
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.18358 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -27.7203
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.18226 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -28.2495
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.18226 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -30.9834
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.18226 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -28.2495
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.14614 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -3.2151
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.14614 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.6076
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.14614 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.6076
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -7.0362
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -5.5021
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -6.7855
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -7.0805
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.15435 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.8522
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.15435 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -1.6979
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.16151 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.8762
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.16151 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.8762
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.16151 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -3.7147
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.17135 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -67.8534
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.092891 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -123.8237
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.092891 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -123.3592
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.15183 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -5.7695
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.15183 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -2.9303
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.15183 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -2.2774
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.15183 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -7.136
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11169 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 8.3771
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.13116 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 19.6737
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.12385 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 20.9929
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.056787 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 8.5181
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.12921 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 8.1405
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.13854 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 90.0088
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14762 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.9048
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14762 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.9048
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.20514 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -86.5699
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.23004 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -30.3649
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.23004 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -30.825
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.23004 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -74.302
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.23264 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -36.7578
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.23264 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -37.223
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.23264 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -40.7127
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.20677 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -120.7554
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.20677 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -123.0299
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.20656 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -89.4422
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -45.2403
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -45.4626
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -45.3818
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -45.8061
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.23938 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.9151
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.23938 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.9151
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.20337 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.6606
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.20337 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.6606
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.20337 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -3.0505
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.20051 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -2.747
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.21311 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.836
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.21311 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.836
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.23118 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -8.0913
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.23118 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -7.8601
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.23118 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -8.0913
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.20669 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -5.7873
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.20669 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -5.994
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12462 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 4.3617
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12462 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.7386
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.4507
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.4507
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.4507
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.4507
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.20713 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -1.2428
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.19548 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.46914
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.19548 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.46914
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.19548 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.54733
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.19262 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.77047
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.19277 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.46264
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.19277 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.46264
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -27.5943
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -25.9048
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -26.2802
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -27.5943
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -34.1643
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -37.1678
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.2343 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -35.7312
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.2343 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -35.0283
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.2343 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -54.4989
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -27.6474
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -28.2315
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -29.3997
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -56.463
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.087145 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -2.8758
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.087145 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -2.1786
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.15435 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.8522
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.14783 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -10.7917
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -10.8917
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -11.1675
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -4.0083
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -1.0021
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -10.8917
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -11.0296
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -10.809
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -3.4468
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -6.342
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.15682 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -98.641
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.14954 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -21.5332
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.14954 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -28.1128
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.18085 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -2.1702
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.11027 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.6616
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.15017 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -50.4571
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.15052 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -50.2747
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.15052 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -51.1778
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.15074 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -5.7282
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.15058 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.7645
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.15058 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.7645
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.15073 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -5.7278
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.15148 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -4.3929
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.15019 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -22.2729
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.15019 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -22.3179
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.15019 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -22.9788
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -23.4753
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -22.7324
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -14.8578
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -21.5438
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -21.841
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -18.8694
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.15244 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -22.3323
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.15244 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -22.5457
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.15244 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -26.3719
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -31.4913
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -32.967
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -36.8159
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -21.9063
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -21.9063
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -26.0137
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.24041 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -74.5262
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.24041 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -99.2881
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -10.2059
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -10.6919
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -10.6919
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -11.4209
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -11.6477
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.9346
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.9346
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -11.1723
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23771 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -36.607
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23771 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -35.1808
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -11.41
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -11.41
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.8773
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.8773
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 11.7687
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 10.1454
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 10.1454
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 14.5841
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 26.3989
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 18.0177
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 16.7878
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 17.2443
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 18.639
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 26.6272
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 27.394
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 16.5806
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 32.6369
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 25.8212
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 25.7662
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 15.7045
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.12501 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 18.6268
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12845 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 23.1212
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12845 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 23.1212
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.12833 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 28.8742
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.13011 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 16.2643
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.13011 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 16.2643
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 20.6389
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 20.7864
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 45.5531
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 21.0812
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 21.2286
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 45.7005
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14915 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 29.2328
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14915 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 16.5553
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.14838 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 23.5248
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 23.9632
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 23.9632
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 60.4924
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 23.671
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 23.5248
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 23.8171
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 59.7619
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14781 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14781 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 20.8559
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 18.3193
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 20.4331
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 56.2263
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.13454 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 20.2746
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.13454 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 20.3149
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.13454 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 23.8667
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.13472 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 20.4102
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.13472 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 20.518
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.13472 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 23.913
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.28628 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -166.3304
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 80.9155
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 80.9155
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.04587 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 1.4678
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.041643 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 1.9989
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.041643 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 1.9156
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.55144
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 2.3436
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.045953 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.7812
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 1.011
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 1.1488
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.041643 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 4.3725
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.1297 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 10.8944
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.11146 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 8.9172
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.11135 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.7019
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.11135 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.7019
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -2.9583
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -2.787
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -2.2146
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -6.4013
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -6.4138
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -6.3637
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -4.0113
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -10.1953
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.6714
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -4.1942
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -3.8848
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -4.2946
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -4.2653
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.041815 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -1.3381
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.041815 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -1.2545
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -6.9099
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -6.9099
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -7.4079
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -6.8165
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 14.4134
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 14.4796
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.029329 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -3.9887
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.048601 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -1.6038
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.2288
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.2288
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.1117
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.1117
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.065532 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -4.6528
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.065532 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.65532
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.049846 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -8.1249
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.049846 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -8.1249
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.049846 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -12.2123
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.2086
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -2.0387
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.2086
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.2086
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.030946 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -4.611
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.030946 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -2.0146
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -3.1753
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -3.0566
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -3.0357
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -1.9017
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.42569
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.025449 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -18.9086
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.026994 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -19.8406
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.024984 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.2972
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.024984 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.2972
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.024984 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.2972
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -2.8396
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.029022 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -5.0208
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.029022 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -3.918
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -3.8896
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -3.8562
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -3.7964
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -6.4317
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -1.974
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -1.9493
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -2.5477
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -2.2701
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -5.1919
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -4.9978
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -5.0105
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -4.9946
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -8.5577
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.025531 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.12765
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.025531 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.53615
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 6.7867
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 6.8659
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 6.8659
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 16.7246
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.023514 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -9.3586
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.5005
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.5005
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.5005
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.7941
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.7941
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -1.7615
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.11162 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 92.3097
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.11162 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 91.4168
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.050375 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -2.3223
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -7.0115
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -7.0115
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -9.687
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.827
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.827
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -9.4102
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.030816 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -5.5469
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.030816 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -4.8874
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.030816 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -4.8381
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.031433 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -1.1002
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.037224 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -17.0858
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -1.6589
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -1.6844
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -1.7865
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -1.6078
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -1.5823
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -2.6542
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -1.5057
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -2.5606
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.5278
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.5278
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016414 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -2.6591
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.025168 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -3.9514
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -2.1471
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -2.1774
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -1.1794
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.90723
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.032281 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -2.5179
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.032281 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -2.5825
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.030852 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.4998
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.03097 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -5.1101
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.031003 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -5.2395
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.030862 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -6.5736
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.03083 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -7.0292
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.031026 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.37231
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.031026 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.55847
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.039222 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -1.9611
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.8659
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.8659
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4881
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.4605
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4881
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -1.5707
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4881
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4881
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5983
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5983
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.026139 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.31367
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2795
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.3481
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2795
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2795
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.3481
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2795
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.086821 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -5.7302
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.048066 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -7.7386
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.048066 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -7.979
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.048066 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -11.9204
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.048066 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -26.244
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.048066 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -30.9064
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.049946 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -32.5148
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.049946 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -28.1695
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.049946 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -29.9676
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.048066 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.62486
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.025492 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.3059
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.90505
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.92368
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.87044
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -1.2218
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.47116
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.54303
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.52972
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.93166
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.47914
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -2.2733
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -3.9396
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -4.3204
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -4.9754
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -3.1358
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -7.0381
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -5.9928
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -6.1322
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -3.4842
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -1.2543
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -6.5503
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -4.8779
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -4.3901
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -5.0172
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -4.5155
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -7.0381
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -6.7593
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -7.1775
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -5.296
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.5747
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.5747
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -11.916
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3412
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.10587 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 8.0988
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11169 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 8.9355
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11169 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 4.4678
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11263 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 9.0102
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.11149 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 8.9194
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.10668 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 8.5346
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.10511 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 8.8291
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11263 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 9.0102
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -21.835
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12786 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 15.3428
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12786 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 29.7907
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12786 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 21.7613
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -42.5208
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -35.2424
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -42.9038
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -22.0265
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -19.1535
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.13303 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.982
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.10079 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.080025 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.11611 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.55732
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.9041
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 14.0583
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 17.6546
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 15.5622
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 13.7314
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 10.5274
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 18.9648
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 14.1591
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 18.8159
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 23.4098
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 26.9968
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.15183 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.11564 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.16031 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -3.8604
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -6.0111
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -10.2024
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -14.2621
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -6.2207
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -5.7655
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -2.8828
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -14.2621
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -5.4621
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -6.5241
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -3.3379
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.583
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.1473
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -1.0021
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.1473
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.583
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.583
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -22.4552
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.5862
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -8.3448
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.5862
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14858 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -1.7829
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.14485 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -2.1727
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.14485 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -3.3315
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.13911 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -6.6775
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.14375 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -1.15
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.15022 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -27.0392
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.15017 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -27.0306
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.15052 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -27.0941
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.15052 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -27.0941
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.16032 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -16.032
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.16032 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -16.032
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.7302
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.7302
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.7302
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -2.3873
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.7302
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.7302
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.7302
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -2.2381
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.16032 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.16032 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -80.16
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.16032 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -80.16
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.16032 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.15896 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.087145 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.15618 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.15437 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:3409 LAKE_CRK 3414 TEMP_SS_ctg1 C:3405 THOUSE__3412 TEMP_PEC | [7 empty] | 78.0168
Number of Bus | Name of Bus | ID | Max MW | L:3409 LAKE_CRK 3414 TEMP_SS_ctg1 C:3405 THOUSE__3412 TEMP_PEC | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.19712 | north | Y | 0.055386 | 0.38875 | 0.070331 | 0.23672 | 0.055386 | North | N | 0.055386 | 0
239 | BOSQUESW | 1 | 149 | 0.19712 | north | Y | 0.055386 | 0.38875 | 0.070331 | 0.23672 | 0.055386 | North | N | 0.055386 | 0
244 | WHITNYDM | 1 | 15 | 0.16262 | north | N | 0.020884 | 0.35425 | 0.035829 | 0.20222 | 0.020884 | North | N | 0.020884 | 0
245 | WHITNYDM | 2 | 15 | 0.16262 | north | N | 0.020884 | 0.35425 | 0.035829 | 0.20222 | 0.020884 | North | N | 0.020884 | 0
247 | BOSQUESW | 2 | 153 | 0.19712 | north | Y | 0.055386 | 0.38875 | 0.070331 | 0.23672 | 0.055386 | North | N | 0.055386 | 0
251 | BOSQUESW | 2 | 150 | 0.16628 | north | Y | 0.024544 | 0.35791 | 0.039489 | 0.20588 | 0.024544 | North | N | 0.024544 | 0
253 | BOSQUESW | 2 | 80 | 0.16628 | north | Y | 0.024544 | 0.35791 | 0.039489 | 0.20588 | 0.024544 | North | N | 0.024544 | 0
332 | RWMILLER | 1 | 73 | 0.14563 | north | Y | 0.0038891 | 0.33725 | 0.018834 | 0.18522 | 0.0038891 | North | N | 0.0038891 | 0
333 | RWMILLER | 2 | 119 | 0.14563 | north | Y | 0.0038891 | 0.33725 | 0.018834 | 0.18522 | 0.0038891 | North | N | 0.0038891 | 0
334 | RWMILLER | 3 | 205 | 0.14563 | north | Y | 0.0038891 | 0.33725 | 0.018834 | 0.18522 | 0.0038891 | North | N | 0.0038891 | 0
335 | RWMILLER | 4 | 102 | 0.14563 | north | Y | 0.0038891 | 0.33725 | 0.018834 | 0.18522 | 0.0038891 | North | N | 0.0038891 | 0
336 | RWMILLER | 5 | 96 | 0.14563 | north | Y | 0.0038891 | 0.33725 | 0.018834 | 0.18522 | 0.0038891 | North | N | 0.0038891 | 0
344 | MRSSHPRD | 1 | 12 | 0.14443 | north | N | 0.0026921 | 0.33606 | 0.017637 | 0.18403 | 0.0026921 | North | N | 0.0026921 | 0
345 | MRSSHPRD | 2 | 12 | 0.14443 | north | N | 0.0026921 | 0.33606 | 0.017637 | 0.18403 | 0.0026921 | North | N | 0.0026921 | 0
366 | JNSNCNTY | 1 | 168 | 0.1541 | north | Y | 0.012366 | 0.34573 | 0.027311 | 0.1937 | 0.012366 | North | N | 0.012366 | 0
367 | JNSNCNTY | 2 | 90 | 0.1541 | north | Y | 0.012366 | 0.34573 | 0.027311 | 0.1937 | 0.012366 | North | N | 0.012366 | 0
503 | NTHTEXAS | 1 | 18 | 0.14747 | north | Y | 0.0057351 | 0.3391 | 0.02068 | 0.18707 | 0.0057351 | North | N | 0.0057351 | 0
504 | NTHTEXAS | 2 | 18 | 0.14747 | north | Y | 0.0057351 | 0.3391 | 0.02068 | 0.18707 | 0.0057351 | North | N | 0.0057351 | 0
505 | NTHTEXAS | 3 | 38 | 0.14747 | north | Y | 0.0057351 | 0.3391 | 0.02068 | 0.18707 | 0.0057351 | North | N | 0.0057351 | 0
580 | JCKCNTY8 | 1 | 288 | 0.14775 | north | Y | 0.0060121 | 0.33938 | 0.020957 | 0.18735 | 0.0060121 | North | N | 0.0060121 | 0
581 | JCKCNTY8 | 2 | 147 | 0.14775 | north | Y | 0.0060121 | 0.33938 | 0.020957 | 0.18735 | 0.0060121 | North | N | 0.0060121 | 0
582 | JCKCNTY8 | 3 | 147 | 0.14775 | north | Y | 0.0060121 | 0.33938 | 0.020957 | 0.18735 | 0.0060121 | North | N | 0.0060121 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.14766 | north | Y | 0.0059191 | 0.33928 | 0.020864 | 0.18725 | 0.0059191 | North | N | 0.0059191 | 0
837 | NEWMAN_G | 1 | 40 | 0.1472 | north | Y | 0.0054651 | 0.33883 | 0.02041 | 0.1868 | 0.0054651 | North | N | 0.0054651 | 0
842 | OLINGER_ | 1 | 79 | 0.1472 | north | Y | 0.0054601 | 0.33882 | 0.020405 | 0.18679 | 0.0054601 | North | N | 0.0054601 | 0
843 | OLINGER_ | 1 | 106 | 0.1472 | north | Y | 0.0054601 | 0.33882 | 0.020405 | 0.18679 | 0.0054601 | North | N | 0.0054601 | 0
844 | OLINGER_ | 1 | 146 | 0.1472 | north | Y | 0.0054601 | 0.33882 | 0.020405 | 0.18679 | 0.0054601 | North | N | 0.0054601 | 0
845 | OLINGER_ | 1 | 76 | 0.1472 | north | Y | 0.0054601 | 0.33882 | 0.020405 | 0.18679 | 0.0054601 | North | N | 0.0054601 | 0
923 | SPENCER_ | 1 | 60 | 0.14858 | north | Y | 0.0068361 | 0.3402 | 0.021781 | 0.18817 | 0.0068361 | North | N | 0.0068361 | 0
924 | SPENCER_ | 1 | 63 | 0.14858 | north | Y | 0.0068361 | 0.3402 | 0.021781 | 0.18817 | 0.0068361 | North | N | 0.0068361 | 0
948 | STEAM1 | 1 | 20 | 0.14702 | north | Y | 0.0052801 | 0.33864 | 0.020225 | 0.18661 | 0.0052801 | North | N | 0.0052801 | 0
949 | STEAM2 | 1 | 25 | 0.14702 | north | Y | 0.0052801 | 0.33864 | 0.020225 | 0.18661 | 0.0052801 | North | N | 0.0052801 | 0
950 | STEAM3 | 1 | 41 | 0.14702 | north | Y | 0.0052801 | 0.33864 | 0.020225 | 0.18661 | 0.0052801 | North | N | 0.0052801 | 0
990 | GIBN_CRE | 1 | 463 | 0.055301 | north | Y | -0.086438 | 0.24693 | -0.071493 | 0.094896 | 0.071493 | west | Y | 0.086438 | 6.9193
1002 | PBCTAGE_ | A | 66 | 0.12451 | west | Y | -0.017232 | 0.31613 | -0.0022874 | 0.1641 | 0.0022874 | west | N | 0.0022874 | 0
1003 | PBCTBGE_ | B | 65 | 0.12451 | west | Y | -0.017232 | 0.31613 | -0.0022874 | 0.1641 | 0.0022874 | west | N | 0.0022874 | 0
1004 | PBCTCGE_ | C | 67 | 0.12451 | west | Y | -0.017232 | 0.31613 | -0.0022874 | 0.1641 | 0.0022874 | west | N | 0.0022874 | 0
1005 | PBCTDGE_ | D | 67 | 0.12451 | west | Y | -0.017232 | 0.31613 | -0.0022874 | 0.1641 | 0.0022874 | west | N | 0.0022874 | 0
1006 | PBCTEGE_ | E | 67 | 0.12451 | west | Y | -0.017232 | 0.31613 | -0.0022874 | 0.1641 | 0.0022874 | west | N | 0.0022874 | 0
1007 | PB5GEN_6 | MB | 114 | 0.12451 | west | Y | -0.017232 | 0.31613 | -0.0022874 | 0.1641 | 0.0022874 | west | N | 0.0022874 | 0
1008 | PB6GEN_7 | MB | 515 | 0.12451 | west | Y | -0.017232 | 0.31613 | -0.0022874 | 0.1641 | 0.0022874 | west | N | 0.0022874 | 0
1039 | MRGNAG_1 | A | 66 | 0.12911 | west | Y | -0.012632 | 0.32073 | 0.0023126 | 0.1687 | 0.0023126 | west | N | 0.0023126 | 0
1040 | MRGNBG_2 | B | 69 | 0.12911 | west | Y | -0.012632 | 0.32073 | 0.0023126 | 0.1687 | 0.0023126 | west | N | 0.0023126 | 0
1041 | MRGNCG_3 | C | 69 | 0.12911 | west | Y | -0.012632 | 0.32073 | 0.0023126 | 0.1687 | 0.0023126 | west | N | 0.0023126 | 0
1042 | MRGNDG_4 | D | 67 | 0.12911 | west | Y | -0.012632 | 0.32073 | 0.0023126 | 0.1687 | 0.0023126 | west | N | 0.0023126 | 0
1043 | MRGNEG_5 | E | 67 | 0.12911 | west | Y | -0.012632 | 0.32073 | 0.0023126 | 0.1687 | 0.0023126 | west | N | 0.0023126 | 0
1044 | MRGNFG_6 | F | 65 | 0.12911 | west | Y | -0.012632 | 0.32073 | 0.0023126 | 0.1687 | 0.0023126 | west | N | 0.0023126 | 0
1045 | CALENG1G | 1 | 70 | 0.12846 | west | N | -0.013282 | 0.32008 | 0.0016626 | 0.16805 | 0.0016626 | west | N | 0.0016626 | 0
1046 | CALENG2G | 2 | 73.4 | 0.12846 | west | N | -0.013282 | 0.32008 | 0.0016626 | 0.16805 | 0.0016626 | west | N | 0.0016626 | 0
1047 | CALENG3G | 3 | 70.4 | 0.12846 | west | N | -0.013282 | 0.32008 | 0.0016626 | 0.16805 | 0.0016626 | west | N | 0.0016626 | 0
1058 | LONGSHOR | 1 | 150 | 0.12883 | west | Y | -0.012908 | 0.32046 | 0.0020366 | 0.16843 | 0.0020366 | west | N | 0.0020366 | 0
1058 | LONGSHOR | 2 | 220 | 0.12883 | west | Y | -0.012908 | 0.32046 | 0.0020366 | 0.16843 | 0.0020366 | west | N | 0.0020366 | 0
1061 | CIELOGEN | 1 | 99 | 0.12936 | west | Y | -0.012378 | 0.32099 | 0.0025666 | 0.16896 | 0.0025666 | west | N | 0.0025666 | 0
1062 | CIELOGEN | 1 | 61 | 0.12936 | west | Y | -0.012378 | 0.32099 | 0.0025666 | 0.16896 | 0.0025666 | west | N | 0.0025666 | 0
1068 | SCURRYCW | 1 | 141 | 0.12932 | west | Y | -0.012415 | 0.32095 | 0.0025296 | 0.16892 | 0.0025296 | west | N | 0.0025296 | 0
1069 | KINDERMG | 1 | 25 | 0.12936 | west | N | -0.012378 | 0.32099 | 0.0025666 | 0.16896 | 0.0025666 | west | N | 0.0025666 | 0
1070 | KINDERMG | 1 | 45.7 | 0.12936 | west | N | -0.012378 | 0.32099 | 0.0025666 | 0.16896 | 0.0025666 | west | N | 0.0025666 | 0
1071 | KINDERMG | 1 | 45.7 | 0.12936 | west | N | -0.012378 | 0.32099 | 0.0025666 | 0.16896 | 0.0025666 | west | N | 0.0025666 | 0
1073 | SCURRYCW | 2 | 120 | 0.12932 | west | Y | -0.012415 | 0.32095 | 0.0025296 | 0.16892 | 0.0025296 | west | N | 0.0025296 | 0
1320 | BSP 1 | 1 | 25.8 | 0.12718 | west | N | -0.014555 | 0.31881 | 0.00038957 | 0.16678 | 0.00038957 | west | N | 0.00038957 | 0
1326 | STANTONW | 1 | 100.5 | 0.12689 | west | Y | -0.014847 | 0.31852 | 9.7573e-05 | 0.16649 | 9.7573e-05 | west | N | 9.7573e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.128 | west | Y | -0.013736 | 0.31963 | 0.0012086 | 0.1676 | 0.0012086 | west | N | 0.0012086 | 0
1328 | OCOTILLO | 1 | 58 | 0.12687 | west | Y | -0.014867 | 0.3185 | 7.7573e-05 | 0.16647 | 7.7573e-05 | west | N | 7.7573e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.12718 | west | Y | -0.014554 | 0.31881 | 0.00039057 | 0.16678 | 0.00039057 | west | N | 0.00039057 | 0
1343 | TRENTIPP | 1 | 150 | 0.12976 | west | Y | -0.011976 | 0.32139 | 0.0029686 | 0.16936 | 0.0029686 | west | N | 0.0029686 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.12526 | west | Y | -0.016474 | 0.31689 | -0.0015294 | 0.16486 | 0.0015294 | west | N | 0.0015294 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.12526 | west | Y | -0.016474 | 0.31689 | -0.0015294 | 0.16486 | 0.0015294 | west | N | 0.0015294 | 0
1354 | AEPWIND_ | 1 | 101 | 0.12976 | west | Y | -0.011976 | 0.32139 | 0.0029686 | 0.16936 | 0.0029686 | west | N | 0.0029686 | 0
1360 | GUNSIGHT | 1 | 120 | 0.12806 | west | Y | -0.013681 | 0.31968 | 0.0012636 | 0.16765 | 0.0012636 | west | N | 0.0012636 | 0
1432 | GRHAMSES | 2 | 366 | 0.14245 | north | Y | 0.00070913 | 0.33407 | 0.015654 | 0.18204 | 0.00070913 | North | N | 0.00070913 | 0
1433 | GRHAMSES | 1 | 242 | 0.1416 | north | Y | -0.00013887 | 0.33322 | 0.014806 | 0.18119 | 0.00013887 | North | N | 0.00013887 | 0
1437 | MESQUITW | 1 | 400 | 0.1357 | west | Y | -0.0060429 | 0.32732 | 0.0089016 | 0.17529 | 0.0060429 | North | Y | 0.0089016 | 1.1435
1438 | MESQUITW | 1 | 236 | 0.13571 | west | Y | -0.0060329 | 0.32733 | 0.0089116 | 0.1753 | 0.0060329 | North | Y | 0.0089116 | 0.67937
1442 | COKFIELD | 1 | 165 | 0.13732 | west | Y | -0.0044149 | 0.32895 | 0.01053 | 0.17692 | 0.0044149 | North | Y | 0.01053 | 1.0089
1453 | WCPWRCO_ | 1 | 204 | 0.14633 | north | Y | 0.0045871 | 0.33795 | 0.019532 | 0.18592 | 0.0045871 | North | N | 0.0045871 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.14633 | north | Y | 0.0045871 | 0.33795 | 0.019532 | 0.18592 | 0.0045871 | North | N | 0.0045871 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.14633 | north | Y | 0.0045871 | 0.33795 | 0.019532 | 0.18592 | 0.0045871 | North | N | 0.0045871 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.14253 | west | Y | 0.00079313 | 0.33416 | 0.015738 | 0.18213 | 0.00079313 | North | Y | 0.015738 | 0.29889
1479 | WFCOGEN_ | 2 | 20 | 0.14253 | west | Y | 0.00079313 | 0.33416 | 0.015738 | 0.18213 | 0.00079313 | North | Y | 0.015738 | 0.29889
1482 | WFCOGEN_ | 1 | 20 | 0.14253 | west | Y | 0.00079313 | 0.33416 | 0.015738 | 0.18213 | 0.00079313 | North | Y | 0.015738 | 0.29889
1482 | WFCOGEN_ | 2 | 17 | 0.14253 | west | Y | 0.00079313 | 0.33416 | 0.015738 | 0.18213 | 0.00079313 | North | Y | 0.015738 | 0.25406
1600 | BARTNWND | 1 | 120 | 0.14426 | north | Y | 0.0025251 | 0.33589 | 0.01747 | 0.18386 | 0.0025251 | North | N | 0.0025251 | 0
1643 | SLSTR1PP | 1 | 60 | 0.13912 | north | Y | -0.0026159 | 0.33075 | 0.012329 | 0.17872 | 0.0026159 | North | N | 0.0026159 | 0
1675 | PEC_1G | 1 | 75 | 0.14722 | north | N | 0.0054821 | 0.33885 | 0.020427 | 0.18682 | 0.0054821 | North | N | 0.0054821 | 0
1676 | PEC_2G | 2 | 79.6 | 0.14722 | north | N | 0.0054821 | 0.33885 | 0.020427 | 0.18682 | 0.0054821 | North | N | 0.0054821 | 0
1677 | PEC_3G | 3 | 88.4 | 0.14722 | north | N | 0.0054821 | 0.33885 | 0.020427 | 0.18682 | 0.0054821 | North | N | 0.0054821 | 0
1678 | LAMARPWR | 1 | 160 | 0.14733 | north | Y | 0.0055861 | 0.33895 | 0.020531 | 0.18692 | 0.0055861 | North | N | 0.0055861 | 0
1679 | LAMARPWR | 2 | 156 | 0.14733 | north | Y | 0.0055861 | 0.33895 | 0.020531 | 0.18692 | 0.0055861 | North | N | 0.0055861 | 0
1680 | LAMARPWR | 3 | 196 | 0.14733 | north | Y | 0.0055861 | 0.33895 | 0.020531 | 0.18692 | 0.0055861 | North | N | 0.0055861 | 0
1681 | LAMARPWR | 4 | 156 | 0.14733 | north | Y | 0.0055861 | 0.33895 | 0.020531 | 0.18692 | 0.0055861 | North | N | 0.0055861 | 0
1682 | LAMARPWR | 5 | 157 | 0.14733 | north | Y | 0.0055861 | 0.33895 | 0.020531 | 0.18692 | 0.0055861 | North | N | 0.0055861 | 0
1683 | LAMARPWR | 6 | 198 | 0.14733 | north | Y | 0.0055861 | 0.33895 | 0.020531 | 0.18692 | 0.0055861 | North | N | 0.0055861 | 0
1687 | VALLEY_1 | 1 | 170 | 0.14752 | north | Y | 0.0057801 | 0.33914 | 0.020725 | 0.18711 | 0.0057801 | North | N | 0.0057801 | 0
1688 | VALLEY_2 | 2 | 520 | 0.14752 | north | Y | 0.0057801 | 0.33914 | 0.020725 | 0.18711 | 0.0057801 | North | N | 0.0057801 | 0
1689 | VALLEY_3 | 3 | 370 | 0.14742 | north | Y | 0.0056821 | 0.33905 | 0.020627 | 0.18702 | 0.0056821 | North | N | 0.0056821 | 0
1701 | MOSES_1G | 1 | 558 | 0.14718 | north | Y | 0.0054441 | 0.33881 | 0.020389 | 0.18678 | 0.0054441 | North | N | 0.0054441 | 0
1702 | MOSES_2G | 2 | 579 | 0.14718 | north | Y | 0.0054441 | 0.33881 | 0.020389 | 0.18678 | 0.0054441 | North | N | 0.0054441 | 0
1703 | MOSES_3G | 3 | 808 | 0.14718 | north | Y | 0.0054441 | 0.33881 | 0.020389 | 0.18678 | 0.0054441 | North | N | 0.0054441 | 0
1861 | EAGLEMNT | MB | 112 | 0.15014 | north | Y | 0.0084021 | 0.34177 | 0.023347 | 0.18974 | 0.0084021 | North | N | 0.0084021 | 0
1862 | EAGLEMNT | MB | 100 | 0.15014 | north | Y | 0.0084021 | 0.34177 | 0.023347 | 0.18974 | 0.0084021 | North | N | 0.0084021 | 0
1863 | EAGLEMNT | MB | 378 | 0.15014 | north | Y | 0.0084021 | 0.34177 | 0.023347 | 0.18974 | 0.0084021 | North | N | 0.0084021 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.15071 | north | Y | 0.0089661 | 0.34233 | 0.023911 | 0.1903 | 0.0089661 | North | N | 0.0089661 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.15071 | north | Y | 0.0089661 | 0.34233 | 0.023911 | 0.1903 | 0.0089661 | North | N | 0.0089661 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.15071 | north | Y | 0.0089661 | 0.34233 | 0.023911 | 0.1903 | 0.0089661 | North | N | 0.0089661 | 0
1889 | DECRDOVA | MB | 770 | 0.15118 | north | Y | 0.0094421 | 0.34281 | 0.024387 | 0.19078 | 0.0094421 | North | N | 0.0094421 | 0
1892 | DECRDOVA | A | 70 | 0.15055 | north | Y | 0.0088081 | 0.34217 | 0.023753 | 0.19014 | 0.0088081 | North | N | 0.0088081 | 0
1893 | DECRDOVA | B | 69 | 0.15055 | north | Y | 0.0088081 | 0.34217 | 0.023753 | 0.19014 | 0.0088081 | North | N | 0.0088081 | 0
1894 | DECRDOVA | C | 69 | 0.15055 | north | Y | 0.0088081 | 0.34217 | 0.023753 | 0.19014 | 0.0088081 | North | N | 0.0088081 | 0
1895 | DECRDOVA | D | 68 | 0.15055 | north | Y | 0.0088081 | 0.34217 | 0.023753 | 0.19014 | 0.0088081 | North | N | 0.0088081 | 0
1898 | COMCHEPK | 1 | 1157 | 0.15004 | north | N | 0.0083051 | 0.34167 | 0.02325 | 0.18964 | 0.0083051 | North | N | 0.0083051 | 0
1899 | COMCHEPK | 2 | 1158 | 0.15004 | north | N | 0.0083051 | 0.34167 | 0.02325 | 0.18964 | 0.0083051 | North | N | 0.0083051 | 0
1937 | MDLTHELP | 5 | 224 | 0.16019 | north | Y | 0.018454 | 0.35182 | 0.033399 | 0.19979 | 0.018454 | North | N | 0.018454 | 0
1938 | MDLTHELP | 6 | 226 | 0.16019 | north | Y | 0.018454 | 0.35182 | 0.033399 | 0.19979 | 0.018454 | North | N | 0.018454 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.16064 | north | Y | 0.018899 | 0.35226 | 0.033844 | 0.20023 | 0.018899 | North | N | 0.018899 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.16064 | north | Y | 0.018899 | 0.35226 | 0.033844 | 0.20023 | 0.018899 | North | N | 0.018899 | 0
1943 | MDLTHELP | 3 | 212 | 0.16019 | north | Y | 0.018454 | 0.35182 | 0.033399 | 0.19979 | 0.018454 | North | N | 0.018454 | 0
1944 | MDLTHELP | 4 | 211 | 0.16019 | north | Y | 0.018454 | 0.35182 | 0.033399 | 0.19979 | 0.018454 | North | N | 0.018454 | 0
1947 | HANDLEY_ | 3 | 395 | 0.15327 | north | Y | 0.011536 | 0.3449 | 0.026481 | 0.19287 | 0.011536 | North | N | 0.011536 | 0
1948 | HANDLEY_ | 4 | 435 | 0.15298 | north | Y | 0.011244 | 0.34461 | 0.026189 | 0.19258 | 0.011244 | North | N | 0.011244 | 0
1949 | HANDLEY_ | 5 | 435 | 0.15327 | north | Y | 0.011536 | 0.3449 | 0.026481 | 0.19287 | 0.011536 | North | N | 0.011536 | 0
2371 | COLLIN_1 | MB | 138 | 0.14828 | north | Y | 0.0065441 | 0.33991 | 0.021489 | 0.18788 | 0.0065441 | North | N | 0.0065441 | 0
2413 | MTCK6_G | 6 | 118 | 0.14982 | north | Y | 0.0080841 | 0.34145 | 0.023029 | 0.18942 | 0.0080841 | North | N | 0.0080841 | 0
2414 | MTCK7_G | 7 | 115 | 0.14982 | north | Y | 0.0080841 | 0.34145 | 0.023029 | 0.18942 | 0.0080841 | North | N | 0.0080841 | 0
2417 | MTCK8_G | 8 | 556 | 0.14982 | north | Y | 0.0080841 | 0.34145 | 0.023029 | 0.18942 | 0.0080841 | North | N | 0.0080841 | 0
2451 | LKHB1_G | 1 | 388 | 0.14726 | north | Y | 0.0055221 | 0.33889 | 0.020467 | 0.18686 | 0.0055221 | North | N | 0.0055221 | 0
2452 | LKHB2_G | 2 | 515 | 0.14726 | north | Y | 0.0055221 | 0.33889 | 0.020467 | 0.18686 | 0.0055221 | North | N | 0.0055221 | 0
3097 | MARTLAKE | 1 | 785 | 0.14148 | north | Y | -0.00025587 | 0.33311 | 0.014689 | 0.18108 | 0.00025587 | North | N | 0.00025587 | 0
3098 | MARTLAKE | 2 | 795 | 0.14148 | north | Y | -0.00025587 | 0.33311 | 0.014689 | 0.18108 | 0.00025587 | North | N | 0.00025587 | 0
3099 | MARTLAKE | 3 | 780 | 0.14148 | north | Y | -0.00025587 | 0.33311 | 0.014689 | 0.18108 | 0.00025587 | North | N | 0.00025587 | 0
3107 | STRYKER_ | 1 | 182 | 0.13933 | north | Y | -0.0024079 | 0.33096 | 0.012537 | 0.17893 | 0.0024079 | North | N | 0.0024079 | 0
3108 | STRYKER_ | 2 | 484 | 0.13933 | north | Y | -0.0024079 | 0.33096 | 0.012537 | 0.17893 | 0.0024079 | North | N | 0.0024079 | 0
3126 | TRINIDAD | 1 | 224 | 0.14319 | north | Y | 0.0014531 | 0.33482 | 0.016398 | 0.18279 | 0.0014531 | North | N | 0.0014531 | 0
3309 | ASPN_G | 1 | 50 | 0.14009 | north | Y | -0.0016529 | 0.33171 | 0.013292 | 0.17968 | 0.0016529 | North | N | 0.0016529 | 0
3348 | CHAMPION | MB | 42 | 0.14013 | north | N | -0.0016129 | 0.33175 | 0.013332 | 0.17972 | 0.0016129 | North | N | 0.0016129 | 0
3381 | BBRN_1G | 1 | 615 | 0.13309 | north | Y | -0.0086539 | 0.32471 | 0.0062906 | 0.17268 | 0.0062906 | west | Y | 0.0086539 | 1.4534
3382 | BBRN_2G | 2 | 587 | 0.13309 | north | Y | -0.0086539 | 0.32471 | 0.0062906 | 0.17268 | 0.0062906 | west | Y | 0.0086539 | 1.3873
3403 | THOUSE_1 | MB | 537 | 0.24375 | north | Y | 0.10201 | 0.43537 | 0.11695 | 0.28334 | 0.10201 | North | N | 0.10201 | 0
3404 | THOUSE_2 | 2 | 787 | 0.24375 | north | Y | 0.10201 | 0.43537 | 0.11695 | 0.28334 | 0.10201 | North | N | 0.10201 | 0
3416 | LAKE_CRK | MB | 75 | 0.17421 | north | Y | 0.032471 | 0.36583 | 0.047416 | 0.2138 | 0.032471 | North | N | 0.032471 | 0
3417 | LAKE_CRK | MB | 222 | 0.17421 | north | Y | 0.032471 | 0.36583 | 0.047416 | 0.2138 | 0.032471 | North | N | 0.032471 | 0
3432 | SANDOW_4 | 4 | 569 | -0.28628 | south | Y | -0.42802 | -0.094658 | -0.41308 | -0.24669 | 0.094658 | south | N | 0.094658 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.18271 | south | Y | -0.32444 | 0.0089197 | -0.3095 | -0.14311 | 0.0089197 | south | N | 0.0089197 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.18271 | south | Y | -0.32444 | 0.0089197 | -0.3095 | -0.14311 | 0.0089197 | south | N | 0.0089197 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.18262 | south | Y | -0.32436 | 0.0090007 | -0.30942 | -0.14303 | 0.0090007 | south | N | 0.0090007 | 0
5031 | BRA_VHBC | 1 | 46 | -0.18271 | south | Y | -0.32444 | 0.0089197 | -0.3095 | -0.14311 | 0.0089197 | south | N | 0.0089197 | 0
5032 | BRA_VHBC | 2 | 47 | -0.18271 | south | Y | -0.32444 | 0.0089197 | -0.3095 | -0.14311 | 0.0089197 | south | N | 0.0089197 | 0
5033 | BRA_VHBC | 3 | 46 | -0.18271 | south | Y | -0.32444 | 0.0089197 | -0.3095 | -0.14311 | 0.0089197 | south | N | 0.0089197 | 0
5034 | BRA_VHBC | 4 | 46 | -0.18271 | south | Y | -0.32444 | 0.0089197 | -0.3095 | -0.14311 | 0.0089197 | south | N | 0.0089197 | 0
5111 | CALAVER_ | 1 | 424 | -0.18305 | south | Y | -0.32479 | 0.0085747 | -0.30984 | -0.14346 | 0.0085747 | south | N | 0.0085747 | 0
5112 | CALAVER_ | 2 | 425 | -0.18305 | south | Y | -0.32479 | 0.0085747 | -0.30984 | -0.14346 | 0.0085747 | south | N | 0.0085747 | 0
5264 | LEON_LCP | 3 | 58 | -0.1816 | south | Y | -0.32333 | 0.01003 | -0.30839 | -0.142 | 0.01003 | south | N | 0.01003 | 0
5265 | LEON_LCP | 4 | 89 | -0.1816 | south | Y | -0.32333 | 0.01003 | -0.30839 | -0.142 | 0.01003 | south | N | 0.01003 | 0
5266 | LEON_LCP | 1 | 44 | -0.1816 | south | Y | -0.32333 | 0.01003 | -0.30839 | -0.142 | 0.01003 | south | N | 0.01003 | 0
5267 | LEON_LCP | 2 | 44 | -0.1816 | south | Y | -0.32333 | 0.01003 | -0.30839 | -0.142 | 0.01003 | south | N | 0.01003 | 0
5268 | LEON_LCP | 3 | 43 | -0.1816 | south | Y | -0.32333 | 0.01003 | -0.30839 | -0.142 | 0.01003 | south | N | 0.01003 | 0
5269 | LEON_LCP | 4 | 45 | -0.1816 | south | Y | -0.32333 | 0.01003 | -0.30839 | -0.142 | 0.01003 | south | N | 0.01003 | 0
5396 | CALAVER_ | 1 | 412 | -0.18291 | south | Y | -0.32465 | 0.0087097 | -0.30971 | -0.14332 | 0.0087097 | south | N | 0.0087097 | 0
5397 | CALAVER_ | 2 | 400 | -0.18291 | south | Y | -0.32465 | 0.0087097 | -0.30971 | -0.14332 | 0.0087097 | south | N | 0.0087097 | 0
5401 | CALAVER_ | 1 | 546 | -0.18132 | south | Y | -0.32306 | 0.010306 | -0.30811 | -0.14172 | 0.010306 | south | N | 0.010306 | 0
5402 | CALAVER_ | 2 | 750 | -0.18132 | south | Y | -0.32306 | 0.010306 | -0.30811 | -0.14172 | 0.010306 | south | N | 0.010306 | 0
5436 | TUTTL_WB | MB | 61 | -0.18358 | south | Y | -0.32532 | 0.0080467 | -0.31037 | -0.14398 | 0.0080467 | south | N | 0.0080467 | 0
5438 | TUTTL_WB | MB | 95 | -0.18358 | south | Y | -0.32532 | 0.0080467 | -0.31037 | -0.14398 | 0.0080467 | south | N | 0.0080467 | 0
5439 | TUTTL_WB | MB | 151 | -0.18358 | south | Y | -0.32532 | 0.0080467 | -0.31037 | -0.14398 | 0.0080467 | south | N | 0.0080467 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.18226 | south | Y | -0.32399 | 0.0093697 | -0.30905 | -0.14266 | 0.0093697 | south | N | 0.0093697 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.18226 | south | Y | -0.32399 | 0.0093697 | -0.30905 | -0.14266 | 0.0093697 | south | N | 0.0093697 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.18226 | south | Y | -0.32399 | 0.0093697 | -0.30905 | -0.14266 | 0.0093697 | south | N | 0.0093697 | 0
5503 | RAYBURNG | 1 | 22 | -0.14614 | south | Y | -0.28788 | 0.045484 | -0.27294 | -0.10655 | 0.045484 | south | N | 0.045484 | 0
5505 | RAYBURNG | 1 | 11 | -0.14614 | south | Y | -0.28788 | 0.045484 | -0.27294 | -0.10655 | 0.045484 | south | N | 0.045484 | 0
5506 | RAYBURNG | 1 | 11 | -0.14614 | south | Y | -0.28788 | 0.045484 | -0.27294 | -0.10655 | 0.045484 | south | N | 0.045484 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.14751 | south | Y | -0.28925 | 0.044115 | -0.2743 | -0.10792 | 0.044115 | south | N | 0.044115 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.14751 | south | Y | -0.28925 | 0.044115 | -0.2743 | -0.10792 | 0.044115 | south | N | 0.044115 | 0
5511 | RAYBURNC | 1 | 46 | -0.14751 | south | Y | -0.28925 | 0.044115 | -0.2743 | -0.10792 | 0.044115 | south | N | 0.044115 | 0
5512 | RAYBURNC | 1 | 48 | -0.14751 | south | Y | -0.28925 | 0.044115 | -0.2743 | -0.10792 | 0.044115 | south | N | 0.044115 | 0
5728 | FALCONHY | 2 | 12 | -0.15435 | south | N | -0.29609 | 0.037275 | -0.28114 | -0.11476 | 0.037275 | south | N | 0.037275 | 0
5729 | FALCONHY | 3 | 11 | -0.15435 | south | N | -0.29609 | 0.037275 | -0.28114 | -0.11476 | 0.037275 | south | N | 0.037275 | 0
5890 | PEARSALL | 1 | 24 | -0.16151 | south | Y | -0.30325 | 0.030115 | -0.2883 | -0.12192 | 0.030115 | south | N | 0.030115 | 0
5891 | PEARSALL | 1 | 24 | -0.16151 | south | Y | -0.30325 | 0.030115 | -0.2883 | -0.12192 | 0.030115 | south | N | 0.030115 | 0
5892 | PEARSALL | 1 | 23 | -0.16151 | south | Y | -0.30325 | 0.030115 | -0.2883 | -0.12192 | 0.030115 | south | N | 0.030115 | 0
5903 | SANMIGUE | 1 | 396 | -0.17135 | south | Y | -0.31309 | 0.020278 | -0.29814 | -0.13175 | 0.020278 | south | N | 0.020278 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.092891 | houston | N | -0.23463 | 0.098734 | -0.21969 | -0.053296 | 0.053296 | houston | N | 0.053296 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.092891 | houston | N | -0.23463 | 0.098734 | -0.21969 | -0.053296 | 0.053296 | houston | N | 0.053296 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.14174 | 0
5932 | SI_RAY9 | 9 | 38 | -0.15183 | south | Y | -0.29357 | 0.039795 | -0.27862 | -0.11224 | 0.039795 | south | N | 0.039795 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.15183 | south | Y | -0.29357 | 0.039795 | -0.27862 | -0.11224 | 0.039795 | south | N | 0.039795 | 0
5934 | SI_RAY5 | 5 | 15 | -0.15183 | south | Y | -0.29357 | 0.039795 | -0.27862 | -0.11224 | 0.039795 | south | N | 0.039795 | 0
5935 | SI_RAY10 | 10 | 47 | -0.15183 | south | Y | -0.29357 | 0.039795 | -0.27862 | -0.11224 | 0.039795 | south | N | 0.039795 | 0
6016 | SWMESA | 1 | 75 | 0.11169 | west | Y | -0.030045 | 0.30332 | -0.0151 | 0.15129 | 0.0151 | west | N | 0.0151 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.12679 | 0
6144 | MCADOO1A | 1 | 150 | 0.13116 | west | Y | -0.010581 | 0.32278 | 0.0043636 | 0.17075 | 0.0043636 | west | N | 0.0043636 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.12385 | west | Y | -0.017887 | 0.31548 | -0.0029424 | 0.16345 | 0.0029424 | west | N | 0.0029424 | 0
6476 | LANGFORD | 1 | 150 | 0.056787 | west | Y | -0.084952 | 0.24841 | -0.070007 | 0.096382 | 0.070007 | west | N | 0.070007 | 0
6637 | SNYDERW1 | 1 | 63 | 0.12921 | west | Y | -0.012524 | 0.32084 | 0.0024206 | 0.16881 | 0.0024206 | west | N | 0.0024206 | 0
6752 | OKLA0A | 1 | 649.7 | 0.13854 | west | Y | -0.0031999 | 0.33016 | 0.011745 | 0.17813 | 0.0031999 | North | Y | 0.011745 | 5.5515
6948 | DENISNDM | 1 | 40 | 0.14762 | north | N | 0.0058821 | 0.33925 | 0.020827 | 0.18722 | 0.0058821 | North | N | 0.0058821 | 0
6948 | DENISNDM | 2 | 40 | 0.14762 | north | N | 0.0058821 | 0.33925 | 0.020827 | 0.18722 | 0.0058821 | North | N | 0.0058821 | 0
7000 | L_FERGUS | 1 | 422 | -0.20514 | south | Y | -0.34688 | -0.013517 | -0.33194 | -0.16555 | 0.013517 | south | N | 0.013517 | 0
7004 | L_SIMGID | 1 | 132 | -0.23004 | south | Y | -0.37178 | -0.038412 | -0.35683 | -0.19044 | 0.038412 | south | N | 0.038412 | 0
7005 | L_SIMGID | 2 | 134 | -0.23004 | south | Y | -0.37178 | -0.038412 | -0.35683 | -0.19044 | 0.038412 | south | N | 0.038412 | 0
7006 | L_SIMGID | 3 | 323 | -0.23004 | south | Y | -0.37178 | -0.038412 | -0.35683 | -0.19044 | 0.038412 | south | N | 0.038412 | 0
7007 | L_LOSTPI | 1 | 158 | -0.23264 | south | Y | -0.37438 | -0.041019 | -0.35944 | -0.19305 | 0.041019 | south | N | 0.041019 | 0
7008 | L_LOSTPI | 2 | 160 | -0.23264 | south | Y | -0.37438 | -0.041019 | -0.35944 | -0.19305 | 0.041019 | south | N | 0.041019 | 0
7009 | L_LOSTPI | 3 | 175 | -0.23264 | south | Y | -0.37438 | -0.041019 | -0.35944 | -0.19305 | 0.041019 | south | N | 0.041019 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.20677 | south | Y | -0.34851 | -0.015148 | -0.33357 | -0.16718 | 0.015148 | south | N | 0.015148 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.20677 | south | Y | -0.34851 | -0.015148 | -0.33357 | -0.16718 | 0.015148 | south | N | 0.015148 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.20656 | south | Y | -0.3483 | -0.014939 | -0.33336 | -0.16697 | 0.014939 | south | N | 0.014939 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.20206 | south | Y | -0.34379 | -0.010431 | -0.32885 | -0.16246 | 0.010431 | south | N | 0.010431 | 0
7015 | L_HAYSEN | 2 | 225 | -0.20206 | south | Y | -0.34379 | -0.010431 | -0.32885 | -0.16246 | 0.010431 | south | N | 0.010431 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.20206 | south | Y | -0.34379 | -0.010431 | -0.32885 | -0.16246 | 0.010431 | south | N | 0.010431 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.20206 | south | Y | -0.34379 | -0.010431 | -0.32885 | -0.16246 | 0.010431 | south | N | 0.010431 | 0
7020 | L_AUSTPL | 1 | 8 | -0.23938 | south | N | -0.38112 | -0.047758 | -0.36618 | -0.19979 | 0.047758 | south | N | 0.047758 | 0
7020 | L_AUSTPL | 2 | 8 | -0.23938 | south | N | -0.38112 | -0.047758 | -0.36618 | -0.19979 | 0.047758 | south | N | 0.047758 | 0
7022 | L_BUCHAN | 1 | 18 | -0.20337 | south | N | -0.34511 | -0.011743 | -0.33016 | -0.16377 | 0.011743 | south | N | 0.011743 | 0
7023 | L_BUCHAN | 2 | 18 | -0.20337 | south | N | -0.34511 | -0.011743 | -0.33016 | -0.16377 | 0.011743 | south | N | 0.011743 | 0
7024 | L_BUCHAN | 3 | 15 | -0.20337 | south | N | -0.34511 | -0.011743 | -0.33016 | -0.16377 | 0.011743 | south | N | 0.011743 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.20051 | south | N | -0.34225 | -0.0088863 | -0.32731 | -0.16092 | 0.0088863 | south | N | 0.0088863 | 0
7028 | L_MARBFA | 1 | 18 | -0.21311 | south | N | -0.35485 | -0.021485 | -0.3399 | -0.17352 | 0.021485 | south | N | 0.021485 | 0
7029 | L_MARBFA | 2 | 18 | -0.21311 | south | N | -0.35485 | -0.021485 | -0.3399 | -0.17352 | 0.021485 | south | N | 0.021485 | 0
7031 | L_MARSFO | 1 | 35 | -0.23118 | south | N | -0.37292 | -0.039554 | -0.35797 | -0.19158 | 0.039554 | south | N | 0.039554 | 0
7032 | L_MARSFO | 2 | 34 | -0.23118 | south | N | -0.37292 | -0.039554 | -0.35797 | -0.19158 | 0.039554 | south | N | 0.039554 | 0
7033 | L_MARSFO | 3 | 35 | -0.23118 | south | N | -0.37292 | -0.039554 | -0.35797 | -0.19158 | 0.039554 | south | N | 0.039554 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.20669 | south | N | -0.34843 | -0.015063 | -0.33348 | -0.16709 | 0.015063 | south | N | 0.015063 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.20669 | south | N | -0.34843 | -0.015063 | -0.33348 | -0.16709 | 0.015063 | south | N | 0.015063 | 0
7038 | L_DELAWA | 1 | 35 | 0.12462 | west | Y | -0.017118 | 0.31625 | -0.0021734 | 0.16422 | 0.0021734 | west | N | 0.0021734 | 0
7038 | L_DELAWA | 2 | 30 | 0.12462 | west | Y | -0.017118 | 0.31625 | -0.0021734 | 0.16422 | 0.0021734 | west | N | 0.0021734 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.20901 | south | Y | -0.35075 | -0.017389 | -0.33581 | -0.16942 | 0.017389 | south | N | 0.017389 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.20901 | south | Y | -0.35075 | -0.017389 | -0.33581 | -0.16942 | 0.017389 | south | N | 0.017389 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.20901 | south | Y | -0.35075 | -0.017389 | -0.33581 | -0.16942 | 0.017389 | south | N | 0.017389 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.20901 | south | Y | -0.35075 | -0.017389 | -0.33581 | -0.16942 | 0.017389 | south | N | 0.017389 | 0
7487 | L_CANYHY | 1 | 6 | -0.20713 | south | N | -0.34887 | -0.015503 | -0.33392 | -0.16753 | 0.015503 | south | N | 0.015503 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.19548 | south | N | -0.33721 | -0.0038513 | -0.32227 | -0.15588 | 0.0038513 | south | N | 0.0038513 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.19548 | south | N | -0.33721 | -0.0038513 | -0.32227 | -0.15588 | 0.0038513 | south | N | 0.0038513 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.19548 | south | N | -0.33721 | -0.0038513 | -0.32227 | -0.15588 | 0.0038513 | south | N | 0.0038513 | 0
7609 | L_SCHUMA | 1 | 4 | -0.19262 | south | N | -0.33436 | -0.00099227 | -0.31941 | -0.15302 | 0.00099227 | south | N | 0.00099227 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.19277 | south | N | -0.3345 | -0.0011413 | -0.31956 | -0.15317 | 0.0011413 | south | N | 0.0011413 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.19277 | south | N | -0.3345 | -0.0011413 | -0.31956 | -0.15317 | 0.0011413 | south | N | 0.0011413 | 0
7800 | L_GUADGE | 1 | 147 | -0.18772 | south | Y | -0.32945 | 0.0039087 | -0.31451 | -0.14812 | 0.0039087 | south | N | 0.0039087 | 0
7801 | L_GUADGE | 2 | 138 | -0.18772 | south | Y | -0.32945 | 0.0039087 | -0.31451 | -0.14812 | 0.0039087 | south | N | 0.0039087 | 0
7802 | L_GUADGE | 3 | 140 | -0.18772 | south | Y | -0.32945 | 0.0039087 | -0.31451 | -0.14812 | 0.0039087 | south | N | 0.0039087 | 0
7803 | L_GUADGE | 4 | 147 | -0.18772 | south | Y | -0.32945 | 0.0039087 | -0.31451 | -0.14812 | 0.0039087 | south | N | 0.0039087 | 0
7804 | L_GUADGE | 5 | 182 | -0.18772 | south | Y | -0.32945 | 0.0039087 | -0.31451 | -0.14812 | 0.0039087 | south | N | 0.0039087 | 0
7805 | L_GUADGE | 6 | 198 | -0.18772 | south | Y | -0.32945 | 0.0039087 | -0.31451 | -0.14812 | 0.0039087 | south | N | 0.0039087 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.2343 | south | Y | -0.37604 | -0.042678 | -0.3611 | -0.19471 | 0.042678 | south | N | 0.042678 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.2343 | south | Y | -0.37604 | -0.042678 | -0.3611 | -0.19471 | 0.042678 | south | N | 0.042678 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.2343 | south | Y | -0.37604 | -0.042678 | -0.3611 | -0.19471 | 0.042678 | south | N | 0.042678 | 0
7810 | L_RIONOG | 1 | 142 | -0.1947 | south | Y | -0.33644 | -0.0030753 | -0.32149 | -0.15511 | 0.0030753 | south | N | 0.0030753 | 0
7811 | L_RIONOG | 2 | 145 | -0.1947 | south | Y | -0.33644 | -0.0030753 | -0.32149 | -0.15511 | 0.0030753 | south | N | 0.0030753 | 0
7812 | L_RIONOG | 3 | 151 | -0.1947 | south | Y | -0.33644 | -0.0030753 | -0.32149 | -0.15511 | 0.0030753 | south | N | 0.0030753 | 0
7813 | L_RIONOG | 4 | 290 | -0.1947 | south | Y | -0.33644 | -0.0030753 | -0.32149 | -0.15511 | 0.0030753 | south | N | 0.0030753 | 0
8032 | AMISTADH | 1 | 33 | -0.087145 | south | N | -0.22888 | 0.10448 | -0.21394 | -0.04755 | 0.04755 | houston | Y | 0.10448 | 0
8033 | AMISTADH | 2 | 25 | -0.087145 | south | N | -0.22888 | 0.10448 | -0.21394 | -0.04755 | 0.04755 | houston | Y | 0.10448 | 0
8048 | FALCONHY | 1 | 12 | -0.15435 | south | N | -0.29609 | 0.037275 | -0.28114 | -0.11476 | 0.037275 | south | N | 0.037275 | 0
8066 | DUP1V#1 | 1 | 73 | -0.14783 | south | N | -0.28957 | 0.043794 | -0.27463 | -0.10824 | 0.043794 | south | N | 0.043794 | 0
8134 | FOR69CG0 | 1 | 79 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
8138 | FOR69CG0 | 2 | 81 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.19162 | 0
8147 | UCAR #2 | 10 | 28 | -0.14315 | south | N | -0.28489 | 0.048472 | -0.26995 | -0.10356 | 0.048472 | south | N | 0.048472 | 0
8148 | UCAR #1 | 2 | 7 | -0.14315 | south | N | -0.28489 | 0.048472 | -0.26995 | -0.10356 | 0.048472 | south | N | 0.048472 | 0
8153 | FOR69CG0 | 3 | 79 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
8154 | FOR69CG0 | 4 | 80 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
8156 | FOR69CG0 | 6 | 25 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
8157 | FOR69CG0 | 7 | 46 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
8161 | COLETOU1 | 1 | 629 | -0.15682 | south | Y | -0.29856 | 0.034803 | -0.28362 | -0.11723 | 0.034803 | south | N | 0.034803 | 0
8173 | VICEC51A | 5 | 144 | -0.14954 | south | Y | -0.29127 | 0.042089 | -0.27633 | -0.10994 | 0.042089 | south | N | 0.042089 | 0
8174 | VICEC61A | 6 | 188 | -0.14954 | south | Y | -0.29127 | 0.042089 | -0.27633 | -0.10994 | 0.042089 | south | N | 0.042089 | 0
8189 | CUERO 2 | 1 | 12 | -0.18085 | south | N | -0.32259 | 0.010771 | -0.30765 | -0.14126 | 0.010771 | south | N | 0.010771 | 0
8262 | ELPS | 1 | 6 | -0.11027 | south | N | -0.25201 | 0.081358 | -0.23706 | -0.070672 | 0.070672 | houston | Y | 0.081358 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.19162 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.19162 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.19162 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.19162 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.19162 | 0
8442 | NBEC71A | 1 | 336 | -0.15017 | south | Y | -0.29191 | 0.041455 | -0.27696 | -0.11058 | 0.041455 | south | N | 0.041455 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.19162 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.14174 | 0.19162 | -0.12679 | 0.039595 | 0.039595 | houston | Y | 0.19162 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.15052 | south | Y | -0.29226 | 0.041102 | -0.27732 | -0.11093 | 0.041102 | south | N | 0.041102 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.15052 | south | Y | -0.29226 | 0.041102 | -0.27732 | -0.11093 | 0.041102 | south | N | 0.041102 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.15074 | south | N | -0.29248 | 0.040883 | -0.27754 | -0.11115 | 0.040883 | south | N | 0.040883 | 0
8506 | VAL #1 | 1 | 25 | -0.15058 | south | N | -0.29232 | 0.041047 | -0.27737 | -0.11098 | 0.041047 | south | N | 0.041047 | 0
8507 | VAL #2 | 2 | 25 | -0.15058 | south | N | -0.29232 | 0.041047 | -0.27737 | -0.11098 | 0.041047 | south | N | 0.041047 | 0
8511 | OXY_CC0A | 1 | 38 | -0.15073 | south | N | -0.29247 | 0.040894 | -0.27753 | -0.11114 | 0.040894 | south | N | 0.040894 | 0
8517 | CELANEBI | 1 | 29 | -0.15148 | south | N | -0.29322 | 0.040147 | -0.27827 | -0.11188 | 0.040147 | south | N | 0.040147 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.15019 | south | N | -0.29193 | 0.041437 | -0.27698 | -0.11059 | 0.041437 | south | N | 0.041437 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.15019 | south | N | -0.29193 | 0.041437 | -0.27698 | -0.11059 | 0.041437 | south | N | 0.041437 | 0
8562 | CNOPST1 | 3 | 153 | -0.15019 | south | N | -0.29193 | 0.041437 | -0.27698 | -0.11059 | 0.041437 | south | N | 0.041437 | 0
8926 | LGE_GT10 | 1 | 158 | -0.14858 | south | N | -0.29032 | 0.043047 | -0.27537 | -0.10898 | 0.043047 | south | N | 0.043047 | 0
8927 | LGE_GT20 | 2 | 153 | -0.14858 | south | N | -0.29032 | 0.043047 | -0.27537 | -0.10898 | 0.043047 | south | N | 0.043047 | 0
8928 | LGE_STG0 | 3 | 100 | -0.14858 | south | N | -0.29032 | 0.043047 | -0.27537 | -0.10898 | 0.043047 | south | N | 0.043047 | 0
8930 | ICPGN10A | 1 | 145 | -0.14858 | south | N | -0.29032 | 0.043047 | -0.27537 | -0.10898 | 0.043047 | south | N | 0.043047 | 0
8931 | ICPGN20A | 2 | 147 | -0.14858 | south | N | -0.29032 | 0.043047 | -0.27537 | -0.10898 | 0.043047 | south | N | 0.043047 | 0
8932 | ICPGN30A | 3 | 127 | -0.14858 | south | N | -0.29032 | 0.043047 | -0.27537 | -0.10898 | 0.043047 | south | N | 0.043047 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.15244 | south | Y | -0.29418 | 0.039186 | -0.27923 | -0.11284 | 0.039186 | south | N | 0.039186 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.15244 | south | Y | -0.29418 | 0.039186 | -0.27923 | -0.11284 | 0.039186 | south | N | 0.039186 | 0
8935 | FGNTS201 | 3 | 173 | -0.15244 | south | Y | -0.29418 | 0.039186 | -0.27923 | -0.11284 | 0.039186 | south | N | 0.039186 | 0
8936 | MVGN#1 | 1 | 207 | -0.15213 | south | Y | -0.29387 | 0.039493 | -0.27893 | -0.11254 | 0.039493 | south | N | 0.039493 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.15213 | south | Y | -0.29387 | 0.039493 | -0.27893 | -0.11254 | 0.039493 | south | N | 0.039493 | 0
8938 | MVGN#3 | 3 | 242 | -0.15213 | south | Y | -0.29387 | 0.039493 | -0.27893 | -0.11254 | 0.039493 | south | N | 0.039493 | 0
8981 | HECN1 | 1 | 144 | -0.15213 | south | Y | -0.29387 | 0.039498 | -0.27892 | -0.11253 | 0.039498 | south | N | 0.039498 | 0
8982 | HECN2 | 2 | 144 | -0.15213 | south | Y | -0.29387 | 0.039498 | -0.27892 | -0.11253 | 0.039498 | south | N | 0.039498 | 0
8983 | HECN3 | 3 | 171 | -0.15213 | south | Y | -0.29387 | 0.039498 | -0.27892 | -0.11253 | 0.039498 | south | N | 0.039498 | 0
9000 | DECKR_G1 | 1 | 310 | -0.24041 | south | Y | -0.38215 | -0.048782 | -0.3672 | -0.20081 | 0.048782 | south | N | 0.048782 | 0
9001 | DECKR_G2 | 2 | 413 | -0.24041 | south | Y | -0.38215 | -0.048782 | -0.3672 | -0.20081 | 0.048782 | south | N | 0.048782 | 0
9002 | DECKR_G3 | 3 | 42 | -0.243 | south | Y | -0.38474 | -0.051372 | -0.36979 | -0.2034 | 0.051372 | south | N | 0.051372 | 0
9003 | DECKR_G4 | 4 | 44 | -0.243 | south | Y | -0.38474 | -0.051372 | -0.36979 | -0.2034 | 0.051372 | south | N | 0.051372 | 0
9004 | DECKR_G5 | 5 | 44 | -0.243 | south | Y | -0.38474 | -0.051372 | -0.36979 | -0.2034 | 0.051372 | south | N | 0.051372 | 0
9005 | DECKR_G6 | 6 | 47 | -0.243 | south | Y | -0.38474 | -0.051372 | -0.36979 | -0.2034 | 0.051372 | south | N | 0.051372 | 0
9016 | SANDH_G1 | 1 | 49 | -0.23771 | south | Y | -0.37945 | -0.046083 | -0.3645 | -0.19811 | 0.046083 | south | N | 0.046083 | 0
9017 | SANDH_G2 | 2 | 46 | -0.23771 | south | Y | -0.37945 | -0.046083 | -0.3645 | -0.19811 | 0.046083 | south | N | 0.046083 | 0
9018 | SANDH_G3 | 3 | 46 | -0.23771 | south | Y | -0.37945 | -0.046083 | -0.3645 | -0.19811 | 0.046083 | south | N | 0.046083 | 0
9019 | SANDH_G4 | 4 | 47 | -0.23771 | south | Y | -0.37945 | -0.046083 | -0.3645 | -0.19811 | 0.046083 | south | N | 0.046083 | 0
9020 | SANDHG5A | 5A | 154 | -0.23771 | south | Y | -0.37945 | -0.046083 | -0.3645 | -0.19811 | 0.046083 | south | N | 0.046083 | 0
9021 | SANDHG5C | 5C | 148 | -0.23771 | south | Y | -0.37945 | -0.046083 | -0.3645 | -0.19811 | 0.046083 | south | N | 0.046083 | 0
9022 | SANDH_G6 | 6 | 48 | -0.23771 | south | Y | -0.37945 | -0.046083 | -0.3645 | -0.19811 | 0.046083 | south | N | 0.046083 | 0
9023 | SANDH_G7 | 7 | 48 | -0.23771 | south | Y | -0.37945 | -0.046083 | -0.3645 | -0.19811 | 0.046083 | south | N | 0.046083 | 0
11001 | NAV1CT | 1 | 70 | 0.12682 | west | Y | -0.014921 | 0.31844 | 2.3573e-05 | 0.16641 | 2.3573e-05 | west | N | 2.3573e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.12682 | west | Y | -0.014921 | 0.31844 | 2.3573e-05 | 0.16641 | 2.3573e-05 | west | N | 2.3573e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.12682 | west | Y | -0.014921 | 0.31844 | 2.3573e-05 | 0.16641 | 2.3573e-05 | west | N | 2.3573e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.12682 | west | Y | -0.014921 | 0.31844 | 2.3573e-05 | 0.16641 | 2.3573e-05 | west | N | 2.3573e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.12682 | west | Y | -0.014921 | 0.31844 | 2.3573e-05 | 0.16641 | 2.3573e-05 | west | N | 2.3573e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.12682 | west | Y | -0.014921 | 0.31844 | 2.3573e-05 | 0.16641 | 2.3573e-05 | west | N | 2.3573e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.1268 | west | Y | -0.014943 | 0.31842 | 1.5725e-06 | 0.16639 | 1.5725e-06 | west | N | 1.5725e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.1268 | west | Y | -0.014943 | 0.31842 | 1.5725e-06 | 0.16639 | 1.5725e-06 | west | N | 1.5725e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.1268 | west | Y | -0.014943 | 0.31842 | 1.5725e-06 | 0.16639 | 1.5725e-06 | west | N | 1.5725e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.1268 | west | Y | -0.014943 | 0.31842 | 1.5725e-06 | 0.16639 | 1.5725e-06 | west | N | 1.5725e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.1268 | west | Y | -0.014943 | 0.31842 | 1.5725e-06 | 0.16639 | 1.5725e-06 | west | N | 1.5725e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.1268 | west | Y | -0.014943 | 0.31842 | 1.5725e-06 | 0.16639 | 1.5725e-06 | west | N | 1.5725e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.13107 | west | Y | -0.010667 | 0.3227 | 0.0042776 | 0.17067 | 0.0042776 | west | N | 0.0042776 | 0
11057 | CHAMPION | 1 | 126.5 | 0.13107 | west | Y | -0.010667 | 0.3227 | 0.0042776 | 0.17067 | 0.0042776 | west | N | 0.0042776 | 0
11058 | PYRON_1G | 1 | 249 | 0.13107 | west | Y | -0.010667 | 0.3227 | 0.0042776 | 0.17067 | 0.0042776 | west | N | 0.0042776 | 0
11059 | INADALE_ | 1 | 197 | 0.13107 | west | Y | -0.010667 | 0.3227 | 0.0042776 | 0.17067 | 0.0042776 | west | N | 0.0042776 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.12883 | west | Y | -0.012908 | 0.32046 | 0.0020366 | 0.16843 | 0.0020366 | west | N | 0.0020366 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.12883 | west | Y | -0.012908 | 0.32046 | 0.0020366 | 0.16843 | 0.0020366 | west | N | 0.0020366 | 0
11147 | NOTREES_ | 1 | 149 | 0.12501 | west | Y | -0.016727 | 0.31664 | -0.0017824 | 0.16461 | 0.0017824 | west | N | 0.0017824 | 0
11309 | BULLCREK | 1 | 180 | 0.12845 | west | Y | -0.013288 | 0.32008 | 0.0016566 | 0.16805 | 0.0016566 | west | N | 0.0016566 | 0
11310 | BULLCREK | 1 | 180 | 0.12845 | west | Y | -0.013288 | 0.32008 | 0.0016566 | 0.16805 | 0.0016566 | west | N | 0.0016566 | 0
11320 | COYOTE_1 | 1 | 225 | 0.12833 | west | Y | -0.013409 | 0.31995 | 0.0015356 | 0.16792 | 0.0015356 | west | N | 0.0015356 | 0
11415 | LORAINE_ | 1 | 125 | 0.13011 | west | Y | -0.011625 | 0.32174 | 0.0033196 | 0.16971 | 0.0033196 | west | N | 0.0033196 | 0
11416 | LORAINE_ | 1 | 125 | 0.13011 | west | Y | -0.011625 | 0.32174 | 0.0033196 | 0.16971 | 0.0033196 | west | N | 0.0033196 | 0
11691 | KMICHICT | 1 | 140 | 0.14742 | north | N | 0.0056821 | 0.33905 | 0.020627 | 0.18702 | 0.0056821 | North | N | 0.0056821 | 0
11692 | KMICHICT | 2 | 141 | 0.14742 | north | N | 0.0056821 | 0.33905 | 0.020627 | 0.18702 | 0.0056821 | North | N | 0.0056821 | 0
11693 | KMICHIST | 3 | 309 | 0.14742 | north | N | 0.0056821 | 0.33905 | 0.020627 | 0.18702 | 0.0056821 | North | N | 0.0056821 | 0
11694 | KMICHICT | 4 | 143 | 0.14742 | north | N | 0.0056821 | 0.33905 | 0.020627 | 0.18702 | 0.0056821 | North | N | 0.0056821 | 0
11695 | KMICHICT | 5 | 144 | 0.14742 | north | N | 0.0056821 | 0.33905 | 0.020627 | 0.18702 | 0.0056821 | North | N | 0.0056821 | 0
11696 | KMICHIST | 6 | 310 | 0.14742 | north | N | 0.0056821 | 0.33905 | 0.020627 | 0.18702 | 0.0056821 | North | N | 0.0056821 | 0
12322 | ENNSTRAC | 1 | 196 | 0.14915 | north | Y | 0.0074081 | 0.34077 | 0.022353 | 0.18874 | 0.0074081 | North | N | 0.0074081 | 0
12323 | ENNSTRAC | 2 | 111 | 0.14915 | north | Y | 0.0074081 | 0.34077 | 0.022353 | 0.18874 | 0.0074081 | North | N | 0.0074081 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.14838 | north | N | 0.0066461 | 0.34001 | 0.021591 | 0.18798 | 0.0066461 | North | N | 0.0066461 | 0
12411 | FPLEFR1A | 1 | 161 | 0.14612 | north | Y | 0.0043781 | 0.33774 | 0.019323 | 0.18571 | 0.0043781 | North | N | 0.0043781 | 0
12412 | FPLEFR1B | 2 | 164 | 0.14612 | north | Y | 0.0043781 | 0.33774 | 0.019323 | 0.18571 | 0.0043781 | North | N | 0.0043781 | 0
12413 | FPLEFR1C | 3 | 164 | 0.14612 | north | Y | 0.0043781 | 0.33774 | 0.019323 | 0.18571 | 0.0043781 | North | N | 0.0043781 | 0
12414 | FPLEFR1S | 4 | 414 | 0.14612 | north | Y | 0.0043781 | 0.33774 | 0.019323 | 0.18571 | 0.0043781 | North | N | 0.0043781 | 0
12421 | FPLEFR2A | 1 | 162 | 0.14612 | north | Y | 0.0043781 | 0.33774 | 0.019323 | 0.18571 | 0.0043781 | North | N | 0.0043781 | 0
12422 | FPLEFR2B | 2 | 161 | 0.14612 | north | Y | 0.0043781 | 0.33774 | 0.019323 | 0.18571 | 0.0043781 | North | N | 0.0043781 | 0
12423 | FPLEFR2C | 3 | 163 | 0.14612 | north | Y | 0.0043781 | 0.33774 | 0.019323 | 0.18571 | 0.0043781 | North | N | 0.0043781 | 0
12424 | FPLEFR2S | 4 | 409 | 0.14612 | north | Y | 0.0043781 | 0.33774 | 0.019323 | 0.18571 | 0.0043781 | North | N | 0.0043781 | 0
12440 | PARKD_1S | 1 | 0 | 0.14781 | north | N | 0.0060741 | 0.33944 | 0.021019 | 0.18741 | 0.0060741 | North | N | 0.0060741 | 0
12449 | PARKD_2S | 1 | 0 | 0.14781 | north | N | 0.0060741 | 0.33944 | 0.021019 | 0.18741 | 0.0060741 | North | N | 0.0060741 | 0
13116 | TGATEWAY | 1 | 148 | 0.14092 | north | N | -0.00082087 | 0.33254 | 0.014124 | 0.18051 | 0.00082087 | North | N | 0.00082087 | 0
13117 | TGATEWAY | 2 | 130 | 0.14092 | north | N | -0.00082087 | 0.33254 | 0.014124 | 0.18051 | 0.00082087 | North | N | 0.00082087 | 0
13118 | TGATEWAY | 3 | 145 | 0.14092 | north | N | -0.00082087 | 0.33254 | 0.014124 | 0.18051 | 0.00082087 | North | N | 0.00082087 | 0
13119 | TGATEWAY | 4 | 399 | 0.14092 | north | N | -0.00082087 | 0.33254 | 0.014124 | 0.18051 | 0.00082087 | North | N | 0.00082087 | 0
13131 | CALFREST | 1 | 150.7 | 0.13454 | north | Y | -0.0072029 | 0.32616 | 0.0077416 | 0.17413 | 0.0072029 | North | N | 0.0072029 | 0
13132 | CALFREST | 2 | 151 | 0.13454 | north | Y | -0.0072029 | 0.32616 | 0.0077416 | 0.17413 | 0.0072029 | North | N | 0.0072029 | 0
13133 | CALFREST | 3 | 177.4 | 0.13454 | north | Y | -0.0072029 | 0.32616 | 0.0077416 | 0.17413 | 0.0072029 | North | N | 0.0072029 | 0
13134 | CALFREST | 4 | 151.5 | 0.13472 | north | Y | -0.0070179 | 0.32635 | 0.0079266 | 0.17432 | 0.0070179 | North | N | 0.0070179 | 0
13135 | CALFREST | 5 | 152.3 | 0.13472 | north | Y | -0.0070179 | 0.32635 | 0.0079266 | 0.17432 | 0.0070179 | North | N | 0.0070179 | 0
13136 | CALFREST | 6 | 177.5 | 0.13472 | north | Y | -0.0070179 | 0.32635 | 0.0079266 | 0.17432 | 0.0070179 | North | N | 0.0070179 | 0
13432 | SANDOW_5 | 5 | 581 | -0.28628 | south | Y | -0.42802 | -0.094658 | -0.41308 | -0.24669 | 0.094658 | south | N | 0.094658 | 0
13691 | OAKGROVE | 1 | 855 | 0.094638 | north | Y | -0.047101 | 0.28626 | -0.032156 | 0.13423 | 0.032156 | west | Y | 0.047101 | 12.7775
13692 | OAKGROVE | 2 | 855 | 0.094638 | north | Y | -0.047101 | 0.28626 | -0.032156 | 0.13423 | 0.032156 | west | Y | 0.047101 | 12.7775
32798 | BRYN_TAM | 1 | 32 | 0.04587 | north | N | -0.095869 | 0.23749 | -0.080924 | 0.085465 | 0.080924 | west | Y | 0.095869 | 0
32883 | BRYN_DNS | 1 | 48 | 0.041643 | north | Y | -0.1001 | 0.23327 | -0.085151 | 0.081238 | 0.081238 | houston | Y | 0.1001 | 0.90518
32884 | BRYN_DNS | 1 | 46 | 0.041643 | north | Y | -0.1001 | 0.23327 | -0.085151 | 0.081238 | 0.081238 | houston | Y | 0.1001 | 0.86746
32886 | BRYN_ATK | MB | 12 | 0.045953 | north | Y | -0.095786 | 0.23758 | -0.080841 | 0.085548 | 0.080841 | west | Y | 0.095786 | 0
32887 | BRYN_ATK | MB | 51 | 0.045953 | north | Y | -0.095786 | 0.23758 | -0.080841 | 0.085548 | 0.080841 | west | Y | 0.095786 | 0
32888 | BRYN_ATK | 1 | 17 | 0.045953 | north | Y | -0.095786 | 0.23758 | -0.080841 | 0.085548 | 0.080841 | west | Y | 0.095786 | 0.25406
32890 | BRYN_ATK | MB | 22 | 0.045953 | north | Y | -0.095786 | 0.23758 | -0.080841 | 0.085548 | 0.080841 | west | Y | 0.095786 | 0
32891 | BRYN_ATK | MB | 25 | 0.045953 | north | Y | -0.095786 | 0.23758 | -0.080841 | 0.085548 | 0.080841 | west | Y | 0.095786 | 0
32892 | BRYN_DNS | 1 | 105 | 0.041643 | north | Y | -0.1001 | 0.23327 | -0.085151 | 0.081238 | 0.081238 | houston | Y | 0.1001 | 1.9801
36998 | RDCNYNG1 | 1 | 84 | 0.1297 | west | Y | -0.012044 | 0.32132 | 0.0029006 | 0.16929 | 0.0029006 | west | N | 0.0029006 | 0
38332 | WDWRDU2 | 1 | 80 | 0.11146 | west | Y | -0.030274 | 0.30309 | -0.015329 | 0.15106 | 0.015329 | west | N | 0.015329 | 0
38437 | TNSRBNMS | 1 | 150 | 0.11135 | west | Y | -0.030393 | 0.30297 | -0.015448 | 0.15094 | 0.015448 | west | N | 0.015448 | 0
38438 | TNSRBNMS | 1 | 150 | 0.11135 | west | Y | -0.030393 | 0.30297 | -0.015448 | 0.15094 | 0.015448 | west | N | 0.015448 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.041784 | houston | N | -0.18352 | 0.14984 | -0.16858 | -0.0021891 | 0.0021891 | houston | N | 0.0021891 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.041784 | houston | N | -0.18352 | 0.14984 | -0.16858 | -0.0021891 | 0.0021891 | houston | N | 0.0021891 | 0
38600 | TNBP_CGN | 5 | 53 | -0.041784 | houston | N | -0.18352 | 0.14984 | -0.16858 | -0.0021891 | 0.0021891 | houston | N | 0.0021891 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.041784 | houston | N | -0.18352 | 0.14984 | -0.16858 | -0.0021891 | 0.0021891 | houston | N | 0.0021891 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.041784 | houston | N | -0.18352 | 0.14984 | -0.16858 | -0.0021891 | 0.0021891 | houston | N | 0.0021891 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.041784 | houston | N | -0.18352 | 0.14984 | -0.16858 | -0.0021891 | 0.0021891 | houston | N | 0.0021891 | 0
38614 | TNBPAMCG | 4 | 96 | -0.041784 | houston | N | -0.18352 | 0.14984 | -0.16858 | -0.0021891 | 0.0021891 | houston | N | 0.0021891 | 0
38615 | TNBPAMCG | 1 | 244 | -0.041784 | houston | N | -0.18352 | 0.14984 | -0.16858 | -0.0021891 | 0.0021891 | houston | N | 0.0021891 | 0
38690 | TNBP_CGN | 3 | 40 | -0.041784 | houston | N | -0.18352 | 0.14984 | -0.16858 | -0.0021891 | 0.0021891 | houston | N | 0.0021891 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.041817 | houston | N | -0.18356 | 0.14981 | -0.16861 | -0.0022221 | 0.0022221 | houston | N | 0.0022221 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.041817 | houston | N | -0.18356 | 0.14981 | -0.16861 | -0.0022221 | 0.0022221 | houston | N | 0.0022221 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.041817 | houston | N | -0.18356 | 0.14981 | -0.16861 | -0.0022221 | 0.0022221 | houston | N | 0.0022221 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.041817 | houston | N | -0.18356 | 0.14981 | -0.16861 | -0.0022221 | 0.0022221 | houston | N | 0.0022221 | 0
39470 | TNDOWCGN | 1 | 32 | -0.041815 | houston | N | -0.18355 | 0.14981 | -0.16861 | -0.0022201 | 0.0022201 | houston | N | 0.0022201 | 0
39480 | TNDOWCGN | 1 | 30 | -0.041815 | houston | N | -0.18355 | 0.14981 | -0.16861 | -0.0022201 | 0.0022201 | houston | N | 0.0022201 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.062251 | houston | N | -0.20399 | 0.12937 | -0.18905 | -0.022656 | 0.022656 | houston | N | 0.022656 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.062251 | houston | N | -0.20399 | 0.12937 | -0.18905 | -0.022656 | 0.022656 | houston | N | 0.022656 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.062251 | houston | N | -0.20399 | 0.12937 | -0.18905 | -0.022656 | 0.022656 | houston | N | 0.022656 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.062251 | houston | N | -0.20399 | 0.12937 | -0.18905 | -0.022656 | 0.022656 | houston | N | 0.022656 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.094638 | north | Y | -0.047101 | 0.28626 | -0.032156 | 0.13423 | 0.032156 | west | Y | 0.047101 | 2.276
39970 | TNTNPONE | 1 | 153 | 0.094638 | north | Y | -0.047101 | 0.28626 | -0.032156 | 0.13423 | 0.032156 | west | Y | 0.047101 | 2.2865
48500 | APD_GT1_ | 1 | 136 | -0.029329 | houston | N | -0.17107 | 0.1623 | -0.15612 | 0.010266 | 0.010266 | houston | N | 0.010266 | 0
48510 | AK_GT1__ | 1 | 33 | -0.048601 | houston | N | -0.19034 | 0.14302 | -0.1754 | -0.0090061 | 0.0090061 | houston | N | 0.0090061 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.029256 | houston | Y | -0.17099 | 0.16237 | -0.15605 | 0.010339 | 0.010339 | houston | N | 0.010339 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.029256 | houston | Y | -0.17099 | 0.16237 | -0.15605 | 0.010339 | 0.010339 | houston | N | 0.010339 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.029256 | houston | Y | -0.17099 | 0.16237 | -0.15605 | 0.010339 | 0.010339 | houston | N | 0.010339 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.029256 | houston | Y | -0.17099 | 0.16237 | -0.15605 | 0.010339 | 0.010339 | houston | N | 0.010339 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.065532 | houston | N | -0.20727 | 0.12609 | -0.19233 | -0.025937 | 0.025937 | houston | N | 0.025937 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.065532 | houston | N | -0.20727 | 0.12609 | -0.19233 | -0.025937 | 0.025937 | houston | N | 0.025937 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.049846 | houston | N | -0.19158 | 0.14178 | -0.17664 | -0.010251 | 0.010251 | houston | N | 0.010251 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.049846 | houston | N | -0.19158 | 0.14178 | -0.17664 | -0.010251 | 0.010251 | houston | N | 0.010251 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.049846 | houston | N | -0.19158 | 0.14178 | -0.17664 | -0.010251 | 0.010251 | houston | N | 0.010251 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.033979 | houston | N | -0.17572 | 0.15765 | -0.16077 | 0.0056159 | 0.0056159 | houston | N | 0.0056159 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.033979 | houston | N | -0.17572 | 0.15765 | -0.16077 | 0.0056159 | 0.0056159 | houston | N | 0.0056159 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.033979 | houston | N | -0.17572 | 0.15765 | -0.16077 | 0.0056159 | 0.0056159 | houston | N | 0.0056159 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.033979 | houston | N | -0.17572 | 0.15765 | -0.16077 | 0.0056159 | 0.0056159 | houston | N | 0.0056159 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.030946 | houston | N | -0.17268 | 0.16068 | -0.15774 | 0.0086489 | 0.0086489 | houston | N | 0.0086489 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.030946 | houston | N | -0.17268 | 0.16068 | -0.15774 | 0.0086489 | 0.0086489 | houston | N | 0.0086489 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.034893 | houston | N | -0.17663 | 0.15673 | -0.16169 | 0.0047019 | 0.0047019 | houston | N | 0.0047019 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.034893 | houston | N | -0.17663 | 0.15673 | -0.16169 | 0.0047019 | 0.0047019 | houston | N | 0.0047019 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.034893 | houston | N | -0.17663 | 0.15673 | -0.16169 | 0.0047019 | 0.0047019 | houston | N | 0.0047019 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.034893 | houston | N | -0.17663 | 0.15673 | -0.16169 | 0.0047019 | 0.0047019 | houston | N | 0.0047019 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.034893 | houston | N | -0.17663 | 0.15673 | -0.16169 | 0.0047019 | 0.0047019 | houston | N | 0.0047019 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.025449 | houston | Y | -0.16719 | 0.16618 | -0.15224 | 0.014146 | 0.014146 | houston | N | 0.014146 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.026994 | houston | Y | -0.16873 | 0.16463 | -0.15379 | 0.012601 | 0.012601 | houston | N | 0.012601 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.024984 | houston | Y | -0.16672 | 0.16664 | -0.15178 | 0.014611 | 0.014611 | houston | N | 0.014611 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.024984 | houston | Y | -0.16672 | 0.16664 | -0.15178 | 0.014611 | 0.014611 | houston | N | 0.014611 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.024984 | houston | Y | -0.16672 | 0.16664 | -0.15178 | 0.014611 | 0.014611 | houston | N | 0.014611 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.016414 | houston | N | -0.15815 | 0.17521 | -0.14321 | 0.023181 | 0.023181 | houston | N | 0.023181 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.029022 | houston | N | -0.17076 | 0.1626 | -0.15582 | 0.010573 | 0.010573 | houston | N | 0.010573 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.029022 | houston | N | -0.17076 | 0.1626 | -0.15582 | 0.010573 | 0.010573 | houston | N | 0.010573 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.023892 | houston | N | -0.16563 | 0.16773 | -0.15069 | 0.015703 | 0.015703 | houston | N | 0.015703 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.023892 | houston | N | -0.16563 | 0.16773 | -0.15069 | 0.015703 | 0.015703 | houston | N | 0.015703 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.023892 | houston | N | -0.16563 | 0.16773 | -0.15069 | 0.015703 | 0.015703 | houston | N | 0.015703 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.023892 | houston | N | -0.16563 | 0.16773 | -0.15069 | 0.015703 | 0.015703 | houston | N | 0.015703 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.030844 | houston | N | -0.17258 | 0.16078 | -0.15764 | 0.0087509 | 0.0087509 | houston | N | 0.0087509 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.030844 | houston | N | -0.17258 | 0.16078 | -0.15764 | 0.0087509 | 0.0087509 | houston | N | 0.0087509 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.030844 | houston | N | -0.17258 | 0.16078 | -0.15764 | 0.0087509 | 0.0087509 | houston | N | 0.0087509 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.030844 | houston | N | -0.17258 | 0.16078 | -0.15764 | 0.0087509 | 0.0087509 | houston | N | 0.0087509 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.031813 | houston | N | -0.17355 | 0.15981 | -0.15861 | 0.0077819 | 0.0077819 | houston | N | 0.0077819 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.031813 | houston | N | -0.17355 | 0.15981 | -0.15861 | 0.0077819 | 0.0077819 | houston | N | 0.0077819 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.031813 | houston | N | -0.17355 | 0.15981 | -0.15861 | 0.0077819 | 0.0077819 | houston | N | 0.0077819 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.031813 | houston | N | -0.17355 | 0.15981 | -0.15861 | 0.0077819 | 0.0077819 | houston | N | 0.0077819 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.031813 | houston | N | -0.17355 | 0.15981 | -0.15861 | 0.0077819 | 0.0077819 | houston | N | 0.0077819 | 0
48651 | EP_1_2 | 1 | 5 | -0.025531 | houston | N | -0.16727 | 0.16609 | -0.15233 | 0.014064 | 0.014064 | houston | N | 0.014064 | 0
48651 | EP_1_2 | 2 | 21 | -0.025531 | houston | N | -0.16727 | 0.16609 | -0.15233 | 0.014064 | 0.014064 | houston | N | 0.014064 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.044012 | north | N | -0.097727 | 0.23564 | -0.082782 | 0.083607 | 0.082782 | west | Y | 0.097727 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.044012 | north | N | -0.097727 | 0.23564 | -0.082782 | 0.083607 | 0.082782 | west | Y | 0.097727 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.044012 | north | N | -0.097727 | 0.23564 | -0.082782 | 0.083607 | 0.082782 | west | Y | 0.097727 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.044012 | north | N | -0.097727 | 0.23564 | -0.082782 | 0.083607 | 0.082782 | west | Y | 0.097727 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.023514 | houston | Y | -0.16525 | 0.16811 | -0.15031 | 0.016081 | 0.016081 | houston | N | 0.016081 | 0
48691 | GBY_7374 | A | 46 | -0.03262 | houston | Y | -0.17436 | 0.159 | -0.15941 | 0.0069749 | 0.0069749 | houston | N | 0.0069749 | 0
48691 | GBY_7374 | B | 46 | -0.03262 | houston | Y | -0.17436 | 0.159 | -0.15941 | 0.0069749 | 0.0069749 | houston | N | 0.0069749 | 0
48692 | GBY_8182 | C | 46 | -0.03262 | houston | Y | -0.17436 | 0.159 | -0.15941 | 0.0069749 | 0.0069749 | houston | N | 0.0069749 | 0
48692 | GBY_8182 | D | 55 | -0.03262 | houston | Y | -0.17436 | 0.159 | -0.15941 | 0.0069749 | 0.0069749 | houston | N | 0.0069749 | 0
48693 | GBY_8384 | E | 55 | -0.03262 | houston | Y | -0.17436 | 0.159 | -0.15941 | 0.0069749 | 0.0069749 | houston | N | 0.0069749 | 0
48693 | GBY_8384 | F | 54 | -0.03262 | houston | Y | -0.17436 | 0.159 | -0.15941 | 0.0069749 | 0.0069749 | houston | N | 0.0069749 | 0
48721 | LEG_1___ | 1 | 827 | 0.11162 | north | Y | -0.030119 | 0.30324 | -0.015174 | 0.15121 | 0.015174 | west | Y | 0.030119 | 12.3591
48722 | LEG_2___ | 2 | 819 | 0.11162 | north | Y | -0.030119 | 0.30324 | -0.015174 | 0.15121 | 0.015174 | west | Y | 0.030119 | 12.2395
48730 | MNS_GT | 1 | 46.1 | -0.050375 | houston | N | -0.19211 | 0.14125 | -0.17717 | -0.01078 | 0.01078 | houston | N | 0.01078 | 0
48731 | CBE_GT1 | 1 | 76 | -0.092257 | houston | Y | -0.234 | 0.099368 | -0.21905 | -0.052662 | 0.052662 | houston | N | 0.052662 | 0
48732 | CBE_GT2 | 1 | 76 | -0.092257 | houston | Y | -0.234 | 0.099368 | -0.21905 | -0.052662 | 0.052662 | houston | N | 0.052662 | 0
48733 | CBE_ST12 | 1 | 105 | -0.092257 | houston | Y | -0.234 | 0.099368 | -0.21905 | -0.052662 | 0.052662 | houston | N | 0.052662 | 0
48734 | CBE_GT3 | 1 | 74 | -0.092257 | houston | Y | -0.234 | 0.099368 | -0.21905 | -0.052662 | 0.052662 | houston | N | 0.052662 | 0
48735 | CBE_GT4 | 1 | 74 | -0.092257 | houston | Y | -0.234 | 0.099368 | -0.21905 | -0.052662 | 0.052662 | houston | N | 0.052662 | 0
48736 | CBE_ST34 | 1 | 102 | -0.092257 | houston | Y | -0.234 | 0.099368 | -0.21905 | -0.052662 | 0.052662 | houston | N | 0.052662 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.030816 | houston | N | -0.17255 | 0.16081 | -0.15761 | 0.0087789 | 0.0087789 | houston | N | 0.0087789 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.030816 | houston | N | -0.17255 | 0.16081 | -0.15761 | 0.0087789 | 0.0087789 | houston | N | 0.0087789 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.030816 | houston | N | -0.17255 | 0.16081 | -0.15761 | 0.0087789 | 0.0087789 | houston | N | 0.0087789 | 0
48761 | PR_GT1__ | 1 | 35 | -0.031433 | houston | N | -0.17317 | 0.16019 | -0.15823 | 0.0081619 | 0.0081619 | houston | N | 0.0081619 | 0
48772 | PHR_GN2_ | MB | 459 | -0.037224 | houston | Y | -0.17896 | 0.1544 | -0.16402 | 0.0023709 | 0.0023709 | houston | N | 0.0023709 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.025521 | houston | N | -0.16726 | 0.1661 | -0.15232 | 0.014074 | 0.014074 | houston | N | 0.014074 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.025521 | houston | N | -0.16726 | 0.1661 | -0.15232 | 0.014074 | 0.014074 | houston | N | 0.014074 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.025521 | houston | N | -0.16726 | 0.1661 | -0.15232 | 0.014074 | 0.014074 | houston | N | 0.014074 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.025521 | houston | N | -0.16726 | 0.1661 | -0.15232 | 0.014074 | 0.014074 | houston | N | 0.014074 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.025521 | houston | N | -0.16726 | 0.1661 | -0.15232 | 0.014074 | 0.014074 | houston | N | 0.014074 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.025521 | houston | N | -0.16726 | 0.1661 | -0.15232 | 0.014074 | 0.014074 | houston | N | 0.014074 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.025521 | houston | N | -0.16726 | 0.1661 | -0.15232 | 0.014074 | 0.014074 | houston | N | 0.014074 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.016414 | houston | N | -0.15815 | 0.17521 | -0.14321 | 0.023181 | 0.023181 | houston | N | 0.023181 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.016414 | houston | N | -0.15815 | 0.17521 | -0.14321 | 0.023181 | 0.023181 | houston | N | 0.023181 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.016414 | houston | N | -0.15815 | 0.17521 | -0.14321 | 0.023181 | 0.023181 | houston | N | 0.023181 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.016414 | houston | N | -0.15815 | 0.17521 | -0.14321 | 0.023181 | 0.023181 | houston | N | 0.023181 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.025168 | houston | N | -0.16691 | 0.16646 | -0.15196 | 0.014427 | 0.014427 | houston | N | 0.014427 | 0
48820 | SHELLG1_ | 1 | 71 | -0.030241 | houston | N | -0.17198 | 0.16138 | -0.15704 | 0.0093539 | 0.0093539 | houston | N | 0.0093539 | 0
48821 | SHELLG2 | 2 | 72 | -0.030241 | houston | N | -0.17198 | 0.16138 | -0.15704 | 0.0093539 | 0.0093539 | houston | N | 0.0093539 | 0
48822 | SHELLG3_ | 1 | 39 | -0.030241 | houston | N | -0.17198 | 0.16138 | -0.15704 | 0.0093539 | 0.0093539 | houston | N | 0.0093539 | 0
48822 | SHELLG3_ | 2 | 30 | -0.030241 | houston | N | -0.17198 | 0.16138 | -0.15704 | 0.0093539 | 0.0093539 | houston | N | 0.0093539 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.032281 | houston | N | -0.17402 | 0.15934 | -0.15908 | 0.0073139 | 0.0073139 | houston | N | 0.0073139 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.032281 | houston | N | -0.17402 | 0.15934 | -0.15908 | 0.0073139 | 0.0073139 | houston | N | 0.0073139 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.030852 | houston | N | -0.17259 | 0.16077 | -0.15765 | 0.0087429 | 0.0087429 | houston | N | 0.0087429 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.03097 | houston | Y | -0.17271 | 0.16065 | -0.15776 | 0.0086249 | 0.0086249 | houston | N | 0.0086249 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.031003 | houston | Y | -0.17274 | 0.16062 | -0.1578 | 0.0085919 | 0.0085919 | houston | N | 0.0085919 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.030862 | houston | Y | -0.1726 | 0.16076 | -0.15766 | 0.0087329 | 0.0087329 | houston | N | 0.0087329 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.03083 | houston | Y | -0.17257 | 0.16079 | -0.15762 | 0.0087649 | 0.0087649 | houston | N | 0.0087649 | 0
48855 | SRB_GT21 | B2 | 12 | -0.031026 | houston | Y | -0.17276 | 0.1606 | -0.15782 | 0.0085689 | 0.0085689 | houston | N | 0.0085689 | 0
48855 | SRB_GT21 | MB | 18 | -0.031026 | houston | Y | -0.17276 | 0.1606 | -0.15782 | 0.0085689 | 0.0085689 | houston | N | 0.0085689 | 0
48865 | TECO_GT1 | 1 | 50 | -0.039222 | houston | Y | -0.18096 | 0.1524 | -0.16602 | 0.00037295 | 0.00037295 | houston | N | 0.00037295 | 0
48873 | THW_ST3_ | 3 | 104 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48874 | THW_ST4_ | 4 | 104 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48875 | THW_3132 | A | 54 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48875 | THW_3132 | B | 53 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48877 | THW_3334 | C | 54 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48877 | THW_3334 | D | 57 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48879 | THW_4142 | E | 54 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48879 | THW_4142 | F | 54 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48881 | THW_4344 | G | 58 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48881 | THW_4344 | H | 58 | -0.027557 | houston | Y | -0.1693 | 0.16407 | -0.15435 | 0.012038 | 0.012038 | houston | N | 0.012038 | 0
48883 | THW_GT1_ | B2 | 12 | -0.026139 | houston | Y | -0.16788 | 0.16549 | -0.15293 | 0.013456 | 0.013456 | houston | N | 0.013456 | 0
48885 | THW_5152 | A | 56 | -0.022849 | houston | Y | -0.16459 | 0.16878 | -0.14964 | 0.016746 | 0.016746 | houston | N | 0.016746 | 0
48885 | THW_5152 | B | 59 | -0.022849 | houston | Y | -0.16459 | 0.16878 | -0.14964 | 0.016746 | 0.016746 | houston | N | 0.016746 | 0
48886 | THW_5354 | C | 56 | -0.022849 | houston | Y | -0.16459 | 0.16878 | -0.14964 | 0.016746 | 0.016746 | houston | N | 0.016746 | 0
48886 | THW_5354 | D | 56 | -0.022849 | houston | Y | -0.16459 | 0.16878 | -0.14964 | 0.016746 | 0.016746 | houston | N | 0.016746 | 0
48887 | THW_5556 | E | 59 | -0.022849 | houston | Y | -0.16459 | 0.16878 | -0.14964 | 0.016746 | 0.016746 | houston | N | 0.016746 | 0
48887 | THW_5556 | F | 56 | -0.022849 | houston | Y | -0.16459 | 0.16878 | -0.14964 | 0.016746 | 0.016746 | houston | N | 0.016746 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.086821 | houston | Y | -0.22856 | 0.1048 | -0.21362 | -0.047226 | 0.047226 | houston | N | 0.047226 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.048066 | houston | Y | -0.1898 | 0.14356 | -0.17486 | -0.0084711 | 0.0084711 | houston | N | 0.0084711 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.048066 | houston | Y | -0.1898 | 0.14356 | -0.17486 | -0.0084711 | 0.0084711 | houston | N | 0.0084711 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.048066 | houston | Y | -0.1898 | 0.14356 | -0.17486 | -0.0084711 | 0.0084711 | houston | N | 0.0084711 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.048066 | houston | Y | -0.1898 | 0.14356 | -0.17486 | -0.0084711 | 0.0084711 | houston | N | 0.0084711 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.048066 | houston | N | -0.1898 | 0.14356 | -0.17486 | -0.0084711 | 0.0084711 | houston | N | 0.0084711 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.049946 | houston | Y | -0.19168 | 0.14168 | -0.17674 | -0.010351 | 0.010351 | houston | N | 0.010351 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.049946 | houston | Y | -0.19168 | 0.14168 | -0.17674 | -0.010351 | 0.010351 | houston | N | 0.010351 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.049946 | houston | Y | -0.19168 | 0.14168 | -0.17674 | -0.010351 | 0.010351 | houston | N | 0.010351 | 0
48929 | WAPGT21_ | B1 | 13 | -0.048066 | houston | Y | -0.1898 | 0.14356 | -0.17486 | -0.0084711 | 0.0084711 | houston | N | 0.0084711 | 0
48940 | WARVUE_G | G1 | 12 | -0.025492 | houston | Y | -0.16723 | 0.16613 | -0.15229 | 0.014103 | 0.014103 | houston | N | 0.014103 | 0
49803 | EXN_15GT | 1 | 34 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49826 | EXN938GT | 5 | 45.9 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49828 | EXN941GT | 10 | 17.7 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49829 | EXN942GT | 11 | 20.4 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49830 | EXN943GT | 12 | 19.9 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49831 | EXN944GT | 13 | 35 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49832 | EXN945GT | 9 | 18 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49837 | EXN_GT | 4 | 85.4 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49838 | EXN_14GT | 14 | 148 | -0.026619 | houston | N | -0.16836 | 0.16501 | -0.15341 | 0.012976 | 0.012976 | houston | N | 0.012976 | 0
49851 | DOW17000 | 37 | 62 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49858 | DOW38100 | 31 | 71.4 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49859 | DOW38200 | 33 | 45 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49860 | DOW38300 | 32 | 101 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49862 | DOW39100 | 36 | 86 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49863 | DOW39200 | 35 | 88 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49865 | DOW41000 | 41 | 50 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49866 | DOW42000 | 42 | 18 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49869 | DOW49000 | 45 | 94 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49870 | DOW61000 | 61 | 70 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49871 | DOW62000 | 62 | 63 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49872 | DOW63000 | 63 | 72 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49873 | DOW64000 | 64 | 64.8 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49876 | DOW65000 | 65 | 101 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49877 | DOW66000 | 66 | 97 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49878 | DOW67000 | 67 | 103 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49882 | DOW81000 | 81 | 76 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49884 | DOW82000 | 82 | 80 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49885 | DOW83000 | 83 | 80 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
49886 | DOW84000 | 84 | 171 | -0.069684 | houston | N | -0.21142 | 0.12194 | -0.19648 | -0.030089 | 0.030089 | houston | N | 0.030089 | 0
58909 | PEARSALL | 1 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58909 | PEARSALL | 2 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58909 | PEARSALL | 3 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58909 | PEARSALL | 4 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58909 | PEARSALL | 5 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58909 | PEARSALL | 6 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58919 | PEARSALL | 1 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58919 | PEARSALL | 2 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58919 | PEARSALL | 3 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58919 | PEARSALL | 4 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58919 | PEARSALL | 5 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58919 | PEARSALL | 6 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58929 | PEARSALL | 1 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58929 | PEARSALL | 2 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58929 | PEARSALL | 3 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58929 | PEARSALL | 4 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58929 | PEARSALL | 5 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58929 | PEARSALL | 6 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58949 | PEARSALL | 1 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58949 | PEARSALL | 2 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58949 | PEARSALL | 3 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58949 | PEARSALL | 4 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58949 | PEARSALL | 5 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
58949 | PEARSALL | 6 | 8.4 | -0.15966 | south | Y | -0.3014 | 0.031963 | -0.28646 | -0.12007 | 0.031963 | south | N | 0.031963 | 0
60000 | DSKY2 | 1 | 76.5 | 0.10587 | west | Y | -0.035872 | 0.29749 | -0.020927 | 0.14546 | 0.020927 | west | N | 0.020927 | 0
60003 | KING_NE1 | 1 | 80 | 0.11169 | west | Y | -0.030045 | 0.30332 | -0.0151 | 0.15129 | 0.0151 | west | N | 0.0151 | 0
60005 | KING_SE1 | 1 | 40 | 0.11169 | west | Y | -0.030045 | 0.30332 | -0.0151 | 0.15129 | 0.0151 | west | N | 0.0151 | 0
60007 | KING_SW1 | 1 | 80 | 0.11263 | west | Y | -0.029112 | 0.30425 | -0.014167 | 0.15222 | 0.014167 | west | N | 0.014167 | 0
60016 | WOODWRD1 | 1 | 80 | 0.11149 | west | Y | -0.030247 | 0.30312 | -0.015302 | 0.15109 | 0.015302 | west | N | 0.015302 | 0
60017 | ORNNWP1 | 1 | 80 | 0.10668 | west | Y | -0.035057 | 0.29831 | -0.020112 | 0.14628 | 0.020112 | west | N | 0.020112 | 0
60018 | DSKY1 | 1 | 84 | 0.10511 | west | Y | -0.036631 | 0.29673 | -0.021686 | 0.1447 | 0.021686 | west | N | 0.021686 | 0
60019 | KING_NW1 | 1 | 80 | 0.11263 | west | Y | -0.029112 | 0.30425 | -0.014167 | 0.15222 | 0.014167 | west | N | 0.014167 | 0
60057 | CALLAHAN | 1 | 114 | -0.19154 | south | Y | -0.33327 | 8.9733e-05 | -0.31833 | -0.15194 | 8.9733e-05 | south | N | 8.9733e-05 | 0
60058 | BUFF_GAP | 1 | 120 | 0.12786 | west | Y | -0.013882 | 0.31948 | 0.0010626 | 0.16745 | 0.0010626 | west | N | 0.0010626 | 0
60060 | CIRELLO | 1 | 233 | 0.12786 | west | Y | -0.013882 | 0.31948 | 0.0010626 | 0.16745 | 0.0010626 | west | N | 0.0010626 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.12786 | west | Y | -0.013882 | 0.31948 | 0.0010626 | 0.16745 | 0.0010626 | west | N | 0.0010626 | 0
60066 | H_HOLLOW | 1 | 222 | -0.19154 | south | Y | -0.33327 | 8.9733e-05 | -0.31833 | -0.15194 | 8.9733e-05 | south | N | 8.9733e-05 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.19154 | south | Y | -0.33327 | 8.9733e-05 | -0.31833 | -0.15194 | 8.9733e-05 | south | N | 8.9733e-05 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.19154 | south | Y | -0.33327 | 8.9733e-05 | -0.31833 | -0.15194 | 8.9733e-05 | south | N | 8.9733e-05 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.19154 | south | Y | -0.33327 | 8.9733e-05 | -0.31833 | -0.15194 | 8.9733e-05 | south | N | 8.9733e-05 | 0
60074 | HORSH5 | 1 | 100 | -0.19154 | south | Y | -0.33327 | 8.9733e-05 | -0.31833 | -0.15194 | 8.9733e-05 | south | N | 8.9733e-05 | 0
60081 | WHRLWIND | 1 | 60 | 0.13303 | west | Y | -0.0087059 | 0.32466 | 0.0062386 | 0.17263 | 0.0062386 | west | N | 0.0062386 | 0
60201 | RIO DRCS | F | 0 | -0.10079 | south | N | -0.24253 | 0.09083 | -0.22759 | -0.0612 | 0.0612 | houston | Y | 0.09083 | 0
60202 | FRIEND_R | F | 0 | 0.080025 | west | N | -0.061714 | 0.27165 | -0.046769 | 0.11962 | 0.046769 | west | N | 0.046769 | 0
60203 | PRES0A | BT | 4.8 | 0.11611 | west | N | -0.025631 | 0.30773 | -0.010686 | 0.1557 | 0.010686 | west | N | 0.010686 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.13078 | west | Y | -0.010964 | 0.3224 | 0.0039806 | 0.17037 | 0.0039806 | west | N | 0.0039806 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.13078 | west | Y | -0.010964 | 0.3224 | 0.0039806 | 0.17037 | 0.0039806 | west | N | 0.0039806 | 0
71057 | L_SWEETW | W1 | 135 | 0.13078 | west | Y | -0.010964 | 0.3224 | 0.0039806 | 0.17037 | 0.0039806 | west | N | 0.0039806 | 0
71059 | L_SWEETW | W1 | 119 | 0.13078 | west | Y | -0.010964 | 0.3224 | 0.0039806 | 0.17037 | 0.0039806 | west | N | 0.0039806 | 0
71060 | L_SWEETW | W1 | 105 | 0.13078 | west | Y | -0.010964 | 0.3224 | 0.0039806 | 0.17037 | 0.0039806 | west | N | 0.0039806 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.13078 | west | Y | -0.010964 | 0.3224 | 0.0039806 | 0.17037 | 0.0039806 | west | N | 0.0039806 | 0
76031 | L_GASCCR | W1 | 150 | 0.12643 | west | Y | -0.015307 | 0.31806 | -0.00036243 | 0.16603 | 0.00036243 | west | N | 0.00036243 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.12586 | west | Y | -0.01588 | 0.31748 | -0.00093543 | 0.16545 | 0.00093543 | west | N | 0.00093543 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.12586 | west | Y | -0.01588 | 0.31748 | -0.00093543 | 0.16545 | 0.00093543 | west | N | 0.00093543 | 0
76096 | L_CAPRSI | W1 | 186 | 0.12586 | west | Y | -0.01588 | 0.31748 | -0.00093543 | 0.16545 | 0.00093543 | west | N | 0.00093543 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.12586 | west | Y | -0.01588 | 0.31748 | -0.00093543 | 0.16545 | 0.00093543 | west | N | 0.00093543 | 0
80003 | MILHWYS | F | 0 | -0.15183 | south | N | -0.29357 | 0.039795 | -0.27862 | -0.11224 | 0.039795 | south | N | 0.039795 | 0
80010 | EPLVT1 | F | 0 | -0.11564 | south | N | -0.25738 | 0.075981 | -0.24244 | -0.076049 | 0.075981 | south | N | 0.075981 | 0
80012 | LAR | F | 0 | -0.16031 | south | N | -0.30204 | 0.031319 | -0.2871 | -0.12071 | 0.031319 | south | N | 0.031319 | 0
80051 | FORPVCM0 | 8 | 28 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
80053 | FOR69CG0 | 10 | 74 | -0.13787 | south | N | -0.27961 | 0.053755 | -0.26466 | -0.098275 | 0.053755 | south | N | 0.053755 | 0
80080 | GWINDT11 | 1 | 94 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80080 | GWINDT11 | 2 | 41 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80080 | GWINDT11 | 3 | 38 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80080 | GWINDT11 | 4 | 19 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80081 | GWINDT21 | 1 | 94 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80081 | GWINDT21 | 2 | 36 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80081 | GWINDT21 | 3 | 43 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80081 | GWINDT21 | 4 | 22 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80137 | CSDR89 | 8 | 39 | -0.14315 | south | N | -0.28489 | 0.048472 | -0.26995 | -0.10356 | 0.048472 | south | N | 0.048472 | 0
80137 | CSDR89 | 9 | 15 | -0.14315 | south | N | -0.28489 | 0.048472 | -0.26995 | -0.10356 | 0.048472 | south | N | 0.048472 | 0
80138 | CSDR7 | 7 | 7 | -0.14315 | south | N | -0.28489 | 0.048472 | -0.26995 | -0.10356 | 0.048472 | south | N | 0.048472 | 0
80139 | CSDR56 | 5 | 15 | -0.14315 | south | N | -0.28489 | 0.048472 | -0.26995 | -0.10356 | 0.048472 | south | N | 0.048472 | 0
80139 | CSDR56 | 6 | 39 | -0.14315 | south | N | -0.28489 | 0.048472 | -0.26995 | -0.10356 | 0.048472 | south | N | 0.048472 | 0
80140 | CSDR11 | 11 | 39 | -0.14315 | south | N | -0.28489 | 0.048472 | -0.26995 | -0.10356 | 0.048472 | south | N | 0.048472 | 0
80180 | PNSCALT1 | 1 | 148 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80180 | PNSCALT1 | 2 | 50 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80181 | PNSCALT2 | 1 | 55 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80181 | PNSCALT2 | 2 | 50 | -0.15172 | south | Y | -0.29346 | 0.039901 | -0.27852 | -0.11213 | 0.039901 | south | N | 0.039901 | 0
80223 | REYSHR G | 1 | 12 | -0.14858 | south | N | -0.29032 | 0.043047 | -0.27537 | -0.10898 | 0.043047 | south | N | 0.043047 | 0
80224 | VISTRONG | 1 | 15 | -0.14485 | south | N | -0.28659 | 0.046778 | -0.27164 | -0.10525 | 0.046778 | south | N | 0.046778 | 0
80225 | VISTRONG | 2 | 23 | -0.14485 | south | N | -0.28659 | 0.046778 | -0.27164 | -0.10525 | 0.046778 | south | N | 0.046778 | 0
80226 | ALCOA G | 1 | 48 | -0.13911 | south | N | -0.28085 | 0.052511 | -0.26591 | -0.099519 | 0.052511 | south | N | 0.052511 | 0
80227 | AIRCO G | 1 | 8 | -0.14375 | south | N | -0.28549 | 0.047871 | -0.27055 | -0.10416 | 0.047871 | south | N | 0.047871 | 0
80261 | NBEC81A | 1 | 180 | -0.15022 | south | Y | -0.29196 | 0.041407 | -0.27701 | -0.11062 | 0.041407 | south | N | 0.041407 | 0
80262 | NBEC91A | 1 | 180 | -0.15017 | south | Y | -0.29191 | 0.041455 | -0.27696 | -0.11058 | 0.041455 | south | N | 0.041455 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.15052 | south | Y | -0.29226 | 0.041102 | -0.27732 | -0.11093 | 0.041102 | south | N | 0.041102 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.15052 | south | Y | -0.29226 | 0.041102 | -0.27732 | -0.11093 | 0.041102 | south | N | 0.041102 | 0
80265 | LARECU40 | 4 | 100 | -0.16032 | south | Y | -0.30206 | 0.031305 | -0.28711 | -0.12073 | 0.031305 | south | N | 0.031305 | 0
80266 | LARECU50 | 5 | 100 | -0.16032 | south | Y | -0.30206 | 0.031305 | -0.28711 | -0.12073 | 0.031305 | south | N | 0.031305 | 0
80291 | PAPALOTE | 1 | 25 | -0.14921 | south | Y | -0.29094 | 0.042419 | -0.276 | -0.10961 | 0.042419 | south | N | 0.042419 | 0
80291 | PAPALOTE | 2 | 25 | -0.14921 | south | Y | -0.29094 | 0.042419 | -0.276 | -0.10961 | 0.042419 | south | N | 0.042419 | 0
80291 | PAPALOTE | 3 | 25 | -0.14921 | south | Y | -0.29094 | 0.042419 | -0.276 | -0.10961 | 0.042419 | south | N | 0.042419 | 0
80291 | PAPALOTE | 4 | 16 | -0.14921 | south | Y | -0.29094 | 0.042419 | -0.276 | -0.10961 | 0.042419 | south | N | 0.042419 | 0
80294 | PAPALOTE | 5 | 25 | -0.14921 | south | Y | -0.29094 | 0.042419 | -0.276 | -0.10961 | 0.042419 | south | N | 0.042419 | 0
80294 | PAPALOTE | 6 | 25 | -0.14921 | south | Y | -0.29094 | 0.042419 | -0.276 | -0.10961 | 0.042419 | south | N | 0.042419 | 0
80294 | PAPALOTE | 7 | 25 | -0.14921 | south | Y | -0.29094 | 0.042419 | -0.276 | -0.10961 | 0.042419 | south | N | 0.042419 | 0
80294 | PAPALOTE | 8 | 15 | -0.14921 | south | Y | -0.29094 | 0.042419 | -0.276 | -0.10961 | 0.042419 | south | N | 0.042419 | 0
86104 | CID-138 | EQ | 0 | -0.16032 | south | N | -0.30206 | 0.031305 | -0.28711 | -0.12073 | 0.031305 | south | N | 0.031305 | 0
86105 | CID-230 | EQ | 500 | -0.16032 | south | N | -0.30206 | 0.031305 | -0.28711 | -0.12073 | 0.031305 | south | N | 0.031305 | 0
86106 | CUF-230 | EQ | 500 | -0.16032 | south | N | -0.30206 | 0.031305 | -0.28711 | -0.12073 | 0.031305 | south | N | 0.031305 | 0
86107 | CUF-138 | EQ | 0 | -0.16032 | south | N | -0.30206 | 0.031305 | -0.28711 | -0.12073 | 0.031305 | south | N | 0.031305 | 0
88198 | BEEVILLE | F | 0 | -0.15896 | south | N | -0.30069 | 0.03267 | -0.28575 | -0.11936 | 0.03267 | south | N | 0.03267 | 0
88253 | HAMILTON | F | 0 | -0.087145 | south | N | -0.22888 | 0.10448 | -0.21394 | -0.04755 | 0.04755 | houston | Y | 0.10448 | 0
88299 | ZAPATA | F | 0 | -0.15618 | south | N | -0.29792 | 0.035446 | -0.28297 | -0.11658 | 0.035446 | south | N | 0.035446 | 0
88508 | FALFURRI | F | 0 | -0.15437 | south | N | -0.29611 | 0.037253 | -0.28117 | -0.11478 | 0.037253 | south | N | 0.037253 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3409 LAKE_CRK 3414 TEMP_SS_ctg1 C:3405 THOUSE__3412 TEMP_PEC | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0 | 0 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0 | 0 | 0 | Weighted Shift Factors
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0 | 0 | 0 | South | -0.19162
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0 | 0 | 0 | North | 0.15292
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.19162 | 0 | 0 | 0 |  | -0.34454
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.19162 | 0 | 0 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8396 | 0 | 0.17521 | 0 | 0 | 0 | Line Rating | 1239.6
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5606 | 0 | 0.17521 | 0 | 0 | 0 | Conc Gen | 2023
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5278 | 0 | 0.17521 | 0 | 0 | 0 | Weighted Imp. | 338.064
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5278 | 0 | 0.17521 | 0 | 0 | 0 | PTDF | 0.16711
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.016414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6591 | 0 | 0.17521 | 0 | 0 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2795 | 56 | 0.16878 | 9.4514 | 56 | 9.4514 | Concentration | -0.48502
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3481 | 59 | 0.16878 | 9.9578 | 115 | 19.4092
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2795 | 56 | 0.16878 | 9.4514 | 171 | 28.8607
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2795 | 56 | 0.16878 | 9.4514 | 227 | 38.3121
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3481 | 59 | 0.16878 | 9.9578 | 286 | 48.2699
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2795 | 56 | 0.16878 | 9.4514 | 342 | 57.7213
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.023514 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.3586 | 398 | 0.16811 | 66.9081 | 740 | 124.6294
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8896 | 0 | 0.16773 | 0 | 740 | 124.6294
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8562 | 0 | 0.16773 | 0 | 740 | 124.6294
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7964 | 0 | 0.16773 | 0 | 740 | 124.6294
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4317 | 0 | 0.16773 | 0 | 740 | 124.6294
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.024984 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2972 | 172 | 0.16664 | 28.6622 | 912 | 153.2916
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.024984 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2972 | 172 | 0.16664 | 28.6622 | 1084 | 181.9538
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.024984 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2972 | 172 | 0.16664 | 28.6622 | 1256 | 210.616
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.025168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.9514 | 0 | 0.16646 | 0 | 1256 | 210.616
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.025449 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -18.9086 | 743 | 0.16618 | 123.4686 | 1999 | 334.0846
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.025492 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.3059 | 12 | 0.16613 | 1.9936 | 2011 | 336.0782
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6589 | 0 | 0.1661 | 0 | 2011 | 336.0782
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6844 | 0 | 0.1661 | 0 | 2011 | 336.0782
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7865 | 0 | 0.1661 | 0 | 2011 | 336.0782
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6078 | 0 | 0.1661 | 0 | 2011 | 336.0782
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5823 | 0 | 0.1661 | 0 | 2011 | 336.0782
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6542 | 0 | 0.1661 | 0 | 2011 | 336.0782
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5057 | 0 | 0.1661 | 0 | 2011 | 336.0782
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.025531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12765 | 0 | 0.16609 | 0 | 2011 | 336.0782
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.025531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53615 | 0 | 0.16609 | 0 | 2011 | 336.0782
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.026139 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31367 | 12 | 0.16549 | 1.9858 | 2023 | 338.064
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90505 | 0 | 0.16501 | 0 | 2023 | 338.064
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92368 | 0 | 0.16501 | 0 | 2023 | 338.064
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.87044 | 0 | 0.16501 | 0 | 2023 | 338.064
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2218 | 0 | 0.16501 | 0 | 2023 | 338.064
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47116 | 0 | 0.16501 | 0 | 2023 | 338.064
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54303 | 0 | 0.16501 | 0 | 2023 | 338.064
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52972 | 0 | 0.16501 | 0 | 2023 | 338.064
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93166 | 0 | 0.16501 | 0 | 2023 | 338.064
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47914 | 0 | 0.16501 | 0 | 2023 | 338.064
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2733 | 0 | 0.16501 | 0 | 2023 | 338.064
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9396 | 0 | 0.16501 | 0 | 2023 | 338.064
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.026994 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -19.8406 | 735 | 0.16463 | 121.0036
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8659 | 104 | 0.16407 | 17.063
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8659 | 104 | 0.16407 | 17.063
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4881 | 54 | 0.16407 | 8.8597
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4605 | 53 | 0.16407 | 8.6956
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4881 | 54 | 0.16407 | 8.8597
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5707 | 57 | 0.16407 | 9.3519
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4881 | 54 | 0.16407 | 8.8597
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4881 | 54 | 0.16407 | 8.8597
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5983 | 58 | 0.16407 | 9.5159
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5983 | 58 | 0.16407 | 9.5159
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.029022 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0208 | 0 | 0.1626 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.029022 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.918 | 0 | 0.1626 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2288 | 42 | 0.16237 | 6.8195
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2288 | 42 | 0.16237 | 6.8195
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1117 | 38 | 0.16237 | 6.17
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1117 | 38 | 0.16237 | 6.17
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.029329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.9887 | 0 | 0.1623 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1471 | 0 | 0.16138 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1774 | 0 | 0.16138 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1794 | 0 | 0.16138 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90723 | 0 | 0.16138 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.030816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.5469 | 0 | 0.16081 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.030816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8874 | 0 | 0.16081 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.030816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8381 | 0 | 0.16081 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.03083 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.0292 | 228 | 0.16079 | 36.6612
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.974 | 0 | 0.16078 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9493 | 0 | 0.16078 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5477 | 0 | 0.16078 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2701 | 0 | 0.16078 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.030852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4998 | 0 | 0.16077 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.030862 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.5736 | 213 | 0.16076 | 34.2425
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.030946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.611 | 0 | 0.16068 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.030946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0146 | 0 | 0.16068 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.03097 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.1101 | 165 | 0.16065 | 26.508
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.031003 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.2395 | 169 | 0.16062 | 27.1451
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.031026 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.37231 | 12 | 0.1606 | 1.9272
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.031026 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1606 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.031433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1002 | 0 | 0.16019 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1919 | 0 | 0.15981 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9978 | 0 | 0.15981 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.0105 | 0 | 0.15981 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9946 | 0 | 0.15981 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.5577 | 0 | 0.15981 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.032281 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5179 | 0 | 0.15934 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.032281 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5825 | 0 | 0.15934 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5005 | 46 | 0.159 | 7.3142
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5005 | 46 | 0.159 | 7.3142
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5005 | 46 | 0.159 | 7.3142
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7941 | 55 | 0.159 | 8.7453
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7941 | 55 | 0.159 | 8.7453
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7615 | 54 | 0.159 | 8.5863
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2086 | 0 | 0.15765 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0387 | 0 | 0.15765 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2086 | 0 | 0.15765 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2086 | 0 | 0.15765 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1753 | 0 | 0.15673 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0566 | 0 | 0.15673 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0357 | 0 | 0.15673 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9017 | 0 | 0.15673 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42569 | 0 | 0.15673 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.037224 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1544 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.039222 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9611 | 50 | 0.1524 | 7.6201
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9583 | 0 | 0.14984 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.787 | 0 | 0.14984 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2146 | 0 | 0.14984 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.4013 | 0 | 0.14984 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.4138 | 0 | 0.14984 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3637 | 0 | 0.14984 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0113 | 0 | 0.14984 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1953 | 0 | 0.14984 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6714 | 0 | 0.14984 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.041815 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3381 | 0 | 0.14981 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.041815 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2545 | 0 | 0.14981 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1942 | 0 | 0.14981 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8848 | 0 | 0.14981 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2946 | 0 | 0.14981 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2653 | 0 | 0.14981 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.048066 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.7386 | 161 | 0.14356 | 23.113
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.048066 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.979 | 166 | 0.14356 | 23.8307
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.048066 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.9204 | 248 | 0.14356 | 35.6026
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.048066 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.244 | 546 | 0.14356 | 78.3831
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.048066 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -30.9064 | 0 | 0.14356 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.048066 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.62486 | 13 | 0.14356 | 1.8663
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.048601 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6038 | 0 | 0.14302 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.049846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.1249 | 0 | 0.14178 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.049846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.1249 | 0 | 0.14178 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.049846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.2123 | 0 | 0.14178 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.049946 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -32.5148 | 651 | 0.14168 | 92.2329
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.049946 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -28.1695 | 564 | 0.14168 | 79.9068
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.049946 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -29.9676 | 600 | 0.14168 | 85.0072
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.050375 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3223 | 0 | 0.14125 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.9099 | 0 | 0.12937 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.9099 | 0 | 0.12937 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.4079 | 0 | 0.12937 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8165 | 0 | 0.12937 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.065532 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6528 | 0 | 0.12609 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.065532 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65532 | 0 | 0.12609 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3204 | 0 | 0.12194 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9754 | 0 | 0.12194 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1358 | 0 | 0.12194 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0381 | 0 | 0.12194 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9928 | 0 | 0.12194 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1322 | 0 | 0.12194 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4842 | 0 | 0.12194 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2543 | 0 | 0.12194 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5503 | 0 | 0.12194 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8779 | 0 | 0.12194 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3901 | 0 | 0.12194 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0172 | 0 | 0.12194 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5155 | 0 | 0.12194 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0381 | 0 | 0.12194 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.7593 | 0 | 0.12194 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1775 | 0 | 0.12194 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.296 | 0 | 0.12194 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5747 | 0 | 0.12194 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5747 | 0 | 0.12194 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.916 | 0 | 0.12194 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.086821 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.7302 | 66 | 0.1048 | 6.917
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.087145 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8758 | 0 | 0.10448 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.087145 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1786 | 0 | 0.10448 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.087145 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.10448 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.0115 | 76 | 0.099368 | 7.5519
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.0115 | 76 | 0.099368 | 7.5519
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.687 | 105 | 0.099368 | 10.4336
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.827 | 74 | 0.099368 | 7.3532
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.827 | 74 | 0.099368 | 7.3532
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4102 | 102 | 0.099368 | 10.1355
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.092891 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -123.8237 | 0 | 0.098734 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.092891 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -123.3592 | 0 | 0.098734 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.24375 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.090833 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.24375 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 191.8297 | 787 | 0.090833 | 71.4853
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.11027 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6616 | 0 | 0.081358 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.11564 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.075981 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.8917 | 0 | 0.053755 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.1675 | 0 | 0.053755 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.8917 | 0 | 0.053755 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.0296 | 0 | 0.053755 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.809 | 0 | 0.053755 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4468 | 0 | 0.053755 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.342 | 0 | 0.053755 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8604 | 0 | 0.053755 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0111 | 0 | 0.053755 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.2024 | 0 | 0.053755 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.13911 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.6775 | 0 | 0.052511 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.0083 | 0 | 0.048472 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0021 | 0 | 0.048472 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.583 | 0 | 0.048472 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1473 | 0 | 0.048472 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0021 | 0 | 0.048472 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1473 | 0 | 0.048472 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.583 | 0 | 0.048472 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.583 | 0 | 0.048472 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.14375 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.15 | 0 | 0.047871 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.14485 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1727 | 0 | 0.046778 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.14485 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3315 | 0 | 0.046778 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.14614 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.2151 | 22 | 0.045484 | 1.0006
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14614 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6076 | 11 | 0.045484 | 0.50032
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14614 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6076 | 11 | 0.045484 | 0.50032
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.19712 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 50.2669 | 255 | 0.04421 | 11.2735
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.19712 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 29.3716 | 149 | 0.04421 | 6.5872
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.19712 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 30.1601 | 153 | 0.04421 | 6.7641
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0362 | 47.7 | 0.044115 | 2.1043
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.5021 | 37.3 | 0.044115 | 1.6455
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7855 | 46 | 0.044115 | 2.0293
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0805 | 48 | 0.044115 | 2.1175
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.14783 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.7917 | 0 | 0.043794 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.4753 | 0 | 0.043047 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.7324 | 0 | 0.043047 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -14.8578 | 0 | 0.043047 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.5438 | 0 | 0.043047 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.841 | 0 | 0.043047 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -18.8694 | 0 | 0.043047 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.14858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7829 | 0 | 0.043047 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 25 | 0.042419 | 1.0605
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 25 | 0.042419 | 1.0605
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 25 | 0.042419 | 1.0605
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.3873 | 16 | 0.042419 | 0.6787
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 25 | 0.042419 | 1.0605
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 25 | 0.042419 | 1.0605
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 25 | 0.042419 | 1.0605
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2381 | 15 | 0.042419 | 0.63628
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.14954 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.5332 | 144 | 0.042089 | 6.0608
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.14954 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.1128 | 188 | 0.042089 | 7.9127
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.15017 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -50.4571 | 336 | 0.041455 | 13.9288
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.15017 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.0306 | 180 | 0.041455 | 7.4619
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.15019 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.2729 | 0 | 0.041437 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.15019 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.3179 | 0 | 0.041437 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.15019 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.9788 | 0 | 0.041437 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.15022 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.0392 | 180 | 0.041407 | 7.4532
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.15052 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -50.2747 | 334 | 0.041102 | 13.728
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.15052 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -51.1778 | 340 | 0.041102 | 13.9746
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.15052 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.0941 | 180 | 0.041102 | 7.3983
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.15052 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.0941 | 180 | 0.041102 | 7.3983
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.15058 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7645 | 0 | 0.041047 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.15058 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7645 | 0 | 0.041047 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.15073 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7278 | 0 | 0.040894 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.15074 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7282 | 0 | 0.040883 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.15148 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.3929 | 0 | 0.040147 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.2621 | 94 | 0.039901 | 3.7507
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.2207 | 41 | 0.039901 | 1.6359
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7655 | 38 | 0.039901 | 1.5162
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8828 | 19 | 0.039901 | 0.75811
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.2621 | 94 | 0.039901 | 3.7507
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4621 | 36 | 0.039901 | 1.4364
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5241 | 43 | 0.039901 | 1.7157
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3379 | 22 | 0.039901 | 0.87782
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.4552 | 148 | 0.039901 | 5.9053
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.5862 | 50 | 0.039901 | 1.995
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.3448 | 55 | 0.039901 | 2.1945
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.5862 | 50 | 0.039901 | 1.995
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.15183 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039795 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.15183 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.7695 | 38 | 0.039795 | 1.5122
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.15183 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.9303 | 19.3 | 0.039795 | 0.76804
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.15183 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2774 | 15 | 0.039795 | 0.59692
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.15183 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.136 | 47 | 0.039795 | 1.8704
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9063 | 144 | 0.039498 | 5.6877
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9063 | 144 | 0.039498 | 5.6877
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0137 | 171 | 0.039498 | 6.7541
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.4913 | 207 | 0.039493 | 8.175
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.967 | 216.7 | 0.039493 | 8.5581
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.8159 | 242 | 0.039493 | 9.5572
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.15244 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.3323 | 146.5 | 0.039186 | 5.7407
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.15244 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.5457 | 147.9 | 0.039186 | 5.7956
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.15244 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.3719 | 173 | 0.039186 | 6.7791
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.15435 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8522 | 0 | 0.037275 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.15435 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6979 | 0 | 0.037275 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.15435 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8522 | 0 | 0.037275 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.15437 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.037253 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.15618 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.035446 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.15682 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -98.641 | 629 | 0.034803 | 21.8909
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.15896 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.03267 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.16031 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031319 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.16032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -16.032 | 100 | 0.031305 | 3.1305
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.16032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -16.032 | 100 | 0.031305 | 3.1305
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.16032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031305 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.16032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031305 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.16032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031305 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.16032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031305 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.16151 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.8762 | 24 | 0.030115 | 0.72275
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.16151 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.8762 | 24 | 0.030115 | 0.72275
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.16151 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.7147 | 23 | 0.030115 | 0.69264
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.17421 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.021295 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.17421 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.021295 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.17135 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -67.8534 | 396 | 0.020278 | 8.03
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.16628 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.9425 | 150 | 0.013368 | 2.0051
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.16628 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.3026 | 80 | 0.013368 | 1.0694
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.18085 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1702 | 0 | 0.010771 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.18132 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -99.0002 | 546 | 0.010306 | 5.6269
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.18132 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -135.9892 | 750 | 0.010306 | 7.7293
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.1816 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.5325 | 58 | 0.01003 | 0.58172
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.1816 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.162 | 89 | 0.01003 | 0.89265
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9902 | 44 | 0.01003 | 0.44131
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9902 | 44 | 0.01003 | 0.44131
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8086 | 43 | 0.01003 | 0.43128
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.1718 | 45 | 0.01003 | 0.45134
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.16262 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.4393 | 0 | 0.0097076 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.16262 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.4393 | 0 | 0.0097076 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.18226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.2495 | 155 | 0.0093697 | 1.4523
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.18226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -30.9834 | 170 | 0.0093697 | 1.5929
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.18226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.2495 | 155 | 0.0093697 | 1.4523
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.18262 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.328 | 407 | 0.0090007 | 3.6633
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.18271 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -38.1853 | 209 | 0.0089197 | 1.8642
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.18271 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -39.4643 | 216 | 0.0089197 | 1.9267
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4044 | 46 | 0.0089197 | 0.41031
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.5871 | 47 | 0.0089197 | 0.41923
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4044 | 46 | 0.0089197 | 0.41031
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4044 | 46 | 0.0089197 | 0.41031
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.18291 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -75.361 | 412 | 0.0087097 | 3.5884
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.18291 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.166 | 400 | 0.0087097 | 3.4839
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.18305 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -77.6132 | 424 | 0.0085747 | 3.6357
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.18305 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -77.7963 | 425 | 0.0085747 | 3.6443
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.18358 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0080467 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.18358 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0080467 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.18358 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0080467 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.16064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7621 | 216.4 | 0.0077226 | 1.6712
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.16064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7139 | 216.1 | 0.0077226 | 1.6689
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.8832 | 224 | 0.0072776 | 1.6302
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 36.2036 | 226 | 0.0072776 | 1.6447
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.9609 | 212 | 0.0072776 | 1.5429
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.8007 | 211 | 0.0072776 | 1.5356
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5943 | 147 | 0.0039087 | 0.57458
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.9048 | 138 | 0.0039087 | 0.53941
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.2802 | 140 | 0.0039087 | 0.54722
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5943 | 147 | 0.0039087 | 0.57458
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.1643 | 182 | 0.0039087 | 0.71139
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.1678 | 198 | 0.0039087 | 0.77393
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.1541 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.8896 | 168 | 0.0011896 | 0.19986
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.1541 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8695 | 90 | 0.0011896 | 0.10707
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.15327 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.5436 | 395 | 0.00035964 | 0.14206
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.15327 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 66.6746 | 435 | 0.00035964 | 0.15644
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.835 | 114 | 8.9733e-05 | 0.01023
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -42.5208 | 222 | 8.9733e-05 | 0.019921
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.2424 | 184 | 8.9733e-05 | 0.016511
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -42.9038 | 224 | 8.9733e-05 | 0.0201
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.0265 | 115 | 8.9733e-05 | 0.010319
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.15298 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 66.5476 | 435 | 6.7638e-05 | 0.029423
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.19262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.77047 | 0 | -0.00099227 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19277 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46264 | 0 | -0.0011413 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19277 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46264 | 0 | -0.0011413 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.15118 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0017344 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.15071 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.7482 | 217.3 | -0.0022104 | -0.48031
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.15071 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.8945 | 205 | -0.0022104 | -0.45312
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.15071 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.052 | 272.4 | -0.0022104 | -0.6021
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.5383 | 70 | -0.0023684 | -0.16579
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.3877 | 69 | -0.0023684 | -0.16342
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.3877 | 69 | -0.0023684 | -0.16342
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.2372 | 68 | -0.0023684 | -0.16105
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.15014 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0027744 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.15014 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0027744 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.15014 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0027744 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.15004 | north | 3 | N | N | Nnorth | Nnorth | 1 | 173.6009 | 0 | -0.0028714 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.15004 | north | 3 | N | N | Nnorth | Nnorth | 1 | 173.751 | 0 | -0.0028714 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.6474 | 142 | -0.0030753 | -0.43669
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.2315 | 145 | -0.0030753 | -0.44591
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.3997 | 151 | -0.0030753 | -0.46437
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -56.463 | 290 | -0.0030753 | -0.89183
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14982 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.6791 | 118 | -0.0030924 | -0.3649
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14982 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 17.2296 | 115 | -0.0030924 | -0.35562
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14982 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 83.3016 | 556 | -0.0030924 | -1.7194
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.2328 | 196 | -0.0037684 | -0.7386
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.5553 | 111 | -0.0037684 | -0.41829
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19548 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46914 | 0 | -0.0038513 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19548 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46914 | 0 | -0.0038513 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.19548 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54733 | 0 | -0.0038513 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14858 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.9145 | 60 | -0.0043404 | -0.26042
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14858 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.3602 | 63 | -0.0043404 | -0.27344
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14838 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0045304 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14828 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0046324 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14781 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0051024 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14781 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0051024 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.14775 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 42.5523 | 288 | -0.0051644 | -1.4873
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.14775 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7194 | 147 | -0.0051644 | -0.75916
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.14775 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7194 | 147 | -0.0051644 | -0.75916
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.14766 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.6115 | 112.5 | -0.0052574 | -0.59145
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14762 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.9048 | 0 | -0.0052944 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14762 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.9048 | 0 | -0.0052944 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14752 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 25.0782 | 170 | -0.0053964 | -0.91738
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14752 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 76.7099 | 520 | -0.0053964 | -2.8061
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.14747 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6545 | 18 | -0.0054414 | -0.097945
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.14747 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6545 | 18 | -0.0054414 | -0.097945
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.14747 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.604 | 38 | -0.0054414 | -0.20677
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14742 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 54.5458 | 370 | -0.0054944 | -2.0329
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.6389 | 0 | -0.0054944 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.7864 | 0 | -0.0054944 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 45.5531 | 0 | -0.0054944 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.0812 | 0 | -0.0054944 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.2286 | 0 | -0.0054944 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 45.7005 | 0 | -0.0054944 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.572 | 160 | -0.0055904 | -0.89446
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9827 | 156 | -0.0055904 | -0.8721
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8757 | 196 | -0.0055904 | -1.0957
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9827 | 156 | -0.0055904 | -0.8721
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.13 | 157 | -0.0055904 | -0.87769
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.1703 | 198 | -0.0055904 | -1.1069
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14726 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 57.1373 | 388 | -0.0056544 | -2.1939
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14726 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.8394 | 515 | -0.0056544 | -2.912
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.14722 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.0416 | 0 | -0.0056944 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.14722 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.7188 | 0 | -0.0056944 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.14722 | north | 8 | N | N | Nnorth | Nnorth | 1 | 13.0143 | 0 | -0.0056944 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.8882 | 40 | -0.0057114 | -0.22845
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.6287 | 79 | -0.0057164 | -0.45159
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.6031 | 106 | -0.0057164 | -0.60593
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 21.4911 | 146 | -0.0057164 | -0.83459
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.1472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.1871 | 76 | -0.0057164 | -0.43444
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14718 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 82.1281 | 558 | -0.0057324 | -3.1987
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14718 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 85.219 | 579 | -0.0057324 | -3.319
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14718 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 118.9239 | 808 | -0.0057324 | -4.6317
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.14702 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.9404 | 20 | -0.0058964 | -0.11793
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.14702 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.6755 | 25 | -0.0058964 | -0.14741
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.14702 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.0278 | 41 | -0.0058964 | -0.24175
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.14633 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8505 | 204 | -0.0065894 | -1.3442
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.14633 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.4115 | 201 | -0.0065894 | -1.3245
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.14633 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.4109 | 242 | -0.0065894 | -1.5946
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5248 | 161 | -0.0067984 | -1.0945
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.9632 | 164 | -0.0067984 | -1.1149
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.9632 | 164 | -0.0067984 | -1.1149
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 60.4924 | 414 | -0.0067984 | -2.8145
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.671 | 162 | -0.0067984 | -1.1013
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5248 | 161 | -0.0067984 | -1.0945
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.8171 | 163 | -0.0067984 | -1.1081
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 59.7619 | 409 | -0.0067984 | -2.7805
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.14563 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.6308 | 73 | -0.0072874 | -0.53198
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.14563 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.3297 | 119 | -0.0072874 | -0.8672
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.14563 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.8537 | 205 | -0.0072874 | -1.4939
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.14563 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.8541 | 102 | -0.0072874 | -0.74331
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.14563 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.9803 | 96 | -0.0072874 | -0.69959
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.14443 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.7332 | 0 | -0.0084844 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.14443 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.7332 | 0 | -0.0084844 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.14426 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 17.3117 | 120 | -0.0086514 | -1.0382
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.20051 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.747 | 0 | -0.0088863 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.14319 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 32.075 | 224 | -0.0097234 | -2.178
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8506 | 20 | -0.010383 | -0.20767
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8506 | 20 | -0.010383 | -0.20767
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8506 | 20 | -0.010383 | -0.20767
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.423 | 17 | -0.010383 | -0.17652
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.2403 | 223.9 | -0.010431 | -2.3356
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.4626 | 225 | -0.010431 | -2.347
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.3818 | 224.6 | -0.010431 | -2.3429
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.8061 | 226.7 | -0.010431 | -2.3648
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.14245 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 52.136 | 366 | -0.010467 | -3.8311
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1416 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 34.2672 | 242 | -0.011315 | -2.7383
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.14148 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 111.0642 | 785 | -0.011432 | -8.9744
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.14148 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 112.479 | 795 | -0.011432 | -9.0887
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.14148 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 110.3567 | 780 | -0.011432 | -8.9172
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.20337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6606 | 0 | -0.011743 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.20337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6606 | 0 | -0.011743 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.20337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.0505 | 0 | -0.011743 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.8559 | 0 | -0.011997 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.3193 | 0 | -0.011997 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.4331 | 0 | -0.011997 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | 1 | 56.2263 | 0 | -0.011997 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.14013 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.012789 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.14009 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.0043 | 50 | -0.012829 | -0.64147
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.20514 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -86.5699 | 422 | -0.013517 | -5.7043
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13933 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.3582 | 182 | -0.013584 | -2.4724
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13933 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 67.4362 | 484 | -0.013584 | -6.5748
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.13912 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.3474 | 60 | -0.013792 | -0.82754
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13854 | west | 4 | Y | N | Ywest | Nwest | 1 | 90.0088 | 649.7 | -0.014376 | -9.3403
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.20656 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -89.4422 | 433 | -0.014939 | -6.4687
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.20669 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.7873 | 0 | -0.015063 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.20669 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.994 | 0 | -0.015063 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.20677 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -120.7554 | 584 | -0.015148 | -8.8466
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.20677 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -123.0299 | 595 | -0.015148 | -9.0132
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.20713 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2428 | 0 | -0.015503 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13732 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6585 | 165 | -0.015591 | -2.5726
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13571 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.0266 | 236 | -0.017209 | -4.0614
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.1357 | west | 6 | Y | N | Ywest | Nwest | 1 | 54.2784 | 400 | -0.017219 | -6.8877
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.4507 | 50 | -0.017389 | -0.86946
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.4507 | 50 | -0.017389 | -0.86946
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.4507 | 50 | -0.017389 | -0.86946
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.4507 | 50 | -0.017389 | -0.86946
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.13472 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.4102 | 151.5 | -0.018194 | -2.7564
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.13472 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.518 | 152.3 | -0.018194 | -2.771
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.13472 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.913 | 177.5 | -0.018194 | -3.2295
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.13454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.2746 | 150.7 | -0.018379 | -2.7698
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.13454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.3149 | 151 | -0.018379 | -2.7753
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.13454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.8667 | 177.4 | -0.018379 | -3.2605
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.13309 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.8473 | 615 | -0.01983 | -12.1957
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.13309 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.1209 | 587 | -0.01983 | -11.6404
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.13303 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.982 | 60 | -0.019882 | -1.1929
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.21311 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.836 | 0 | -0.021485 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.21311 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.836 | 0 | -0.021485 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.13116 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.6737 | 150 | -0.021757 | -3.2636
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.394 | 209 | -0.021843 | -4.5653
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5806 | 126.5 | -0.021843 | -2.7632
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.6369 | 249 | -0.021843 | -5.439
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.8212 | 197 | -0.021843 | -4.3031
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9041 | 37.5 | -0.02214 | -0.83026
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0583 | 107.5 | -0.02214 | -2.3801
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6546 | 135 | -0.02214 | -2.9889
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.5622 | 119 | -0.02214 | -2.6347
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7314 | 105 | -0.02214 | -2.3247
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5274 | 80.5 | -0.02214 | -1.7823
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.13011 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2643 | 125 | -0.022801 | -2.8502
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.13011 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2643 | 125 | -0.022801 | -2.8502
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12976 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4644 | 150 | -0.023152 | -3.4729
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12976 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.1061 | 101 | -0.023152 | -2.3384
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.1297 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8944 | 84 | -0.02322 | -1.9505
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12936 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8067 | 99 | -0.023554 | -2.3319
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12936 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.891 | 61 | -0.023554 | -1.4368
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12936 | west | 7 | N | N | Nwest | Nwest | 1 | 3.234 | 0 | -0.023554 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12936 | west | 7 | N | N | Nwest | Nwest | 1 | 5.9118 | 0 | -0.023554 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12936 | west | 7 | N | N | Nwest | Nwest | 1 | 5.9118 | 0 | -0.023554 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.2347 | 141 | -0.023591 | -3.3264
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.5189 | 120 | -0.023591 | -2.831
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12921 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1405 | 63 | -0.0237 | -1.4931
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5211 | 66 | -0.023808 | -1.5714
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.9084 | 69 | -0.023808 | -1.6428
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.9084 | 69 | -0.023808 | -1.6428
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.6502 | 67 | -0.023808 | -1.5952
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.6502 | 67 | -0.023808 | -1.5952
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.392 | 65 | -0.023808 | -1.5475
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.3246 | 150 | -0.024084 | -3.6127
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.3428 | 220 | -0.024084 | -5.2986
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.7662 | 200 | -0.024084 | -4.8169
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7045 | 121.9 | -0.024084 | -2.9359
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12846 | west | 8 | N | N | Nwest | Nwest | 1 | 8.992 | 0 | -0.024458 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12846 | west | 8 | N | N | Nwest | Nwest | 1 | 9.4287 | 0 | -0.024458 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12846 | west | 8 | N | N | Nwest | Nwest | 1 | 9.0434 | 0 | -0.024458 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12845 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.1212 | 180 | -0.024464 | -4.4036
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12845 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.1212 | 180 | -0.024464 | -4.4036
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12833 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.8742 | 225 | -0.024585 | -5.5317
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12806 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.367 | 120 | -0.024857 | -2.9829
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.128 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3604 | 120 | -0.024912 | -2.9895
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12786 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3428 | 120 | -0.025058 | -3.007
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12786 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.7907 | 233 | -0.025058 | -5.8386
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12786 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.7613 | 170.2 | -0.025058 | -4.2649
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.243 | 214.2 | -0.02573 | -5.5114
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12718 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2813 | 0 | -0.025731 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12689 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7526 | 100.5 | -0.026023 | -2.6153
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12687 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3586 | 58 | -0.026043 | -1.5105
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.8773 | 70 | -0.026097 | -1.8268
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.8773 | 70 | -0.026097 | -1.8268
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.7687 | 92.8 | -0.026097 | -2.4218
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.1454 | 80 | -0.026097 | -2.0878
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.1454 | 80 | -0.026097 | -2.0878
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.5841 | 115 | -0.026097 | -3.0012
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.3989 | 208.2 | -0.026119 | -5.4381
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.0177 | 142.1 | -0.026119 | -3.7116
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.7878 | 132.4 | -0.026119 | -3.4582
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.2443 | 136 | -0.026119 | -3.5522
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.639 | 147 | -0.026119 | -3.8395
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.6272 | 210 | -0.026119 | -5.4851
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9648 | 150 | -0.026483 | -3.9725
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1591 | 112.5 | -0.027056 | -3.0438
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.8159 | 149.5 | -0.027056 | -4.0449
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.4098 | 186 | -0.027056 | -5.0325
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.9968 | 214.5 | -0.027056 | -5.8036
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12526 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82675 | 6.6 | -0.02765 | -0.18249
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12526 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2966 | 34.3 | -0.02765 | -0.94841
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.12501 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.6268 | 149 | -0.027903 | -4.1576
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12462 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3617 | 35 | -0.028294 | -0.9903
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12462 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7386 | 30 | -0.028294 | -0.84883
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2175 | 66 | -0.028408 | -1.875
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.093 | 65 | -0.028408 | -1.8465
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.342 | 67 | -0.028408 | -1.9034
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.342 | 67 | -0.028408 | -1.9034
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.342 | 67 | -0.028408 | -1.9034
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12451 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.028408 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12451 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.028408 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12385 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9929 | 169.5 | -0.029063 | -4.9262
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11611 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.55732 | 0 | -0.036807 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.23004 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.3649 | 132 | -0.038412 | -5.0704
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.23004 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.825 | 134 | -0.038412 | -5.1472
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.23004 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.302 | 323 | -0.038412 | -12.4072
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.23118 | south | 5 | N | N | Nsouth | Nsouth | -1 | -8.0913 | 0 | -0.039554 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.23118 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.8601 | 0 | -0.039554 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.23118 | south | 5 | N | N | Nsouth | Nsouth | -1 | -8.0913 | 0 | -0.039554 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11263 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0102 | 80 | -0.040288 | -3.2231
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11263 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0102 | 80 | -0.040288 | -3.2231
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.23264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.7578 | 158 | -0.041019 | -6.481
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.23264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.223 | 160 | -0.041019 | -6.5631
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.23264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -40.7127 | 175 | -0.041019 | -7.1784
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11169 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3771 | 75 | -0.041221 | -3.0916
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11169 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9355 | 80 | -0.041221 | -3.2977
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11169 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4678 | 40 | -0.041221 | -1.6489
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.11162 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 92.3097 | 827 | -0.041295 | -34.1513
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.11162 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.4168 | 819 | -0.041295 | -33.8209
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11149 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9194 | 80 | -0.041423 | -3.3139
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11146 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9172 | 80 | -0.04145 | -3.316
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.11135 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.7019 | 150 | -0.041569 | -6.2354
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.11135 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.7019 | 150 | -0.041569 | -6.2354
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.2343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.7312 | 152.5 | -0.042678 | -6.5084
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.2343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.0283 | 149.5 | -0.042678 | -6.3804
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.2343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -54.4989 | 232.6 | -0.042678 | -9.927
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.6477 | 49 | -0.046083 | -2.2581
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.9346 | 46 | -0.046083 | -2.1198
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.9346 | 46 | -0.046083 | -2.1198
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.1723 | 47 | -0.046083 | -2.1659
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.23771 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.607 | 154 | -0.046083 | -7.0968
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.23771 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.1808 | 148 | -0.046083 | -6.8203
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.41 | 48 | -0.046083 | -2.212
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.41 | 48 | -0.046083 | -2.212
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10668 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5346 | 80 | -0.046233 | -3.6987
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10587 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0988 | 76.5 | -0.047048 | -3.5992
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.23938 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9151 | 0 | -0.047758 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.23938 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9151 | 0 | -0.047758 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10511 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8291 | 84 | -0.047807 | -4.0158
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.24041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.5262 | 310 | -0.048782 | -15.1225
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.24041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -99.2881 | 413 | -0.048782 | -20.1471
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.2059 | 42 | -0.051372 | -2.1576
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.6919 | 44 | -0.051372 | -2.2604
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.6919 | 44 | -0.051372 | -2.2604
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.4209 | 47 | -0.051372 | -2.4145
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.9155 | 855 | -0.058277 | -49.8271
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.9155 | 855 | -0.058277 | -49.8271
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.4134 | 152.3 | -0.058277 | -8.8756
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.4796 | 153 | -0.058277 | -8.9164
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.080025 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.07289 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.28628 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -162.895 | 569 | -0.094658 | -53.8606
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.28628 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -166.3304 | 581 | -0.094658 | -54.9965
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.056787 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5181 | 150 | -0.096128 | -14.4193
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.055301 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 25.6044 | 463 | -0.097614 | -45.1954
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.10696 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.10696 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.045953 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.7812 | 17 | -0.10696 | -1.8184
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.10696 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.10696 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.04587 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.4678 | 0 | -0.10705 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.7867 | 0 | -0.1089 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.8659 | 0 | -0.1089 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.8659 | 0 | -0.1089 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.7246 | 0 | -0.1089 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.041643 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9989 | 48 | -0.11127 | -5.3411
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.041643 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9156 | 46 | -0.11127 | -5.1185
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.041643 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3725 | 105 | -0.11127 | -11.6836
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.15292 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.15292 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.10079 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.25371 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -19.1535 | 100 | -0.34445 | -34.445

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3409 LAKE_CRK 3414 TEMP_SS_ctg1 C:3405 THOUSE__3412 TEMP_PEC | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -19.1535 | 0 | -0.34445 | 0 | 0 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.10079 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.25371 | 0 | 0 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.15292 | 0 | 0 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.15292 | 0 | 0 | 0 | Weighted Shift Factors
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.041643 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9989 | 48 | -0.11127 | -5.3411 | 48 | 5.3411 | South | -0.19162
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.041643 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9156 | 46 | -0.11127 | -5.1185 | 94 | 10.4596 | North | 0.15292
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.041643 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3725 | 105 | -0.11127 | -11.6836 | 199 | 22.1432 |  | -0.34454
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.7867 | 0 | -0.1089 | 0 | 199 | 22.1432
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.8659 | 0 | -0.1089 | 0 | 199 | 22.1432 | Line Rating | 1239.6
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.8659 | 0 | -0.1089 | 0 | 199 | 22.1432 | Conc Gen | 2394.6
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.044012 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.7246 | 0 | -0.1089 | 0 | 199 | 22.1432 | Weighted Imp. | 124.6257
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.04587 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.4678 | 0 | -0.10705 | 0 | 199 | 22.1432 | PTDF | 0.052044
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.10696 | 0 | 199 | 22.1432
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.10696 | 0 | 199 | 22.1432 | Concentration | -0.15105
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.045953 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.7812 | 17 | -0.10696 | -1.8184 | 216 | 23.9616
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.10696 | 0 | 216 | 23.9616
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.045953 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.10696 | 0 | 216 | 23.9616
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.055301 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 25.6044 | 0 | -0.097614 | 0 | 216 | 23.9616
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.056787 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5181 | 0 | -0.096128 | 0 | 216 | 23.9616
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.28628 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -162.895 | 0 | -0.094658 | 0 | 216 | 23.9616
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.28628 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -166.3304 | 0 | -0.094658 | 0 | 216 | 23.9616
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.080025 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.07289 | 0 | 216 | 23.9616
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.9155 | 0 | -0.058277 | 0 | 216 | 23.9616
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.9155 | 0 | -0.058277 | 0 | 216 | 23.9616
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.4134 | 0 | -0.058277 | 0 | 216 | 23.9616
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.094638 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.4796 | 0 | -0.058277 | 0 | 216 | 23.9616
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.2059 | 42 | -0.051372 | -2.1576 | 258 | 26.1192
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.6919 | 44 | -0.051372 | -2.2604 | 302 | 28.3796
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.6919 | 44 | -0.051372 | -2.2604 | 346 | 30.64
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.243 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.4209 | 47 | -0.051372 | -2.4145 | 393 | 33.0545
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.24041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.5262 | 310 | -0.048782 | -15.1225 | 703 | 48.177
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.24041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -99.2881 | 413 | -0.048782 | -20.1471 | 1116 | 68.324
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10511 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8291 | 0 | -0.047807 | 0 | 1116 | 68.324
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.23938 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9151 | 0 | -0.047758 | 0 | 1116 | 68.324
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.23938 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9151 | 0 | -0.047758 | 0 | 1116 | 68.324
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10587 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0988 | 0 | -0.047048 | 0 | 1116 | 68.324
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10668 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5346 | 0 | -0.046233 | 0 | 1116 | 68.324
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.6477 | 49 | -0.046083 | -2.2581 | 1165 | 70.5821
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.9346 | 46 | -0.046083 | -2.1198 | 1211 | 72.7019
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.9346 | 46 | -0.046083 | -2.1198 | 1257 | 74.8218
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.1723 | 47 | -0.046083 | -2.1659 | 1304 | 76.9877
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.23771 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.607 | 154 | -0.046083 | -7.0968 | 1458 | 84.0845
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.23771 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.1808 | 148 | -0.046083 | -6.8203 | 1606 | 90.9048
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.41 | 48 | -0.046083 | -2.212 | 1654 | 93.1168
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.23771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.41 | 48 | -0.046083 | -2.212 | 1702 | 95.3288
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.2343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.7312 | 152.5 | -0.042678 | -6.5084 | 1854.5 | 101.8373
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.2343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.0283 | 149.5 | -0.042678 | -6.3804 | 2004 | 108.2177
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.2343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -54.4989 | 232.6 | -0.042678 | -9.927 | 2236.6 | 118.1446
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.11135 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.7019 | 0 | -0.041569 | 0 | 2236.6 | 118.1446
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.11135 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.7019 | 0 | -0.041569 | 0 | 2236.6 | 118.1446
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11146 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9172 | 0 | -0.04145 | 0 | 2236.6 | 118.1446
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11149 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9194 | 0 | -0.041423 | 0 | 2236.6 | 118.1446
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.11162 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 92.3097 | 0 | -0.041295 | 0 | 2236.6 | 118.1446
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.11162 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.4168 | 0 | -0.041295 | 0 | 2236.6 | 118.1446
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11169 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3771 | 0 | -0.041221 | 0 | 2236.6 | 118.1446
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11169 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9355 | 0 | -0.041221 | 0 | 2236.6 | 118.1446
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11169 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4678 | 0 | -0.041221 | 0 | 2236.6 | 118.1446
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.23264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.7578 | 158 | -0.041019 | -6.481 | 2394.6 | 124.6257
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.23264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.223 | 160 | -0.041019 | -6.5631
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.23264 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -40.7127 | 175 | -0.041019 | -7.1784
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11263 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0102 | 0 | -0.040288 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11263 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0102 | 0 | -0.040288 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.23118 | south | 5 | N | N | Nsouth | Nsouth | -1 | -8.0913 | 0 | -0.039554 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.23118 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.8601 | 0 | -0.039554 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.23118 | south | 5 | N | N | Nsouth | Nsouth | -1 | -8.0913 | 0 | -0.039554 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.23004 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.3649 | 132 | -0.038412 | -5.0704
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.23004 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.825 | 134 | -0.038412 | -5.1472
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.23004 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.302 | 323 | -0.038412 | -12.4072
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11611 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.55732 | 0 | -0.036807 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12385 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9929 | 0 | -0.029063 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2175 | 66 | -0.028408 | -1.875
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.093 | 65 | -0.028408 | -1.8465
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.342 | 67 | -0.028408 | -1.9034
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.342 | 67 | -0.028408 | -1.9034
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12451 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.342 | 67 | -0.028408 | -1.9034
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12451 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.028408 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12451 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.028408 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12462 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3617 | 0 | -0.028294 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12462 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7386 | 0 | -0.028294 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.12501 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.6268 | 0 | -0.027903 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12526 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82675 | 0 | -0.02765 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12526 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2966 | 0 | -0.02765 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1591 | 0 | -0.027056 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.8159 | 0 | -0.027056 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.4098 | 0 | -0.027056 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.9968 | 0 | -0.027056 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9648 | 0 | -0.026483 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.3989 | 208.2 | -0.026119 | -5.4381
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.0177 | 142.1 | -0.026119 | -3.7116
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.7878 | 132.4 | -0.026119 | -3.4582
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.2443 | 136 | -0.026119 | -3.5522
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.639 | 147 | -0.026119 | -3.8395
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.1268 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.6272 | 210 | -0.026119 | -5.4851
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.8773 | 70 | -0.026097 | -1.8268
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.8773 | 70 | -0.026097 | -1.8268
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.7687 | 92.8 | -0.026097 | -2.4218
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.1454 | 80 | -0.026097 | -2.0878
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.1454 | 80 | -0.026097 | -2.0878
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12682 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.5841 | 115 | -0.026097 | -3.0012
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12687 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3586 | 0 | -0.026043 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12689 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7526 | 0 | -0.026023 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12718 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2813 | 0 | -0.025731 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.243 | 0 | -0.02573 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12786 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3428 | 0 | -0.025058 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12786 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.7907 | 0 | -0.025058 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12786 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.7613 | 0 | -0.025058 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.128 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3604 | 0 | -0.024912 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12806 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.367 | 0 | -0.024857 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12833 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.8742 | 0 | -0.024585 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12845 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.1212 | 0 | -0.024464 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12845 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.1212 | 0 | -0.024464 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12846 | west | 8 | N | N | Nwest | Nwest | 1 | 8.992 | 0 | -0.024458 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12846 | west | 8 | N | N | Nwest | Nwest | 1 | 9.4287 | 0 | -0.024458 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12846 | west | 8 | N | N | Nwest | Nwest | 1 | 9.0434 | 0 | -0.024458 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.3246 | 0 | -0.024084 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.3428 | 0 | -0.024084 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.7662 | 0 | -0.024084 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12883 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7045 | 0 | -0.024084 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5211 | 66 | -0.023808 | -1.5714
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.9084 | 69 | -0.023808 | -1.6428
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.9084 | 69 | -0.023808 | -1.6428
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.6502 | 67 | -0.023808 | -1.5952
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.6502 | 67 | -0.023808 | -1.5952
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12911 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.392 | 65 | -0.023808 | -1.5475
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12921 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1405 | 0 | -0.0237 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.2347 | 0 | -0.023591 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.5189 | 0 | -0.023591 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12936 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8067 | 0 | -0.023554 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12936 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.891 | 0 | -0.023554 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12936 | west | 7 | N | N | Nwest | Nwest | 1 | 3.234 | 0 | -0.023554 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12936 | west | 7 | N | N | Nwest | Nwest | 1 | 5.9118 | 0 | -0.023554 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12936 | west | 7 | N | N | Nwest | Nwest | 1 | 5.9118 | 0 | -0.023554 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.1297 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8944 | 0 | -0.02322 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12976 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4644 | 0 | -0.023152 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12976 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.1061 | 0 | -0.023152 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.13011 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2643 | 0 | -0.022801 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.13011 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2643 | 0 | -0.022801 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9041 | 0 | -0.02214 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0583 | 0 | -0.02214 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6546 | 0 | -0.02214 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.5622 | 0 | -0.02214 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7314 | 0 | -0.02214 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.13078 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5274 | 0 | -0.02214 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.394 | 0 | -0.021843 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5806 | 0 | -0.021843 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.6369 | 0 | -0.021843 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.13107 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.8212 | 0 | -0.021843 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.13116 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.6737 | 0 | -0.021757 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.21311 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.836 | 0 | -0.021485 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.21311 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.836 | 0 | -0.021485 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.13303 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.982 | 0 | -0.019882 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.13309 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.8473 | 0 | -0.01983 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.13309 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.1209 | 0 | -0.01983 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.13454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.2746 | 150.7 | -0.018379 | -2.7698
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.13454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.3149 | 151 | -0.018379 | -2.7753
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.13454 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.8667 | 177.4 | -0.018379 | -3.2605
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.13472 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.4102 | 151.5 | -0.018194 | -2.7564
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.13472 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.518 | 152.3 | -0.018194 | -2.771
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.13472 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.913 | 177.5 | -0.018194 | -3.2295
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.4507 | 50 | -0.017389 | -0.86946
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.4507 | 50 | -0.017389 | -0.86946
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.4507 | 50 | -0.017389 | -0.86946
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.20901 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.4507 | 50 | -0.017389 | -0.86946
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.1357 | west | 6 | Y | N | Ywest | Nwest | 1 | 54.2784 | 0 | -0.017219 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13571 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.0266 | 0 | -0.017209 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13732 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6585 | 0 | -0.015591 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.20713 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2428 | 0 | -0.015503 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.20677 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -120.7554 | 0 | -0.015148 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.20677 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -123.0299 | 0 | -0.015148 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.20669 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.7873 | 0 | -0.015063 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.20669 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.994 | 0 | -0.015063 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.20656 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -89.4422 | 0 | -0.014939 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13854 | west | 4 | Y | N | Ywest | Nwest | 1 | 90.0088 | 0 | -0.014376 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.13912 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.3474 | 0 | -0.013792 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13933 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.3582 | 182 | -0.013584 | -2.4724
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13933 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 67.4362 | 484 | -0.013584 | -6.5748
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.20514 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -86.5699 | 422 | -0.013517 | -5.7043
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.14009 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.0043 | 0 | -0.012829 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.14013 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.012789 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.8559 | 0 | -0.011997 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.3193 | 0 | -0.011997 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.4331 | 0 | -0.011997 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.14092 | north | 1 | N | N | Nnorth | Nnorth | 1 | 56.2263 | 0 | -0.011997 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.20337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6606 | 0 | -0.011743 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.20337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6606 | 0 | -0.011743 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.20337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.0505 | 0 | -0.011743 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.14148 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 111.0642 | 0 | -0.011432 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.14148 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 112.479 | 0 | -0.011432 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.14148 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 110.3567 | 0 | -0.011432 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1416 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 34.2672 | 242 | -0.011315 | -2.7383
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.14245 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 52.136 | 366 | -0.010467 | -3.8311
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.2403 | 223.9 | -0.010431 | -2.3356
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.4626 | 225 | -0.010431 | -2.347
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.3818 | 224.6 | -0.010431 | -2.3429
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.20206 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.8061 | 226.7 | -0.010431 | -2.3648
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8506 | 20 | -0.010383 | -0.20767
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8506 | 20 | -0.010383 | -0.20767
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8506 | 20 | -0.010383 | -0.20767
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.14253 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.423 | 17 | -0.010383 | -0.17652
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.14319 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 32.075 | 224 | -0.0097234 | -2.178
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.20051 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.747 | 0 | -0.0088863 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.14426 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 17.3117 | 0 | -0.0086514 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.14443 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.7332 | 0 | -0.0084844 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.14443 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.7332 | 0 | -0.0084844 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.14563 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.6308 | 73 | -0.0072874 | -0.53198
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.14563 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.3297 | 119 | -0.0072874 | -0.8672
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.14563 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.8537 | 205 | -0.0072874 | -1.4939
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.14563 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.8541 | 102 | -0.0072874 | -0.74331
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.14563 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.9803 | 96 | -0.0072874 | -0.69959
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5248 | 161 | -0.0067984 | -1.0945
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.9632 | 164 | -0.0067984 | -1.1149
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.9632 | 164 | -0.0067984 | -1.1149
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 60.4924 | 414 | -0.0067984 | -2.8145
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.671 | 162 | -0.0067984 | -1.1013
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5248 | 161 | -0.0067984 | -1.0945
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.8171 | 163 | -0.0067984 | -1.1081
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 59.7619 | 409 | -0.0067984 | -2.7805
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.14633 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8505 | 204 | -0.0065894 | -1.3442
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.14633 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.4115 | 201 | -0.0065894 | -1.3245
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.14633 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.4109 | 242 | -0.0065894 | -1.5946
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.14702 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.9404 | 20 | -0.0058964 | -0.11793
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.14702 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.6755 | 25 | -0.0058964 | -0.14741
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.14702 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.0278 | 41 | -0.0058964 | -0.24175
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14718 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 82.1281 | 0 | -0.0057324 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14718 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 85.219 | 0 | -0.0057324 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14718 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 118.9239 | 0 | -0.0057324 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.6287 | 79 | -0.0057164 | -0.45159
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.6031 | 106 | -0.0057164 | -0.60593
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 21.4911 | 146 | -0.0057164 | -0.83459
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.1472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.1871 | 76 | -0.0057164 | -0.43444
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.1472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.8882 | 40 | -0.0057114 | -0.22845
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.14722 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.0416 | 0 | -0.0056944 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.14722 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.7188 | 0 | -0.0056944 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.14722 | north | 8 | N | N | Nnorth | Nnorth | 1 | 13.0143 | 0 | -0.0056944 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14726 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 57.1373 | 388 | -0.0056544 | -2.1939
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14726 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.8394 | 515 | -0.0056544 | -2.912
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.572 | 160 | -0.0055904 | -0.89446
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9827 | 156 | -0.0055904 | -0.8721
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8757 | 196 | -0.0055904 | -1.0957
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9827 | 156 | -0.0055904 | -0.8721
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.13 | 157 | -0.0055904 | -0.87769
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14733 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.1703 | 198 | -0.0055904 | -1.1069
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14742 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 54.5458 | 370 | -0.0054944 | -2.0329
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.6389 | 0 | -0.0054944 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.7864 | 0 | -0.0054944 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 45.5531 | 0 | -0.0054944 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.0812 | 0 | -0.0054944 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.2286 | 0 | -0.0054944 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14742 | north | 1 | N | N | Nnorth | Nnorth | 1 | 45.7005 | 0 | -0.0054944 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.14747 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6545 | 18 | -0.0054414 | -0.097945
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.14747 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6545 | 18 | -0.0054414 | -0.097945
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.14747 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.604 | 38 | -0.0054414 | -0.20677
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14752 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 25.0782 | 170 | -0.0053964 | -0.91738
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14752 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 76.7099 | 520 | -0.0053964 | -2.8061
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14762 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.9048 | 0 | -0.0052944 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14762 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.9048 | 0 | -0.0052944 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.14766 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.6115 | 0 | -0.0052574 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.14775 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 42.5523 | 288 | -0.0051644 | -1.4873
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.14775 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7194 | 147 | -0.0051644 | -0.75916
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.14775 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7194 | 147 | -0.0051644 | -0.75916
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14781 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0051024 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14781 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0051024 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14828 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0046324 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14838 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0045304 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14858 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.9145 | 60 | -0.0043404 | -0.26042
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14858 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.3602 | 63 | -0.0043404 | -0.27344
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19548 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46914 | 0 | -0.0038513 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19548 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46914 | 0 | -0.0038513 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.19548 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54733 | 0 | -0.0038513 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.2328 | 196 | -0.0037684 | -0.7386
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.5553 | 111 | -0.0037684 | -0.41829
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14982 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.6791 | 118 | -0.0030924 | -0.3649
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14982 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 17.2296 | 115 | -0.0030924 | -0.35562
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14982 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 83.3016 | 556 | -0.0030924 | -1.7194
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.6474 | 142 | -0.0030753 | -0.43669
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.2315 | 145 | -0.0030753 | -0.44591
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.3997 | 151 | -0.0030753 | -0.46437
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.1947 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -56.463 | 290 | -0.0030753 | -0.89183
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.15004 | north | 3 | N | N | Nnorth | Nnorth | 1 | 173.6009 | 0 | -0.0028714 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.15004 | north | 3 | N | N | Nnorth | Nnorth | 1 | 173.751 | 0 | -0.0028714 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.15014 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0027744 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.15014 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0027744 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.15014 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0027744 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.5383 | 70 | -0.0023684 | -0.16579
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.3877 | 69 | -0.0023684 | -0.16342
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.3877 | 69 | -0.0023684 | -0.16342
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.15055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.2372 | 68 | -0.0023684 | -0.16105
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.15071 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.7482 | 217.3 | -0.0022104 | -0.48031
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.15071 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.8945 | 205 | -0.0022104 | -0.45312
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.15071 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.052 | 272.4 | -0.0022104 | -0.6021
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.15118 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0017344 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19277 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46264 | 0 | -0.0011413 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19277 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46264 | 0 | -0.0011413 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.19262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.77047 | 0 | -0.00099227 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.15298 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 66.5476 | 435 | 6.7638e-05 | 0.029423
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.835 | 0 | 8.9733e-05 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -42.5208 | 0 | 8.9733e-05 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.2424 | 0 | 8.9733e-05 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -42.9038 | 0 | 8.9733e-05 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.19154 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.0265 | 0 | 8.9733e-05 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.15327 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.5436 | 395 | 0.00035964 | 0.14206
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.15327 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 66.6746 | 435 | 0.00035964 | 0.15644
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.1541 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.8896 | 168 | 0.0011896 | 0.19986
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.1541 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8695 | 90 | 0.0011896 | 0.10707
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5943 | 147 | 0.0039087 | 0.57458
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.9048 | 138 | 0.0039087 | 0.53941
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.2802 | 140 | 0.0039087 | 0.54722
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5943 | 147 | 0.0039087 | 0.57458
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.1643 | 182 | 0.0039087 | 0.71139
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.18772 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.1678 | 198 | 0.0039087 | 0.77393
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.8832 | 224 | 0.0072776 | 1.6302
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 36.2036 | 226 | 0.0072776 | 1.6447
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.9609 | 212 | 0.0072776 | 1.5429
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.16019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.8007 | 211 | 0.0072776 | 1.5356
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.16064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7621 | 216.4 | 0.0077226 | 1.6712
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.16064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7139 | 216.1 | 0.0077226 | 1.6689
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.18358 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0080467 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.18358 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0080467 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.18358 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0080467 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.18305 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -77.6132 | 0 | 0.0085747 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.18305 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -77.7963 | 0 | 0.0085747 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.18291 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -75.361 | 412 | 0.0087097 | 3.5884
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.18291 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.166 | 400 | 0.0087097 | 3.4839
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.18271 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -38.1853 | 209 | 0.0089197 | 1.8642
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.18271 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -39.4643 | 216 | 0.0089197 | 1.9267
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4044 | 46 | 0.0089197 | 0.41031
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.5871 | 47 | 0.0089197 | 0.41923
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4044 | 46 | 0.0089197 | 0.41031
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.18271 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4044 | 46 | 0.0089197 | 0.41031
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.18262 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.328 | 407 | 0.0090007 | 3.6633
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.18226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.2495 | 155 | 0.0093697 | 1.4523
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.18226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -30.9834 | 170 | 0.0093697 | 1.5929
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.18226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.2495 | 155 | 0.0093697 | 1.4523
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.16262 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.4393 | 0 | 0.0097076 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.16262 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.4393 | 0 | 0.0097076 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.1816 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.5325 | 58 | 0.01003 | 0.58172
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.1816 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.162 | 89 | 0.01003 | 0.89265
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9902 | 44 | 0.01003 | 0.44131
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.9902 | 44 | 0.01003 | 0.44131
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8086 | 43 | 0.01003 | 0.43128
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.1816 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.1718 | 45 | 0.01003 | 0.45134
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.18132 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -99.0002 | 0 | 0.010306 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.18132 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -135.9892 | 0 | 0.010306 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.18085 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1702 | 0 | 0.010771 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.16628 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.9425 | 150 | 0.013368 | 2.0051
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.16628 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.3026 | 80 | 0.013368 | 1.0694
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.17135 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -67.8534 | 0 | 0.020278 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.17421 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.021295 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.17421 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.021295 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.16151 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.8762 | 24 | 0.030115 | 0.72275
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.16151 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.8762 | 24 | 0.030115 | 0.72275
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.16151 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.7147 | 23 | 0.030115 | 0.69264
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.16032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -16.032 | 100 | 0.031305 | 3.1305
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.16032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -16.032 | 100 | 0.031305 | 3.1305
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.16032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031305 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.16032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031305 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.16032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031305 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.16032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031305 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.16031 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.031319 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15966 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3412 | 8.4 | 0.031963 | 0.26849
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.15896 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.03267 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.15682 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -98.641 | 0 | 0.034803 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.15618 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.035446 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.15437 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.037253 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.15435 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8522 | 0 | 0.037275 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.15435 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6979 | 0 | 0.037275 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.15435 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8522 | 0 | 0.037275 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.15244 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.3323 | 146.5 | 0.039186 | 5.7407
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.15244 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.5457 | 147.9 | 0.039186 | 5.7956
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.15244 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.3719 | 173 | 0.039186 | 6.7791
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.4913 | 207 | 0.039493 | 8.175
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.967 | 216.7 | 0.039493 | 8.5581
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.8159 | 242 | 0.039493 | 9.5572
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9063 | 144 | 0.039498 | 5.6877
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9063 | 144 | 0.039498 | 5.6877
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.15213 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0137 | 171 | 0.039498 | 6.7541
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.15183 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.7695 | 38 | 0.039795 | 1.5122
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.15183 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.9303 | 19.3 | 0.039795 | 0.76804
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.15183 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2774 | 15 | 0.039795 | 0.59692
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.15183 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.136 | 47 | 0.039795 | 1.8704
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.15183 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039795 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.2621 | 0 | 0.039901 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.2207 | 0 | 0.039901 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7655 | 0 | 0.039901 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8828 | 0 | 0.039901 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.2621 | 0 | 0.039901 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4621 | 0 | 0.039901 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5241 | 0 | 0.039901 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3379 | 0 | 0.039901 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.4552 | 0 | 0.039901 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.5862 | 0 | 0.039901 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.3448 | 0 | 0.039901 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.15172 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.5862 | 0 | 0.039901 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.15148 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.3929 | 0 | 0.040147 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.15074 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7282 | 0 | 0.040883 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.15073 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7278 | 0 | 0.040894 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.15058 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7645 | 0 | 0.041047 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.15058 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7645 | 0 | 0.041047 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.15052 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -50.2747 | 334 | 0.041102 | 13.728
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.15052 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -51.1778 | 340 | 0.041102 | 13.9746
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.15052 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.0941 | 180 | 0.041102 | 7.3983
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.15052 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.0941 | 180 | 0.041102 | 7.3983
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.15022 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.0392 | 180 | 0.041407 | 7.4532
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.15019 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.2729 | 0 | 0.041437 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.15019 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.3179 | 0 | 0.041437 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.15019 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.9788 | 0 | 0.041437 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.15017 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -50.4571 | 336 | 0.041455 | 13.9288
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.15017 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.0306 | 180 | 0.041455 | 7.4619
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.14954 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.5332 | 144 | 0.042089 | 6.0608
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.14954 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.1128 | 188 | 0.042089 | 7.9127
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 0 | 0.042419 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 0 | 0.042419 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 0 | 0.042419 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.3873 | 0 | 0.042419 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 0 | 0.042419 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 0 | 0.042419 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7302 | 0 | 0.042419 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.14921 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2381 | 0 | 0.042419 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.4753 | 0 | 0.043047 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.7324 | 0 | 0.043047 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -14.8578 | 0 | 0.043047 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.5438 | 0 | 0.043047 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.841 | 0 | 0.043047 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.14858 | south | 8 | N | N | Nsouth | Nsouth | -1 | -18.8694 | 0 | 0.043047 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.14858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7829 | 0 | 0.043047 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.14783 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.7917 | 0 | 0.043794 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0362 | 47.7 | 0.044115 | 2.1043
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.5021 | 37.3 | 0.044115 | 1.6455
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7855 | 46 | 0.044115 | 2.0293
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.14751 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0805 | 48 | 0.044115 | 2.1175
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.19712 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 50.2669 | 255 | 0.04421 | 11.2735
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.19712 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 29.3716 | 149 | 0.04421 | 6.5872
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.19712 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 30.1601 | 153 | 0.04421 | 6.7641
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.14614 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.2151 | 22 | 0.045484 | 1.0006
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14614 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6076 | 11 | 0.045484 | 0.50032
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14614 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6076 | 11 | 0.045484 | 0.50032
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.14485 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1727 | 0 | 0.046778 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.14485 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3315 | 0 | 0.046778 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.14375 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.15 | 0 | 0.047871 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.0083 | 0 | 0.048472 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0021 | 0 | 0.048472 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.583 | 0 | 0.048472 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1473 | 0 | 0.048472 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0021 | 0 | 0.048472 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1473 | 0 | 0.048472 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.583 | 0 | 0.048472 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.14315 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.583 | 0 | 0.048472 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.13911 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.6775 | 0 | 0.052511 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.8917 | 0 | 0.053755 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.1675 | 0 | 0.053755 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.8917 | 0 | 0.053755 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.0296 | 0 | 0.053755 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.809 | 0 | 0.053755 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4468 | 0 | 0.053755 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.342 | 0 | 0.053755 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8604 | 0 | 0.053755 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0111 | 0 | 0.053755 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.13787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.2024 | 0 | 0.053755 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.11564 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.075981 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.11027 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6616 | 0 | 0.081358 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.24375 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.090833 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.24375 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 191.8297 | 787 | 0.090833 | 71.4853
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.092891 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -123.8237 | 0 | 0.098734 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.092891 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -123.3592 | 0 | 0.098734 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.0115 | 76 | 0.099368 | 7.5519
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.0115 | 76 | 0.099368 | 7.5519
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.687 | 105 | 0.099368 | 10.4336
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.827 | 74 | 0.099368 | 7.3532
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.827 | 74 | 0.099368 | 7.3532
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.092257 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4102 | 102 | 0.099368 | 10.1355
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.087145 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8758 | 0 | 0.10448 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.087145 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1786 | 0 | 0.10448 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.087145 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.10448 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.086821 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.7302 | 66 | 0.1048 | 6.917
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3204 | 0 | 0.12194 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9754 | 0 | 0.12194 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1358 | 0 | 0.12194 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0381 | 0 | 0.12194 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9928 | 0 | 0.12194 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1322 | 0 | 0.12194 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4842 | 0 | 0.12194 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2543 | 0 | 0.12194 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5503 | 0 | 0.12194 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8779 | 0 | 0.12194 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3901 | 0 | 0.12194 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0172 | 0 | 0.12194 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5155 | 0 | 0.12194 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0381 | 0 | 0.12194 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.7593 | 0 | 0.12194 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1775 | 0 | 0.12194 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.296 | 0 | 0.12194 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5747 | 0 | 0.12194 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5747 | 0 | 0.12194 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.069684 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.916 | 0 | 0.12194 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.065532 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6528 | 0 | 0.12609 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.065532 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65532 | 0 | 0.12609 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.9099 | 0 | 0.12937 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.9099 | 0 | 0.12937 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.4079 | 0 | 0.12937 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.062251 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8165 | 0 | 0.12937 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.050375 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3223 | 0 | 0.14125 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.049946 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -32.5148 | 0 | 0.14168 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.049946 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -28.1695 | 0 | 0.14168 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.049946 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -29.9676 | 0 | 0.14168 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.049846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.1249 | 0 | 0.14178 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.049846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.1249 | 0 | 0.14178 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.049846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.2123 | 0 | 0.14178 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.048601 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6038 | 0 | 0.14302 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.048066 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.7386 | 161 | 0.14356 | 23.113
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.048066 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.979 | 166 | 0.14356 | 23.8307
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.048066 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.9204 | 248 | 0.14356 | 35.6026
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.048066 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.244 | 546 | 0.14356 | 78.3831
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.048066 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -30.9064 | 0 | 0.14356 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.048066 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.62486 | 13 | 0.14356 | 1.8663
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1942 | 0 | 0.14981 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8848 | 0 | 0.14981 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2946 | 0 | 0.14981 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.041817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2653 | 0 | 0.14981 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.041815 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3381 | 0 | 0.14981 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.041815 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2545 | 0 | 0.14981 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9583 | 0 | 0.14984 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.787 | 0 | 0.14984 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2146 | 0 | 0.14984 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.4013 | 0 | 0.14984 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.4138 | 0 | 0.14984 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3637 | 0 | 0.14984 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0113 | 0 | 0.14984 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.041784 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1953 | 0 | 0.14984 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.041784 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6714 | 0 | 0.14984 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.039222 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9611 | 50 | 0.1524 | 7.6201
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.037224 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1544 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1753 | 0 | 0.15673 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0566 | 0 | 0.15673 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0357 | 0 | 0.15673 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9017 | 0 | 0.15673 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.034893 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42569 | 0 | 0.15673 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2086 | 0 | 0.15765 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0387 | 0 | 0.15765 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2086 | 0 | 0.15765 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.033979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2086 | 0 | 0.15765 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5005 | 46 | 0.159 | 7.3142
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5005 | 46 | 0.159 | 7.3142
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5005 | 46 | 0.159 | 7.3142
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7941 | 55 | 0.159 | 8.7453
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7941 | 55 | 0.159 | 8.7453
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.03262 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7615 | 54 | 0.159 | 8.5863
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.032281 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5179 | 0 | 0.15934 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.032281 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5825 | 0 | 0.15934 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1919 | 0 | 0.15981 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9978 | 0 | 0.15981 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.0105 | 0 | 0.15981 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9946 | 0 | 0.15981 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.031813 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.5577 | 0 | 0.15981 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.031433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1002 | 0 | 0.16019 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.031026 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.37231 | 12 | 0.1606 | 1.9272
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.031026 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1606 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.031003 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.2395 | 169 | 0.16062 | 27.1451
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.03097 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.1101 | 165 | 0.16065 | 26.508
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.030946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.611 | 0 | 0.16068 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.030946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0146 | 0 | 0.16068 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.030862 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.5736 | 213 | 0.16076 | 34.2425
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.030852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4998 | 0 | 0.16077 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.974 | 0 | 0.16078 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9493 | 0 | 0.16078 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5477 | 0 | 0.16078 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.030844 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2701 | 0 | 0.16078 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.03083 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.0292 | 228 | 0.16079 | 36.6612
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.030816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.5469 | 0 | 0.16081 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.030816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8874 | 0 | 0.16081 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.030816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8381 | 0 | 0.16081 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1471 | 0 | 0.16138 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1774 | 0 | 0.16138 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1794 | 0 | 0.16138 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.030241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90723 | 0 | 0.16138 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.029329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.9887 | 0 | 0.1623 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2288 | 42 | 0.16237 | 6.8195
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2288 | 42 | 0.16237 | 6.8195
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1117 | 38 | 0.16237 | 6.17
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.029256 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1117 | 38 | 0.16237 | 6.17
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.029022 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0208 | 0 | 0.1626 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.029022 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.918 | 0 | 0.1626 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8659 | 104 | 0.16407 | 17.063
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8659 | 104 | 0.16407 | 17.063
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4881 | 54 | 0.16407 | 8.8597
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4605 | 53 | 0.16407 | 8.6956
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4881 | 54 | 0.16407 | 8.8597
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5707 | 57 | 0.16407 | 9.3519
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4881 | 54 | 0.16407 | 8.8597
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4881 | 54 | 0.16407 | 8.8597
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5983 | 58 | 0.16407 | 9.5159
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.027557 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5983 | 58 | 0.16407 | 9.5159
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.026994 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -19.8406 | 735 | 0.16463 | 121.0036
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90505 | 0 | 0.16501 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92368 | 0 | 0.16501 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.87044 | 0 | 0.16501 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2218 | 0 | 0.16501 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47116 | 0 | 0.16501 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54303 | 0 | 0.16501 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52972 | 0 | 0.16501 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93166 | 0 | 0.16501 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47914 | 0 | 0.16501 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2733 | 0 | 0.16501 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.026619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.9396 | 0 | 0.16501 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.026139 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31367 | 12 | 0.16549 | 1.9858
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.025531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12765 | 0 | 0.16609 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.025531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53615 | 0 | 0.16609 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6589 | 0 | 0.1661 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6844 | 0 | 0.1661 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7865 | 0 | 0.1661 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6078 | 0 | 0.1661 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5823 | 0 | 0.1661 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6542 | 0 | 0.1661 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.025521 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5057 | 0 | 0.1661 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.025492 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.3059 | 0 | 0.16613 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.025449 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -18.9086 | 743 | 0.16618 | 123.4686
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.025168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.9514 | 0 | 0.16646 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.024984 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2972 | 172 | 0.16664 | 28.6622
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.024984 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2972 | 172 | 0.16664 | 28.6622
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.024984 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.2972 | 172 | 0.16664 | 28.6622
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8896 | 0 | 0.16773 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8562 | 0 | 0.16773 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7964 | 0 | 0.16773 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.023892 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4317 | 0 | 0.16773 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.023514 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.3586 | 398 | 0.16811 | 66.9081
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2795 | 56 | 0.16878 | 9.4514
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3481 | 59 | 0.16878 | 9.9578
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2795 | 56 | 0.16878 | 9.4514
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2795 | 56 | 0.16878 | 9.4514
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3481 | 59 | 0.16878 | 9.9578
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.022849 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2795 | 56 | 0.16878 | 9.4514
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8396 | 0 | 0.17521 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5606 | 0 | 0.17521 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5278 | 0 | 0.17521 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5278 | 0 | 0.17521 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.016414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6591 | 0 | 0.17521 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19162 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.19162 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.19162 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1334
| 65 | 1307
| 70 | 1280
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| Max | 1340
| Min | 994
| Avg | 1239.6