## test results
CRE test for: |  | Brownwood Switch - Goldthwaite [1655 - 7070] | [5 empty] | FAIL
Line Rating: |  | 265
Direction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Brownwood Switch - Goldthwaite [1655 - 7070]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.018389
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.026461
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.033463
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.0075781
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Brownwood Switch - Goldthwaite [1655 - 7070]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.020792
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.027075
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.033597
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0072392
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Brownwood Switch - Goldthwaite [1655 - 7070]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.045465
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.015207
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.025629
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.060058
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.018883
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.040702
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | -0.047253 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.047253 | 0.045465
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.020832
[6 empty] | Concentration |  | -0.44086 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.041743
[6 empty] | Concentration |  | -0.88339 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 21.2191
| Percent of line rating => | [6 empty] | 8.007% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -8.9033
[7 empty] | B1(N-S) | 0.0028613 | -0.40193 | -0.40479 | 0.0028613
[7 empty] | B2 (N-W) | -0.15201 | -0.016614 | 0.13539 | -0.15201
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.0090277 | -0.21915 | -0.22818 | 0.0090277
[7 empty] | B4 (S-W) | -0.14513 | 0.38958 | 0.53471 | -0.14513
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.018925 | 0.18705 | 0.16812 | 0.018925
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.16059 | -0.20179 | -0.36239 | 0.16059
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | 0.6801%
Deployment Error Percent | [6 empty] | B2 | -36.13%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 2.146%
[7 empty] | B4 | -34.5%
[7 empty] | B5 | 4.498%
[7 empty] | B6 | 38.17%
[7 empty] | Max Abs Error | 38.17% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | n-s
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: Brownwood Switch - Goldthwaite [1655 - 7070] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: Brownwood Switch - Goldthwaite [1655 - 7070] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 3.3176
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.01301 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.9385
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.015485 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.23228
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.015485 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.23228
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.01301 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.9905
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.013462 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 2.0193
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.013462 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 1.077
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.031827 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 2.3234
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.031827 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 3.7874
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.031827 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 6.5245
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.031827 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 3.2464
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.031827 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 3.0554
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.029332 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.35198
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.029332 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.35198
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.024645 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 4.1404
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.024645 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 2.218
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.027877 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.50179
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.027877 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.50179
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.027877 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 1.0593
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.02606 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 7.5053
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.02606 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.8308
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.02606 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.8308
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.024265 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 2.7298
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.02009 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.8036
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.020139 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 1.591
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.020139 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 2.1347
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.020139 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 2.9403
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.020139 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 1.5306
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.022797 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.3678
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.022797 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.4362
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.020052 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.40104
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.020053 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.50133
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.020053 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.82217
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.003498 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 1.6196
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 2.2101
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 2.1767
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.2436
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.2436
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.2436
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.033487 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 3.8175
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.033487 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 17.2458
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 2.2521
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.3545
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.3545
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.2862
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.2862
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 2.218
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.033895 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 2.3727
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.033895 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 2.4879
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.033895 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 2.3862
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 5.088
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 7.4624
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034163 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 3.3821
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034163 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 2.0839
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.034161 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 4.8167
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034163 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.85408
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034163 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.5612
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034163 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.5612
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.034161 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 4.0993
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.034642 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.89376
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.033964 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 3.4134
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.034251 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 4.1101
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.033886 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 1.9654
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.033919 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 7.2654
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.035537 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 5.3305
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.03579 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.23621
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.03579 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.2276
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.035537 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 3.5892
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.034258 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 4.111
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.028602 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 10.4683
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.030174 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 7.3021
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.031876 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 12.7504
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.031869 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 7.5211
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.031085 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 5.129
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.026518 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 5.4097
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.026518 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 5.3301
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.026518 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 6.4174
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.57384
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.57384
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.57384
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.48776
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.029599 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 3.5519
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.040151 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 2.4091
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.020408 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 1.5306
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.020408 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 1.6245
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.020408 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 1.8041
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 3.2717
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 3.1899
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 4.0078
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 3.1899
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 3.2103
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 4.0487
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.020696 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 3.5183
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.020696 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 10.7619
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020513 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 7.5898
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.020329 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 11.3436
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.020329 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 11.7705
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.020329 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 16.4258
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.024012 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 2.6893
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.024012 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 2.4012
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.024012 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 9.0765
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.027705 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 6.0203
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.027705 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 5.6795
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.027705 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 7.5468
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.02649 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 20.3973
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 1.927
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.8995
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.8995
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 1.872
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.02853 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 33.0092
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.02853 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 33.0377
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 4.7705
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 4.8131
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.019905 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 4.3074
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.019905 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 4.3015
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 4.515
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 4.4937
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.022636 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 8.9412
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.022435 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 9.7592
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.022636 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 9.8467
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.021133 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 2.9164
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.020284 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 2.3935
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.020284 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 2.3327
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.020284 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 11.2779
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.019891 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 7.7177
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.019891 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 10.2439
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.017879 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 14.035
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.017879 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 14.2138
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.017879 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 13.9456
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.017282 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 3.1453
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.017282 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 8.3645
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.017422 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 3.9025
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.017401 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.87005
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.01742 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.73164
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.014689 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 9.0337
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.014689 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 8.6224
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.013082 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 7.025
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.013082 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 10.2955
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.007354 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.55155
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.007354 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 1.6326
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.026975 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -15.3488
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.025784 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -5.3889
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.025784 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -5.5693
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.025853 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -10.5222
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.1861
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -1.2118
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.1861
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.1861
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.025872 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -10.9697
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.025872 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -10.9956
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.025727 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -1.4922
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.025727 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -2.2897
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.132
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.132
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -1.1063
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.1577
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.025831 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -10.6424
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.025831 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -10.3324
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.02552 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -13.9339
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.02552 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -19.14
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.02584 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -1.5762
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.02584 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -2.4548
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.02584 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -3.9018
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.025794 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.9981
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.025794 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -4.385
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.025794 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.9981
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.020568 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.4525
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.020568 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.22625
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.020568 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.22625
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.99001
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.77416
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.95473
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.99624
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.021505 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.25806
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.021505 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.23655
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.022038 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.52891
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.022038 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.52891
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.022038 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.50687
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.023827 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -9.4355
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.013886 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -18.51
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.013886 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -18.4406
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.021356 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.81153
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.021356 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.41217
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.021356 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.32034
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.021356 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -1.0037
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.031899 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 2.3924
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.034205 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 5.1307
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.036674 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 6.2162
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.023191 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 3.4787
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.034204 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 2.1549
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.030641 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 19.9075
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.020836 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.83344
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.020836 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.83344
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.073428 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -30.9866
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.029567 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -3.9028
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.029567 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -3.962
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.029567 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -9.5501
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.027277 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -4.3098
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.027277 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -4.3643
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.027277 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -4.7735
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.025479 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -14.8797
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.025479 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -15.16
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.025467 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -11.0272
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -6.0822
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -6.1121
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -6.1013
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -6.1583
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.034155 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.27324
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.034155 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.27324
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.10244 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.8439
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.10244 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.8439
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.10244 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -1.5366
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.087859 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -1.2037
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.064709 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.1648
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.064709 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.1648
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.044936 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -1.5728
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.044936 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -1.5278
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.044936 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -1.5728
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.074493 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -2.0858
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.074493 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -2.1603
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.033509 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.1728
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.033509 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.0053
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.3338
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.3338
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.3338
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.3338
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.030304 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.18182
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.027054 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.06493
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.027054 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.06493
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.027054 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.075751
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.026824 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.1073
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.026383 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.063319
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.026383 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.063319
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.7983
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -3.5658
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -3.6175
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.7983
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -4.7027
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -5.1161
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.028395 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -4.3302
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.028395 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -4.2451
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.028395 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -6.6047
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -3.7613
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -3.8408
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -3.9997
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -7.6815
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.00685 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.22605
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.00685 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.17125
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.021505 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.25806
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.020787 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -1.5175
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -1.5428
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -1.5818
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.56557
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.14139
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -1.5428
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -1.5623
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -1.5311
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.48823
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.89833
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.022011 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -13.8449
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.021001 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -3.0241
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.021001 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -3.9482
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.024755 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.29706
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.011599 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.069594
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.021152 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -7.1071
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.021198 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -7.0801
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.021198 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -7.2073
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.021221 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.8064
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.021201 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.53002
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.021201 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.53002
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.021223 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.80647
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.021319 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.61825
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.021154 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -3.1371
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.021154 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -3.1435
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.021154 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -3.2366
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -3.3099
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -3.2052
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -2.0949
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -3.0376
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -3.0795
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -2.6605
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.021397 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -3.1347
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.021397 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -3.1646
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.021397 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -3.7017
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.021381 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -4.4259
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.021381 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -4.6333
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.021381 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -5.1742
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.02138 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -3.0787
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.02138 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -3.0787
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.02138 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -3.656
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.03328 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -10.3168
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.03328 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -13.7446
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -1.3849
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -1.4509
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -1.4509
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -1.5498
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -1.6136
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -1.5148
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -1.5148
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -1.5478
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.032931 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -5.0714
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.032931 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -4.8738
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -1.5807
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -1.5807
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.3614
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.3614
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 3.1305
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.6987
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.6987
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 3.8794
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 7.023
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 4.7933
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 4.4661
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 4.5876
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 4.9586
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 7.0837
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 6.9538
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 4.2089
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 8.2847
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 6.5546
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 6.784
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 4.1348
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.033574 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 5.0025
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.034094 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 6.1369
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.034094 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 6.1369
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.034082 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 7.6684
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.033724 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 4.2155
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.033724 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 4.2155
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 2.8718
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 2.8923
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 6.3385
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 2.9334
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 2.9539
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 6.359
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.019302 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 3.7832
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.019302 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 2.1425
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.020844 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 3.1535
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 3.2123
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 3.2123
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 8.109
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 3.1731
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 3.1535
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 3.1927
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 8.0111
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.019945 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.019945 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 2.6119
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 2.2942
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 2.559
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 7.0416
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.015191 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 2.2893
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.015191 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 2.2938
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.015191 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 2.6949
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.015262 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 2.3122
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.015262 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 2.3244
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.015262 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 2.709
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.026975 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -15.6725
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 7.0161
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 7.0161
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.002829 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.090528
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.0025 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.12
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.0025 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.115
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.034164
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.1452
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002847 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.048399
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.062634
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.071175
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.0025 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.2625
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.034171 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 2.8704
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.031861 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 2.5489
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.031846 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.7769
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.031846 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.7769
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.55521
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.52306
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.41563
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -1.2014
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -1.2037
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -1.1943
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.75283
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -1.9134
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.31368
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.78695
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.72889
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.80578
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.80029
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.007845 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.25104
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.007845 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.23535
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.1361
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.1361
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -1.218
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -1.1207
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 1.2498
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 1.2555
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.006384 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.86822
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.00864 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.28512
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.26788
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.26788
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.24236
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.24236
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.010635 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.75509
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.010635 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.10635
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.008773 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.43
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.008773 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.43
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.008773 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -2.1494
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.45045
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.4158
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.45045
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.45045
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.006575 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.97967
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.006575 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.42803
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.64028
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.61635
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.61213
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.38346
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.085839
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.005935 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -4.4097
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.006115 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -4.4945
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.005881 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.0115
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.005881 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.0115
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.005881 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.0115
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.84459
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.006349 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -1.0984
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.006349 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.85711
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.93675
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.9287
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.91431
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -1.549
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.42003
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.41478
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.5421
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.48304
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -1.09
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -1.0493
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -1.0519
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -1.0486
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -1.7967
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.005944 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.02972
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.005944 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.12482
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 0.32737
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.33119
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.33119
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 0.80674
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.005708 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -2.2718
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.31124
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.31124
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.31124
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.37213
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.37213
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.36536
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.010145 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 8.3899
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.010145 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 8.3088
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.008847 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.40785
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -1.0418
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -1.0418
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -1.4393
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -1.0144
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -1.0144
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -1.3982
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.006559 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -1.1806
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.006559 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -1.0403
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.006559 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -1.0298
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.006631 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.23209
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.007309 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -3.3548
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.38623
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.39217
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.41594
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.37435
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.3684
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.61797
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.35058
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.76159
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.75183
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.75183
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004882 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.79088
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.005901 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.92646
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.461
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.4675
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.25323
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.19479
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.006731 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.52502
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.006731 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.53848
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.006564 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.10634
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.006578 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -1.0854
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.006582 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -1.1124
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.006565 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -1.3983
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.006561 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -1.4959
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.006584 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.079008
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.006584 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.11851
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.007534 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.3767
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.6421
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.6421
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.3334
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.32722
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.3334
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.35192
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.3334
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.3334
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.35809
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.35809
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.00601 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.07212
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.31522
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.33211
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.31522
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.31522
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.33211
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.31522
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.013127 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.86638
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.008551 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -1.3767
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.008551 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -1.4195
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.008551 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -2.1206
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.008551 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -4.6688
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.008551 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -5.4983
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.008784 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -5.7184
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.008784 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -4.9542
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.008784 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -5.2704
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.008551 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.11116
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.00594 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.07128
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.20641
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.21066
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.19852
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.27866
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.10746
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.12385
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.12081
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.21249
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.10928
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.51846
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.89851
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.69025
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.7949
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.50099
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -1.1244
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.95744
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.9797
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.55665
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.20039
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -1.0465
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.77931
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.70138
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.80158
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.72142
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -1.1244
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -1.0799
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -1.1467
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.84611
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.89064
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.89064
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -1.9037
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.18179
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.031186 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 2.3857
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.031899 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 2.5519
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.031899 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.276
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.03204 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.5632
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.031865 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 2.5492
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.031181 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 2.4945
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.030956 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 2.6003
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.03204 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.5632
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -3.3533
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.035987 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 4.3184
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.035987 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 8.385
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.035987 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 6.125
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -6.5301
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -5.4124
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -6.589
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -3.3827
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -2.9415
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.033776 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 2.0266
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.027075 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.027326 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.03244 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.15571
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 1.2708
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 3.643
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 4.5749
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 4.0327
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 3.5582
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 2.728
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.035734 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 5.3601
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 4.0588
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 5.3937
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 6.7105
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 7.7387
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.021356 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.012704 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.021991 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.54681
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.85146
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -1.4451
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -2.0067
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.87527
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.81122
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.40561
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -2.0067
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.76853
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.91796
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.46966
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.78776
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.30299
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.14139
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.30299
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.78776
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.78776
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -3.1595
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -1.0674
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -1.1741
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -1.0674
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.020949 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.25139
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.020415 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.30623
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.020415 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.46954
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.019687 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.94498
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.020281 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.16225
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.021158 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -3.8084
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.021152 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -3.8074
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.021198 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -3.8156
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.021198 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -3.8156
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.021993 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -2.1993
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.021993 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -2.1993
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.52575
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.52575
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.52575
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.33648
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.52575
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.52575
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.52575
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.31545
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.021993 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.021993 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -10.9965
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.021993 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -10.9965
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.021993 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.022233 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.00685 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.021608 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.021616 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L: Brownwood Switch - Goldthwaite [1655 - 7070] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | [7 empty] | 21.2191
Number of Bus | Name of Bus | ID | Max MW | L: Brownwood Switch - Goldthwaite [1655 - 7070] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.01301 | north | Y | -0.0053794 | 0.039471 | -0.020453 | 0.020588 | 0.0053794 | North | N | 0.0053794 | 0
239 | BOSQUESW | 1 | 149 | 0.01301 | north | Y | -0.0053794 | 0.039471 | -0.020453 | 0.020588 | 0.0053794 | North | N | 0.0053794 | 0
244 | WHITNYDM | 1 | 15 | 0.015485 | north | N | -0.0029044 | 0.041946 | -0.017978 | 0.023063 | 0.0029044 | North | N | 0.0029044 | 0
245 | WHITNYDM | 2 | 15 | 0.015485 | north | N | -0.0029044 | 0.041946 | -0.017978 | 0.023063 | 0.0029044 | North | N | 0.0029044 | 0
247 | BOSQUESW | 2 | 153 | 0.01301 | north | Y | -0.0053794 | 0.039471 | -0.020453 | 0.020588 | 0.0053794 | North | N | 0.0053794 | 0
251 | BOSQUESW | 2 | 150 | 0.013462 | north | Y | -0.0049274 | 0.039923 | -0.020001 | 0.02104 | 0.0049274 | North | N | 0.0049274 | 0
253 | BOSQUESW | 2 | 80 | 0.013462 | north | Y | -0.0049274 | 0.039923 | -0.020001 | 0.02104 | 0.0049274 | North | N | 0.0049274 | 0
332 | RWMILLER | 1 | 73 | 0.031827 | north | Y | 0.013438 | 0.058288 | -0.0016361 | 0.039405 | 0.0016361 | west | Y | 0.013438 | 0.86151
333 | RWMILLER | 2 | 119 | 0.031827 | north | Y | 0.013438 | 0.058288 | -0.0016361 | 0.039405 | 0.0016361 | west | Y | 0.013438 | 1.4044
334 | RWMILLER | 3 | 205 | 0.031827 | north | Y | 0.013438 | 0.058288 | -0.0016361 | 0.039405 | 0.0016361 | west | Y | 0.013438 | 2.4193
335 | RWMILLER | 4 | 102 | 0.031827 | north | Y | 0.013438 | 0.058288 | -0.0016361 | 0.039405 | 0.0016361 | west | Y | 0.013438 | 1.2038
336 | RWMILLER | 5 | 96 | 0.031827 | north | Y | 0.013438 | 0.058288 | -0.0016361 | 0.039405 | 0.0016361 | west | Y | 0.013438 | 1.1329
344 | MRSSHPRD | 1 | 12 | 0.029332 | north | N | 0.010943 | 0.055793 | -0.0041311 | 0.03691 | 0.0041311 | west | Y | 0.010943 | 0
345 | MRSSHPRD | 2 | 12 | 0.029332 | north | N | 0.010943 | 0.055793 | -0.0041311 | 0.03691 | 0.0041311 | west | Y | 0.010943 | 0
366 | JNSNCNTY | 1 | 168 | 0.024645 | north | Y | 0.0062556 | 0.051106 | -0.0088181 | 0.032223 | 0.0062556 | North | N | 0.0062556 | 0
367 | JNSNCNTY | 2 | 90 | 0.024645 | north | Y | 0.0062556 | 0.051106 | -0.0088181 | 0.032223 | 0.0062556 | North | N | 0.0062556 | 0
503 | NTHTEXAS | 1 | 18 | 0.027877 | north | Y | 0.0094876 | 0.054338 | -0.0055861 | 0.035455 | 0.0055861 | west | Y | 0.0094876 | 0.070227
504 | NTHTEXAS | 2 | 18 | 0.027877 | north | Y | 0.0094876 | 0.054338 | -0.0055861 | 0.035455 | 0.0055861 | west | Y | 0.0094876 | 0.070227
505 | NTHTEXAS | 3 | 38 | 0.027877 | north | Y | 0.0094876 | 0.054338 | -0.0055861 | 0.035455 | 0.0055861 | west | Y | 0.0094876 | 0.14826
580 | JCKCNTY8 | 1 | 288 | 0.02606 | north | Y | 0.0076706 | 0.052521 | -0.0074031 | 0.033638 | 0.0074031 | west | Y | 0.0076706 | 0.077039
581 | JCKCNTY8 | 2 | 147 | 0.02606 | north | Y | 0.0076706 | 0.052521 | -0.0074031 | 0.033638 | 0.0074031 | west | Y | 0.0076706 | 0.039322
582 | JCKCNTY8 | 3 | 147 | 0.02606 | north | Y | 0.0076706 | 0.052521 | -0.0074031 | 0.033638 | 0.0074031 | west | Y | 0.0076706 | 0.039322
728 | WOLFRIDG | 1 | 112.5 | 0.024265 | north | Y | 0.0058756 | 0.050726 | -0.0091981 | 0.031843 | 0.0058756 | North | N | 0.0058756 | 0
837 | NEWMAN_G | 1 | 40 | 0.02009 | north | Y | 0.0017006 | 0.046551 | -0.013373 | 0.027668 | 0.0017006 | North | N | 0.0017006 | 0
842 | OLINGER_ | 1 | 79 | 0.020139 | north | Y | 0.0017496 | 0.0466 | -0.013324 | 0.027717 | 0.0017496 | North | N | 0.0017496 | 0
843 | OLINGER_ | 1 | 106 | 0.020139 | north | Y | 0.0017496 | 0.0466 | -0.013324 | 0.027717 | 0.0017496 | North | N | 0.0017496 | 0
844 | OLINGER_ | 1 | 146 | 0.020139 | north | Y | 0.0017496 | 0.0466 | -0.013324 | 0.027717 | 0.0017496 | North | N | 0.0017496 | 0
845 | OLINGER_ | 1 | 76 | 0.020139 | north | Y | 0.0017496 | 0.0466 | -0.013324 | 0.027717 | 0.0017496 | North | N | 0.0017496 | 0
923 | SPENCER_ | 1 | 60 | 0.022797 | north | Y | 0.0044076 | 0.049258 | -0.010666 | 0.030375 | 0.0044076 | North | N | 0.0044076 | 0
924 | SPENCER_ | 1 | 63 | 0.022797 | north | Y | 0.0044076 | 0.049258 | -0.010666 | 0.030375 | 0.0044076 | North | N | 0.0044076 | 0
948 | STEAM1 | 1 | 20 | 0.020052 | north | Y | 0.0016626 | 0.046513 | -0.013411 | 0.02763 | 0.0016626 | North | N | 0.0016626 | 0
949 | STEAM2 | 1 | 25 | 0.020053 | north | Y | 0.0016636 | 0.046514 | -0.01341 | 0.027631 | 0.0016636 | North | N | 0.0016636 | 0
950 | STEAM3 | 1 | 41 | 0.020053 | north | Y | 0.0016636 | 0.046514 | -0.01341 | 0.027631 | 0.0016636 | North | N | 0.0016636 | 0
990 | GIBN_CRE | 1 | 463 | 0.003498 | north | Y | -0.014891 | 0.029959 | -0.029965 | 0.011076 | 0.011076 | houston | Y | 0.014891 | 1.7665
1002 | PBCTAGE_ | A | 66 | 0.033487 | west | Y | 0.015098 | 0.059948 | 2.3902e-05 | 0.041065 | 2.3902e-05 | west | N | 2.3902e-05 | 0
1003 | PBCTBGE_ | B | 65 | 0.033487 | west | Y | 0.015098 | 0.059948 | 2.3902e-05 | 0.041065 | 2.3902e-05 | west | N | 2.3902e-05 | 0
1004 | PBCTCGE_ | C | 67 | 0.033487 | west | Y | 0.015098 | 0.059948 | 2.3902e-05 | 0.041065 | 2.3902e-05 | west | N | 2.3902e-05 | 0
1005 | PBCTDGE_ | D | 67 | 0.033487 | west | Y | 0.015098 | 0.059948 | 2.3902e-05 | 0.041065 | 2.3902e-05 | west | N | 2.3902e-05 | 0
1006 | PBCTEGE_ | E | 67 | 0.033487 | west | Y | 0.015098 | 0.059948 | 2.3902e-05 | 0.041065 | 2.3902e-05 | west | N | 2.3902e-05 | 0
1007 | PB5GEN_6 | MB | 114 | 0.033487 | west | Y | 0.015098 | 0.059948 | 2.3902e-05 | 0.041065 | 2.3902e-05 | west | N | 2.3902e-05 | 0
1008 | PB6GEN_7 | MB | 515 | 0.033487 | west | Y | 0.015098 | 0.059948 | 2.3902e-05 | 0.041065 | 2.3902e-05 | west | N | 2.3902e-05 | 0
1039 | MRGNAG_1 | A | 66 | 0.034123 | west | Y | 0.015734 | 0.060584 | 0.0006599 | 0.041701 | 0.0006599 | west | N | 0.0006599 | 0
1040 | MRGNBG_2 | B | 69 | 0.034123 | west | Y | 0.015734 | 0.060584 | 0.0006599 | 0.041701 | 0.0006599 | west | N | 0.0006599 | 0
1041 | MRGNCG_3 | C | 69 | 0.034123 | west | Y | 0.015734 | 0.060584 | 0.0006599 | 0.041701 | 0.0006599 | west | N | 0.0006599 | 0
1042 | MRGNDG_4 | D | 67 | 0.034123 | west | Y | 0.015734 | 0.060584 | 0.0006599 | 0.041701 | 0.0006599 | west | N | 0.0006599 | 0
1043 | MRGNEG_5 | E | 67 | 0.034123 | west | Y | 0.015734 | 0.060584 | 0.0006599 | 0.041701 | 0.0006599 | west | N | 0.0006599 | 0
1044 | MRGNFG_6 | F | 65 | 0.034123 | west | Y | 0.015734 | 0.060584 | 0.0006599 | 0.041701 | 0.0006599 | west | N | 0.0006599 | 0
1045 | CALENG1G | 1 | 70 | 0.033895 | west | N | 0.015506 | 0.060356 | 0.0004319 | 0.041473 | 0.0004319 | west | N | 0.0004319 | 0
1046 | CALENG2G | 2 | 73.4 | 0.033895 | west | N | 0.015506 | 0.060356 | 0.0004319 | 0.041473 | 0.0004319 | west | N | 0.0004319 | 0
1047 | CALENG3G | 3 | 70.4 | 0.033895 | west | N | 0.015506 | 0.060356 | 0.0004319 | 0.041473 | 0.0004319 | west | N | 0.0004319 | 0
1058 | LONGSHOR | 1 | 150 | 0.03392 | west | Y | 0.015531 | 0.060381 | 0.0004569 | 0.041498 | 0.0004569 | west | N | 0.0004569 | 0
1058 | LONGSHOR | 2 | 220 | 0.03392 | west | Y | 0.015531 | 0.060381 | 0.0004569 | 0.041498 | 0.0004569 | west | N | 0.0004569 | 0
1061 | CIELOGEN | 1 | 99 | 0.034163 | west | Y | 0.015774 | 0.060624 | 0.0006999 | 0.041741 | 0.0006999 | west | N | 0.0006999 | 0
1062 | CIELOGEN | 1 | 61 | 0.034163 | west | Y | 0.015774 | 0.060624 | 0.0006999 | 0.041741 | 0.0006999 | west | N | 0.0006999 | 0
1068 | SCURRYCW | 1 | 141 | 0.034161 | west | Y | 0.015772 | 0.060622 | 0.0006979 | 0.041739 | 0.0006979 | west | N | 0.0006979 | 0
1069 | KINDERMG | 1 | 25 | 0.034163 | west | N | 0.015774 | 0.060624 | 0.0006999 | 0.041741 | 0.0006999 | west | N | 0.0006999 | 0
1070 | KINDERMG | 1 | 45.7 | 0.034163 | west | N | 0.015774 | 0.060624 | 0.0006999 | 0.041741 | 0.0006999 | west | N | 0.0006999 | 0
1071 | KINDERMG | 1 | 45.7 | 0.034163 | west | N | 0.015774 | 0.060624 | 0.0006999 | 0.041741 | 0.0006999 | west | N | 0.0006999 | 0
1073 | SCURRYCW | 2 | 120 | 0.034161 | west | Y | 0.015772 | 0.060622 | 0.0006979 | 0.041739 | 0.0006979 | west | N | 0.0006979 | 0
1320 | BSP 1 | 1 | 25.8 | 0.034642 | west | N | 0.016253 | 0.061103 | 0.0011789 | 0.04222 | 0.0011789 | west | N | 0.0011789 | 0
1326 | STANTONW | 1 | 100.5 | 0.033964 | west | Y | 0.015575 | 0.060425 | 0.0005009 | 0.041542 | 0.0005009 | west | N | 0.0005009 | 0
1327 | WILDHRSE | 1 | 120 | 0.034251 | west | Y | 0.015862 | 0.060712 | 0.0007879 | 0.041829 | 0.0007879 | west | N | 0.0007879 | 0
1328 | OCOTILLO | 1 | 58 | 0.033886 | west | Y | 0.015497 | 0.060347 | 0.0004229 | 0.041464 | 0.0004229 | west | N | 0.0004229 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.033919 | west | Y | 0.01553 | 0.06038 | 0.0004559 | 0.041497 | 0.0004559 | west | N | 0.0004559 | 0
1343 | TRENTIPP | 1 | 150 | 0.035537 | west | Y | 0.017148 | 0.061998 | 0.0020739 | 0.043115 | 0.0020739 | west | N | 0.0020739 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.03579 | west | Y | 0.017401 | 0.062251 | 0.0023269 | 0.043368 | 0.0023269 | west | N | 0.0023269 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.03579 | west | Y | 0.017401 | 0.062251 | 0.0023269 | 0.043368 | 0.0023269 | west | N | 0.0023269 | 0
1354 | AEPWIND_ | 1 | 101 | 0.035537 | west | Y | 0.017148 | 0.061998 | 0.0020739 | 0.043115 | 0.0020739 | west | N | 0.0020739 | 0
1360 | GUNSIGHT | 1 | 120 | 0.034258 | west | Y | 0.015869 | 0.060719 | 0.0007949 | 0.041836 | 0.0007949 | west | N | 0.0007949 | 0
1432 | GRHAMSES | 2 | 366 | 0.028602 | north | Y | 0.010213 | 0.055063 | -0.0048611 | 0.03618 | 0.0048611 | west | Y | 0.010213 | 1.9586
1433 | GRHAMSES | 1 | 242 | 0.030174 | north | Y | 0.011785 | 0.056635 | -0.0032891 | 0.037752 | 0.0032891 | west | Y | 0.011785 | 2.0559
1437 | MESQUITW | 1 | 400 | 0.031876 | west | Y | 0.013487 | 0.058337 | -0.0015871 | 0.039454 | 0.0015871 | west | N | 0.0015871 | 0
1438 | MESQUITW | 1 | 236 | 0.031869 | west | Y | 0.01348 | 0.05833 | -0.0015941 | 0.039447 | 0.0015941 | west | N | 0.0015941 | 0
1442 | COKFIELD | 1 | 165 | 0.031085 | west | Y | 0.012696 | 0.057546 | -0.0023781 | 0.038663 | 0.0023781 | west | N | 0.0023781 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.026518 | north | Y | 0.0081286 | 0.052979 | -0.0069451 | 0.034096 | 0.0069451 | west | Y | 0.0081286 | 0.24143
1454 | WCPWRCO_ | 2 | 201 | 0.026518 | north | Y | 0.0081286 | 0.052979 | -0.0069451 | 0.034096 | 0.0069451 | west | Y | 0.0081286 | 0.23788
1455 | WCPWRCO_ | 3 | 242 | 0.026518 | north | Y | 0.0081286 | 0.052979 | -0.0069451 | 0.034096 | 0.0069451 | west | Y | 0.0081286 | 0.28641
1479 | WFCOGEN_ | 1 | 20 | 0.028692 | west | Y | 0.010303 | 0.055153 | -0.0047711 | 0.03627 | 0.0047711 | west | N | 0.0047711 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.028692 | west | Y | 0.010303 | 0.055153 | -0.0047711 | 0.03627 | 0.0047711 | west | N | 0.0047711 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.028692 | west | Y | 0.010303 | 0.055153 | -0.0047711 | 0.03627 | 0.0047711 | west | N | 0.0047711 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.028692 | west | Y | 0.010303 | 0.055153 | -0.0047711 | 0.03627 | 0.0047711 | west | N | 0.0047711 | 0
1600 | BARTNWND | 1 | 120 | 0.029599 | north | Y | 0.01121 | 0.05606 | -0.0038641 | 0.037177 | 0.0038641 | west | Y | 0.01121 | 0.88146
1643 | SLSTR1PP | 1 | 60 | 0.040151 | north | Y | 0.021762 | 0.066612 | 0.0066879 | 0.047729 | 0.0066879 | west | Y | 0.021762 | 0.90442
1675 | PEC_1G | 1 | 75 | 0.020408 | north | N | 0.0020186 | 0.046869 | -0.013055 | 0.027986 | 0.0020186 | North | N | 0.0020186 | 0
1676 | PEC_2G | 2 | 79.6 | 0.020408 | north | N | 0.0020186 | 0.046869 | -0.013055 | 0.027986 | 0.0020186 | North | N | 0.0020186 | 0
1677 | PEC_3G | 3 | 88.4 | 0.020408 | north | N | 0.0020186 | 0.046869 | -0.013055 | 0.027986 | 0.0020186 | North | N | 0.0020186 | 0
1678 | LAMARPWR | 1 | 160 | 0.020448 | north | Y | 0.0020586 | 0.046909 | -0.013015 | 0.028026 | 0.0020586 | North | N | 0.0020586 | 0
1679 | LAMARPWR | 2 | 156 | 0.020448 | north | Y | 0.0020586 | 0.046909 | -0.013015 | 0.028026 | 0.0020586 | North | N | 0.0020586 | 0
1680 | LAMARPWR | 3 | 196 | 0.020448 | north | Y | 0.0020586 | 0.046909 | -0.013015 | 0.028026 | 0.0020586 | North | N | 0.0020586 | 0
1681 | LAMARPWR | 4 | 156 | 0.020448 | north | Y | 0.0020586 | 0.046909 | -0.013015 | 0.028026 | 0.0020586 | North | N | 0.0020586 | 0
1682 | LAMARPWR | 5 | 157 | 0.020448 | north | Y | 0.0020586 | 0.046909 | -0.013015 | 0.028026 | 0.0020586 | North | N | 0.0020586 | 0
1683 | LAMARPWR | 6 | 198 | 0.020448 | north | Y | 0.0020586 | 0.046909 | -0.013015 | 0.028026 | 0.0020586 | North | N | 0.0020586 | 0
1687 | VALLEY_1 | 1 | 170 | 0.020696 | north | Y | 0.0023066 | 0.047157 | -0.012767 | 0.028274 | 0.0023066 | North | N | 0.0023066 | 0
1688 | VALLEY_2 | 2 | 520 | 0.020696 | north | Y | 0.0023066 | 0.047157 | -0.012767 | 0.028274 | 0.0023066 | North | N | 0.0023066 | 0
1689 | VALLEY_3 | 3 | 370 | 0.020513 | north | Y | 0.0021236 | 0.046974 | -0.01295 | 0.028091 | 0.0021236 | North | N | 0.0021236 | 0
1701 | MOSES_1G | 1 | 558 | 0.020329 | north | Y | 0.0019396 | 0.04679 | -0.013134 | 0.027907 | 0.0019396 | North | N | 0.0019396 | 0
1702 | MOSES_2G | 2 | 579 | 0.020329 | north | Y | 0.0019396 | 0.04679 | -0.013134 | 0.027907 | 0.0019396 | North | N | 0.0019396 | 0
1703 | MOSES_3G | 3 | 808 | 0.020329 | north | Y | 0.0019396 | 0.04679 | -0.013134 | 0.027907 | 0.0019396 | North | N | 0.0019396 | 0
1861 | EAGLEMNT | MB | 112 | 0.024012 | north | Y | 0.0056226 | 0.050473 | -0.0094511 | 0.03159 | 0.0056226 | North | N | 0.0056226 | 0
1862 | EAGLEMNT | MB | 100 | 0.024012 | north | Y | 0.0056226 | 0.050473 | -0.0094511 | 0.03159 | 0.0056226 | North | N | 0.0056226 | 0
1863 | EAGLEMNT | MB | 378 | 0.024012 | north | Y | 0.0056226 | 0.050473 | -0.0094511 | 0.03159 | 0.0056226 | North | N | 0.0056226 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.027705 | north | Y | 0.0093156 | 0.054166 | -0.0057581 | 0.035283 | 0.0057581 | west | Y | 0.0093156 | 0.77304
1878 | WLFHOLW_ | 2 | 205 | 0.027705 | north | Y | 0.0093156 | 0.054166 | -0.0057581 | 0.035283 | 0.0057581 | west | Y | 0.0093156 | 0.72929
1879 | WLFHOLW_ | 3 | 272.4 | 0.027705 | north | Y | 0.0093156 | 0.054166 | -0.0057581 | 0.035283 | 0.0057581 | west | Y | 0.0093156 | 0.96906
1889 | DECRDOVA | MB | 770 | 0.02649 | north | Y | 0.0081006 | 0.052951 | -0.0069731 | 0.034068 | 0.0069731 | west | Y | 0.0081006 | 0
1892 | DECRDOVA | A | 70 | 0.027529 | north | Y | 0.0091396 | 0.05399 | -0.0059341 | 0.035107 | 0.0059341 | west | Y | 0.0091396 | 0.22438
1893 | DECRDOVA | B | 69 | 0.027529 | north | Y | 0.0091396 | 0.05399 | -0.0059341 | 0.035107 | 0.0059341 | west | Y | 0.0091396 | 0.22118
1894 | DECRDOVA | C | 69 | 0.027529 | north | Y | 0.0091396 | 0.05399 | -0.0059341 | 0.035107 | 0.0059341 | west | Y | 0.0091396 | 0.22118
1895 | DECRDOVA | D | 68 | 0.027529 | north | Y | 0.0091396 | 0.05399 | -0.0059341 | 0.035107 | 0.0059341 | west | Y | 0.0091396 | 0.21797
1898 | COMCHEPK | 1 | 1157 | 0.02853 | north | N | 0.010141 | 0.054991 | -0.0049331 | 0.036108 | 0.0049331 | west | Y | 0.010141 | 0
1899 | COMCHEPK | 2 | 1158 | 0.02853 | north | N | 0.010141 | 0.054991 | -0.0049331 | 0.036108 | 0.0049331 | west | Y | 0.010141 | 0
1937 | MDLTHELP | 5 | 224 | 0.021297 | north | Y | 0.0029076 | 0.047758 | -0.012166 | 0.028875 | 0.0029076 | North | N | 0.0029076 | 0
1938 | MDLTHELP | 6 | 226 | 0.021297 | north | Y | 0.0029076 | 0.047758 | -0.012166 | 0.028875 | 0.0029076 | North | N | 0.0029076 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.019905 | north | Y | 0.0015156 | 0.046366 | -0.013558 | 0.027483 | 0.0015156 | North | N | 0.0015156 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.019905 | north | Y | 0.0015156 | 0.046366 | -0.013558 | 0.027483 | 0.0015156 | North | N | 0.0015156 | 0
1943 | MDLTHELP | 3 | 212 | 0.021297 | north | Y | 0.0029076 | 0.047758 | -0.012166 | 0.028875 | 0.0029076 | North | N | 0.0029076 | 0
1944 | MDLTHELP | 4 | 211 | 0.021297 | north | Y | 0.0029076 | 0.047758 | -0.012166 | 0.028875 | 0.0029076 | North | N | 0.0029076 | 0
1947 | HANDLEY_ | 3 | 395 | 0.022636 | north | Y | 0.0042466 | 0.049097 | -0.010827 | 0.030214 | 0.0042466 | North | N | 0.0042466 | 0
1948 | HANDLEY_ | 4 | 435 | 0.022435 | north | Y | 0.0040456 | 0.048896 | -0.011028 | 0.030013 | 0.0040456 | North | N | 0.0040456 | 0
1949 | HANDLEY_ | 5 | 435 | 0.022636 | north | Y | 0.0042466 | 0.049097 | -0.010827 | 0.030214 | 0.0042466 | North | N | 0.0042466 | 0
2371 | COLLIN_1 | MB | 138 | 0.021133 | north | Y | 0.0027436 | 0.047594 | -0.01233 | 0.028711 | 0.0027436 | North | N | 0.0027436 | 0
2413 | MTCK6_G | 6 | 118 | 0.020284 | north | Y | 0.0018946 | 0.046745 | -0.013179 | 0.027862 | 0.0018946 | North | N | 0.0018946 | 0
2414 | MTCK7_G | 7 | 115 | 0.020284 | north | Y | 0.0018946 | 0.046745 | -0.013179 | 0.027862 | 0.0018946 | North | N | 0.0018946 | 0
2417 | MTCK8_G | 8 | 556 | 0.020284 | north | Y | 0.0018946 | 0.046745 | -0.013179 | 0.027862 | 0.0018946 | North | N | 0.0018946 | 0
2451 | LKHB1_G | 1 | 388 | 0.019891 | north | Y | 0.0015016 | 0.046352 | -0.013572 | 0.027469 | 0.0015016 | North | N | 0.0015016 | 0
2452 | LKHB2_G | 2 | 515 | 0.019891 | north | Y | 0.0015016 | 0.046352 | -0.013572 | 0.027469 | 0.0015016 | North | N | 0.0015016 | 0
3097 | MARTLAKE | 1 | 785 | 0.017879 | north | Y | -0.0005104 | 0.04434 | -0.015584 | 0.025457 | 0.0005104 | North | N | 0.0005104 | 0
3098 | MARTLAKE | 2 | 795 | 0.017879 | north | Y | -0.0005104 | 0.04434 | -0.015584 | 0.025457 | 0.0005104 | North | N | 0.0005104 | 0
3099 | MARTLAKE | 3 | 780 | 0.017879 | north | Y | -0.0005104 | 0.04434 | -0.015584 | 0.025457 | 0.0005104 | North | N | 0.0005104 | 0
3107 | STRYKER_ | 1 | 182 | 0.017282 | north | Y | -0.0011074 | 0.043743 | -0.016181 | 0.02486 | 0.0011074 | North | N | 0.0011074 | 0
3108 | STRYKER_ | 2 | 484 | 0.017282 | north | Y | -0.0011074 | 0.043743 | -0.016181 | 0.02486 | 0.0011074 | North | N | 0.0011074 | 0
3126 | TRINIDAD | 1 | 224 | 0.017422 | north | Y | -0.0009674 | 0.043883 | -0.016041 | 0.025 | 0.0009674 | North | N | 0.0009674 | 0
3309 | ASPN_G | 1 | 50 | 0.017401 | north | Y | -0.0009884 | 0.043862 | -0.016062 | 0.024979 | 0.0009884 | North | N | 0.0009884 | 0
3348 | CHAMPION | MB | 42 | 0.01742 | north | N | -0.0009694 | 0.043881 | -0.016043 | 0.024998 | 0.0009694 | North | N | 0.0009694 | 0
3381 | BBRN_1G | 1 | 615 | 0.014689 | north | Y | -0.0037004 | 0.04115 | -0.018774 | 0.022267 | 0.0037004 | North | N | 0.0037004 | 0
3382 | BBRN_2G | 2 | 587 | 0.014689 | north | Y | -0.0037004 | 0.04115 | -0.018774 | 0.022267 | 0.0037004 | North | N | 0.0037004 | 0
3403 | THOUSE_1 | MB | 537 | 0.013082 | north | Y | -0.0053074 | 0.039543 | -0.020381 | 0.02066 | 0.0053074 | North | N | 0.0053074 | 0
3404 | THOUSE_2 | 2 | 787 | 0.013082 | north | Y | -0.0053074 | 0.039543 | -0.020381 | 0.02066 | 0.0053074 | North | N | 0.0053074 | 0
3416 | LAKE_CRK | MB | 75 | 0.007354 | north | Y | -0.011035 | 0.033815 | -0.026109 | 0.014932 | 0.011035 | North | N | 0.011035 | 0
3417 | LAKE_CRK | MB | 222 | 0.007354 | north | Y | -0.011035 | 0.033815 | -0.026109 | 0.014932 | 0.011035 | North | N | 0.011035 | 0
3432 | SANDOW_4 | 4 | 569 | -0.026975 | south | Y | -0.045364 | -0.000514 | -0.060438 | -0.019397 | 0.000514 | south | N | 0.000514 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.025784 | south | Y | -0.044173 | 0.000677 | -0.059247 | -0.018206 | 0.000677 | south | N | 0.000677 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.025784 | south | Y | -0.044173 | 0.000677 | -0.059247 | -0.018206 | 0.000677 | south | N | 0.000677 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.025853 | south | Y | -0.044242 | 0.000608 | -0.059316 | -0.018275 | 0.000608 | south | N | 0.000608 | 0
5031 | BRA_VHBC | 1 | 46 | -0.025784 | south | Y | -0.044173 | 0.000677 | -0.059247 | -0.018206 | 0.000677 | south | N | 0.000677 | 0
5032 | BRA_VHBC | 2 | 47 | -0.025784 | south | Y | -0.044173 | 0.000677 | -0.059247 | -0.018206 | 0.000677 | south | N | 0.000677 | 0
5033 | BRA_VHBC | 3 | 46 | -0.025784 | south | Y | -0.044173 | 0.000677 | -0.059247 | -0.018206 | 0.000677 | south | N | 0.000677 | 0
5034 | BRA_VHBC | 4 | 46 | -0.025784 | south | Y | -0.044173 | 0.000677 | -0.059247 | -0.018206 | 0.000677 | south | N | 0.000677 | 0
5111 | CALAVER_ | 1 | 424 | -0.025872 | south | Y | -0.044261 | 0.000589 | -0.059335 | -0.018294 | 0.000589 | south | N | 0.000589 | 0
5112 | CALAVER_ | 2 | 425 | -0.025872 | south | Y | -0.044261 | 0.000589 | -0.059335 | -0.018294 | 0.000589 | south | N | 0.000589 | 0
5264 | LEON_LCP | 3 | 58 | -0.025727 | south | Y | -0.044116 | 0.000734 | -0.05919 | -0.018149 | 0.000734 | south | N | 0.000734 | 0
5265 | LEON_LCP | 4 | 89 | -0.025727 | south | Y | -0.044116 | 0.000734 | -0.05919 | -0.018149 | 0.000734 | south | N | 0.000734 | 0
5266 | LEON_LCP | 1 | 44 | -0.025727 | south | Y | -0.044116 | 0.000734 | -0.05919 | -0.018149 | 0.000734 | south | N | 0.000734 | 0
5267 | LEON_LCP | 2 | 44 | -0.025727 | south | Y | -0.044116 | 0.000734 | -0.05919 | -0.018149 | 0.000734 | south | N | 0.000734 | 0
5268 | LEON_LCP | 3 | 43 | -0.025727 | south | Y | -0.044116 | 0.000734 | -0.05919 | -0.018149 | 0.000734 | south | N | 0.000734 | 0
5269 | LEON_LCP | 4 | 45 | -0.025727 | south | Y | -0.044116 | 0.000734 | -0.05919 | -0.018149 | 0.000734 | south | N | 0.000734 | 0
5396 | CALAVER_ | 1 | 412 | -0.025831 | south | Y | -0.04422 | 0.00063 | -0.059294 | -0.018253 | 0.00063 | south | N | 0.00063 | 0
5397 | CALAVER_ | 2 | 400 | -0.025831 | south | Y | -0.04422 | 0.00063 | -0.059294 | -0.018253 | 0.00063 | south | N | 0.00063 | 0
5401 | CALAVER_ | 1 | 546 | -0.02552 | south | Y | -0.043909 | 0.000941 | -0.058983 | -0.017942 | 0.000941 | south | N | 0.000941 | 0
5402 | CALAVER_ | 2 | 750 | -0.02552 | south | Y | -0.043909 | 0.000941 | -0.058983 | -0.017942 | 0.000941 | south | N | 0.000941 | 0
5436 | TUTTL_WB | MB | 61 | -0.02584 | south | Y | -0.044229 | 0.000621 | -0.059303 | -0.018262 | 0.000621 | south | N | 0.000621 | 0
5438 | TUTTL_WB | MB | 95 | -0.02584 | south | Y | -0.044229 | 0.000621 | -0.059303 | -0.018262 | 0.000621 | south | N | 0.000621 | 0
5439 | TUTTL_WB | MB | 151 | -0.02584 | south | Y | -0.044229 | 0.000621 | -0.059303 | -0.018262 | 0.000621 | south | N | 0.000621 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.025794 | south | Y | -0.044183 | 0.000667 | -0.059257 | -0.018216 | 0.000667 | south | N | 0.000667 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.025794 | south | Y | -0.044183 | 0.000667 | -0.059257 | -0.018216 | 0.000667 | south | N | 0.000667 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.025794 | south | Y | -0.044183 | 0.000667 | -0.059257 | -0.018216 | 0.000667 | south | N | 0.000667 | 0
5503 | RAYBURNG | 1 | 22 | -0.020568 | south | Y | -0.038957 | 0.005893 | -0.054031 | -0.01299 | 0.005893 | south | N | 0.005893 | 0
5505 | RAYBURNG | 1 | 11 | -0.020568 | south | Y | -0.038957 | 0.005893 | -0.054031 | -0.01299 | 0.005893 | south | N | 0.005893 | 0
5506 | RAYBURNG | 1 | 11 | -0.020568 | south | Y | -0.038957 | 0.005893 | -0.054031 | -0.01299 | 0.005893 | south | N | 0.005893 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.020755 | south | Y | -0.039144 | 0.005706 | -0.054218 | -0.013177 | 0.005706 | south | N | 0.005706 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.020755 | south | Y | -0.039144 | 0.005706 | -0.054218 | -0.013177 | 0.005706 | south | N | 0.005706 | 0
5511 | RAYBURNC | 1 | 46 | -0.020755 | south | Y | -0.039144 | 0.005706 | -0.054218 | -0.013177 | 0.005706 | south | N | 0.005706 | 0
5512 | RAYBURNC | 1 | 48 | -0.020755 | south | Y | -0.039144 | 0.005706 | -0.054218 | -0.013177 | 0.005706 | south | N | 0.005706 | 0
5728 | FALCONHY | 2 | 12 | -0.021505 | south | N | -0.039894 | 0.004956 | -0.054968 | -0.013927 | 0.004956 | south | N | 0.004956 | 0
5729 | FALCONHY | 3 | 11 | -0.021505 | south | N | -0.039894 | 0.004956 | -0.054968 | -0.013927 | 0.004956 | south | N | 0.004956 | 0
5890 | PEARSALL | 1 | 24 | -0.022038 | south | Y | -0.040427 | 0.004423 | -0.055501 | -0.01446 | 0.004423 | south | N | 0.004423 | 0
5891 | PEARSALL | 1 | 24 | -0.022038 | south | Y | -0.040427 | 0.004423 | -0.055501 | -0.01446 | 0.004423 | south | N | 0.004423 | 0
5892 | PEARSALL | 1 | 23 | -0.022038 | south | Y | -0.040427 | 0.004423 | -0.055501 | -0.01446 | 0.004423 | south | N | 0.004423 | 0
5903 | SANMIGUE | 1 | 396 | -0.023827 | south | Y | -0.042216 | 0.002634 | -0.05729 | -0.016249 | 0.002634 | south | N | 0.002634 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.013886 | houston | N | -0.032275 | 0.012575 | -0.047349 | -0.0063079 | 0.0063079 | houston | N | 0.0063079 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.013886 | houston | N | -0.032275 | 0.012575 | -0.047349 | -0.0063079 | 0.0063079 | houston | N | 0.0063079 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.018389 | 0
5932 | SI_RAY9 | 9 | 38 | -0.021356 | south | Y | -0.039745 | 0.005105 | -0.054819 | -0.013778 | 0.005105 | south | N | 0.005105 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.021356 | south | Y | -0.039745 | 0.005105 | -0.054819 | -0.013778 | 0.005105 | south | N | 0.005105 | 0
5934 | SI_RAY5 | 5 | 15 | -0.021356 | south | Y | -0.039745 | 0.005105 | -0.054819 | -0.013778 | 0.005105 | south | N | 0.005105 | 0
5935 | SI_RAY10 | 10 | 47 | -0.021356 | south | Y | -0.039745 | 0.005105 | -0.054819 | -0.013778 | 0.005105 | south | N | 0.005105 | 0
6016 | SWMESA | 1 | 75 | 0.031899 | west | Y | 0.01351 | 0.05836 | -0.0015641 | 0.039477 | 0.0015641 | west | N | 0.0015641 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.033463 | 0
6144 | MCADOO1A | 1 | 150 | 0.034205 | west | Y | 0.015816 | 0.060666 | 0.0007419 | 0.041783 | 0.0007419 | west | N | 0.0007419 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.036674 | west | Y | 0.018285 | 0.063135 | 0.0032109 | 0.044252 | 0.0032109 | west | N | 0.0032109 | 0
6476 | LANGFORD | 1 | 150 | 0.023191 | west | Y | 0.0048016 | 0.049652 | -0.010272 | 0.030769 | 0.0048016 | North | Y | 0.010272 | 0.82058
6637 | SNYDERW1 | 1 | 63 | 0.034204 | west | Y | 0.015815 | 0.060665 | 0.0007409 | 0.041782 | 0.0007409 | west | N | 0.0007409 | 0
6752 | OKLA0A | 1 | 649.7 | 0.030641 | west | Y | 0.012252 | 0.057102 | -0.0028221 | 0.038219 | 0.0028221 | west | N | 0.0028221 | 0
6948 | DENISNDM | 1 | 40 | 0.020836 | north | N | 0.0024466 | 0.047297 | -0.012627 | 0.028414 | 0.0024466 | North | N | 0.0024466 | 0
6948 | DENISNDM | 2 | 40 | 0.020836 | north | N | 0.0024466 | 0.047297 | -0.012627 | 0.028414 | 0.0024466 | North | N | 0.0024466 | 0
7000 | L_FERGUS | 1 | 422 | -0.073428 | south | Y | -0.091817 | -0.046967 | -0.10689 | -0.06585 | 0.046967 | south | N | 0.046967 | 0
7004 | L_SIMGID | 1 | 132 | -0.029567 | south | Y | -0.047956 | -0.003106 | -0.06303 | -0.021989 | 0.003106 | south | N | 0.003106 | 0
7005 | L_SIMGID | 2 | 134 | -0.029567 | south | Y | -0.047956 | -0.003106 | -0.06303 | -0.021989 | 0.003106 | south | N | 0.003106 | 0
7006 | L_SIMGID | 3 | 323 | -0.029567 | south | Y | -0.047956 | -0.003106 | -0.06303 | -0.021989 | 0.003106 | south | N | 0.003106 | 0
7007 | L_LOSTPI | 1 | 158 | -0.027277 | south | Y | -0.045666 | -0.000816 | -0.06074 | -0.019699 | 0.000816 | south | N | 0.000816 | 0
7008 | L_LOSTPI | 2 | 160 | -0.027277 | south | Y | -0.045666 | -0.000816 | -0.06074 | -0.019699 | 0.000816 | south | N | 0.000816 | 0
7009 | L_LOSTPI | 3 | 175 | -0.027277 | south | Y | -0.045666 | -0.000816 | -0.06074 | -0.019699 | 0.000816 | south | N | 0.000816 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.025479 | south | Y | -0.043868 | 0.000982 | -0.058942 | -0.017901 | 0.000982 | south | N | 0.000982 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.025479 | south | Y | -0.043868 | 0.000982 | -0.058942 | -0.017901 | 0.000982 | south | N | 0.000982 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.025467 | south | Y | -0.043856 | 0.000994 | -0.05893 | -0.017889 | 0.000994 | south | N | 0.000994 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.027165 | south | Y | -0.045554 | -0.000704 | -0.060628 | -0.019587 | 0.000704 | south | N | 0.000704 | 0
7015 | L_HAYSEN | 2 | 225 | -0.027165 | south | Y | -0.045554 | -0.000704 | -0.060628 | -0.019587 | 0.000704 | south | N | 0.000704 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.027165 | south | Y | -0.045554 | -0.000704 | -0.060628 | -0.019587 | 0.000704 | south | N | 0.000704 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.027165 | south | Y | -0.045554 | -0.000704 | -0.060628 | -0.019587 | 0.000704 | south | N | 0.000704 | 0
7020 | L_AUSTPL | 1 | 8 | -0.034155 | south | N | -0.052544 | -0.007694 | -0.067618 | -0.026577 | 0.007694 | south | N | 0.007694 | 0
7020 | L_AUSTPL | 2 | 8 | -0.034155 | south | N | -0.052544 | -0.007694 | -0.067618 | -0.026577 | 0.007694 | south | N | 0.007694 | 0
7022 | L_BUCHAN | 1 | 18 | -0.10244 | south | N | -0.12083 | -0.07598 | -0.1359 | -0.094863 | 0.07598 | south | N | 0.07598 | 0
7023 | L_BUCHAN | 2 | 18 | -0.10244 | south | N | -0.12083 | -0.07598 | -0.1359 | -0.094863 | 0.07598 | south | N | 0.07598 | 0
7024 | L_BUCHAN | 3 | 15 | -0.10244 | south | N | -0.12083 | -0.07598 | -0.1359 | -0.094863 | 0.07598 | south | N | 0.07598 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.087859 | south | N | -0.10625 | -0.061398 | -0.12132 | -0.080281 | 0.061398 | south | N | 0.061398 | 0
7028 | L_MARBFA | 1 | 18 | -0.064709 | south | N | -0.083098 | -0.038248 | -0.098172 | -0.057131 | 0.038248 | south | N | 0.038248 | 0
7029 | L_MARBFA | 2 | 18 | -0.064709 | south | N | -0.083098 | -0.038248 | -0.098172 | -0.057131 | 0.038248 | south | N | 0.038248 | 0
7031 | L_MARSFO | 1 | 35 | -0.044936 | south | N | -0.063325 | -0.018475 | -0.078399 | -0.037358 | 0.018475 | south | N | 0.018475 | 0
7032 | L_MARSFO | 2 | 34 | -0.044936 | south | N | -0.063325 | -0.018475 | -0.078399 | -0.037358 | 0.018475 | south | N | 0.018475 | 0
7033 | L_MARSFO | 3 | 35 | -0.044936 | south | N | -0.063325 | -0.018475 | -0.078399 | -0.037358 | 0.018475 | south | N | 0.018475 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.074493 | south | N | -0.092882 | -0.048032 | -0.10796 | -0.066915 | 0.048032 | south | N | 0.048032 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.074493 | south | N | -0.092882 | -0.048032 | -0.10796 | -0.066915 | 0.048032 | south | N | 0.048032 | 0
7038 | L_DELAWA | 1 | 35 | 0.033509 | west | Y | 0.01512 | 0.05997 | 4.5902e-05 | 0.041087 | 4.5902e-05 | west | N | 4.5902e-05 | 0
7038 | L_DELAWA | 2 | 30 | 0.033509 | west | Y | 0.01512 | 0.05997 | 4.5902e-05 | 0.041087 | 4.5902e-05 | west | N | 4.5902e-05 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.026677 | south | Y | -0.045066 | -0.000216 | -0.06014 | -0.019099 | 0.000216 | south | N | 0.000216 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.026677 | south | Y | -0.045066 | -0.000216 | -0.06014 | -0.019099 | 0.000216 | south | N | 0.000216 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.026677 | south | Y | -0.045066 | -0.000216 | -0.06014 | -0.019099 | 0.000216 | south | N | 0.000216 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.026677 | south | Y | -0.045066 | -0.000216 | -0.06014 | -0.019099 | 0.000216 | south | N | 0.000216 | 0
7487 | L_CANYHY | 1 | 6 | -0.030304 | south | N | -0.048693 | -0.003843 | -0.063767 | -0.022726 | 0.003843 | south | N | 0.003843 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.027054 | south | N | -0.045443 | -0.000593 | -0.060517 | -0.019476 | 0.000593 | south | N | 0.000593 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.027054 | south | N | -0.045443 | -0.000593 | -0.060517 | -0.019476 | 0.000593 | south | N | 0.000593 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.027054 | south | N | -0.045443 | -0.000593 | -0.060517 | -0.019476 | 0.000593 | south | N | 0.000593 | 0
7609 | L_SCHUMA | 1 | 4 | -0.026824 | south | N | -0.045213 | -0.000363 | -0.060287 | -0.019246 | 0.000363 | south | N | 0.000363 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.026383 | south | N | -0.044772 | 7.8004e-05 | -0.059846 | -0.018805 | 7.8004e-05 | south | N | 7.8004e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.026383 | south | N | -0.044772 | 7.8004e-05 | -0.059846 | -0.018805 | 7.8004e-05 | south | N | 7.8004e-05 | 0
7800 | L_GUADGE | 1 | 147 | -0.025839 | south | Y | -0.044228 | 0.000622 | -0.059302 | -0.018261 | 0.000622 | south | N | 0.000622 | 0
7801 | L_GUADGE | 2 | 138 | -0.025839 | south | Y | -0.044228 | 0.000622 | -0.059302 | -0.018261 | 0.000622 | south | N | 0.000622 | 0
7802 | L_GUADGE | 3 | 140 | -0.025839 | south | Y | -0.044228 | 0.000622 | -0.059302 | -0.018261 | 0.000622 | south | N | 0.000622 | 0
7803 | L_GUADGE | 4 | 147 | -0.025839 | south | Y | -0.044228 | 0.000622 | -0.059302 | -0.018261 | 0.000622 | south | N | 0.000622 | 0
7804 | L_GUADGE | 5 | 182 | -0.025839 | south | Y | -0.044228 | 0.000622 | -0.059302 | -0.018261 | 0.000622 | south | N | 0.000622 | 0
7805 | L_GUADGE | 6 | 198 | -0.025839 | south | Y | -0.044228 | 0.000622 | -0.059302 | -0.018261 | 0.000622 | south | N | 0.000622 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.028395 | south | Y | -0.046784 | -0.001934 | -0.061858 | -0.020817 | 0.001934 | south | N | 0.001934 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.028395 | south | Y | -0.046784 | -0.001934 | -0.061858 | -0.020817 | 0.001934 | south | N | 0.001934 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.028395 | south | Y | -0.046784 | -0.001934 | -0.061858 | -0.020817 | 0.001934 | south | N | 0.001934 | 0
7810 | L_RIONOG | 1 | 142 | -0.026488 | south | Y | -0.044877 | -2.6996e-05 | -0.059951 | -0.01891 | 2.6996e-05 | south | N | 2.6996e-05 | 0
7811 | L_RIONOG | 2 | 145 | -0.026488 | south | Y | -0.044877 | -2.6996e-05 | -0.059951 | -0.01891 | 2.6996e-05 | south | N | 2.6996e-05 | 0
7812 | L_RIONOG | 3 | 151 | -0.026488 | south | Y | -0.044877 | -2.6996e-05 | -0.059951 | -0.01891 | 2.6996e-05 | south | N | 2.6996e-05 | 0
7813 | L_RIONOG | 4 | 290 | -0.026488 | south | Y | -0.044877 | -2.6996e-05 | -0.059951 | -0.01891 | 2.6996e-05 | south | N | 2.6996e-05 | 0
8032 | AMISTADH | 1 | 33 | -0.00685 | south | N | -0.025239 | 0.019611 | -0.040313 | 0.00072806 | 0.00072806 | houston | Y | 0.019611 | 0
8033 | AMISTADH | 2 | 25 | -0.00685 | south | N | -0.025239 | 0.019611 | -0.040313 | 0.00072806 | 0.00072806 | houston | Y | 0.019611 | 0
8048 | FALCONHY | 1 | 12 | -0.021505 | south | N | -0.039894 | 0.004956 | -0.054968 | -0.013927 | 0.004956 | south | N | 0.004956 | 0
8066 | DUP1V#1 | 1 | 73 | -0.020787 | south | N | -0.039176 | 0.005674 | -0.05425 | -0.013209 | 0.005674 | south | N | 0.005674 | 0
8134 | FOR69CG0 | 1 | 79 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
8138 | FOR69CG0 | 2 | 81 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.026461 | 0
8147 | UCAR #2 | 10 | 28 | -0.020199 | south | N | -0.038588 | 0.006262 | -0.053662 | -0.012621 | 0.006262 | south | N | 0.006262 | 0
8148 | UCAR #1 | 2 | 7 | -0.020199 | south | N | -0.038588 | 0.006262 | -0.053662 | -0.012621 | 0.006262 | south | N | 0.006262 | 0
8153 | FOR69CG0 | 3 | 79 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
8154 | FOR69CG0 | 4 | 80 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
8156 | FOR69CG0 | 6 | 25 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
8157 | FOR69CG0 | 7 | 46 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
8161 | COLETOU1 | 1 | 629 | -0.022011 | south | Y | -0.0404 | 0.00445 | -0.055474 | -0.014433 | 0.00445 | south | N | 0.00445 | 0
8173 | VICEC51A | 5 | 144 | -0.021001 | south | Y | -0.03939 | 0.00546 | -0.054464 | -0.013423 | 0.00546 | south | N | 0.00546 | 0
8174 | VICEC61A | 6 | 188 | -0.021001 | south | Y | -0.03939 | 0.00546 | -0.054464 | -0.013423 | 0.00546 | south | N | 0.00546 | 0
8189 | CUERO 2 | 1 | 12 | -0.024755 | south | N | -0.043144 | 0.001706 | -0.058218 | -0.017177 | 0.001706 | south | N | 0.001706 | 0
8262 | ELPS | 1 | 6 | -0.011599 | south | N | -0.029988 | 0.014862 | -0.045062 | -0.0040209 | 0.0040209 | houston | Y | 0.014862 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.026461 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.026461 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.026461 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.026461 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.026461 | 0
8442 | NBEC71A | 1 | 336 | -0.021152 | south | Y | -0.039541 | 0.005309 | -0.054615 | -0.013574 | 0.005309 | south | N | 0.005309 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.026461 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.018389 | 0.026461 | -0.033463 | 0.0075781 | 0.0075781 | houston | Y | 0.026461 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.021198 | south | Y | -0.039587 | 0.005263 | -0.054661 | -0.01362 | 0.005263 | south | N | 0.005263 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.021198 | south | Y | -0.039587 | 0.005263 | -0.054661 | -0.01362 | 0.005263 | south | N | 0.005263 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.021221 | south | N | -0.03961 | 0.00524 | -0.054684 | -0.013643 | 0.00524 | south | N | 0.00524 | 0
8506 | VAL #1 | 1 | 25 | -0.021201 | south | N | -0.03959 | 0.00526 | -0.054664 | -0.013623 | 0.00526 | south | N | 0.00526 | 0
8507 | VAL #2 | 2 | 25 | -0.021201 | south | N | -0.03959 | 0.00526 | -0.054664 | -0.013623 | 0.00526 | south | N | 0.00526 | 0
8511 | OXY_CC0A | 1 | 38 | -0.021223 | south | N | -0.039612 | 0.005238 | -0.054686 | -0.013645 | 0.005238 | south | N | 0.005238 | 0
8517 | CELANEBI | 1 | 29 | -0.021319 | south | N | -0.039708 | 0.005142 | -0.054782 | -0.013741 | 0.005142 | south | N | 0.005142 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.021154 | south | N | -0.039543 | 0.005307 | -0.054617 | -0.013576 | 0.005307 | south | N | 0.005307 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.021154 | south | N | -0.039543 | 0.005307 | -0.054617 | -0.013576 | 0.005307 | south | N | 0.005307 | 0
8562 | CNOPST1 | 3 | 153 | -0.021154 | south | N | -0.039543 | 0.005307 | -0.054617 | -0.013576 | 0.005307 | south | N | 0.005307 | 0
8926 | LGE_GT10 | 1 | 158 | -0.020949 | south | N | -0.039338 | 0.005512 | -0.054412 | -0.013371 | 0.005512 | south | N | 0.005512 | 0
8927 | LGE_GT20 | 2 | 153 | -0.020949 | south | N | -0.039338 | 0.005512 | -0.054412 | -0.013371 | 0.005512 | south | N | 0.005512 | 0
8928 | LGE_STG0 | 3 | 100 | -0.020949 | south | N | -0.039338 | 0.005512 | -0.054412 | -0.013371 | 0.005512 | south | N | 0.005512 | 0
8930 | ICPGN10A | 1 | 145 | -0.020949 | south | N | -0.039338 | 0.005512 | -0.054412 | -0.013371 | 0.005512 | south | N | 0.005512 | 0
8931 | ICPGN20A | 2 | 147 | -0.020949 | south | N | -0.039338 | 0.005512 | -0.054412 | -0.013371 | 0.005512 | south | N | 0.005512 | 0
8932 | ICPGN30A | 3 | 127 | -0.020949 | south | N | -0.039338 | 0.005512 | -0.054412 | -0.013371 | 0.005512 | south | N | 0.005512 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.021397 | south | Y | -0.039786 | 0.005064 | -0.05486 | -0.013819 | 0.005064 | south | N | 0.005064 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.021397 | south | Y | -0.039786 | 0.005064 | -0.05486 | -0.013819 | 0.005064 | south | N | 0.005064 | 0
8935 | FGNTS201 | 3 | 173 | -0.021397 | south | Y | -0.039786 | 0.005064 | -0.05486 | -0.013819 | 0.005064 | south | N | 0.005064 | 0
8936 | MVGN#1 | 1 | 207 | -0.021381 | south | Y | -0.03977 | 0.00508 | -0.054844 | -0.013803 | 0.00508 | south | N | 0.00508 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.021381 | south | Y | -0.03977 | 0.00508 | -0.054844 | -0.013803 | 0.00508 | south | N | 0.00508 | 0
8938 | MVGN#3 | 3 | 242 | -0.021381 | south | Y | -0.03977 | 0.00508 | -0.054844 | -0.013803 | 0.00508 | south | N | 0.00508 | 0
8981 | HECN1 | 1 | 144 | -0.02138 | south | Y | -0.039769 | 0.005081 | -0.054843 | -0.013802 | 0.005081 | south | N | 0.005081 | 0
8982 | HECN2 | 2 | 144 | -0.02138 | south | Y | -0.039769 | 0.005081 | -0.054843 | -0.013802 | 0.005081 | south | N | 0.005081 | 0
8983 | HECN3 | 3 | 171 | -0.02138 | south | Y | -0.039769 | 0.005081 | -0.054843 | -0.013802 | 0.005081 | south | N | 0.005081 | 0
9000 | DECKR_G1 | 1 | 310 | -0.03328 | south | Y | -0.051669 | -0.006819 | -0.066743 | -0.025702 | 0.006819 | south | N | 0.006819 | 0
9001 | DECKR_G2 | 2 | 413 | -0.03328 | south | Y | -0.051669 | -0.006819 | -0.066743 | -0.025702 | 0.006819 | south | N | 0.006819 | 0
9002 | DECKR_G3 | 3 | 42 | -0.032974 | south | Y | -0.051363 | -0.006513 | -0.066437 | -0.025396 | 0.006513 | south | N | 0.006513 | 0
9003 | DECKR_G4 | 4 | 44 | -0.032974 | south | Y | -0.051363 | -0.006513 | -0.066437 | -0.025396 | 0.006513 | south | N | 0.006513 | 0
9004 | DECKR_G5 | 5 | 44 | -0.032974 | south | Y | -0.051363 | -0.006513 | -0.066437 | -0.025396 | 0.006513 | south | N | 0.006513 | 0
9005 | DECKR_G6 | 6 | 47 | -0.032974 | south | Y | -0.051363 | -0.006513 | -0.066437 | -0.025396 | 0.006513 | south | N | 0.006513 | 0
9016 | SANDH_G1 | 1 | 49 | -0.032931 | south | Y | -0.05132 | -0.00647 | -0.066394 | -0.025353 | 0.00647 | south | N | 0.00647 | 0
9017 | SANDH_G2 | 2 | 46 | -0.032931 | south | Y | -0.05132 | -0.00647 | -0.066394 | -0.025353 | 0.00647 | south | N | 0.00647 | 0
9018 | SANDH_G3 | 3 | 46 | -0.032931 | south | Y | -0.05132 | -0.00647 | -0.066394 | -0.025353 | 0.00647 | south | N | 0.00647 | 0
9019 | SANDH_G4 | 4 | 47 | -0.032931 | south | Y | -0.05132 | -0.00647 | -0.066394 | -0.025353 | 0.00647 | south | N | 0.00647 | 0
9020 | SANDHG5A | 5A | 154 | -0.032931 | south | Y | -0.05132 | -0.00647 | -0.066394 | -0.025353 | 0.00647 | south | N | 0.00647 | 0
9021 | SANDHG5C | 5C | 148 | -0.032931 | south | Y | -0.05132 | -0.00647 | -0.066394 | -0.025353 | 0.00647 | south | N | 0.00647 | 0
9022 | SANDH_G6 | 6 | 48 | -0.032931 | south | Y | -0.05132 | -0.00647 | -0.066394 | -0.025353 | 0.00647 | south | N | 0.00647 | 0
9023 | SANDH_G7 | 7 | 48 | -0.032931 | south | Y | -0.05132 | -0.00647 | -0.066394 | -0.025353 | 0.00647 | south | N | 0.00647 | 0
11001 | NAV1CT | 1 | 70 | 0.033734 | west | Y | 0.015345 | 0.060195 | 0.0002709 | 0.041312 | 0.0002709 | west | N | 0.0002709 | 0
11009 | NAV2CT | 1 | 70 | 0.033734 | west | Y | 0.015345 | 0.060195 | 0.0002709 | 0.041312 | 0.0002709 | west | N | 0.0002709 | 0
11011 | NAV3ST | 1 | 92.8 | 0.033734 | west | Y | 0.015345 | 0.060195 | 0.0002709 | 0.041312 | 0.0002709 | west | N | 0.0002709 | 0
11012 | NAV4CT | 1 | 80 | 0.033734 | west | Y | 0.015345 | 0.060195 | 0.0002709 | 0.041312 | 0.0002709 | west | N | 0.0002709 | 0
11013 | NAV5CT | 1 | 80 | 0.033734 | west | Y | 0.015345 | 0.060195 | 0.0002709 | 0.041312 | 0.0002709 | west | N | 0.0002709 | 0
11014 | NAV6ST | 1 | 115 | 0.033734 | west | Y | 0.015345 | 0.060195 | 0.0002709 | 0.041312 | 0.0002709 | west | N | 0.0002709 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.033732 | west | Y | 0.015343 | 0.060193 | 0.0002689 | 0.04131 | 0.0002689 | west | N | 0.0002689 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.033732 | west | Y | 0.015343 | 0.060193 | 0.0002689 | 0.04131 | 0.0002689 | west | N | 0.0002689 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.033732 | west | Y | 0.015343 | 0.060193 | 0.0002689 | 0.04131 | 0.0002689 | west | N | 0.0002689 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.033732 | west | Y | 0.015343 | 0.060193 | 0.0002689 | 0.04131 | 0.0002689 | west | N | 0.0002689 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.033732 | west | Y | 0.015343 | 0.060193 | 0.0002689 | 0.04131 | 0.0002689 | west | N | 0.0002689 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.033732 | west | Y | 0.015343 | 0.060193 | 0.0002689 | 0.04131 | 0.0002689 | west | N | 0.0002689 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.033272 | west | Y | 0.014883 | 0.059733 | -0.0001911 | 0.04085 | 0.0001911 | west | N | 0.0001911 | 0
11057 | CHAMPION | 1 | 126.5 | 0.033272 | west | Y | 0.014883 | 0.059733 | -0.0001911 | 0.04085 | 0.0001911 | west | N | 0.0001911 | 0
11058 | PYRON_1G | 1 | 249 | 0.033272 | west | Y | 0.014883 | 0.059733 | -0.0001911 | 0.04085 | 0.0001911 | west | N | 0.0001911 | 0
11059 | INADALE_ | 1 | 197 | 0.033272 | west | Y | 0.014883 | 0.059733 | -0.0001911 | 0.04085 | 0.0001911 | west | N | 0.0001911 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.03392 | west | Y | 0.015531 | 0.060381 | 0.0004569 | 0.041498 | 0.0004569 | west | N | 0.0004569 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.03392 | west | Y | 0.015531 | 0.060381 | 0.0004569 | 0.041498 | 0.0004569 | west | N | 0.0004569 | 0
11147 | NOTREES_ | 1 | 149 | 0.033574 | west | Y | 0.015185 | 0.060035 | 0.0001109 | 0.041152 | 0.0001109 | west | N | 0.0001109 | 0
11309 | BULLCREK | 1 | 180 | 0.034094 | west | Y | 0.015705 | 0.060555 | 0.0006309 | 0.041672 | 0.0006309 | west | N | 0.0006309 | 0
11310 | BULLCREK | 1 | 180 | 0.034094 | west | Y | 0.015705 | 0.060555 | 0.0006309 | 0.041672 | 0.0006309 | west | N | 0.0006309 | 0
11320 | COYOTE_1 | 1 | 225 | 0.034082 | west | Y | 0.015693 | 0.060543 | 0.0006189 | 0.04166 | 0.0006189 | west | N | 0.0006189 | 0
11415 | LORAINE_ | 1 | 125 | 0.033724 | west | Y | 0.015335 | 0.060185 | 0.0002609 | 0.041302 | 0.0002609 | west | N | 0.0002609 | 0
11416 | LORAINE_ | 1 | 125 | 0.033724 | west | Y | 0.015335 | 0.060185 | 0.0002609 | 0.041302 | 0.0002609 | west | N | 0.0002609 | 0
11691 | KMICHICT | 1 | 140 | 0.020513 | north | N | 0.0021236 | 0.046974 | -0.01295 | 0.028091 | 0.0021236 | North | N | 0.0021236 | 0
11692 | KMICHICT | 2 | 141 | 0.020513 | north | N | 0.0021236 | 0.046974 | -0.01295 | 0.028091 | 0.0021236 | North | N | 0.0021236 | 0
11693 | KMICHIST | 3 | 309 | 0.020513 | north | N | 0.0021236 | 0.046974 | -0.01295 | 0.028091 | 0.0021236 | North | N | 0.0021236 | 0
11694 | KMICHICT | 4 | 143 | 0.020513 | north | N | 0.0021236 | 0.046974 | -0.01295 | 0.028091 | 0.0021236 | North | N | 0.0021236 | 0
11695 | KMICHICT | 5 | 144 | 0.020513 | north | N | 0.0021236 | 0.046974 | -0.01295 | 0.028091 | 0.0021236 | North | N | 0.0021236 | 0
11696 | KMICHIST | 6 | 310 | 0.020513 | north | N | 0.0021236 | 0.046974 | -0.01295 | 0.028091 | 0.0021236 | North | N | 0.0021236 | 0
12322 | ENNSTRAC | 1 | 196 | 0.019302 | north | Y | 0.0009126 | 0.045763 | -0.014161 | 0.02688 | 0.0009126 | North | N | 0.0009126 | 0
12323 | ENNSTRAC | 2 | 111 | 0.019302 | north | Y | 0.0009126 | 0.045763 | -0.014161 | 0.02688 | 0.0009126 | North | N | 0.0009126 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.020844 | north | N | 0.0024546 | 0.047305 | -0.012619 | 0.028422 | 0.0024546 | North | N | 0.0024546 | 0
12411 | FPLEFR1A | 1 | 161 | 0.019587 | north | Y | 0.0011976 | 0.046048 | -0.013876 | 0.027165 | 0.0011976 | North | N | 0.0011976 | 0
12412 | FPLEFR1B | 2 | 164 | 0.019587 | north | Y | 0.0011976 | 0.046048 | -0.013876 | 0.027165 | 0.0011976 | North | N | 0.0011976 | 0
12413 | FPLEFR1C | 3 | 164 | 0.019587 | north | Y | 0.0011976 | 0.046048 | -0.013876 | 0.027165 | 0.0011976 | North | N | 0.0011976 | 0
12414 | FPLEFR1S | 4 | 414 | 0.019587 | north | Y | 0.0011976 | 0.046048 | -0.013876 | 0.027165 | 0.0011976 | North | N | 0.0011976 | 0
12421 | FPLEFR2A | 1 | 162 | 0.019587 | north | Y | 0.0011976 | 0.046048 | -0.013876 | 0.027165 | 0.0011976 | North | N | 0.0011976 | 0
12422 | FPLEFR2B | 2 | 161 | 0.019587 | north | Y | 0.0011976 | 0.046048 | -0.013876 | 0.027165 | 0.0011976 | North | N | 0.0011976 | 0
12423 | FPLEFR2C | 3 | 163 | 0.019587 | north | Y | 0.0011976 | 0.046048 | -0.013876 | 0.027165 | 0.0011976 | North | N | 0.0011976 | 0
12424 | FPLEFR2S | 4 | 409 | 0.019587 | north | Y | 0.0011976 | 0.046048 | -0.013876 | 0.027165 | 0.0011976 | North | N | 0.0011976 | 0
12440 | PARKD_1S | 1 | 0 | 0.019945 | north | N | 0.0015556 | 0.046406 | -0.013518 | 0.027523 | 0.0015556 | North | N | 0.0015556 | 0
12449 | PARKD_2S | 1 | 0 | 0.019945 | north | N | 0.0015556 | 0.046406 | -0.013518 | 0.027523 | 0.0015556 | North | N | 0.0015556 | 0
13116 | TGATEWAY | 1 | 148 | 0.017648 | north | N | -0.0007414 | 0.044109 | -0.015815 | 0.025226 | 0.0007414 | North | N | 0.0007414 | 0
13117 | TGATEWAY | 2 | 130 | 0.017648 | north | N | -0.0007414 | 0.044109 | -0.015815 | 0.025226 | 0.0007414 | North | N | 0.0007414 | 0
13118 | TGATEWAY | 3 | 145 | 0.017648 | north | N | -0.0007414 | 0.044109 | -0.015815 | 0.025226 | 0.0007414 | North | N | 0.0007414 | 0
13119 | TGATEWAY | 4 | 399 | 0.017648 | north | N | -0.0007414 | 0.044109 | -0.015815 | 0.025226 | 0.0007414 | North | N | 0.0007414 | 0
13131 | CALFREST | 1 | 150.7 | 0.015191 | north | Y | -0.0031984 | 0.041652 | -0.018272 | 0.022769 | 0.0031984 | North | N | 0.0031984 | 0
13132 | CALFREST | 2 | 151 | 0.015191 | north | Y | -0.0031984 | 0.041652 | -0.018272 | 0.022769 | 0.0031984 | North | N | 0.0031984 | 0
13133 | CALFREST | 3 | 177.4 | 0.015191 | north | Y | -0.0031984 | 0.041652 | -0.018272 | 0.022769 | 0.0031984 | North | N | 0.0031984 | 0
13134 | CALFREST | 4 | 151.5 | 0.015262 | north | Y | -0.0031274 | 0.041723 | -0.018201 | 0.02284 | 0.0031274 | North | N | 0.0031274 | 0
13135 | CALFREST | 5 | 152.3 | 0.015262 | north | Y | -0.0031274 | 0.041723 | -0.018201 | 0.02284 | 0.0031274 | North | N | 0.0031274 | 0
13136 | CALFREST | 6 | 177.5 | 0.015262 | north | Y | -0.0031274 | 0.041723 | -0.018201 | 0.02284 | 0.0031274 | North | N | 0.0031274 | 0
13432 | SANDOW_5 | 5 | 581 | -0.026975 | south | Y | -0.045364 | -0.000514 | -0.060438 | -0.019397 | 0.000514 | south | N | 0.000514 | 0
13691 | OAKGROVE | 1 | 855 | 0.008206 | north | Y | -0.010183 | 0.034667 | -0.025257 | 0.015784 | 0.010183 | North | N | 0.010183 | 0
13692 | OAKGROVE | 2 | 855 | 0.008206 | north | Y | -0.010183 | 0.034667 | -0.025257 | 0.015784 | 0.010183 | North | N | 0.010183 | 0
32798 | BRYN_TAM | 1 | 32 | 0.002829 | north | N | -0.01556 | 0.02929 | -0.030634 | 0.010407 | 0.010407 | houston | Y | 0.01556 | 0
32883 | BRYN_DNS | 1 | 48 | 0.0025 | north | Y | -0.015889 | 0.028961 | -0.030963 | 0.010078 | 0.010078 | houston | Y | 0.015889 | 0.27894
32884 | BRYN_DNS | 1 | 46 | 0.0025 | north | Y | -0.015889 | 0.028961 | -0.030963 | 0.010078 | 0.010078 | houston | Y | 0.015889 | 0.26732
32886 | BRYN_ATK | MB | 12 | 0.002847 | north | Y | -0.015542 | 0.029308 | -0.030616 | 0.010425 | 0.010425 | houston | Y | 0.015542 | 0
32887 | BRYN_ATK | MB | 51 | 0.002847 | north | Y | -0.015542 | 0.029308 | -0.030616 | 0.010425 | 0.010425 | houston | Y | 0.015542 | 0
32888 | BRYN_ATK | 1 | 17 | 0.002847 | north | Y | -0.015542 | 0.029308 | -0.030616 | 0.010425 | 0.010425 | houston | Y | 0.015542 | 0.086995
32890 | BRYN_ATK | MB | 22 | 0.002847 | north | Y | -0.015542 | 0.029308 | -0.030616 | 0.010425 | 0.010425 | houston | Y | 0.015542 | 0
32891 | BRYN_ATK | MB | 25 | 0.002847 | north | Y | -0.015542 | 0.029308 | -0.030616 | 0.010425 | 0.010425 | houston | Y | 0.015542 | 0
32892 | BRYN_DNS | 1 | 105 | 0.0025 | north | Y | -0.015889 | 0.028961 | -0.030963 | 0.010078 | 0.010078 | houston | Y | 0.015889 | 0.61019
36998 | RDCNYNG1 | 1 | 84 | 0.034171 | west | Y | 0.015782 | 0.060632 | 0.0007079 | 0.041749 | 0.0007079 | west | N | 0.0007079 | 0
38332 | WDWRDU2 | 1 | 80 | 0.031861 | west | Y | 0.013472 | 0.058322 | -0.0016021 | 0.039439 | 0.0016021 | west | N | 0.0016021 | 0
38437 | TNSRBNMS | 1 | 150 | 0.031846 | west | Y | 0.013457 | 0.058307 | -0.0016171 | 0.039424 | 0.0016171 | west | N | 0.0016171 | 0
38438 | TNSRBNMS | 1 | 150 | 0.031846 | west | Y | 0.013457 | 0.058307 | -0.0016171 | 0.039424 | 0.0016171 | west | N | 0.0016171 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.007842 | houston | N | -0.026231 | 0.018619 | -0.041305 | -0.00026394 | 0.00026394 | houston | N | 0.00026394 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.007842 | houston | N | -0.026231 | 0.018619 | -0.041305 | -0.00026394 | 0.00026394 | houston | N | 0.00026394 | 0
38600 | TNBP_CGN | 5 | 53 | -0.007842 | houston | N | -0.026231 | 0.018619 | -0.041305 | -0.00026394 | 0.00026394 | houston | N | 0.00026394 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.007842 | houston | N | -0.026231 | 0.018619 | -0.041305 | -0.00026394 | 0.00026394 | houston | N | 0.00026394 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.007842 | houston | N | -0.026231 | 0.018619 | -0.041305 | -0.00026394 | 0.00026394 | houston | N | 0.00026394 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.007842 | houston | N | -0.026231 | 0.018619 | -0.041305 | -0.00026394 | 0.00026394 | houston | N | 0.00026394 | 0
38614 | TNBPAMCG | 4 | 96 | -0.007842 | houston | N | -0.026231 | 0.018619 | -0.041305 | -0.00026394 | 0.00026394 | houston | N | 0.00026394 | 0
38615 | TNBPAMCG | 1 | 244 | -0.007842 | houston | N | -0.026231 | 0.018619 | -0.041305 | -0.00026394 | 0.00026394 | houston | N | 0.00026394 | 0
38690 | TNBP_CGN | 3 | 40 | -0.007842 | houston | N | -0.026231 | 0.018619 | -0.041305 | -0.00026394 | 0.00026394 | houston | N | 0.00026394 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.007846 | houston | N | -0.026235 | 0.018615 | -0.041309 | -0.00026794 | 0.00026794 | houston | N | 0.00026794 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.007846 | houston | N | -0.026235 | 0.018615 | -0.041309 | -0.00026794 | 0.00026794 | houston | N | 0.00026794 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.007846 | houston | N | -0.026235 | 0.018615 | -0.041309 | -0.00026794 | 0.00026794 | houston | N | 0.00026794 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.007846 | houston | N | -0.026235 | 0.018615 | -0.041309 | -0.00026794 | 0.00026794 | houston | N | 0.00026794 | 0
39470 | TNDOWCGN | 1 | 32 | -0.007845 | houston | N | -0.026234 | 0.018616 | -0.041308 | -0.00026694 | 0.00026694 | houston | N | 0.00026694 | 0
39480 | TNDOWCGN | 1 | 30 | -0.007845 | houston | N | -0.026234 | 0.018616 | -0.041308 | -0.00026694 | 0.00026694 | houston | N | 0.00026694 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.010235 | houston | N | -0.028624 | 0.016226 | -0.043698 | -0.0026569 | 0.0026569 | houston | N | 0.0026569 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.010235 | houston | N | -0.028624 | 0.016226 | -0.043698 | -0.0026569 | 0.0026569 | houston | N | 0.0026569 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.010235 | houston | N | -0.028624 | 0.016226 | -0.043698 | -0.0026569 | 0.0026569 | houston | N | 0.0026569 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.010235 | houston | N | -0.028624 | 0.016226 | -0.043698 | -0.0026569 | 0.0026569 | houston | N | 0.0026569 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.008206 | north | Y | -0.010183 | 0.034667 | -0.025257 | 0.015784 | 0.010183 | North | N | 0.010183 | 0
39970 | TNTNPONE | 1 | 153 | 0.008206 | north | Y | -0.010183 | 0.034667 | -0.025257 | 0.015784 | 0.010183 | North | N | 0.010183 | 0
48500 | APD_GT1_ | 1 | 136 | -0.006384 | houston | N | -0.024773 | 0.020077 | -0.039847 | 0.0011941 | 0.0011941 | houston | N | 0.0011941 | 0
48510 | AK_GT1__ | 1 | 33 | -0.00864 | houston | N | -0.027029 | 0.017821 | -0.042103 | -0.0010619 | 0.0010619 | houston | N | 0.0010619 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.006378 | houston | Y | -0.024767 | 0.020083 | -0.039841 | 0.0012001 | 0.0012001 | houston | N | 0.0012001 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.006378 | houston | Y | -0.024767 | 0.020083 | -0.039841 | 0.0012001 | 0.0012001 | houston | N | 0.0012001 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.006378 | houston | Y | -0.024767 | 0.020083 | -0.039841 | 0.0012001 | 0.0012001 | houston | N | 0.0012001 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.006378 | houston | Y | -0.024767 | 0.020083 | -0.039841 | 0.0012001 | 0.0012001 | houston | N | 0.0012001 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.010635 | houston | N | -0.029024 | 0.015826 | -0.044098 | -0.0030569 | 0.0030569 | houston | N | 0.0030569 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.010635 | houston | N | -0.029024 | 0.015826 | -0.044098 | -0.0030569 | 0.0030569 | houston | N | 0.0030569 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.008773 | houston | N | -0.027162 | 0.017688 | -0.042236 | -0.0011949 | 0.0011949 | houston | N | 0.0011949 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.008773 | houston | N | -0.027162 | 0.017688 | -0.042236 | -0.0011949 | 0.0011949 | houston | N | 0.0011949 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.008773 | houston | N | -0.027162 | 0.017688 | -0.042236 | -0.0011949 | 0.0011949 | houston | N | 0.0011949 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.00693 | houston | N | -0.025319 | 0.019531 | -0.040393 | 0.00064806 | 0.00064806 | houston | N | 0.00064806 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.00693 | houston | N | -0.025319 | 0.019531 | -0.040393 | 0.00064806 | 0.00064806 | houston | N | 0.00064806 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.00693 | houston | N | -0.025319 | 0.019531 | -0.040393 | 0.00064806 | 0.00064806 | houston | N | 0.00064806 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.00693 | houston | N | -0.025319 | 0.019531 | -0.040393 | 0.00064806 | 0.00064806 | houston | N | 0.00064806 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.006575 | houston | N | -0.024964 | 0.019886 | -0.040038 | 0.0010031 | 0.0010031 | houston | N | 0.0010031 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.006575 | houston | N | -0.024964 | 0.019886 | -0.040038 | 0.0010031 | 0.0010031 | houston | N | 0.0010031 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.007036 | houston | N | -0.025425 | 0.019425 | -0.040499 | 0.00054206 | 0.00054206 | houston | N | 0.00054206 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.007036 | houston | N | -0.025425 | 0.019425 | -0.040499 | 0.00054206 | 0.00054206 | houston | N | 0.00054206 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.007036 | houston | N | -0.025425 | 0.019425 | -0.040499 | 0.00054206 | 0.00054206 | houston | N | 0.00054206 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.007036 | houston | N | -0.025425 | 0.019425 | -0.040499 | 0.00054206 | 0.00054206 | houston | N | 0.00054206 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.007036 | houston | N | -0.025425 | 0.019425 | -0.040499 | 0.00054206 | 0.00054206 | houston | N | 0.00054206 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.005935 | houston | Y | -0.024324 | 0.020526 | -0.039398 | 0.0016431 | 0.0016431 | houston | N | 0.0016431 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.006115 | houston | Y | -0.024504 | 0.020346 | -0.039578 | 0.0014631 | 0.0014631 | houston | N | 0.0014631 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.005881 | houston | Y | -0.02427 | 0.02058 | -0.039344 | 0.0016971 | 0.0016971 | houston | N | 0.0016971 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.005881 | houston | Y | -0.02427 | 0.02058 | -0.039344 | 0.0016971 | 0.0016971 | houston | N | 0.0016971 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.005881 | houston | Y | -0.02427 | 0.02058 | -0.039344 | 0.0016971 | 0.0016971 | houston | N | 0.0016971 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.004882 | houston | N | -0.023271 | 0.021579 | -0.038345 | 0.0026961 | 0.0026961 | houston | N | 0.0026961 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.006349 | houston | N | -0.024738 | 0.020112 | -0.039812 | 0.0012291 | 0.0012291 | houston | N | 0.0012291 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.006349 | houston | N | -0.024738 | 0.020112 | -0.039812 | 0.0012291 | 0.0012291 | houston | N | 0.0012291 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.005754 | houston | N | -0.024143 | 0.020707 | -0.039217 | 0.0018241 | 0.0018241 | houston | N | 0.0018241 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.005754 | houston | N | -0.024143 | 0.020707 | -0.039217 | 0.0018241 | 0.0018241 | houston | N | 0.0018241 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.005754 | houston | N | -0.024143 | 0.020707 | -0.039217 | 0.0018241 | 0.0018241 | houston | N | 0.0018241 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.005754 | houston | N | -0.024143 | 0.020707 | -0.039217 | 0.0018241 | 0.0018241 | houston | N | 0.0018241 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.006563 | houston | N | -0.024952 | 0.019898 | -0.040026 | 0.0010151 | 0.0010151 | houston | N | 0.0010151 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.006563 | houston | N | -0.024952 | 0.019898 | -0.040026 | 0.0010151 | 0.0010151 | houston | N | 0.0010151 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.006563 | houston | N | -0.024952 | 0.019898 | -0.040026 | 0.0010151 | 0.0010151 | houston | N | 0.0010151 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.006563 | houston | N | -0.024952 | 0.019898 | -0.040026 | 0.0010151 | 0.0010151 | houston | N | 0.0010151 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.006679 | houston | N | -0.025068 | 0.019782 | -0.040142 | 0.00089906 | 0.00089906 | houston | N | 0.00089906 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.006679 | houston | N | -0.025068 | 0.019782 | -0.040142 | 0.00089906 | 0.00089906 | houston | N | 0.00089906 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.006679 | houston | N | -0.025068 | 0.019782 | -0.040142 | 0.00089906 | 0.00089906 | houston | N | 0.00089906 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.006679 | houston | N | -0.025068 | 0.019782 | -0.040142 | 0.00089906 | 0.00089906 | houston | N | 0.00089906 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.006679 | houston | N | -0.025068 | 0.019782 | -0.040142 | 0.00089906 | 0.00089906 | houston | N | 0.00089906 | 0
48651 | EP_1_2 | 1 | 5 | -0.005944 | houston | N | -0.024333 | 0.020517 | -0.039407 | 0.0016341 | 0.0016341 | houston | N | 0.0016341 | 0
48651 | EP_1_2 | 2 | 21 | -0.005944 | houston | N | -0.024333 | 0.020517 | -0.039407 | 0.0016341 | 0.0016341 | houston | N | 0.0016341 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.002123 | north | N | -0.016266 | 0.028584 | -0.03134 | 0.0097011 | 0.0097011 | houston | Y | 0.016266 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.002123 | north | N | -0.016266 | 0.028584 | -0.03134 | 0.0097011 | 0.0097011 | houston | Y | 0.016266 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.002123 | north | N | -0.016266 | 0.028584 | -0.03134 | 0.0097011 | 0.0097011 | houston | Y | 0.016266 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.002123 | north | N | -0.016266 | 0.028584 | -0.03134 | 0.0097011 | 0.0097011 | houston | Y | 0.016266 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.005708 | houston | Y | -0.024097 | 0.020753 | -0.039171 | 0.0018701 | 0.0018701 | houston | N | 0.0018701 | 0
48691 | GBY_7374 | A | 46 | -0.006766 | houston | Y | -0.025155 | 0.019695 | -0.040229 | 0.00081206 | 0.00081206 | houston | N | 0.00081206 | 0
48691 | GBY_7374 | B | 46 | -0.006766 | houston | Y | -0.025155 | 0.019695 | -0.040229 | 0.00081206 | 0.00081206 | houston | N | 0.00081206 | 0
48692 | GBY_8182 | C | 46 | -0.006766 | houston | Y | -0.025155 | 0.019695 | -0.040229 | 0.00081206 | 0.00081206 | houston | N | 0.00081206 | 0
48692 | GBY_8182 | D | 55 | -0.006766 | houston | Y | -0.025155 | 0.019695 | -0.040229 | 0.00081206 | 0.00081206 | houston | N | 0.00081206 | 0
48693 | GBY_8384 | E | 55 | -0.006766 | houston | Y | -0.025155 | 0.019695 | -0.040229 | 0.00081206 | 0.00081206 | houston | N | 0.00081206 | 0
48693 | GBY_8384 | F | 54 | -0.006766 | houston | Y | -0.025155 | 0.019695 | -0.040229 | 0.00081206 | 0.00081206 | houston | N | 0.00081206 | 0
48721 | LEG_1___ | 1 | 827 | 0.010145 | north | Y | -0.0082444 | 0.036606 | -0.023318 | 0.017723 | 0.0082444 | North | N | 0.0082444 | 0
48722 | LEG_2___ | 2 | 819 | 0.010145 | north | Y | -0.0082444 | 0.036606 | -0.023318 | 0.017723 | 0.0082444 | North | N | 0.0082444 | 0
48730 | MNS_GT | 1 | 46.1 | -0.008847 | houston | N | -0.027236 | 0.017614 | -0.04231 | -0.0012689 | 0.0012689 | houston | N | 0.0012689 | 0
48731 | CBE_GT1 | 1 | 76 | -0.013708 | houston | Y | -0.032097 | 0.012753 | -0.047171 | -0.0061299 | 0.0061299 | houston | N | 0.0061299 | 0
48732 | CBE_GT2 | 1 | 76 | -0.013708 | houston | Y | -0.032097 | 0.012753 | -0.047171 | -0.0061299 | 0.0061299 | houston | N | 0.0061299 | 0
48733 | CBE_ST12 | 1 | 105 | -0.013708 | houston | Y | -0.032097 | 0.012753 | -0.047171 | -0.0061299 | 0.0061299 | houston | N | 0.0061299 | 0
48734 | CBE_GT3 | 1 | 74 | -0.013708 | houston | Y | -0.032097 | 0.012753 | -0.047171 | -0.0061299 | 0.0061299 | houston | N | 0.0061299 | 0
48735 | CBE_GT4 | 1 | 74 | -0.013708 | houston | Y | -0.032097 | 0.012753 | -0.047171 | -0.0061299 | 0.0061299 | houston | N | 0.0061299 | 0
48736 | CBE_ST34 | 1 | 102 | -0.013708 | houston | Y | -0.032097 | 0.012753 | -0.047171 | -0.0061299 | 0.0061299 | houston | N | 0.0061299 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.006559 | houston | N | -0.024948 | 0.019902 | -0.040022 | 0.0010191 | 0.0010191 | houston | N | 0.0010191 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.006559 | houston | N | -0.024948 | 0.019902 | -0.040022 | 0.0010191 | 0.0010191 | houston | N | 0.0010191 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.006559 | houston | N | -0.024948 | 0.019902 | -0.040022 | 0.0010191 | 0.0010191 | houston | N | 0.0010191 | 0
48761 | PR_GT1__ | 1 | 35 | -0.006631 | houston | N | -0.02502 | 0.01983 | -0.040094 | 0.00094706 | 0.00094706 | houston | N | 0.00094706 | 0
48772 | PHR_GN2_ | MB | 459 | -0.007309 | houston | Y | -0.025698 | 0.019152 | -0.040772 | 0.00026906 | 0.00026906 | houston | N | 0.00026906 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.005942 | houston | N | -0.024331 | 0.020519 | -0.039405 | 0.0016361 | 0.0016361 | houston | N | 0.0016361 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.005942 | houston | N | -0.024331 | 0.020519 | -0.039405 | 0.0016361 | 0.0016361 | houston | N | 0.0016361 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.005942 | houston | N | -0.024331 | 0.020519 | -0.039405 | 0.0016361 | 0.0016361 | houston | N | 0.0016361 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.005942 | houston | N | -0.024331 | 0.020519 | -0.039405 | 0.0016361 | 0.0016361 | houston | N | 0.0016361 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.005942 | houston | N | -0.024331 | 0.020519 | -0.039405 | 0.0016361 | 0.0016361 | houston | N | 0.0016361 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.005942 | houston | N | -0.024331 | 0.020519 | -0.039405 | 0.0016361 | 0.0016361 | houston | N | 0.0016361 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.005942 | houston | N | -0.024331 | 0.020519 | -0.039405 | 0.0016361 | 0.0016361 | houston | N | 0.0016361 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.004882 | houston | N | -0.023271 | 0.021579 | -0.038345 | 0.0026961 | 0.0026961 | houston | N | 0.0026961 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.004882 | houston | N | -0.023271 | 0.021579 | -0.038345 | 0.0026961 | 0.0026961 | houston | N | 0.0026961 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.004882 | houston | N | -0.023271 | 0.021579 | -0.038345 | 0.0026961 | 0.0026961 | houston | N | 0.0026961 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.004882 | houston | N | -0.023271 | 0.021579 | -0.038345 | 0.0026961 | 0.0026961 | houston | N | 0.0026961 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.005901 | houston | N | -0.02429 | 0.02056 | -0.039364 | 0.0016771 | 0.0016771 | houston | N | 0.0016771 | 0
48820 | SHELLG1_ | 1 | 71 | -0.006493 | houston | N | -0.024882 | 0.019968 | -0.039956 | 0.0010851 | 0.0010851 | houston | N | 0.0010851 | 0
48821 | SHELLG2 | 2 | 72 | -0.006493 | houston | N | -0.024882 | 0.019968 | -0.039956 | 0.0010851 | 0.0010851 | houston | N | 0.0010851 | 0
48822 | SHELLG3_ | 1 | 39 | -0.006493 | houston | N | -0.024882 | 0.019968 | -0.039956 | 0.0010851 | 0.0010851 | houston | N | 0.0010851 | 0
48822 | SHELLG3_ | 2 | 30 | -0.006493 | houston | N | -0.024882 | 0.019968 | -0.039956 | 0.0010851 | 0.0010851 | houston | N | 0.0010851 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.006731 | houston | N | -0.02512 | 0.01973 | -0.040194 | 0.00084706 | 0.00084706 | houston | N | 0.00084706 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.006731 | houston | N | -0.02512 | 0.01973 | -0.040194 | 0.00084706 | 0.00084706 | houston | N | 0.00084706 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.006564 | houston | N | -0.024953 | 0.019897 | -0.040027 | 0.0010141 | 0.0010141 | houston | N | 0.0010141 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.006578 | houston | Y | -0.024967 | 0.019883 | -0.040041 | 0.0010001 | 0.0010001 | houston | N | 0.0010001 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.006582 | houston | Y | -0.024971 | 0.019879 | -0.040045 | 0.00099606 | 0.00099606 | houston | N | 0.00099606 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.006565 | houston | Y | -0.024954 | 0.019896 | -0.040028 | 0.0010131 | 0.0010131 | houston | N | 0.0010131 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.006561 | houston | Y | -0.02495 | 0.0199 | -0.040024 | 0.0010171 | 0.0010171 | houston | N | 0.0010171 | 0
48855 | SRB_GT21 | B2 | 12 | -0.006584 | houston | Y | -0.024973 | 0.019877 | -0.040047 | 0.00099406 | 0.00099406 | houston | N | 0.00099406 | 0
48855 | SRB_GT21 | MB | 18 | -0.006584 | houston | Y | -0.024973 | 0.019877 | -0.040047 | 0.00099406 | 0.00099406 | houston | N | 0.00099406 | 0
48865 | TECO_GT1 | 1 | 50 | -0.007534 | houston | Y | -0.025923 | 0.018927 | -0.040997 | 4.4061e-05 | 4.4061e-05 | houston | N | 4.4061e-05 | 0
48873 | THW_ST3_ | 3 | 104 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48874 | THW_ST4_ | 4 | 104 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48875 | THW_3132 | A | 54 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48875 | THW_3132 | B | 53 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48877 | THW_3334 | C | 54 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48877 | THW_3334 | D | 57 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48879 | THW_4142 | E | 54 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48879 | THW_4142 | F | 54 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48881 | THW_4344 | G | 58 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48881 | THW_4344 | H | 58 | -0.006174 | houston | Y | -0.024563 | 0.020287 | -0.039637 | 0.0014041 | 0.0014041 | houston | N | 0.0014041 | 0
48883 | THW_GT1_ | B2 | 12 | -0.00601 | houston | Y | -0.024399 | 0.020451 | -0.039473 | 0.0015681 | 0.0015681 | houston | N | 0.0015681 | 0
48885 | THW_5152 | A | 56 | -0.005629 | houston | Y | -0.024018 | 0.020832 | -0.039092 | 0.0019491 | 0.0019491 | houston | N | 0.0019491 | 0
48885 | THW_5152 | B | 59 | -0.005629 | houston | Y | -0.024018 | 0.020832 | -0.039092 | 0.0019491 | 0.0019491 | houston | N | 0.0019491 | 0
48886 | THW_5354 | C | 56 | -0.005629 | houston | Y | -0.024018 | 0.020832 | -0.039092 | 0.0019491 | 0.0019491 | houston | N | 0.0019491 | 0
48886 | THW_5354 | D | 56 | -0.005629 | houston | Y | -0.024018 | 0.020832 | -0.039092 | 0.0019491 | 0.0019491 | houston | N | 0.0019491 | 0
48887 | THW_5556 | E | 59 | -0.005629 | houston | Y | -0.024018 | 0.020832 | -0.039092 | 0.0019491 | 0.0019491 | houston | N | 0.0019491 | 0
48887 | THW_5556 | F | 56 | -0.005629 | houston | Y | -0.024018 | 0.020832 | -0.039092 | 0.0019491 | 0.0019491 | houston | N | 0.0019491 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.013127 | houston | Y | -0.031516 | 0.013334 | -0.04659 | -0.0055489 | 0.0055489 | houston | N | 0.0055489 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.008551 | houston | Y | -0.02694 | 0.01791 | -0.042014 | -0.00097294 | 0.00097294 | houston | N | 0.00097294 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.008551 | houston | Y | -0.02694 | 0.01791 | -0.042014 | -0.00097294 | 0.00097294 | houston | N | 0.00097294 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.008551 | houston | Y | -0.02694 | 0.01791 | -0.042014 | -0.00097294 | 0.00097294 | houston | N | 0.00097294 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.008551 | houston | Y | -0.02694 | 0.01791 | -0.042014 | -0.00097294 | 0.00097294 | houston | N | 0.00097294 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.008551 | houston | N | -0.02694 | 0.01791 | -0.042014 | -0.00097294 | 0.00097294 | houston | N | 0.00097294 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.008784 | houston | Y | -0.027173 | 0.017677 | -0.042247 | -0.0012059 | 0.0012059 | houston | N | 0.0012059 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.008784 | houston | Y | -0.027173 | 0.017677 | -0.042247 | -0.0012059 | 0.0012059 | houston | N | 0.0012059 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.008784 | houston | Y | -0.027173 | 0.017677 | -0.042247 | -0.0012059 | 0.0012059 | houston | N | 0.0012059 | 0
48929 | WAPGT21_ | B1 | 13 | -0.008551 | houston | Y | -0.02694 | 0.01791 | -0.042014 | -0.00097294 | 0.00097294 | houston | N | 0.00097294 | 0
48940 | WARVUE_G | G1 | 12 | -0.00594 | houston | Y | -0.024329 | 0.020521 | -0.039403 | 0.0016381 | 0.0016381 | houston | N | 0.0016381 | 0
49803 | EXN_15GT | 1 | 34 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49826 | EXN938GT | 5 | 45.9 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49828 | EXN941GT | 10 | 17.7 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49829 | EXN942GT | 11 | 20.4 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49830 | EXN943GT | 12 | 19.9 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49831 | EXN944GT | 13 | 35 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49832 | EXN945GT | 9 | 18 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49837 | EXN_GT | 4 | 85.4 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49838 | EXN_14GT | 14 | 148 | -0.006071 | houston | N | -0.02446 | 0.02039 | -0.039534 | 0.0015071 | 0.0015071 | houston | N | 0.0015071 | 0
49851 | DOW17000 | 37 | 62 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49858 | DOW38100 | 31 | 71.4 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49859 | DOW38200 | 33 | 45 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49860 | DOW38300 | 32 | 101 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49862 | DOW39100 | 36 | 86 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49863 | DOW39200 | 35 | 88 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49865 | DOW41000 | 41 | 50 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49866 | DOW42000 | 42 | 18 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49869 | DOW49000 | 45 | 94 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49870 | DOW61000 | 61 | 70 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49871 | DOW62000 | 62 | 63 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49872 | DOW63000 | 63 | 72 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49873 | DOW64000 | 64 | 64.8 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49876 | DOW65000 | 65 | 101 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49877 | DOW66000 | 66 | 97 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49878 | DOW67000 | 67 | 103 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49882 | DOW81000 | 81 | 76 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49884 | DOW82000 | 82 | 80 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49885 | DOW83000 | 83 | 80 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
49886 | DOW84000 | 84 | 171 | -0.011133 | houston | N | -0.029522 | 0.015328 | -0.044596 | -0.0035549 | 0.0035549 | houston | N | 0.0035549 | 0
58909 | PEARSALL | 1 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58909 | PEARSALL | 2 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58909 | PEARSALL | 3 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58909 | PEARSALL | 4 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58909 | PEARSALL | 5 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58909 | PEARSALL | 6 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58919 | PEARSALL | 1 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58919 | PEARSALL | 2 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58919 | PEARSALL | 3 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58919 | PEARSALL | 4 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58919 | PEARSALL | 5 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58919 | PEARSALL | 6 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58929 | PEARSALL | 1 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58929 | PEARSALL | 2 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58929 | PEARSALL | 3 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58929 | PEARSALL | 4 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58929 | PEARSALL | 5 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58929 | PEARSALL | 6 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58949 | PEARSALL | 1 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58949 | PEARSALL | 2 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58949 | PEARSALL | 3 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58949 | PEARSALL | 4 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58949 | PEARSALL | 5 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
58949 | PEARSALL | 6 | 8.4 | -0.021642 | south | Y | -0.040031 | 0.004819 | -0.055105 | -0.014064 | 0.004819 | south | N | 0.004819 | 0
60000 | DSKY2 | 1 | 76.5 | 0.031186 | west | Y | 0.012797 | 0.057647 | -0.0022771 | 0.038764 | 0.0022771 | west | N | 0.0022771 | 0
60003 | KING_NE1 | 1 | 80 | 0.031899 | west | Y | 0.01351 | 0.05836 | -0.0015641 | 0.039477 | 0.0015641 | west | N | 0.0015641 | 0
60005 | KING_SE1 | 1 | 40 | 0.031899 | west | Y | 0.01351 | 0.05836 | -0.0015641 | 0.039477 | 0.0015641 | west | N | 0.0015641 | 0
60007 | KING_SW1 | 1 | 80 | 0.03204 | west | Y | 0.013651 | 0.058501 | -0.0014231 | 0.039618 | 0.0014231 | west | N | 0.0014231 | 0
60016 | WOODWRD1 | 1 | 80 | 0.031865 | west | Y | 0.013476 | 0.058326 | -0.0015981 | 0.039443 | 0.0015981 | west | N | 0.0015981 | 0
60017 | ORNNWP1 | 1 | 80 | 0.031181 | west | Y | 0.012792 | 0.057642 | -0.0022821 | 0.038759 | 0.0022821 | west | N | 0.0022821 | 0
60018 | DSKY1 | 1 | 84 | 0.030956 | west | Y | 0.012567 | 0.057417 | -0.0025071 | 0.038534 | 0.0025071 | west | N | 0.0025071 | 0
60019 | KING_NW1 | 1 | 80 | 0.03204 | west | Y | 0.013651 | 0.058501 | -0.0014231 | 0.039618 | 0.0014231 | west | N | 0.0014231 | 0
60057 | CALLAHAN | 1 | 114 | -0.029415 | south | Y | -0.047804 | -0.002954 | -0.062878 | -0.021837 | 0.002954 | south | N | 0.002954 | 0
60058 | BUFF_GAP | 1 | 120 | 0.035987 | west | Y | 0.017598 | 0.062448 | 0.0025239 | 0.043565 | 0.0025239 | west | N | 0.0025239 | 0
60060 | CIRELLO | 1 | 233 | 0.035987 | west | Y | 0.017598 | 0.062448 | 0.0025239 | 0.043565 | 0.0025239 | west | N | 0.0025239 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.035987 | west | Y | 0.017598 | 0.062448 | 0.0025239 | 0.043565 | 0.0025239 | west | N | 0.0025239 | 0
60066 | H_HOLLOW | 1 | 222 | -0.029415 | south | Y | -0.047804 | -0.002954 | -0.062878 | -0.021837 | 0.002954 | south | N | 0.002954 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.029415 | south | Y | -0.047804 | -0.002954 | -0.062878 | -0.021837 | 0.002954 | south | N | 0.002954 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.029415 | south | Y | -0.047804 | -0.002954 | -0.062878 | -0.021837 | 0.002954 | south | N | 0.002954 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.029415 | south | Y | -0.047804 | -0.002954 | -0.062878 | -0.021837 | 0.002954 | south | N | 0.002954 | 0
60074 | HORSH5 | 1 | 100 | -0.029415 | south | Y | -0.047804 | -0.002954 | -0.062878 | -0.021837 | 0.002954 | south | N | 0.002954 | 0
60081 | WHRLWIND | 1 | 60 | 0.033776 | west | Y | 0.015387 | 0.060237 | 0.0003129 | 0.041354 | 0.0003129 | west | N | 0.0003129 | 0
60201 | RIO DRCS | F | 0 | -0.027075 | south | N | -0.045464 | -0.000614 | -0.060538 | -0.019497 | 0.000614 | south | N | 0.000614 | 0
60202 | FRIEND_R | F | 0 | 0.027326 | west | N | 0.0089366 | 0.053787 | -0.0061371 | 0.034904 | 0.0061371 | west | N | 0.0061371 | 0
60203 | PRES0A | BT | 4.8 | 0.03244 | west | N | 0.014051 | 0.058901 | -0.0010231 | 0.040018 | 0.0010231 | west | N | 0.0010231 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.033888 | west | Y | 0.015499 | 0.060349 | 0.0004249 | 0.041466 | 0.0004249 | west | N | 0.0004249 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.033888 | west | Y | 0.015499 | 0.060349 | 0.0004249 | 0.041466 | 0.0004249 | west | N | 0.0004249 | 0
71057 | L_SWEETW | W1 | 135 | 0.033888 | west | Y | 0.015499 | 0.060349 | 0.0004249 | 0.041466 | 0.0004249 | west | N | 0.0004249 | 0
71059 | L_SWEETW | W1 | 119 | 0.033888 | west | Y | 0.015499 | 0.060349 | 0.0004249 | 0.041466 | 0.0004249 | west | N | 0.0004249 | 0
71060 | L_SWEETW | W1 | 105 | 0.033888 | west | Y | 0.015499 | 0.060349 | 0.0004249 | 0.041466 | 0.0004249 | west | N | 0.0004249 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.033888 | west | Y | 0.015499 | 0.060349 | 0.0004249 | 0.041466 | 0.0004249 | west | N | 0.0004249 | 0
76031 | L_GASCCR | W1 | 150 | 0.035734 | west | Y | 0.017345 | 0.062195 | 0.0022709 | 0.043312 | 0.0022709 | west | N | 0.0022709 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.036078 | west | Y | 0.017689 | 0.062539 | 0.0026149 | 0.043656 | 0.0026149 | west | N | 0.0026149 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.036078 | west | Y | 0.017689 | 0.062539 | 0.0026149 | 0.043656 | 0.0026149 | west | N | 0.0026149 | 0
76096 | L_CAPRSI | W1 | 186 | 0.036078 | west | Y | 0.017689 | 0.062539 | 0.0026149 | 0.043656 | 0.0026149 | west | N | 0.0026149 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.036078 | west | Y | 0.017689 | 0.062539 | 0.0026149 | 0.043656 | 0.0026149 | west | N | 0.0026149 | 0
80003 | MILHWYS | F | 0 | -0.021356 | south | N | -0.039745 | 0.005105 | -0.054819 | -0.013778 | 0.005105 | south | N | 0.005105 | 0
80010 | EPLVT1 | F | 0 | -0.012704 | south | N | -0.031093 | 0.013757 | -0.046167 | -0.0051259 | 0.0051259 | houston | Y | 0.013757 | 0
80012 | LAR | F | 0 | -0.021991 | south | N | -0.04038 | 0.00447 | -0.055454 | -0.014413 | 0.00447 | south | N | 0.00447 | 0
80051 | FORPVCM0 | 8 | 28 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
80053 | FOR69CG0 | 10 | 74 | -0.019529 | south | N | -0.037918 | 0.006932 | -0.052992 | -0.011951 | 0.006932 | south | N | 0.006932 | 0
80080 | GWINDT11 | 1 | 94 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80080 | GWINDT11 | 2 | 41 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80080 | GWINDT11 | 3 | 38 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80080 | GWINDT11 | 4 | 19 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80081 | GWINDT21 | 1 | 94 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80081 | GWINDT21 | 2 | 36 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80081 | GWINDT21 | 3 | 43 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80081 | GWINDT21 | 4 | 22 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80137 | CSDR89 | 8 | 39 | -0.020199 | south | N | -0.038588 | 0.006262 | -0.053662 | -0.012621 | 0.006262 | south | N | 0.006262 | 0
80137 | CSDR89 | 9 | 15 | -0.020199 | south | N | -0.038588 | 0.006262 | -0.053662 | -0.012621 | 0.006262 | south | N | 0.006262 | 0
80138 | CSDR7 | 7 | 7 | -0.020199 | south | N | -0.038588 | 0.006262 | -0.053662 | -0.012621 | 0.006262 | south | N | 0.006262 | 0
80139 | CSDR56 | 5 | 15 | -0.020199 | south | N | -0.038588 | 0.006262 | -0.053662 | -0.012621 | 0.006262 | south | N | 0.006262 | 0
80139 | CSDR56 | 6 | 39 | -0.020199 | south | N | -0.038588 | 0.006262 | -0.053662 | -0.012621 | 0.006262 | south | N | 0.006262 | 0
80140 | CSDR11 | 11 | 39 | -0.020199 | south | N | -0.038588 | 0.006262 | -0.053662 | -0.012621 | 0.006262 | south | N | 0.006262 | 0
80180 | PNSCALT1 | 1 | 148 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80180 | PNSCALT1 | 2 | 50 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80181 | PNSCALT2 | 1 | 55 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80181 | PNSCALT2 | 2 | 50 | -0.021348 | south | Y | -0.039737 | 0.005113 | -0.054811 | -0.01377 | 0.005113 | south | N | 0.005113 | 0
80223 | REYSHR G | 1 | 12 | -0.020949 | south | N | -0.039338 | 0.005512 | -0.054412 | -0.013371 | 0.005512 | south | N | 0.005512 | 0
80224 | VISTRONG | 1 | 15 | -0.020415 | south | N | -0.038804 | 0.006046 | -0.053878 | -0.012837 | 0.006046 | south | N | 0.006046 | 0
80225 | VISTRONG | 2 | 23 | -0.020415 | south | N | -0.038804 | 0.006046 | -0.053878 | -0.012837 | 0.006046 | south | N | 0.006046 | 0
80226 | ALCOA G | 1 | 48 | -0.019687 | south | N | -0.038076 | 0.006774 | -0.05315 | -0.012109 | 0.006774 | south | N | 0.006774 | 0
80227 | AIRCO G | 1 | 8 | -0.020281 | south | N | -0.03867 | 0.00618 | -0.053744 | -0.012703 | 0.00618 | south | N | 0.00618 | 0
80261 | NBEC81A | 1 | 180 | -0.021158 | south | Y | -0.039547 | 0.005303 | -0.054621 | -0.01358 | 0.005303 | south | N | 0.005303 | 0
80262 | NBEC91A | 1 | 180 | -0.021152 | south | Y | -0.039541 | 0.005309 | -0.054615 | -0.013574 | 0.005309 | south | N | 0.005309 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.021198 | south | Y | -0.039587 | 0.005263 | -0.054661 | -0.01362 | 0.005263 | south | N | 0.005263 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.021198 | south | Y | -0.039587 | 0.005263 | -0.054661 | -0.01362 | 0.005263 | south | N | 0.005263 | 0
80265 | LARECU40 | 4 | 100 | -0.021993 | south | Y | -0.040382 | 0.004468 | -0.055456 | -0.014415 | 0.004468 | south | N | 0.004468 | 0
80266 | LARECU50 | 5 | 100 | -0.021993 | south | Y | -0.040382 | 0.004468 | -0.055456 | -0.014415 | 0.004468 | south | N | 0.004468 | 0
80291 | PAPALOTE | 1 | 25 | -0.02103 | south | Y | -0.039419 | 0.005431 | -0.054493 | -0.013452 | 0.005431 | south | N | 0.005431 | 0
80291 | PAPALOTE | 2 | 25 | -0.02103 | south | Y | -0.039419 | 0.005431 | -0.054493 | -0.013452 | 0.005431 | south | N | 0.005431 | 0
80291 | PAPALOTE | 3 | 25 | -0.02103 | south | Y | -0.039419 | 0.005431 | -0.054493 | -0.013452 | 0.005431 | south | N | 0.005431 | 0
80291 | PAPALOTE | 4 | 16 | -0.02103 | south | Y | -0.039419 | 0.005431 | -0.054493 | -0.013452 | 0.005431 | south | N | 0.005431 | 0
80294 | PAPALOTE | 5 | 25 | -0.02103 | south | Y | -0.039419 | 0.005431 | -0.054493 | -0.013452 | 0.005431 | south | N | 0.005431 | 0
80294 | PAPALOTE | 6 | 25 | -0.02103 | south | Y | -0.039419 | 0.005431 | -0.054493 | -0.013452 | 0.005431 | south | N | 0.005431 | 0
80294 | PAPALOTE | 7 | 25 | -0.02103 | south | Y | -0.039419 | 0.005431 | -0.054493 | -0.013452 | 0.005431 | south | N | 0.005431 | 0
80294 | PAPALOTE | 8 | 15 | -0.02103 | south | Y | -0.039419 | 0.005431 | -0.054493 | -0.013452 | 0.005431 | south | N | 0.005431 | 0
86104 | CID-138 | EQ | 0 | -0.021993 | south | N | -0.040382 | 0.004468 | -0.055456 | -0.014415 | 0.004468 | south | N | 0.004468 | 0
86105 | CID-230 | EQ | 500 | -0.021993 | south | N | -0.040382 | 0.004468 | -0.055456 | -0.014415 | 0.004468 | south | N | 0.004468 | 0
86106 | CUF-230 | EQ | 500 | -0.021993 | south | N | -0.040382 | 0.004468 | -0.055456 | -0.014415 | 0.004468 | south | N | 0.004468 | 0
86107 | CUF-138 | EQ | 0 | -0.021993 | south | N | -0.040382 | 0.004468 | -0.055456 | -0.014415 | 0.004468 | south | N | 0.004468 | 0
88198 | BEEVILLE | F | 0 | -0.022233 | south | N | -0.040622 | 0.004228 | -0.055696 | -0.014655 | 0.004228 | south | N | 0.004228 | 0
88253 | HAMILTON | F | 0 | -0.00685 | south | N | -0.025239 | 0.019611 | -0.040313 | 0.00072806 | 0.00072806 | houston | Y | 0.019611 | 0
88299 | ZAPATA | F | 0 | -0.021608 | south | N | -0.039997 | 0.004853 | -0.055071 | -0.01403 | 0.004853 | south | N | 0.004853 | 0
88508 | FALFURRI | F | 0 | -0.021616 | south | N | -0.040005 | 0.004845 | -0.055079 | -0.014038 | 0.004845 | south | N | 0.004845 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Brownwood Switch - Goldthwaite [1655 - 7070] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0 | 0 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0 | 0 | 0 | Weighted Shift Factors
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0 | 0 | 0 | South | -0.026461
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0 | 0 | 0 | North | 0.020792
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.026461 | 0 | 0 | 0 |  | -0.047253
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.026461 | 0 | 0 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.84459 | 0 | 0.021579 | 0 | 0 | 0 | Line Rating | 265
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.76159 | 0 | 0.021579 | 0 | 0 | 0 | Conc Gen | 342
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75183 | 0 | 0.021579 | 0 | 0 | 0 | Weighted Imp. | 7.1245
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75183 | 0 | 0.021579 | 0 | 0 | 0 | PTDF | 0.020832
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.004882 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79088 | 0 | 0.021579 | 0 | 0 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31522 | 56 | 0.020832 | 1.1666 | 56 | 1.1666 | Concentration | -0.44086
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33211 | 59 | 0.020832 | 1.2291 | 115 | 2.3957
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31522 | 56 | 0.020832 | 1.1666 | 171 | 3.5623
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31522 | 56 | 0.020832 | 1.1666 | 227 | 4.7289
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33211 | 59 | 0.020832 | 1.2291 | 286 | 5.958
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31522 | 56 | 0.020832 | 1.1666 | 342 | 7.1245
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.005708 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.2718 | 398 | 0.020753 | 8.2597
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93675 | 0 | 0.020707 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9287 | 0 | 0.020707 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.91431 | 0 | 0.020707 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.549 | 0 | 0.020707 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.005881 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0115 | 172 | 0.02058 | 3.5398
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.005881 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0115 | 172 | 0.02058 | 3.5398
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.005881 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0115 | 172 | 0.02058 | 3.5398
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.005901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.92646 | 0 | 0.02056 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.005935 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.4097 | 743 | 0.020526 | 15.2508
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.00594 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.07128 | 12 | 0.020521 | 0.24625
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38623 | 0 | 0.020519 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39217 | 0 | 0.020519 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41594 | 0 | 0.020519 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37435 | 0 | 0.020519 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3684 | 0 | 0.020519 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61797 | 0 | 0.020519 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35058 | 0 | 0.020519 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.005944 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02972 | 0 | 0.020517 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.005944 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12482 | 0 | 0.020517 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00601 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.07212 | 12 | 0.020451 | 0.24541
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20641 | 0 | 0.02039 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21066 | 0 | 0.02039 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19852 | 0 | 0.02039 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27866 | 0 | 0.02039 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10746 | 0 | 0.02039 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12385 | 0 | 0.02039 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12081 | 0 | 0.02039 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21249 | 0 | 0.02039 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10928 | 0 | 0.02039 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51846 | 0 | 0.02039 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89851 | 0 | 0.02039 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.006115 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.4945 | 735 | 0.020346 | 14.9543
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.6421 | 104 | 0.020287 | 2.1098
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.6421 | 104 | 0.020287 | 2.1098
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3334 | 54 | 0.020287 | 1.0955
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32722 | 53 | 0.020287 | 1.0752
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3334 | 54 | 0.020287 | 1.0955
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35192 | 57 | 0.020287 | 1.1564
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3334 | 54 | 0.020287 | 1.0955
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3334 | 54 | 0.020287 | 1.0955
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35809 | 58 | 0.020287 | 1.1766
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35809 | 58 | 0.020287 | 1.1766
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.006349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0984 | 0 | 0.020112 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.006349 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85711 | 0 | 0.020112 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.26788 | 42 | 0.020083 | 0.84349
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.26788 | 42 | 0.020083 | 0.84349
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24236 | 38 | 0.020083 | 0.76315
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24236 | 38 | 0.020083 | 0.76315
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.006384 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.86822 | 0 | 0.020077 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.461 | 0 | 0.019968 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4675 | 0 | 0.019968 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25323 | 0 | 0.019968 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19479 | 0 | 0.019968 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.006559 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1806 | 0 | 0.019902 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.006559 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0403 | 0 | 0.019902 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.006559 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0298 | 0 | 0.019902 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.006561 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.4959 | 228 | 0.0199 | 4.5372
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42003 | 0 | 0.019898 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41478 | 0 | 0.019898 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5421 | 0 | 0.019898 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48304 | 0 | 0.019898 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.006564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10634 | 0 | 0.019897 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.006565 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.3983 | 213 | 0.019896 | 4.2378
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.006575 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.97967 | 0 | 0.019886 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.006575 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42803 | 0 | 0.019886 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.006578 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0854 | 165 | 0.019883 | 3.2807
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.006582 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.1124 | 169 | 0.019879 | 3.3596
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.006584 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.079008 | 12 | 0.019877 | 0.23852
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.006584 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.019877 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.006631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23209 | 0 | 0.01983 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.09 | 0 | 0.019782 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0493 | 0 | 0.019782 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0519 | 0 | 0.019782 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0486 | 0 | 0.019782 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7967 | 0 | 0.019782 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.006731 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.52502 | 0 | 0.01973 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.006731 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.53848 | 0 | 0.01973 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31124 | 46 | 0.019695 | 0.90597
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31124 | 46 | 0.019695 | 0.90597
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31124 | 46 | 0.019695 | 0.90597
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.37213 | 55 | 0.019695 | 1.0832
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.37213 | 55 | 0.019695 | 1.0832
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.36536 | 54 | 0.019695 | 1.0635
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.00685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22605 | 0 | 0.019611 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.00685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17125 | 0 | 0.019611 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.00685 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019611 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45045 | 0 | 0.019531 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4158 | 0 | 0.019531 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45045 | 0 | 0.019531 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45045 | 0 | 0.019531 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64028 | 0 | 0.019425 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61635 | 0 | 0.019425 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61213 | 0 | 0.019425 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38346 | 0 | 0.019425 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.085839 | 0 | 0.019425 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.040151 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.4091 | 60 | 0.019359 | 1.1615
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.007309 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.019152 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.007534 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3767 | 50 | 0.018927 | 0.94635
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55521 | 0 | 0.018619 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52306 | 0 | 0.018619 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41563 | 0 | 0.018619 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2014 | 0 | 0.018619 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2037 | 0 | 0.018619 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1943 | 0 | 0.018619 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75283 | 0 | 0.018619 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9134 | 0 | 0.018619 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31368 | 0 | 0.018619 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.007845 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25104 | 0 | 0.018616 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.007845 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23535 | 0 | 0.018616 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.78695 | 0 | 0.018615 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72889 | 0 | 0.018615 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.80578 | 0 | 0.018615 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.80029 | 0 | 0.018615 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.008551 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.3767 | 161 | 0.01791 | 2.8835
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.008551 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.4195 | 166 | 0.01791 | 2.9731
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.008551 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.1206 | 248 | 0.01791 | 4.4417
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.008551 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.6688 | 546 | 0.01791 | 9.7789
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.008551 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -5.4983 | 0 | 0.01791 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.008551 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11116 | 13 | 0.01791 | 0.23283
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.00864 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28512 | 0 | 0.017821 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.008773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.43 | 0 | 0.017688 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.008773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.43 | 0 | 0.017688 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.008773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1494 | 0 | 0.017688 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.008784 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.7184 | 651 | 0.017677 | 11.5077
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.008784 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.9542 | 564 | 0.017677 | 9.9698
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.008784 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.2704 | 600 | 0.017677 | 10.6062
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.008847 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40785 | 0 | 0.017614 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1361 | 0 | 0.016226 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1361 | 0 | 0.016226 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.218 | 0 | 0.016226 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1207 | 0 | 0.016226 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.036674 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.2162 | 169.5 | 0.015882 | 2.6919
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.010635 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75509 | 0 | 0.015826 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.010635 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10635 | 0 | 0.015826 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69025 | 0 | 0.015328 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7949 | 0 | 0.015328 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50099 | 0 | 0.015328 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1244 | 0 | 0.015328 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.95744 | 0 | 0.015328 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9797 | 0 | 0.015328 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55665 | 0 | 0.015328 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20039 | 0 | 0.015328 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0465 | 0 | 0.015328 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.77931 | 0 | 0.015328 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70138 | 0 | 0.015328 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.80158 | 0 | 0.015328 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72142 | 0 | 0.015328 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1244 | 0 | 0.015328 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0799 | 0 | 0.015328 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1467 | 0 | 0.015328 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84611 | 0 | 0.015328 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89064 | 0 | 0.015328 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89064 | 0 | 0.015328 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9037 | 0 | 0.015328 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0588 | 112.5 | 0.015286 | 1.7196
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3937 | 149.5 | 0.015286 | 2.2852
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7105 | 186 | 0.015286 | 2.8431
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7387 | 214.5 | 0.015286 | 3.2788
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.035987 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3184 | 120 | 0.015195 | 1.8234
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.035987 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.385 | 233 | 0.015195 | 3.5403
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.035987 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.125 | 170.2 | 0.015195 | 2.5861
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.03579 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.23621 | 6.6 | 0.014998 | 0.098984
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.03579 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2276 | 34.3 | 0.014998 | 0.51442
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.035734 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3601 | 150 | 0.014942 | 2.2412
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.011599 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.069594 | 0 | 0.014862 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.035537 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3305 | 150 | 0.014745 | 2.2117
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.035537 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5892 | 101 | 0.014745 | 1.4892
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.034642 | west | 8 | N | N | Nwest | Nwest | 1 | 0.89376 | 0 | 0.01385 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.012704 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013757 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.034258 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.111 | 120 | 0.013466 | 1.6159
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.034251 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1101 | 120 | 0.013459 | 1.615
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.034205 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1307 | 150 | 0.013413 | 2.0119
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.034204 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1549 | 63 | 0.013412 | 0.84493
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.034171 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8704 | 84 | 0.013379 | 1.1238
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.034163 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3821 | 99 | 0.013371 | 1.3237
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.034163 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0839 | 61 | 0.013371 | 0.81561
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.034163 | west | 7 | N | N | Nwest | Nwest | 1 | 0.85408 | 0 | 0.013371 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.034163 | west | 7 | N | N | Nwest | Nwest | 1 | 1.5612 | 0 | 0.013371 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.034163 | west | 7 | N | N | Nwest | Nwest | 1 | 1.5612 | 0 | 0.013371 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.034161 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8167 | 141 | 0.013369 | 1.885
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.034161 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0993 | 120 | 0.013369 | 1.6042
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.013127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.86638 | 66 | 0.013334 | 0.88004
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2521 | 66 | 0.013331 | 0.87982
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3545 | 69 | 0.013331 | 0.91981
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3545 | 69 | 0.013331 | 0.91981
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2862 | 67 | 0.013331 | 0.89315
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2862 | 67 | 0.013331 | 0.89315
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.218 | 65 | 0.013331 | 0.86649
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.034094 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1369 | 180 | 0.013302 | 2.3943
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.034094 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1369 | 180 | 0.013302 | 2.3943
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.034082 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6684 | 225 | 0.01329 | 2.9902
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.033964 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4134 | 100.5 | 0.013172 | 1.3237
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.088 | 150 | 0.013128 | 1.9691
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4624 | 220 | 0.013128 | 2.8881
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.784 | 200 | 0.013128 | 2.6255
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1348 | 121.9 | 0.013128 | 1.6003
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.033919 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2654 | 214.2 | 0.013127 | 2.8117
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.033895 | west | 8 | N | N | Nwest | Nwest | 1 | 2.3727 | 0 | 0.013103 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.033895 | west | 8 | N | N | Nwest | Nwest | 1 | 2.4879 | 0 | 0.013103 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.033895 | west | 8 | N | N | Nwest | Nwest | 1 | 2.3862 | 0 | 0.013103 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2708 | 37.5 | 0.013096 | 0.49109
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.643 | 107.5 | 0.013096 | 1.4078
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5749 | 135 | 0.013096 | 1.7679
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0327 | 119 | 0.013096 | 1.5584
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5582 | 105 | 0.013096 | 1.375
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.728 | 80.5 | 0.013096 | 1.0542
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.033886 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9654 | 58 | 0.013094 | 0.75943
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.033776 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0266 | 60 | 0.012984 | 0.77902
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3614 | 70 | 0.012942 | 0.90591
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3614 | 70 | 0.012942 | 0.90591
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1305 | 92.8 | 0.012942 | 1.201
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6987 | 80 | 0.012942 | 1.0353
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6987 | 80 | 0.012942 | 1.0353
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.8794 | 115 | 0.012942 | 1.4883
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.023 | 208.2 | 0.01294 | 2.694
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.7933 | 142.1 | 0.01294 | 1.8387
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.4661 | 132.4 | 0.01294 | 1.7132
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5876 | 136 | 0.01294 | 1.7598
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.9586 | 147 | 0.01294 | 1.9021
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.0837 | 210 | 0.01294 | 2.7173
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.033724 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2155 | 125 | 0.012932 | 1.6165
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.033724 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2155 | 125 | 0.012932 | 1.6165
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.033574 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0025 | 149 | 0.012782 | 1.9045
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0418 | 76 | 0.012753 | 0.96923
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0418 | 76 | 0.012753 | 0.96923
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4393 | 105 | 0.012753 | 1.3391
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0144 | 74 | 0.012753 | 0.94372
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0144 | 74 | 0.012753 | 0.94372
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3982 | 102 | 0.012753 | 1.3008
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.033509 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1728 | 35 | 0.012717 | 0.44508
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.033509 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0053 | 30 | 0.012717 | 0.3815
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2101 | 66 | 0.012695 | 0.83784
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1767 | 65 | 0.012695 | 0.82515
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2436 | 67 | 0.012695 | 0.85054
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2436 | 67 | 0.012695 | 0.85054
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2436 | 67 | 0.012695 | 0.85054
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.033487 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012695 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.033487 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012695 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.013886 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -18.51 | 0 | 0.012575 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.013886 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -18.4406 | 0 | 0.012575 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9538 | 209 | 0.01248 | 2.6082
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2089 | 126.5 | 0.01248 | 1.5787
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2847 | 249 | 0.01248 | 3.1074
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5546 | 197 | 0.01248 | 2.4585
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.03244 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.15571 | 0 | 0.011648 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.03204 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5632 | 80 | 0.011248 | 0.89981
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.03204 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5632 | 80 | 0.011248 | 0.89981
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.031899 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3924 | 75 | 0.011107 | 0.833
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031899 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5519 | 80 | 0.011107 | 0.88853
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.031899 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.276 | 40 | 0.011107 | 0.44426
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.031876 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7504 | 400 | 0.011084 | 4.4334
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.031869 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5211 | 236 | 0.011077 | 2.6141
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031865 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5492 | 80 | 0.011073 | 0.88581
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.031861 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5489 | 80 | 0.011069 | 0.88549
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.031846 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7769 | 150 | 0.011054 | 1.658
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.031846 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7769 | 150 | 0.011054 | 1.658
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.031827 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3234 | 73 | 0.011035 | 0.80553
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.031827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.7874 | 119 | 0.011035 | 1.3131
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.031827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.5245 | 205 | 0.011035 | 2.2621
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.031827 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.2464 | 102 | 0.011035 | 1.1255
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.031827 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.0554 | 96 | 0.011035 | 1.0593
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.031186 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3857 | 76.5 | 0.010394 | 0.79511
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031181 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4945 | 80 | 0.010389 | 0.83109
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.031085 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.129 | 165 | 0.010293 | 1.6983
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.030956 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6003 | 84 | 0.010164 | 0.85374
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.030641 | west | 4 | Y | N | Ywest | Nwest | 1 | 19.9075 | 649.7 | 0.0098486 | 6.3986
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.030174 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.3021 | 242 | 0.0093816 | 2.2703
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.029599 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.5519 | 120 | 0.0088066 | 1.0568
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.029332 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.35198 | 0 | 0.0085396 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.029332 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.35198 | 0 | 0.0085396 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57384 | 20 | 0.0078996 | 0.15799
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57384 | 20 | 0.0078996 | 0.15799
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57384 | 20 | 0.0078996 | 0.15799
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.48776 | 17 | 0.0078996 | 0.13429
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.028602 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.4683 | 366 | 0.0078096 | 2.8583
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.02853 | north | 3 | N | N | Nnorth | Nnorth | 1 | 33.0092 | 0 | 0.0077376 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.02853 | north | 3 | N | N | Nnorth | Nnorth | 1 | 33.0377 | 0 | 0.0077376 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.027877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.50179 | 18 | 0.0070846 | 0.12752
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.027877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.50179 | 18 | 0.0070846 | 0.12752
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.027877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.0593 | 38 | 0.0070846 | 0.26921
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5428 | 0 | 0.006932 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5818 | 0 | 0.006932 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5428 | 0 | 0.006932 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5623 | 0 | 0.006932 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5311 | 0 | 0.006932 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48823 | 0 | 0.006932 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.89833 | 0 | 0.006932 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.54681 | 0 | 0.006932 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.85146 | 0 | 0.006932 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4451 | 0 | 0.006932 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.027705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0203 | 217.3 | 0.0069126 | 1.5021
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.027705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.6795 | 205 | 0.0069126 | 1.4171
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.027705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.5468 | 272.4 | 0.0069126 | 1.883
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.019687 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.94498 | 0 | 0.006774 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.927 | 70 | 0.0067366 | 0.47156
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8995 | 69 | 0.0067366 | 0.46483
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8995 | 69 | 0.0067366 | 0.46483
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.872 | 68 | 0.0067366 | 0.45809
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.027326 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0065336 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56557 | 0 | 0.006262 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14139 | 0 | 0.006262 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78776 | 0 | 0.006262 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30299 | 0 | 0.006262 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14139 | 0 | 0.006262 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30299 | 0 | 0.006262 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78776 | 0 | 0.006262 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78776 | 0 | 0.006262 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.020281 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.16225 | 0 | 0.00618 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.020415 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30623 | 0 | 0.006046 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.020415 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46954 | 0 | 0.006046 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.020568 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.4525 | 22 | 0.005893 | 0.12965
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.020568 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22625 | 11 | 0.005893 | 0.064823
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.020568 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22625 | 11 | 0.005893 | 0.064823
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.026518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.4097 | 204 | 0.0057256 | 1.168
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.026518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.3301 | 201 | 0.0057256 | 1.1508
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.026518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4174 | 242 | 0.0057256 | 1.3856
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.99001 | 47.7 | 0.005706 | 0.27218
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.77416 | 37.3 | 0.005706 | 0.21283
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.95473 | 46 | 0.005706 | 0.26248
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.99624 | 48 | 0.005706 | 0.27389
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.02649 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056976 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5175 | 0 | 0.005674 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.3099 | 0 | 0.005512 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.2052 | 0 | 0.005512 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.0949 | 0 | 0.005512 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.0376 | 0 | 0.005512 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.0795 | 0 | 0.005512 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.6605 | 0 | 0.005512 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.020949 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.25139 | 0 | 0.005512 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.021001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0241 | 144 | 0.00546 | 0.78624
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.021001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9482 | 188 | 0.00546 | 1.0265
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 25 | 0.005431 | 0.13578
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 25 | 0.005431 | 0.13578
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 25 | 0.005431 | 0.13578
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.33648 | 16 | 0.005431 | 0.086896
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 25 | 0.005431 | 0.13578
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 25 | 0.005431 | 0.13578
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 25 | 0.005431 | 0.13578
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.31545 | 15 | 0.005431 | 0.081465
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.021152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1071 | 336 | 0.005309 | 1.7838
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.021152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8074 | 180 | 0.005309 | 0.95562
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.021154 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.1371 | 0 | 0.005307 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.021154 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.1435 | 0 | 0.005307 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.021154 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.2366 | 0 | 0.005307 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.021158 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8084 | 180 | 0.005303 | 0.95454
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.02606 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.5053 | 288 | 0.0052676 | 1.5171
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.02606 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8308 | 147 | 0.0052676 | 0.77434
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.02606 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8308 | 147 | 0.0052676 | 0.77434
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.021198 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.0801 | 334 | 0.005263 | 1.7578
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.021198 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.2073 | 340 | 0.005263 | 1.7894
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.021198 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8156 | 180 | 0.005263 | 0.94734
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.021198 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8156 | 180 | 0.005263 | 0.94734
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.021201 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.53002 | 0 | 0.00526 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.021201 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.53002 | 0 | 0.00526 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.021221 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.8064 | 0 | 0.00524 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.021223 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.80647 | 0 | 0.005238 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.021319 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.61825 | 0 | 0.005142 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0067 | 94 | 0.005113 | 0.48062
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.87527 | 41 | 0.005113 | 0.20963
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.81122 | 38 | 0.005113 | 0.19429
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.40561 | 19 | 0.005113 | 0.097147
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0067 | 94 | 0.005113 | 0.48062
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.76853 | 36 | 0.005113 | 0.18407
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.91796 | 43 | 0.005113 | 0.21986
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46966 | 22 | 0.005113 | 0.11249
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1595 | 148 | 0.005113 | 0.75672
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0674 | 50 | 0.005113 | 0.25565
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1741 | 55 | 0.005113 | 0.28122
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0674 | 50 | 0.005113 | 0.25565
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.021356 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.005105 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.021356 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.81153 | 38 | 0.005105 | 0.19399
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.021356 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.41217 | 19.3 | 0.005105 | 0.098527
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.021356 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.32034 | 15 | 0.005105 | 0.076575
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.021356 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0037 | 47 | 0.005105 | 0.23994
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.02138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0787 | 144 | 0.005081 | 0.73166
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.02138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0787 | 144 | 0.005081 | 0.73166
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.02138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.656 | 171 | 0.005081 | 0.86885
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.021381 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.4259 | 207 | 0.00508 | 1.0516
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.021381 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6333 | 216.7 | 0.00508 | 1.1008
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.021381 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1742 | 242 | 0.00508 | 1.2294
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.021397 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1347 | 146.5 | 0.005064 | 0.74188
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.021397 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1646 | 147.9 | 0.005064 | 0.74897
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.021397 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7017 | 173 | 0.005064 | 0.87607
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.021505 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25806 | 0 | 0.004956 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.021505 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.23655 | 0 | 0.004956 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.021505 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25806 | 0 | 0.004956 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.021608 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004853 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.021616 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004845 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.021991 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00447 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.021993 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1993 | 100 | 0.004468 | 0.4468
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.021993 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1993 | 100 | 0.004468 | 0.4468
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.021993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004468 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.021993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004468 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.021993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004468 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.021993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004468 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.022011 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.8449 | 629 | 0.00445 | 2.7991
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.022038 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.52891 | 24 | 0.004423 | 0.10615
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.022038 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.52891 | 24 | 0.004423 | 0.10615
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.022038 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.50687 | 23 | 0.004423 | 0.10173
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.022233 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004228 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.024645 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1404 | 168 | 0.0038526 | 0.64724
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.024645 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.218 | 90 | 0.0038526 | 0.34673
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.024265 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.7298 | 112.5 | 0.0034726 | 0.39067
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.024012 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0032196 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.024012 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0032196 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.024012 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0032196 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.023827 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.4355 | 396 | 0.002634 | 1.0431
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.023191 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4787 | 150 | 0.0023986 | 0.35979
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.022797 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3678 | 60 | 0.0020046 | 0.12028
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.022797 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4362 | 63 | 0.0020046 | 0.12629
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.022636 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.9412 | 395 | 0.0018436 | 0.72822
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.022636 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.8467 | 435 | 0.0018436 | 0.80197
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.024755 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29706 | 0 | 0.001706 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.022435 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.7592 | 435 | 0.0016426 | 0.71453
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.025467 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -11.0272 | 433 | 0.000994 | 0.4304
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.025479 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.8797 | 584 | 0.000982 | 0.57349
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.025479 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.16 | 595 | 0.000982 | 0.58429
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.02552 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.9339 | 546 | 0.000941 | 0.51379
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.02552 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.14 | 750 | 0.000941 | 0.70575
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.025727 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4922 | 58 | 0.000734 | 0.042572
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.025727 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2897 | 89 | 0.000734 | 0.065326
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.132 | 44 | 0.000734 | 0.032296
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.132 | 44 | 0.000734 | 0.032296
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1063 | 43 | 0.000734 | 0.031562
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1577 | 45 | 0.000734 | 0.03303
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.025784 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.3889 | 209 | 0.000677 | 0.14149
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.025784 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.5693 | 216 | 0.000677 | 0.14623
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1861 | 46 | 0.000677 | 0.031142
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2118 | 47 | 0.000677 | 0.031819
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1861 | 46 | 0.000677 | 0.031142
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1861 | 46 | 0.000677 | 0.031142
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.025794 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9981 | 155 | 0.000667 | 0.10339
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.025794 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.385 | 170 | 0.000667 | 0.11339
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.025794 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9981 | 155 | 0.000667 | 0.10339
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.025831 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.6424 | 412 | 0.00063 | 0.25956
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.025831 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.3324 | 400 | 0.00063 | 0.252
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7983 | 147 | 0.000622 | 0.091435
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5658 | 138 | 0.000622 | 0.085837
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6175 | 140 | 0.000622 | 0.087081
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7983 | 147 | 0.000622 | 0.091435
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.7027 | 182 | 0.000622 | 0.1132
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1161 | 198 | 0.000622 | 0.12316
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.02584 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.000621 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.02584 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.000621 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.02584 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.000621 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.025853 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.5222 | 407 | 0.000608 | 0.24746
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.025872 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.9697 | 424 | 0.000589 | 0.24974
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.025872 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.9956 | 425 | 0.000589 | 0.25033
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7705 | 224 | 0.0005046 | 0.11303
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8131 | 226 | 0.0005046 | 0.11404
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.515 | 212 | 0.0005046 | 0.10698
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4937 | 211 | 0.0005046 | 0.10647
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.021133 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0003406 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.026383 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.063319 | 0 | 7.8004e-05 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.026383 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.063319 | 0 | 7.8004e-05 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.020844 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 5.1605e-05 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.020836 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.83344 | 0 | 4.3605e-05 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.020836 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.83344 | 0 | 4.3605e-05 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7613 | 142 | -2.6996e-05 | -0.0038335
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8408 | 145 | -2.6996e-05 | -0.0039145
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9997 | 151 | -2.6996e-05 | -0.0040764
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6815 | 290 | -2.6996e-05 | -0.0078289
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.020696 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5183 | 170 | -9.6395e-05 | -0.016387
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.020696 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.7619 | 520 | -9.6395e-05 | -0.050126
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3338 | 50 | -0.000216 | -0.0108
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3338 | 50 | -0.000216 | -0.0108
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3338 | 50 | -0.000216 | -0.0108
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3338 | 50 | -0.000216 | -0.0108
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.020513 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.5898 | 370 | -0.0002794 | -0.10338
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8718 | 0 | -0.0002794 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8923 | 0 | -0.0002794 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.3385 | 0 | -0.0002794 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.9334 | 0 | -0.0002794 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.9539 | 0 | -0.0002794 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.359 | 0 | -0.0002794 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2717 | 160 | -0.0003444 | -0.055103
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1899 | 156 | -0.0003444 | -0.053726
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0078 | 196 | -0.0003444 | -0.067501
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1899 | 156 | -0.0003444 | -0.053726
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2103 | 157 | -0.0003444 | -0.05407
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0487 | 198 | -0.0003444 | -0.06819
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.026824 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1073 | 0 | -0.000363 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.020408 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5306 | 0 | -0.0003844 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.020408 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.6245 | 0 | -0.0003844 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.020408 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.8041 | 0 | -0.0003844 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.020329 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.3436 | 558 | -0.0004634 | -0.25857
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.020329 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.7705 | 579 | -0.0004634 | -0.26831
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.020329 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.4258 | 808 | -0.0004634 | -0.37442
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.020284 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.3935 | 118 | -0.0005084 | -0.059991
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.020284 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3327 | 115 | -0.0005084 | -0.058465
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.020284 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 11.2779 | 556 | -0.0005084 | -0.28267
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.026975 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.3488 | 569 | -0.000514 | -0.29246
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.026975 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.6725 | 581 | -0.000514 | -0.29863
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.027054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.06493 | 0 | -0.000593 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.027054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.06493 | 0 | -0.000593 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.027054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.075751 | 0 | -0.000593 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.020139 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.591 | 79 | -0.0006534 | -0.051618
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.020139 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1347 | 106 | -0.0006534 | -0.06926
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.020139 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.9403 | 146 | -0.0006534 | -0.095396
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.020139 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5306 | 76 | -0.0006534 | -0.049658
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.02009 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.8036 | 40 | -0.0007024 | -0.028096
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.0822 | 223.9 | -0.000704 | -0.15762
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1121 | 225 | -0.000704 | -0.1584
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1013 | 224.6 | -0.000704 | -0.15812
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1583 | 226.7 | -0.000704 | -0.1596
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.020053 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.50133 | 25 | -0.0007394 | -0.018485
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.020053 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.82217 | 41 | -0.0007394 | -0.030315
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.020052 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.40104 | 20 | -0.0007404 | -0.014808
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027277 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3098 | 158 | -0.000816 | -0.12893
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027277 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3643 | 160 | -0.000816 | -0.13056
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027277 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.7735 | 175 | -0.000816 | -0.1428
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.019945 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0008474 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.019945 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0008474 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.019905 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3074 | 216.4 | -0.0008874 | -0.19203
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.019905 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3015 | 216.1 | -0.0008874 | -0.19177
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.019891 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.7177 | 388 | -0.0009014 | -0.34974
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.019891 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.2439 | 515 | -0.0009014 | -0.46422
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1535 | 161 | -0.0012054 | -0.19407
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2123 | 164 | -0.0012054 | -0.19768
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2123 | 164 | -0.0012054 | -0.19768
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.109 | 414 | -0.0012054 | -0.49903
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1731 | 162 | -0.0012054 | -0.19527
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1535 | 161 | -0.0012054 | -0.19407
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1927 | 163 | -0.0012054 | -0.19648
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.0111 | 409 | -0.0012054 | -0.49301
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.019302 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7832 | 196 | -0.0014904 | -0.29212
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.019302 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.1425 | 111 | -0.0014904 | -0.16543
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.028395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3302 | 152.5 | -0.001934 | -0.29493
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.028395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.2451 | 149.5 | -0.001934 | -0.28913
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.028395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6047 | 232.6 | -0.001934 | -0.44985
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.017879 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.035 | 785 | -0.0029134 | -2.287
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.017879 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.2138 | 795 | -0.0029134 | -2.3161
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.017879 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.9456 | 780 | -0.0029134 | -2.2724
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3533 | 114 | -0.002954 | -0.33676
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5301 | 222 | -0.002954 | -0.65579
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4124 | 184 | -0.002954 | -0.54354
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.589 | 224 | -0.002954 | -0.6617
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3827 | 115 | -0.002954 | -0.33971
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.029567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.9028 | 132 | -0.003106 | -0.40999
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.029567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.962 | 134 | -0.003106 | -0.4162
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.029567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.5501 | 323 | -0.003106 | -1.0032
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6119 | 0 | -0.0031444 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2942 | 0 | -0.0031444 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.559 | 0 | -0.0031444 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0416 | 0 | -0.0031444 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.017422 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.9025 | 224 | -0.0033704 | -0.75497
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.01742 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0033724 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.017401 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.87005 | 50 | -0.0033914 | -0.16957
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.017282 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.1453 | 182 | -0.0035104 | -0.63889
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.017282 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.3645 | 484 | -0.0035104 | -1.699
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.030304 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18182 | 0 | -0.003843 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.015485 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.23228 | 0 | -0.0053074 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.015485 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.23228 | 0 | -0.0053074 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.015262 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3122 | 151.5 | -0.0055304 | -0.83785
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.015262 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3244 | 152.3 | -0.0055304 | -0.84228
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.015262 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.709 | 177.5 | -0.0055304 | -0.98165
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.015191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2893 | 150.7 | -0.0056014 | -0.84413
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.015191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2938 | 151 | -0.0056014 | -0.84581
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.015191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6949 | 177.4 | -0.0056014 | -0.99369
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.014689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.0337 | 615 | -0.0061034 | -3.7536
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.014689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.6224 | 587 | -0.0061034 | -3.5827
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6136 | 49 | -0.00647 | -0.31703
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5148 | 46 | -0.00647 | -0.29762
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5148 | 46 | -0.00647 | -0.29762
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5478 | 47 | -0.00647 | -0.30409
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.032931 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.0714 | 154 | -0.00647 | -0.99638
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.032931 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8738 | 148 | -0.00647 | -0.95756
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5807 | 48 | -0.00647 | -0.31056
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5807 | 48 | -0.00647 | -0.31056
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3849 | 42 | -0.006513 | -0.27355
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4509 | 44 | -0.006513 | -0.28657
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4509 | 44 | -0.006513 | -0.28657
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5498 | 47 | -0.006513 | -0.30611
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.03328 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.3168 | 310 | -0.006819 | -2.1139
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.03328 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.7446 | 413 | -0.006819 | -2.8162
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.013462 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0193 | 150 | -0.0073304 | -1.0996
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.013462 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.077 | 80 | -0.0073304 | -0.58643
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.034155 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.27324 | 0 | -0.007694 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.034155 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.27324 | 0 | -0.007694 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.013082 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0077104 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.013082 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.2955 | 787 | -0.0077104 | -6.0681
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3176 | 255 | -0.0077824 | -1.9845
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.01301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9385 | 149 | -0.0077824 | -1.1596
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.01301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9905 | 153 | -0.0077824 | -1.1907
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.010145 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.3899 | 827 | -0.010647 | -8.8054
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.010145 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.3088 | 819 | -0.010647 | -8.7202
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0161 | 855 | -0.012586 | -10.7614
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0161 | 855 | -0.012586 | -10.7614
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.2498 | 152.3 | -0.012586 | -1.9169
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.2555 | 153 | -0.012586 | -1.9257
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.007354 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.013438 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.007354 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.013438 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.003498 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.6196 | 463 | -0.017294 | -8.0073
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.017945 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.017945 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.002847 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.048399 | 17 | -0.017945 | -0.30507
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.017945 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.017945 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.002829 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.090528 | 0 | -0.017963 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.0025 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.12 | 48 | -0.018292 | -0.87803
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.0025 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.115 | 46 | -0.018292 | -0.84145
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.0025 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.2625 | 105 | -0.018292 | -1.9207
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.044936 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5728 | 0 | -0.018475 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.044936 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5278 | 0 | -0.018475 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.044936 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5728 | 0 | -0.018475 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.32737 | 0 | -0.018669 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.33119 | 0 | -0.018669 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.33119 | 0 | -0.018669 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.80674 | 0 | -0.018669 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.020792 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.020792 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.064709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1648 | 0 | -0.038248 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.064709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1648 | 0 | -0.038248 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.073428 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.9866 | 422 | -0.046967 | -19.8201
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.027075 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.047867 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.074493 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0858 | 0 | -0.048032 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.074493 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1603 | 0 | -0.048032 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -2.9415 | 100 | -0.050207 | -5.0207
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.087859 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2037 | 0 | -0.061398 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.10244 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8439 | 0 | -0.07598 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.10244 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8439 | 0 | -0.07598 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.10244 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5366 | 0 | -0.07598 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Brownwood Switch - Goldthwaite [1655 - 7070] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.10244 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8439 | 0 | -0.07598 | 0 | 0 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.10244 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8439 | 0 | -0.07598 | 0 | 0 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.10244 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5366 | 0 | -0.07598 | 0 | 0 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.087859 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2037 | 0 | -0.061398 | 0 | 0 | 0 | Weighted Shift Factors
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -2.9415 | 0 | -0.050207 | 0 | 0 | 0 | South | -0.026461
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.074493 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0858 | 0 | -0.048032 | 0 | 0 | 0 | North | 0.020792
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.074493 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1603 | 0 | -0.048032 | 0 | 0 | 0 |  | -0.047253
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.027075 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.047867 | 0 | 0 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.073428 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.9866 | 422 | -0.046967 | -19.8201 | 422 | 19.8201 | Line Rating | 265
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.064709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1648 | 0 | -0.038248 | 0 | 422 | 19.8201 | Conc Gen | 516
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.064709 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1648 | 0 | -0.038248 | 0 | 422 | 19.8201 | Weighted Imp. | 21.5396
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.020792 | 0 | 422 | 19.8201 | PTDF | 0.041743
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.020792 | 0 | 422 | 19.8201
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.32737 | 0 | -0.018669 | 0 | 422 | 19.8201 | Concentration | -0.88339
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.33119 | 0 | -0.018669 | 0 | 422 | 19.8201
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.33119 | 0 | -0.018669 | 0 | 422 | 19.8201
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.002123 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.80674 | 0 | -0.018669 | 0 | 422 | 19.8201
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.044936 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5728 | 0 | -0.018475 | 0 | 422 | 19.8201
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.044936 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5278 | 0 | -0.018475 | 0 | 422 | 19.8201
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.044936 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5728 | 0 | -0.018475 | 0 | 422 | 19.8201
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.0025 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.12 | 48 | -0.018292 | -0.87803 | 470 | 20.6981
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.0025 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.115 | 46 | -0.018292 | -0.84145 | 516 | 21.5396
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.0025 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.2625 | 105 | -0.018292 | -1.9207
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.002829 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.090528 | 0 | -0.017963 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.017945 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.017945 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.002847 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.048399 | 17 | -0.017945 | -0.30507
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.017945 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.002847 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.017945 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.003498 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.6196 | 0 | -0.017294 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.007354 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.013438 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.007354 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.013438 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0161 | 0 | -0.012586 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0161 | 0 | -0.012586 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.2498 | 0 | -0.012586 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.008206 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.2555 | 0 | -0.012586 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.010145 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.3899 | 0 | -0.010647 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.010145 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.3088 | 0 | -0.010647 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3176 | 255 | -0.0077824 | -1.9845
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.01301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9385 | 149 | -0.0077824 | -1.1596
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.01301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9905 | 153 | -0.0077824 | -1.1907
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.013082 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0077104 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.013082 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.2955 | 787 | -0.0077104 | -6.0681
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.034155 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.27324 | 0 | -0.007694 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.034155 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.27324 | 0 | -0.007694 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.013462 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0193 | 150 | -0.0073304 | -1.0996
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.013462 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.077 | 80 | -0.0073304 | -0.58643
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.03328 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.3168 | 310 | -0.006819 | -2.1139
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.03328 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.7446 | 413 | -0.006819 | -2.8162
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3849 | 42 | -0.006513 | -0.27355
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4509 | 44 | -0.006513 | -0.28657
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4509 | 44 | -0.006513 | -0.28657
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.032974 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5498 | 47 | -0.006513 | -0.30611
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6136 | 49 | -0.00647 | -0.31703
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5148 | 46 | -0.00647 | -0.29762
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5148 | 46 | -0.00647 | -0.29762
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5478 | 47 | -0.00647 | -0.30409
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.032931 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.0714 | 154 | -0.00647 | -0.99638
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.032931 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8738 | 148 | -0.00647 | -0.95756
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5807 | 48 | -0.00647 | -0.31056
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.032931 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5807 | 48 | -0.00647 | -0.31056
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.014689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.0337 | 0 | -0.0061034 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.014689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.6224 | 0 | -0.0061034 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.015191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2893 | 150.7 | -0.0056014 | -0.84413
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.015191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2938 | 151 | -0.0056014 | -0.84581
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.015191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6949 | 177.4 | -0.0056014 | -0.99369
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.015262 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3122 | 151.5 | -0.0055304 | -0.83785
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.015262 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3244 | 152.3 | -0.0055304 | -0.84228
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.015262 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.709 | 177.5 | -0.0055304 | -0.98165
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.015485 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.23228 | 0 | -0.0053074 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.015485 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.23228 | 0 | -0.0053074 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.030304 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18182 | 0 | -0.003843 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.017282 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.1453 | 182 | -0.0035104 | -0.63889
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.017282 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.3645 | 484 | -0.0035104 | -1.699
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.017401 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.87005 | 0 | -0.0033914 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.01742 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0033724 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.017422 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.9025 | 224 | -0.0033704 | -0.75497
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6119 | 0 | -0.0031444 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2942 | 0 | -0.0031444 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.559 | 0 | -0.0031444 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.017648 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0416 | 0 | -0.0031444 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.029567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.9028 | 132 | -0.003106 | -0.40999
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.029567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.962 | 134 | -0.003106 | -0.4162
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.029567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.5501 | 323 | -0.003106 | -1.0032
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3533 | 0 | -0.002954 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5301 | 0 | -0.002954 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4124 | 0 | -0.002954 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.589 | 0 | -0.002954 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.029415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3827 | 0 | -0.002954 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.017879 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.035 | 0 | -0.0029134 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.017879 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.2138 | 0 | -0.0029134 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.017879 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.9456 | 0 | -0.0029134 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.028395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3302 | 152.5 | -0.001934 | -0.29493
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.028395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.2451 | 149.5 | -0.001934 | -0.28913
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.028395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6047 | 232.6 | -0.001934 | -0.44985
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.019302 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7832 | 196 | -0.0014904 | -0.29212
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.019302 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.1425 | 111 | -0.0014904 | -0.16543
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1535 | 161 | -0.0012054 | -0.19407
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2123 | 164 | -0.0012054 | -0.19768
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2123 | 164 | -0.0012054 | -0.19768
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.109 | 414 | -0.0012054 | -0.49903
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1731 | 162 | -0.0012054 | -0.19527
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1535 | 161 | -0.0012054 | -0.19407
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1927 | 163 | -0.0012054 | -0.19648
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.019587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.0111 | 409 | -0.0012054 | -0.49301
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.019891 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.7177 | 388 | -0.0009014 | -0.34974
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.019891 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.2439 | 515 | -0.0009014 | -0.46422
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.019905 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3074 | 216.4 | -0.0008874 | -0.19203
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.019905 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3015 | 216.1 | -0.0008874 | -0.19177
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.019945 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0008474 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.019945 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0008474 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027277 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3098 | 158 | -0.000816 | -0.12893
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027277 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3643 | 160 | -0.000816 | -0.13056
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027277 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.7735 | 175 | -0.000816 | -0.1428
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.020052 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.40104 | 20 | -0.0007404 | -0.014808
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.020053 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.50133 | 25 | -0.0007394 | -0.018485
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.020053 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.82217 | 41 | -0.0007394 | -0.030315
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.0822 | 223.9 | -0.000704 | -0.15762
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1121 | 225 | -0.000704 | -0.1584
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1013 | 224.6 | -0.000704 | -0.15812
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.027165 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1583 | 226.7 | -0.000704 | -0.1596
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.02009 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.8036 | 40 | -0.0007024 | -0.028096
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.020139 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.591 | 79 | -0.0006534 | -0.051618
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.020139 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1347 | 106 | -0.0006534 | -0.06926
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.020139 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.9403 | 146 | -0.0006534 | -0.095396
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.020139 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5306 | 76 | -0.0006534 | -0.049658
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.027054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.06493 | 0 | -0.000593 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.027054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.06493 | 0 | -0.000593 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.027054 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.075751 | 0 | -0.000593 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.026975 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.3488 | 0 | -0.000514 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.026975 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.6725 | 0 | -0.000514 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.020284 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.3935 | 118 | -0.0005084 | -0.059991
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.020284 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3327 | 115 | -0.0005084 | -0.058465
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.020284 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 11.2779 | 556 | -0.0005084 | -0.28267
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.020329 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.3436 | 0 | -0.0004634 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.020329 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.7705 | 0 | -0.0004634 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.020329 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.4258 | 0 | -0.0004634 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.020408 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5306 | 0 | -0.0003844 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.020408 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.6245 | 0 | -0.0003844 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.020408 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.8041 | 0 | -0.0003844 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.026824 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1073 | 0 | -0.000363 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2717 | 160 | -0.0003444 | -0.055103
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1899 | 156 | -0.0003444 | -0.053726
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0078 | 196 | -0.0003444 | -0.067501
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1899 | 156 | -0.0003444 | -0.053726
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2103 | 157 | -0.0003444 | -0.05407
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.020448 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0487 | 198 | -0.0003444 | -0.06819
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.020513 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.5898 | 370 | -0.0002794 | -0.10338
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8718 | 0 | -0.0002794 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8923 | 0 | -0.0002794 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.3385 | 0 | -0.0002794 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.9334 | 0 | -0.0002794 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.9539 | 0 | -0.0002794 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.020513 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.359 | 0 | -0.0002794 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3338 | 50 | -0.000216 | -0.0108
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3338 | 50 | -0.000216 | -0.0108
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3338 | 50 | -0.000216 | -0.0108
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.026677 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3338 | 50 | -0.000216 | -0.0108
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.020696 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5183 | 170 | -9.6395e-05 | -0.016387
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.020696 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.7619 | 520 | -9.6395e-05 | -0.050126
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7613 | 142 | -2.6996e-05 | -0.0038335
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8408 | 145 | -2.6996e-05 | -0.0039145
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9997 | 151 | -2.6996e-05 | -0.0040764
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.026488 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6815 | 290 | -2.6996e-05 | -0.0078289
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.020836 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.83344 | 0 | 4.3605e-05 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.020836 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.83344 | 0 | 4.3605e-05 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.020844 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 5.1605e-05 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.026383 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.063319 | 0 | 7.8004e-05 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.026383 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.063319 | 0 | 7.8004e-05 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.021133 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0003406 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7705 | 224 | 0.0005046 | 0.11303
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8131 | 226 | 0.0005046 | 0.11404
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.515 | 212 | 0.0005046 | 0.10698
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.021297 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4937 | 211 | 0.0005046 | 0.10647
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.025872 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.9697 | 0 | 0.000589 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.025872 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -10.9956 | 0 | 0.000589 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.025853 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.5222 | 407 | 0.000608 | 0.24746
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.02584 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.000621 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.02584 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.000621 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.02584 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.000621 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7983 | 147 | 0.000622 | 0.091435
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5658 | 138 | 0.000622 | 0.085837
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.6175 | 140 | 0.000622 | 0.087081
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7983 | 147 | 0.000622 | 0.091435
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.7027 | 182 | 0.000622 | 0.1132
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.025839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1161 | 198 | 0.000622 | 0.12316
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.025831 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.6424 | 412 | 0.00063 | 0.25956
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.025831 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.3324 | 400 | 0.00063 | 0.252
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.025794 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9981 | 155 | 0.000667 | 0.10339
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.025794 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.385 | 170 | 0.000667 | 0.11339
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.025794 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9981 | 155 | 0.000667 | 0.10339
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.025784 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.3889 | 209 | 0.000677 | 0.14149
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.025784 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.5693 | 216 | 0.000677 | 0.14623
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1861 | 46 | 0.000677 | 0.031142
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2118 | 47 | 0.000677 | 0.031819
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1861 | 46 | 0.000677 | 0.031142
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.025784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1861 | 46 | 0.000677 | 0.031142
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.025727 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4922 | 58 | 0.000734 | 0.042572
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.025727 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2897 | 89 | 0.000734 | 0.065326
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.132 | 44 | 0.000734 | 0.032296
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.132 | 44 | 0.000734 | 0.032296
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1063 | 43 | 0.000734 | 0.031562
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.025727 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1577 | 45 | 0.000734 | 0.03303
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.02552 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.9339 | 0 | 0.000941 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.02552 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.14 | 0 | 0.000941 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.025479 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.8797 | 0 | 0.000982 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.025479 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.16 | 0 | 0.000982 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.025467 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -11.0272 | 0 | 0.000994 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.022435 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.7592 | 435 | 0.0016426 | 0.71453
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.024755 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29706 | 0 | 0.001706 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.022636 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.9412 | 395 | 0.0018436 | 0.72822
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.022636 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.8467 | 435 | 0.0018436 | 0.80197
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.022797 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3678 | 60 | 0.0020046 | 0.12028
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.022797 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4362 | 63 | 0.0020046 | 0.12629
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.023191 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4787 | 0 | 0.0023986 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.023827 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.4355 | 0 | 0.002634 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.024012 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0032196 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.024012 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0032196 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.024012 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0032196 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.024265 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.7298 | 0 | 0.0034726 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.024645 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1404 | 168 | 0.0038526 | 0.64724
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.024645 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.218 | 90 | 0.0038526 | 0.34673
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.022233 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004228 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.022038 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.52891 | 24 | 0.004423 | 0.10615
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.022038 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.52891 | 24 | 0.004423 | 0.10615
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.022038 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.50687 | 23 | 0.004423 | 0.10173
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.022011 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.8449 | 0 | 0.00445 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.021993 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1993 | 100 | 0.004468 | 0.4468
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.021993 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1993 | 100 | 0.004468 | 0.4468
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.021993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004468 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.021993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004468 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.021993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004468 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.021993 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004468 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.021991 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00447 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.021642 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.18179 | 8.4 | 0.004819 | 0.04048
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.021616 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004845 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.021608 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004853 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.021505 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25806 | 0 | 0.004956 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.021505 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.23655 | 0 | 0.004956 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.021505 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25806 | 0 | 0.004956 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.021397 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1347 | 146.5 | 0.005064 | 0.74188
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.021397 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1646 | 147.9 | 0.005064 | 0.74897
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.021397 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7017 | 173 | 0.005064 | 0.87607
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.021381 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.4259 | 207 | 0.00508 | 1.0516
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.021381 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6333 | 216.7 | 0.00508 | 1.1008
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.021381 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1742 | 242 | 0.00508 | 1.2294
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.02138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0787 | 144 | 0.005081 | 0.73166
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.02138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0787 | 144 | 0.005081 | 0.73166
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.02138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.656 | 171 | 0.005081 | 0.86885
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.021356 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.81153 | 38 | 0.005105 | 0.19399
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.021356 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.41217 | 19.3 | 0.005105 | 0.098527
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.021356 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.32034 | 15 | 0.005105 | 0.076575
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.021356 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0037 | 47 | 0.005105 | 0.23994
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.021356 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.005105 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0067 | 0 | 0.005113 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.87527 | 0 | 0.005113 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.81122 | 0 | 0.005113 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.40561 | 0 | 0.005113 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0067 | 0 | 0.005113 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.76853 | 0 | 0.005113 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.91796 | 0 | 0.005113 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46966 | 0 | 0.005113 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1595 | 0 | 0.005113 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0674 | 0 | 0.005113 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1741 | 0 | 0.005113 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.021348 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0674 | 0 | 0.005113 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.021319 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.61825 | 0 | 0.005142 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.021223 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.80647 | 0 | 0.005238 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.021221 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.8064 | 0 | 0.00524 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.021201 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.53002 | 0 | 0.00526 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.021201 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.53002 | 0 | 0.00526 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.021198 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.0801 | 334 | 0.005263 | 1.7578
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.021198 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.2073 | 340 | 0.005263 | 1.7894
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.021198 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8156 | 180 | 0.005263 | 0.94734
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.021198 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8156 | 180 | 0.005263 | 0.94734
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.02606 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.5053 | 288 | 0.0052676 | 1.5171
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.02606 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8308 | 147 | 0.0052676 | 0.77434
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.02606 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8308 | 147 | 0.0052676 | 0.77434
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.021158 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8084 | 180 | 0.005303 | 0.95454
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.021154 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.1371 | 0 | 0.005307 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.021154 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.1435 | 0 | 0.005307 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.021154 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.2366 | 0 | 0.005307 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.021152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1071 | 336 | 0.005309 | 1.7838
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.021152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8074 | 180 | 0.005309 | 0.95562
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 0 | 0.005431 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 0 | 0.005431 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 0 | 0.005431 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.33648 | 0 | 0.005431 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 0 | 0.005431 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 0 | 0.005431 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52575 | 0 | 0.005431 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.02103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.31545 | 0 | 0.005431 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.021001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0241 | 144 | 0.00546 | 0.78624
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.021001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9482 | 188 | 0.00546 | 1.0265
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.3099 | 0 | 0.005512 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.2052 | 0 | 0.005512 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.0949 | 0 | 0.005512 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.0376 | 0 | 0.005512 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.0795 | 0 | 0.005512 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.020949 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.6605 | 0 | 0.005512 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.020949 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.25139 | 0 | 0.005512 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5175 | 0 | 0.005674 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.02649 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0056976 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.99001 | 47.7 | 0.005706 | 0.27218
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.77416 | 37.3 | 0.005706 | 0.21283
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.95473 | 46 | 0.005706 | 0.26248
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020755 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.99624 | 48 | 0.005706 | 0.27389
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.026518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.4097 | 204 | 0.0057256 | 1.168
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.026518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.3301 | 201 | 0.0057256 | 1.1508
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.026518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4174 | 242 | 0.0057256 | 1.3856
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.020568 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.4525 | 22 | 0.005893 | 0.12965
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.020568 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22625 | 11 | 0.005893 | 0.064823
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.020568 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22625 | 11 | 0.005893 | 0.064823
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.020415 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30623 | 0 | 0.006046 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.020415 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46954 | 0 | 0.006046 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.020281 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.16225 | 0 | 0.00618 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56557 | 0 | 0.006262 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14139 | 0 | 0.006262 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78776 | 0 | 0.006262 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30299 | 0 | 0.006262 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14139 | 0 | 0.006262 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.30299 | 0 | 0.006262 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78776 | 0 | 0.006262 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.020199 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78776 | 0 | 0.006262 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.027326 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0065336 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.927 | 70 | 0.0067366 | 0.47156
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8995 | 69 | 0.0067366 | 0.46483
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8995 | 69 | 0.0067366 | 0.46483
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.027529 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.872 | 68 | 0.0067366 | 0.45809
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.019687 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.94498 | 0 | 0.006774 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.027705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0203 | 217.3 | 0.0069126 | 1.5021
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.027705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.6795 | 205 | 0.0069126 | 1.4171
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.027705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.5468 | 272.4 | 0.0069126 | 1.883
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5428 | 0 | 0.006932 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5818 | 0 | 0.006932 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5428 | 0 | 0.006932 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5623 | 0 | 0.006932 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5311 | 0 | 0.006932 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48823 | 0 | 0.006932 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.89833 | 0 | 0.006932 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.54681 | 0 | 0.006932 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.85146 | 0 | 0.006932 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.019529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4451 | 0 | 0.006932 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.027877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.50179 | 18 | 0.0070846 | 0.12752
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.027877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.50179 | 18 | 0.0070846 | 0.12752
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.027877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.0593 | 38 | 0.0070846 | 0.26921
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.02853 | north | 3 | N | N | Nnorth | Nnorth | 1 | 33.0092 | 0 | 0.0077376 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.02853 | north | 3 | N | N | Nnorth | Nnorth | 1 | 33.0377 | 0 | 0.0077376 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.028602 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.4683 | 366 | 0.0078096 | 2.8583
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57384 | 20 | 0.0078996 | 0.15799
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57384 | 20 | 0.0078996 | 0.15799
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57384 | 20 | 0.0078996 | 0.15799
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.028692 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.48776 | 17 | 0.0078996 | 0.13429
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.029332 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.35198 | 0 | 0.0085396 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.029332 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.35198 | 0 | 0.0085396 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.029599 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.5519 | 0 | 0.0088066 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.030174 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.3021 | 242 | 0.0093816 | 2.2703
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.030641 | west | 4 | Y | N | Ywest | Nwest | 1 | 19.9075 | 0 | 0.0098486 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.030956 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6003 | 0 | 0.010164 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.031085 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.129 | 0 | 0.010293 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031181 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4945 | 0 | 0.010389 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.031186 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3857 | 0 | 0.010394 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.031827 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3234 | 73 | 0.011035 | 0.80553
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.031827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.7874 | 119 | 0.011035 | 1.3131
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.031827 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.5245 | 205 | 0.011035 | 2.2621
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.031827 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.2464 | 102 | 0.011035 | 1.1255
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.031827 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.0554 | 96 | 0.011035 | 1.0593
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.031846 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7769 | 0 | 0.011054 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.031846 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7769 | 0 | 0.011054 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.031861 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5489 | 0 | 0.011069 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031865 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5492 | 0 | 0.011073 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.031869 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5211 | 0 | 0.011077 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.031876 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7504 | 0 | 0.011084 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.031899 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3924 | 0 | 0.011107 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031899 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5519 | 0 | 0.011107 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.031899 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.276 | 0 | 0.011107 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.03204 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5632 | 0 | 0.011248 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.03204 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5632 | 0 | 0.011248 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.03244 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.15571 | 0 | 0.011648 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9538 | 0 | 0.01248 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2089 | 0 | 0.01248 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2847 | 0 | 0.01248 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.033272 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5546 | 0 | 0.01248 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.013886 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -18.51 | 0 | 0.012575 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.013886 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -18.4406 | 0 | 0.012575 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2101 | 66 | 0.012695 | 0.83784
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1767 | 65 | 0.012695 | 0.82515
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2436 | 67 | 0.012695 | 0.85054
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2436 | 67 | 0.012695 | 0.85054
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.033487 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2436 | 67 | 0.012695 | 0.85054
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.033487 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012695 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.033487 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.012695 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.033509 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1728 | 0 | 0.012717 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.033509 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0053 | 0 | 0.012717 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0418 | 76 | 0.012753 | 0.96923
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0418 | 76 | 0.012753 | 0.96923
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4393 | 105 | 0.012753 | 1.3391
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0144 | 74 | 0.012753 | 0.94372
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0144 | 74 | 0.012753 | 0.94372
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.013708 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3982 | 102 | 0.012753 | 1.3008
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.033574 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0025 | 0 | 0.012782 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.033724 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2155 | 0 | 0.012932 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.033724 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2155 | 0 | 0.012932 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.023 | 208.2 | 0.01294 | 2.694
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.7933 | 142.1 | 0.01294 | 1.8387
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.4661 | 132.4 | 0.01294 | 1.7132
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5876 | 136 | 0.01294 | 1.7598
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.9586 | 147 | 0.01294 | 1.9021
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.033732 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.0837 | 210 | 0.01294 | 2.7173
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3614 | 70 | 0.012942 | 0.90591
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3614 | 70 | 0.012942 | 0.90591
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1305 | 92.8 | 0.012942 | 1.201
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6987 | 80 | 0.012942 | 1.0353
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6987 | 80 | 0.012942 | 1.0353
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.033734 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.8794 | 115 | 0.012942 | 1.4883
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.033776 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0266 | 0 | 0.012984 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.033886 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9654 | 0 | 0.013094 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2708 | 0 | 0.013096 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.643 | 0 | 0.013096 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5749 | 0 | 0.013096 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0327 | 0 | 0.013096 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5582 | 0 | 0.013096 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.033888 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.728 | 0 | 0.013096 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.033895 | west | 8 | N | N | Nwest | Nwest | 1 | 2.3727 | 0 | 0.013103 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.033895 | west | 8 | N | N | Nwest | Nwest | 1 | 2.4879 | 0 | 0.013103 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.033895 | west | 8 | N | N | Nwest | Nwest | 1 | 2.3862 | 0 | 0.013103 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.033919 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2654 | 0 | 0.013127 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.088 | 0 | 0.013128 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4624 | 0 | 0.013128 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.784 | 0 | 0.013128 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.03392 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1348 | 0 | 0.013128 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.033964 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4134 | 0 | 0.013172 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.034082 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6684 | 0 | 0.01329 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.034094 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1369 | 0 | 0.013302 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.034094 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1369 | 0 | 0.013302 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2521 | 66 | 0.013331 | 0.87982
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3545 | 69 | 0.013331 | 0.91981
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3545 | 69 | 0.013331 | 0.91981
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2862 | 67 | 0.013331 | 0.89315
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2862 | 67 | 0.013331 | 0.89315
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.034123 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.218 | 65 | 0.013331 | 0.86649
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.013127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.86638 | 66 | 0.013334 | 0.88004
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.034161 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8167 | 0 | 0.013369 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.034161 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0993 | 0 | 0.013369 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.034163 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3821 | 0 | 0.013371 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.034163 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0839 | 0 | 0.013371 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.034163 | west | 7 | N | N | Nwest | Nwest | 1 | 0.85408 | 0 | 0.013371 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.034163 | west | 7 | N | N | Nwest | Nwest | 1 | 1.5612 | 0 | 0.013371 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.034163 | west | 7 | N | N | Nwest | Nwest | 1 | 1.5612 | 0 | 0.013371 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.034171 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8704 | 0 | 0.013379 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.034204 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1549 | 0 | 0.013412 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.034205 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1307 | 0 | 0.013413 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.034251 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1101 | 0 | 0.013459 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.034258 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.111 | 0 | 0.013466 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.012704 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013757 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.034642 | west | 8 | N | N | Nwest | Nwest | 1 | 0.89376 | 0 | 0.01385 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.035537 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3305 | 0 | 0.014745 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.035537 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5892 | 0 | 0.014745 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.011599 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.069594 | 0 | 0.014862 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.035734 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3601 | 0 | 0.014942 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.03579 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.23621 | 0 | 0.014998 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.03579 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2276 | 0 | 0.014998 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.035987 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3184 | 0 | 0.015195 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.035987 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.385 | 0 | 0.015195 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.035987 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.125 | 0 | 0.015195 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0588 | 0 | 0.015286 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3937 | 0 | 0.015286 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7105 | 0 | 0.015286 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.036078 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7387 | 0 | 0.015286 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69025 | 0 | 0.015328 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7949 | 0 | 0.015328 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50099 | 0 | 0.015328 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1244 | 0 | 0.015328 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.95744 | 0 | 0.015328 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9797 | 0 | 0.015328 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55665 | 0 | 0.015328 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20039 | 0 | 0.015328 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0465 | 0 | 0.015328 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.77931 | 0 | 0.015328 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70138 | 0 | 0.015328 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.80158 | 0 | 0.015328 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72142 | 0 | 0.015328 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1244 | 0 | 0.015328 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0799 | 0 | 0.015328 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1467 | 0 | 0.015328 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84611 | 0 | 0.015328 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89064 | 0 | 0.015328 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89064 | 0 | 0.015328 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9037 | 0 | 0.015328 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.010635 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75509 | 0 | 0.015826 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.010635 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10635 | 0 | 0.015826 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.036674 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.2162 | 0 | 0.015882 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1361 | 0 | 0.016226 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1361 | 0 | 0.016226 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.218 | 0 | 0.016226 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.010235 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1207 | 0 | 0.016226 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.008847 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40785 | 0 | 0.017614 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.008784 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.7184 | 0 | 0.017677 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.008784 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.9542 | 0 | 0.017677 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.008784 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.2704 | 0 | 0.017677 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.008773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.43 | 0 | 0.017688 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.008773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.43 | 0 | 0.017688 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.008773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1494 | 0 | 0.017688 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.00864 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28512 | 0 | 0.017821 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.008551 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.3767 | 161 | 0.01791 | 2.8835
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.008551 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.4195 | 166 | 0.01791 | 2.9731
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.008551 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.1206 | 248 | 0.01791 | 4.4417
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.008551 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.6688 | 546 | 0.01791 | 9.7789
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.008551 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -5.4983 | 0 | 0.01791 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.008551 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11116 | 13 | 0.01791 | 0.23283
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.78695 | 0 | 0.018615 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72889 | 0 | 0.018615 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.80578 | 0 | 0.018615 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.007846 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.80029 | 0 | 0.018615 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.007845 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25104 | 0 | 0.018616 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.007845 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23535 | 0 | 0.018616 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55521 | 0 | 0.018619 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52306 | 0 | 0.018619 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41563 | 0 | 0.018619 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2014 | 0 | 0.018619 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2037 | 0 | 0.018619 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1943 | 0 | 0.018619 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75283 | 0 | 0.018619 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.007842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9134 | 0 | 0.018619 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.007842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31368 | 0 | 0.018619 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.007534 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3767 | 50 | 0.018927 | 0.94635
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.007309 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.019152 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.040151 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.4091 | 0 | 0.019359 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64028 | 0 | 0.019425 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61635 | 0 | 0.019425 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61213 | 0 | 0.019425 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38346 | 0 | 0.019425 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.007036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.085839 | 0 | 0.019425 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45045 | 0 | 0.019531 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4158 | 0 | 0.019531 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45045 | 0 | 0.019531 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.00693 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45045 | 0 | 0.019531 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.00685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22605 | 0 | 0.019611 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.00685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17125 | 0 | 0.019611 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.00685 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019611 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31124 | 46 | 0.019695 | 0.90597
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31124 | 46 | 0.019695 | 0.90597
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31124 | 46 | 0.019695 | 0.90597
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.37213 | 55 | 0.019695 | 1.0832
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.37213 | 55 | 0.019695 | 1.0832
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.006766 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.36536 | 54 | 0.019695 | 1.0635
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.006731 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.52502 | 0 | 0.01973 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.006731 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.53848 | 0 | 0.01973 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.09 | 0 | 0.019782 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0493 | 0 | 0.019782 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0519 | 0 | 0.019782 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0486 | 0 | 0.019782 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.006679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7967 | 0 | 0.019782 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.006631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23209 | 0 | 0.01983 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.006584 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.079008 | 12 | 0.019877 | 0.23852
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.006584 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.019877 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.006582 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.1124 | 169 | 0.019879 | 3.3596
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.006578 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0854 | 165 | 0.019883 | 3.2807
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.006575 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.97967 | 0 | 0.019886 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.006575 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42803 | 0 | 0.019886 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.006565 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.3983 | 213 | 0.019896 | 4.2378
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.006564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10634 | 0 | 0.019897 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42003 | 0 | 0.019898 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41478 | 0 | 0.019898 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5421 | 0 | 0.019898 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.006563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48304 | 0 | 0.019898 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.006561 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.4959 | 228 | 0.0199 | 4.5372
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.006559 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1806 | 0 | 0.019902 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.006559 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0403 | 0 | 0.019902 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.006559 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0298 | 0 | 0.019902 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.461 | 0 | 0.019968 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4675 | 0 | 0.019968 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25323 | 0 | 0.019968 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.006493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19479 | 0 | 0.019968 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.006384 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.86822 | 0 | 0.020077 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.26788 | 42 | 0.020083 | 0.84349
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.26788 | 42 | 0.020083 | 0.84349
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24236 | 38 | 0.020083 | 0.76315
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.006378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24236 | 38 | 0.020083 | 0.76315
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.006349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0984 | 0 | 0.020112 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.006349 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85711 | 0 | 0.020112 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.6421 | 104 | 0.020287 | 2.1098
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.6421 | 104 | 0.020287 | 2.1098
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3334 | 54 | 0.020287 | 1.0955
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32722 | 53 | 0.020287 | 1.0752
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3334 | 54 | 0.020287 | 1.0955
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35192 | 57 | 0.020287 | 1.1564
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3334 | 54 | 0.020287 | 1.0955
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3334 | 54 | 0.020287 | 1.0955
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35809 | 58 | 0.020287 | 1.1766
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.006174 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35809 | 58 | 0.020287 | 1.1766
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.006115 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.4945 | 735 | 0.020346 | 14.9543
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20641 | 0 | 0.02039 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21066 | 0 | 0.02039 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19852 | 0 | 0.02039 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27866 | 0 | 0.02039 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10746 | 0 | 0.02039 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12385 | 0 | 0.02039 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12081 | 0 | 0.02039 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21249 | 0 | 0.02039 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10928 | 0 | 0.02039 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51846 | 0 | 0.02039 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.006071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89851 | 0 | 0.02039 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00601 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.07212 | 12 | 0.020451 | 0.24541
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.005944 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02972 | 0 | 0.020517 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.005944 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12482 | 0 | 0.020517 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38623 | 0 | 0.020519 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39217 | 0 | 0.020519 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41594 | 0 | 0.020519 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37435 | 0 | 0.020519 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3684 | 0 | 0.020519 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61797 | 0 | 0.020519 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.005942 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35058 | 0 | 0.020519 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.00594 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.07128 | 0 | 0.020521 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.005935 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.4097 | 743 | 0.020526 | 15.2508
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.005901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.92646 | 0 | 0.02056 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.005881 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0115 | 172 | 0.02058 | 3.5398
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.005881 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0115 | 172 | 0.02058 | 3.5398
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.005881 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.0115 | 172 | 0.02058 | 3.5398
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93675 | 0 | 0.020707 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9287 | 0 | 0.020707 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.91431 | 0 | 0.020707 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.005754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.549 | 0 | 0.020707 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.005708 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.2718 | 398 | 0.020753 | 8.2597
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31522 | 56 | 0.020832 | 1.1666
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33211 | 59 | 0.020832 | 1.2291
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31522 | 56 | 0.020832 | 1.1666
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31522 | 56 | 0.020832 | 1.1666
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33211 | 59 | 0.020832 | 1.2291
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.005629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31522 | 56 | 0.020832 | 1.1666
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.84459 | 0 | 0.021579 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.76159 | 0 | 0.021579 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75183 | 0 | 0.021579 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004882 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75183 | 0 | 0.021579 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.004882 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79088 | 0 | 0.021579 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.026461 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.026461 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.026461 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown