## test results
CRE test for: |  | Evant - Adamsvill [7068 - 7066] | [5 empty] | FAIL
Line Rating: |  | 260
Direction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Evant - Adamsvill [7068 - 7066]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.015812
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.023486
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.02902
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.0069407
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Evant - Adamsvill [7068 - 7066]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.017918
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.024024
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.029137
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0066439
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Evant - Adamsvill [7068 - 7066]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.039837
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.013325
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.022456
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.052623
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.016545
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.035664
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | -0.041404 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.041404 | 0.039837
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.018253
[6 empty] | Concentration |  | -0.44085 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.036576
[6 empty] | Concentration |  | -0.8834 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 18.5921
| Percent of line rating => | [6 empty] | 7.151% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -10.1612
[7 empty] | B1(N-S) | 0.0028609 | -0.40193 | -0.40479 | 0.0028609
[7 empty] | B2 (N-W) | -0.15201 | -0.016614 | 0.1354 | -0.15201
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.0090296 | -0.21915 | -0.22818 | 0.0090296
[7 empty] | B4 (S-W) | -0.14513 | 0.38958 | 0.53471 | -0.14513
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.018926 | 0.18705 | 0.16812 | 0.018926
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.1606 | -0.20179 | -0.36239 | 0.1606
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | 0.68%
Deployment Error Percent | [6 empty] | B2 | -36.13%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 2.146%
[7 empty] | B4 | -34.5%
[7 empty] | B5 | 4.499%
[7 empty] | B6 | 38.17%
[7 empty] | Max Abs Error | 38.17% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: Evant - Adamsvill [7068 - 7066] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: Evant - Adamsvill [7068 - 7066] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011099 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 2.8302
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011099 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.6538
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.013267 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.199
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.013267 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.199
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011099 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.6981
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.011495 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 1.7243
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.011495 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.9196
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027587 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 2.0139
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027587 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 3.2829
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027587 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 5.6553
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027587 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 2.8139
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027587 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 2.6484
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.0254 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.3048
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.0254 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.3048
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.021294 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 3.5774
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.021294 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 1.9165
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.024125 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.43425
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.024125 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.43425
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.024125 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.91675
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.022533 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 6.4895
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.022533 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.3124
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.022533 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.3124
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.020961 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 2.3581
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.017303 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.69212
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017346 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 1.3703
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017346 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 1.8387
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017346 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 2.5325
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017346 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 1.3183
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.019674 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.1804
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.019674 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.2395
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.01727 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.3454
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.01727 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.43175
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.01727 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.70807
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.002764 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 1.2797
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 1.9167
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 1.8877
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.9457
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.9457
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.9457
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029041 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 3.3107
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029041 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 14.9561
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 1.9535
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.0423
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.0423
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 1.9831
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 1.9831
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 1.9239
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.029398 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 2.0579
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.029398 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 2.1578
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.029398 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 2.0696
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 4.4131
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 6.4726
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029633 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 2.9337
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029633 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 1.8076
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.029632 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 4.1781
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029633 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.74082
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029633 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.3542
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029633 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.3542
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.029632 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 3.5558
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.030053 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.77537
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.029459 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 2.9606
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.02971 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 3.5652
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.029391 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 1.7047
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.02942 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 6.3018
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.030837 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 4.6255
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.031059 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.20499
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.031059 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.0653
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.030837 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 3.1145
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.029717 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 3.566
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.02476 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 9.0622
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.026138 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 6.3254
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.027629 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 11.0516
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.027623 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 6.519
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.026936 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 4.4444
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.022935 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 4.6787
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.022935 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 4.6099
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.022935 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 5.5503
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.4968
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.4968
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.4968
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.42228
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.025634 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 3.0761
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.03488 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 2.0928
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.017581 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 1.3186
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.017581 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 1.3994
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.017581 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 1.5542
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 2.8186
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.7481
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 3.4527
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.7481
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 2.7657
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 3.488
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.017833 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 3.0316
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.017833 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 9.2732
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017673 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 6.539
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.017512 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 9.7717
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.017512 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 10.1394
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.017512 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 14.1497
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.020739 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 2.3228
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.020739 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 2.0739
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.020739 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 7.8393
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.023975 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 5.2098
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.023975 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 4.9149
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.023975 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 6.5308
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.02291 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 17.6407
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 1.6675
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.6436
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.6436
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 1.6198
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.024697 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 28.5744
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.024697 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 28.5991
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 4.1126
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 4.1494
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.01714 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 3.7091
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.01714 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 3.704
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 3.8923
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 3.874
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.019533 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 7.7155
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.019357 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 8.4203
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.019533 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 8.4969
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.018216 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 2.5138
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017473 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 2.0618
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017473 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 2.0094
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017473 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 9.715
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.017128 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 6.6457
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.017128 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 8.8209
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.015365 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 12.0615
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.015365 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 12.2152
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.015365 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 11.9847
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.014842 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 2.7012
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.014842 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 7.1835
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.014965 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 3.3522
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.014946 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.7473
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.014963 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.62845
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.01257 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 7.7306
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.01257 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 7.3786
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.011162 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 5.994
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.011162 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 8.7845
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006143 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.46072
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006143 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 1.3637
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.023936 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -13.6196
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022893 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -4.7846
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022893 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -4.9449
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.022953 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -9.3419
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0531
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -1.076
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0531
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0531
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.02297 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -9.7393
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.02297 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -9.7622
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022843 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -1.3249
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022843 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -2.033
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.0051
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.0051
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.98225
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.0279
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.022934 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -9.4488
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.022934 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -9.1736
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.022662 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -12.3735
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.022662 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -16.9965
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.022942 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -1.3995
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.022942 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -2.1795
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.022942 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -3.4642
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.022902 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.5498
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.022902 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -3.8933
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.022902 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.5498
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.018323 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.40311
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.018323 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.20155
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.018323 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.20155
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.88178
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.68953
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.85036
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.88733
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.019144 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.22973
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.019144 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.21058
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.01961 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.47064
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.01961 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.47064
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.01961 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.45103
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.021178 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -8.3865
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.012467 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -16.6185
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.012467 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -16.5562
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.019013 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.72249
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.019013 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.36695
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.019013 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.28519
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.019013 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.89361
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.02765 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 2.0737
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.02967 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 4.4505
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.031834 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 5.3959
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.02002 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 3.003
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.029669 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 1.8691
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.026547 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 17.2476
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.017956 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.71824
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.017956 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.71824
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.064639 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -27.2777
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.026207 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -3.4593
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.026207 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -3.5117
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.026207 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -8.4649
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.024201 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -3.8238
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.024201 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -3.8722
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.024201 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -4.2352
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.022626 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -13.2136
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.022626 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -13.4625
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.022615 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -9.7923
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -5.3967
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -5.4232
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -5.4135
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -5.4642
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.030228 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.24182
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.030228 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.24182
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.09006 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.6211
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.09006 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.6211
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.09006 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -1.3509
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.077284 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -1.0588
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.056999 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.026
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.056999 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.026
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.039674 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -1.3886
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.039674 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -1.3489
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.039674 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -1.3886
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.065572 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -1.836
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.065572 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -1.9016
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.029061 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.0171
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.029061 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 0.87183
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.1838
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.1838
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.1838
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.1838
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.026853 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.16112
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.024006 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.057614
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.024006 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.057614
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.024006 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.067217
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.023804 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.095216
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.023418 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.056203
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.023418 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.056203
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.3723
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -3.1659
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -3.2117
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.3723
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -4.1753
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -4.5423
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.025181 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -3.8401
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.025181 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -3.7646
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.025181 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -5.8571
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -3.3383
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -3.4088
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -3.5499
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -6.8176
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.006303 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.208
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.006303 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.15757
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.019144 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.22973
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.018514 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -1.3515
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -1.3756
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -1.4105
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.50397
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.12599
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -1.3756
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -1.393
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -1.3652
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.43533
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.801
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.019587 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -12.3202
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.018702 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -2.6931
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.018702 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -3.516
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.021991 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.26389
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.010464 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.062784
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.018834 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -6.3282
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.018874 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -6.3039
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.018874 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -6.4172
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.018895 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.71801
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.018877 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.47192
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.018877 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.47192
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.018897 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.71809
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.01898 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.55042
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.018836 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -2.7934
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.018836 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -2.799
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.018836 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -2.8819
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -2.9476
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -2.8544
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -1.8656
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -2.7051
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -2.7424
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -2.3693
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.019049 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -2.7907
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.019049 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -2.8173
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.019049 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -3.2955
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.019035 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -3.9402
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.019035 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -4.1249
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.019035 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -4.6065
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.019034 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -2.7409
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.019034 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -2.7409
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.019034 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -3.2548
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.029461 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -9.1329
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.029461 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -12.1674
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -1.2261
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -1.2845
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -1.2845
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -1.3721
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -1.4286
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -1.3411
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -1.3411
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -1.3703
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029155 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -4.4899
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029155 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -4.3149
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -1.3994
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -1.3994
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.0481
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.0481
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 2.7151
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.3406
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.3406
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 3.3647
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 6.0911
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 4.1573
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 3.8735
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 3.9788
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 4.3006
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 6.1438
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 6.0303
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 3.6499
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 7.1844
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 5.684
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 5.8842
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 3.5864
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.029117 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 4.3384
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.029573 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 5.3231
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.029573 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 5.3231
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.029563 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 6.6517
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.029249 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 3.6561
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.029249 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 3.6561
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 2.4742
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 2.4919
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 5.461
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 2.5272
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 2.5449
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 5.4786
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.016612 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 3.256
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.016612 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 1.8439
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.017963 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.7146
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.7652
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.7652
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 6.9805
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 2.7315
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.7146
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 2.7483
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 6.8961
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017175 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017175 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 2.2441
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 1.9712
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 2.1986
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 6.05
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 1.9606
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 1.9645
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 2.308
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.013072 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 1.9804
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.013072 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 1.9909
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.013072 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 2.3203
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.023936 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -13.9068
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 5.891
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 5.891
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.002178 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.069696
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.00189 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.09072
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.00189 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.08694
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.026328
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.11189
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002194 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.037298
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.048268
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.05485
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.00189 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.19845
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.02964 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 2.4898
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.027617 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 2.2094
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.027604 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.1406
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.027604 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.1406
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.50778
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.47837
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.38012
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -1.0988
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -1.1009
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -1.0923
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.68851
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -1.75
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.28688
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.71965
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.66656
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.73687
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.73185
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.007175 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.2296
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.007175 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.21525
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.0289
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.0289
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -1.103
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -1.015
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 1.0493
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 1.0542
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.005895 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.80172
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.007871 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.25974
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.24734
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.24734
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.22378
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.22378
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.009619 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.68295
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.009619 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.09619
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.007987 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.3019
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.007987 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.3019
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.007987 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -1.9568
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.41418
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.38232
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.41418
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.41418
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.006062 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.90324
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.006062 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.39464
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.58841
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.56642
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.56254
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.3524
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.078885
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.005501 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -4.0872
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.005659 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -4.1594
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.005454 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.93809
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.005454 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.93809
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.005454 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.93809
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.79199
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.005863 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -1.0143
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.005863 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.79151
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.86968
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.8622
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.84884
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -1.4381
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.38726
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.38242
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.49981
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.44535
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -1.0042
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -0.96664
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -0.9691
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -0.96602
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -1.6552
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.005509 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.027545
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.005509 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.11569
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 0.2404
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.2432
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.2432
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 0.59242
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.005302 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -2.1102
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.28653
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.28653
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.28653
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.34259
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.34259
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.33637
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.008588 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 7.1023
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.008588 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 7.0336
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.008053 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.37124
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.93571
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.93571
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -1.2928
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.91109
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.91109
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -1.2558
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.006048 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -1.0886
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.006048 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -0.95921
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.006048 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -0.94954
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.006111 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.21388
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.006705 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -3.0776
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.35796
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.36346
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.38549
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.34694
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.34143
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.57273
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.32491
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.71417
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.70501
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.70501
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004578 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.74164
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.005471 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.85895
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.42529
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.43128
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.23361
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.1797
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.006199 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.48352
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.006199 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.49592
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.006052 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.098042
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.006064 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -1.0006
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.006068 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -1.0255
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.006053 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -1.2893
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.00605 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -1.3794
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.00607 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.07284
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.00607 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.10926
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.006902 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.3451
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.59394
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.59394
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.30839
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.30268
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.30839
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.32553
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.30839
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.30839
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.33124
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.33124
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.005567 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.066804
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.29305
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.30875
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.29305
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.29305
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.30875
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.29305
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.011803 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.779
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007793 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -1.2547
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007793 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -1.2936
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007793 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -1.9327
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007793 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -4.255
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007793 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -5.0109
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.007997 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -5.206
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.007997 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -4.5103
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.007997 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -4.7982
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007793 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.10131
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.005505 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.06606
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.19108
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.19501
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.18377
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.25796
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.099474
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.11465
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.11184
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.1967
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.10116
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.47995
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.83176
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.62341
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.71793
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.45248
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -1.0156
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.86473
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.88484
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.50275
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.18099
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.94517
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.70385
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.63346
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.72396
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.65156
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -1.0156
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.97533
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -1.0357
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.76418
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.8044
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.8044
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -1.7194
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.16181
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.027025 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 2.0674
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.02765 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 2.212
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.02765 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.106
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.027774 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.2219
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.027619 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 2.2095
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.02702 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 2.1616
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.026823 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 2.2531
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.027774 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.2219
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -2.9724
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.031232 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 3.7478
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.031232 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 7.2771
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.031232 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 5.3157
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -5.7884
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -4.7976
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -5.8406
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -2.9985
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -2.6074
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.029294 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 1.7576
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.024024 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.023642 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.028124 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.135
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 1.1022
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 3.1597
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 3.9681
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 3.4978
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 3.0863
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 2.3661
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.03101 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 4.6515
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 3.5226
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 4.6811
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 5.824
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 6.7164
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.019013 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.011432 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.019569 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.48756
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.75921
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -1.2886
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -1.7866
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.77925
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.72223
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.36111
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -1.7866
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.68422
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.81726
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.41813
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.70196
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.26998
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.12599
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.26998
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.70196
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.70196
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -2.8129
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.9503
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -1.0453
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.9503
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018656 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.22387
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.018189 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.27283
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.018189 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.41835
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.017551 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.84245
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.018071 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.14457
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.018839 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -3.391
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.018834 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -3.3901
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.018874 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -3.3973
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.018874 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -3.3973
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019571 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -1.9571
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019571 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -1.9571
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46818
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46818
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46818
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.29963
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46818
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46818
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46818
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.28091
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019571 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019571 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -9.7855
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019571 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -9.7855
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019571 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.019781 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.006303 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.019234 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.019241 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L: Evant - Adamsvill [7068 - 7066] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | [7 empty] | 18.5921
Number of Bus | Name of Bus | ID | Max MW | L: Evant - Adamsvill [7068 - 7066] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.011099 | north | Y | -0.0047133 | 0.034585 | -0.017921 | 0.01804 | 0.0047133 | North | N | 0.0047133 | 0
239 | BOSQUESW | 1 | 149 | 0.011099 | north | Y | -0.0047133 | 0.034585 | -0.017921 | 0.01804 | 0.0047133 | North | N | 0.0047133 | 0
244 | WHITNYDM | 1 | 15 | 0.013267 | north | N | -0.0025453 | 0.036753 | -0.015753 | 0.020208 | 0.0025453 | North | N | 0.0025453 | 0
245 | WHITNYDM | 2 | 15 | 0.013267 | north | N | -0.0025453 | 0.036753 | -0.015753 | 0.020208 | 0.0025453 | North | N | 0.0025453 | 0
247 | BOSQUESW | 2 | 153 | 0.011099 | north | Y | -0.0047133 | 0.034585 | -0.017921 | 0.01804 | 0.0047133 | North | N | 0.0047133 | 0
251 | BOSQUESW | 2 | 150 | 0.011495 | north | Y | -0.0043173 | 0.034981 | -0.017525 | 0.018436 | 0.0043173 | North | N | 0.0043173 | 0
253 | BOSQUESW | 2 | 80 | 0.011495 | north | Y | -0.0043173 | 0.034981 | -0.017525 | 0.018436 | 0.0043173 | North | N | 0.0043173 | 0
332 | RWMILLER | 1 | 73 | 0.027587 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 0.75492
333 | RWMILLER | 2 | 119 | 0.027587 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 1.2306
334 | RWMILLER | 3 | 205 | 0.027587 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 2.12
335 | RWMILLER | 4 | 102 | 0.027587 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 1.0548
336 | RWMILLER | 5 | 96 | 0.027587 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 0.99277
344 | MRSSHPRD | 1 | 12 | 0.0254 | north | N | 0.0095877 | 0.048886 | -0.0036203 | 0.032341 | 0.0036203 | west | Y | 0.0095877 | 0
345 | MRSSHPRD | 2 | 12 | 0.0254 | north | N | 0.0095877 | 0.048886 | -0.0036203 | 0.032341 | 0.0036203 | west | Y | 0.0095877 | 0
366 | JNSNCNTY | 1 | 168 | 0.021294 | north | Y | 0.0054817 | 0.04478 | -0.0077263 | 0.028235 | 0.0054817 | North | N | 0.0054817 | 0
367 | JNSNCNTY | 2 | 90 | 0.021294 | north | Y | 0.0054817 | 0.04478 | -0.0077263 | 0.028235 | 0.0054817 | North | N | 0.0054817 | 0
503 | NTHTEXAS | 1 | 18 | 0.024125 | north | Y | 0.0083127 | 0.047611 | -0.0048953 | 0.031066 | 0.0048953 | west | Y | 0.0083127 | 0.061513
504 | NTHTEXAS | 2 | 18 | 0.024125 | north | Y | 0.0083127 | 0.047611 | -0.0048953 | 0.031066 | 0.0048953 | west | Y | 0.0083127 | 0.061513
505 | NTHTEXAS | 3 | 38 | 0.024125 | north | Y | 0.0083127 | 0.047611 | -0.0048953 | 0.031066 | 0.0048953 | west | Y | 0.0083127 | 0.12986
580 | JCKCNTY8 | 1 | 288 | 0.022533 | north | Y | 0.0067207 | 0.046019 | -0.0064873 | 0.029474 | 0.0064873 | west | Y | 0.0067207 | 0.067213
581 | JCKCNTY8 | 2 | 147 | 0.022533 | north | Y | 0.0067207 | 0.046019 | -0.0064873 | 0.029474 | 0.0064873 | west | Y | 0.0067207 | 0.034307
582 | JCKCNTY8 | 3 | 147 | 0.022533 | north | Y | 0.0067207 | 0.046019 | -0.0064873 | 0.029474 | 0.0064873 | west | Y | 0.0067207 | 0.034307
728 | WOLFRIDG | 1 | 112.5 | 0.020961 | north | Y | 0.0051487 | 0.044447 | -0.0080593 | 0.027902 | 0.0051487 | North | N | 0.0051487 | 0
837 | NEWMAN_G | 1 | 40 | 0.017303 | north | Y | 0.0014907 | 0.040789 | -0.011717 | 0.024244 | 0.0014907 | North | N | 0.0014907 | 0
842 | OLINGER_ | 1 | 79 | 0.017346 | north | Y | 0.0015337 | 0.040832 | -0.011674 | 0.024287 | 0.0015337 | North | N | 0.0015337 | 0
843 | OLINGER_ | 1 | 106 | 0.017346 | north | Y | 0.0015337 | 0.040832 | -0.011674 | 0.024287 | 0.0015337 | North | N | 0.0015337 | 0
844 | OLINGER_ | 1 | 146 | 0.017346 | north | Y | 0.0015337 | 0.040832 | -0.011674 | 0.024287 | 0.0015337 | North | N | 0.0015337 | 0
845 | OLINGER_ | 1 | 76 | 0.017346 | north | Y | 0.0015337 | 0.040832 | -0.011674 | 0.024287 | 0.0015337 | North | N | 0.0015337 | 0
923 | SPENCER_ | 1 | 60 | 0.019674 | north | Y | 0.0038617 | 0.04316 | -0.0093463 | 0.026615 | 0.0038617 | North | N | 0.0038617 | 0
924 | SPENCER_ | 1 | 63 | 0.019674 | north | Y | 0.0038617 | 0.04316 | -0.0093463 | 0.026615 | 0.0038617 | North | N | 0.0038617 | 0
948 | STEAM1 | 1 | 20 | 0.01727 | north | Y | 0.0014577 | 0.040756 | -0.01175 | 0.024211 | 0.0014577 | North | N | 0.0014577 | 0
949 | STEAM2 | 1 | 25 | 0.01727 | north | Y | 0.0014577 | 0.040756 | -0.01175 | 0.024211 | 0.0014577 | North | N | 0.0014577 | 0
950 | STEAM3 | 1 | 41 | 0.01727 | north | Y | 0.0014577 | 0.040756 | -0.01175 | 0.024211 | 0.0014577 | North | N | 0.0014577 | 0
990 | GIBN_CRE | 1 | 463 | 0.002764 | north | Y | -0.013048 | 0.02625 | -0.026256 | 0.0097047 | 0.0097047 | houston | Y | 0.013048 | 1.5481
1002 | PBCTAGE_ | A | 66 | 0.029041 | west | Y | 0.013229 | 0.052527 | 2.0691e-05 | 0.035982 | 2.0691e-05 | west | N | 2.0691e-05 | 0
1003 | PBCTBGE_ | B | 65 | 0.029041 | west | Y | 0.013229 | 0.052527 | 2.0691e-05 | 0.035982 | 2.0691e-05 | west | N | 2.0691e-05 | 0
1004 | PBCTCGE_ | C | 67 | 0.029041 | west | Y | 0.013229 | 0.052527 | 2.0691e-05 | 0.035982 | 2.0691e-05 | west | N | 2.0691e-05 | 0
1005 | PBCTDGE_ | D | 67 | 0.029041 | west | Y | 0.013229 | 0.052527 | 2.0691e-05 | 0.035982 | 2.0691e-05 | west | N | 2.0691e-05 | 0
1006 | PBCTEGE_ | E | 67 | 0.029041 | west | Y | 0.013229 | 0.052527 | 2.0691e-05 | 0.035982 | 2.0691e-05 | west | N | 2.0691e-05 | 0
1007 | PB5GEN_6 | MB | 114 | 0.029041 | west | Y | 0.013229 | 0.052527 | 2.0691e-05 | 0.035982 | 2.0691e-05 | west | N | 2.0691e-05 | 0
1008 | PB6GEN_7 | MB | 515 | 0.029041 | west | Y | 0.013229 | 0.052527 | 2.0691e-05 | 0.035982 | 2.0691e-05 | west | N | 2.0691e-05 | 0
1039 | MRGNAG_1 | A | 66 | 0.029598 | west | Y | 0.013786 | 0.053084 | 0.00057769 | 0.036539 | 0.00057769 | west | N | 0.00057769 | 0
1040 | MRGNBG_2 | B | 69 | 0.029598 | west | Y | 0.013786 | 0.053084 | 0.00057769 | 0.036539 | 0.00057769 | west | N | 0.00057769 | 0
1041 | MRGNCG_3 | C | 69 | 0.029598 | west | Y | 0.013786 | 0.053084 | 0.00057769 | 0.036539 | 0.00057769 | west | N | 0.00057769 | 0
1042 | MRGNDG_4 | D | 67 | 0.029598 | west | Y | 0.013786 | 0.053084 | 0.00057769 | 0.036539 | 0.00057769 | west | N | 0.00057769 | 0
1043 | MRGNEG_5 | E | 67 | 0.029598 | west | Y | 0.013786 | 0.053084 | 0.00057769 | 0.036539 | 0.00057769 | west | N | 0.00057769 | 0
1044 | MRGNFG_6 | F | 65 | 0.029598 | west | Y | 0.013786 | 0.053084 | 0.00057769 | 0.036539 | 0.00057769 | west | N | 0.00057769 | 0
1045 | CALENG1G | 1 | 70 | 0.029398 | west | N | 0.013586 | 0.052884 | 0.00037769 | 0.036339 | 0.00037769 | west | N | 0.00037769 | 0
1046 | CALENG2G | 2 | 73.4 | 0.029398 | west | N | 0.013586 | 0.052884 | 0.00037769 | 0.036339 | 0.00037769 | west | N | 0.00037769 | 0
1047 | CALENG3G | 3 | 70.4 | 0.029398 | west | N | 0.013586 | 0.052884 | 0.00037769 | 0.036339 | 0.00037769 | west | N | 0.00037769 | 0
1058 | LONGSHOR | 1 | 150 | 0.029421 | west | Y | 0.013609 | 0.052907 | 0.00040069 | 0.036362 | 0.00040069 | west | N | 0.00040069 | 0
1058 | LONGSHOR | 2 | 220 | 0.029421 | west | Y | 0.013609 | 0.052907 | 0.00040069 | 0.036362 | 0.00040069 | west | N | 0.00040069 | 0
1061 | CIELOGEN | 1 | 99 | 0.029633 | west | Y | 0.013821 | 0.053119 | 0.00061269 | 0.036574 | 0.00061269 | west | N | 0.00061269 | 0
1062 | CIELOGEN | 1 | 61 | 0.029633 | west | Y | 0.013821 | 0.053119 | 0.00061269 | 0.036574 | 0.00061269 | west | N | 0.00061269 | 0
1068 | SCURRYCW | 1 | 141 | 0.029632 | west | Y | 0.01382 | 0.053118 | 0.00061169 | 0.036573 | 0.00061169 | west | N | 0.00061169 | 0
1069 | KINDERMG | 1 | 25 | 0.029633 | west | N | 0.013821 | 0.053119 | 0.00061269 | 0.036574 | 0.00061269 | west | N | 0.00061269 | 0
1070 | KINDERMG | 1 | 45.7 | 0.029633 | west | N | 0.013821 | 0.053119 | 0.00061269 | 0.036574 | 0.00061269 | west | N | 0.00061269 | 0
1071 | KINDERMG | 1 | 45.7 | 0.029633 | west | N | 0.013821 | 0.053119 | 0.00061269 | 0.036574 | 0.00061269 | west | N | 0.00061269 | 0
1073 | SCURRYCW | 2 | 120 | 0.029632 | west | Y | 0.01382 | 0.053118 | 0.00061169 | 0.036573 | 0.00061169 | west | N | 0.00061169 | 0
1320 | BSP 1 | 1 | 25.8 | 0.030053 | west | N | 0.014241 | 0.053539 | 0.0010327 | 0.036994 | 0.0010327 | west | N | 0.0010327 | 0
1326 | STANTONW | 1 | 100.5 | 0.029459 | west | Y | 0.013647 | 0.052945 | 0.00043869 | 0.0364 | 0.00043869 | west | N | 0.00043869 | 0
1327 | WILDHRSE | 1 | 120 | 0.02971 | west | Y | 0.013898 | 0.053196 | 0.00068969 | 0.036651 | 0.00068969 | west | N | 0.00068969 | 0
1328 | OCOTILLO | 1 | 58 | 0.029391 | west | Y | 0.013579 | 0.052877 | 0.00037069 | 0.036332 | 0.00037069 | west | N | 0.00037069 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.02942 | west | Y | 0.013608 | 0.052906 | 0.00039969 | 0.036361 | 0.00039969 | west | N | 0.00039969 | 0
1343 | TRENTIPP | 1 | 150 | 0.030837 | west | Y | 0.015025 | 0.054323 | 0.0018167 | 0.037778 | 0.0018167 | west | N | 0.0018167 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.031059 | west | Y | 0.015247 | 0.054545 | 0.0020387 | 0.038 | 0.0020387 | west | N | 0.0020387 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.031059 | west | Y | 0.015247 | 0.054545 | 0.0020387 | 0.038 | 0.0020387 | west | N | 0.0020387 | 0
1354 | AEPWIND_ | 1 | 101 | 0.030837 | west | Y | 0.015025 | 0.054323 | 0.0018167 | 0.037778 | 0.0018167 | west | N | 0.0018167 | 0
1360 | GUNSIGHT | 1 | 120 | 0.029717 | west | Y | 0.013905 | 0.053203 | 0.00069669 | 0.036658 | 0.00069669 | west | N | 0.00069669 | 0
1432 | GRHAMSES | 2 | 366 | 0.02476 | north | Y | 0.0089477 | 0.048246 | -0.0042603 | 0.031701 | 0.0042603 | west | Y | 0.0089477 | 1.7156
1433 | GRHAMSES | 1 | 242 | 0.026138 | north | Y | 0.010326 | 0.049624 | -0.0028823 | 0.033079 | 0.0028823 | west | Y | 0.010326 | 1.8013
1437 | MESQUITW | 1 | 400 | 0.027629 | west | Y | 0.011817 | 0.051115 | -0.0013913 | 0.03457 | 0.0013913 | west | N | 0.0013913 | 0
1438 | MESQUITW | 1 | 236 | 0.027623 | west | Y | 0.011811 | 0.051109 | -0.0013973 | 0.034564 | 0.0013973 | west | N | 0.0013973 | 0
1442 | COKFIELD | 1 | 165 | 0.026936 | west | Y | 0.011124 | 0.050422 | -0.0020843 | 0.033877 | 0.0020843 | west | N | 0.0020843 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.022935 | north | Y | 0.0071227 | 0.046421 | -0.0060853 | 0.029876 | 0.0060853 | west | Y | 0.0071227 | 0.21163
1454 | WCPWRCO_ | 2 | 201 | 0.022935 | north | Y | 0.0071227 | 0.046421 | -0.0060853 | 0.029876 | 0.0060853 | west | Y | 0.0071227 | 0.20851
1455 | WCPWRCO_ | 3 | 242 | 0.022935 | north | Y | 0.0071227 | 0.046421 | -0.0060853 | 0.029876 | 0.0060853 | west | Y | 0.0071227 | 0.25105
1479 | WFCOGEN_ | 1 | 20 | 0.02484 | west | Y | 0.0090277 | 0.048326 | -0.0041803 | 0.031781 | 0.0041803 | west | N | 0.0041803 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.02484 | west | Y | 0.0090277 | 0.048326 | -0.0041803 | 0.031781 | 0.0041803 | west | N | 0.0041803 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.02484 | west | Y | 0.0090277 | 0.048326 | -0.0041803 | 0.031781 | 0.0041803 | west | N | 0.0041803 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.02484 | west | Y | 0.0090277 | 0.048326 | -0.0041803 | 0.031781 | 0.0041803 | west | N | 0.0041803 | 0
1600 | BARTNWND | 1 | 120 | 0.025634 | north | Y | 0.0098217 | 0.04912 | -0.0033863 | 0.032575 | 0.0033863 | west | Y | 0.0098217 | 0.77225
1643 | SLSTR1PP | 1 | 60 | 0.03488 | north | Y | 0.019068 | 0.058366 | 0.0058597 | 0.041821 | 0.0058597 | west | Y | 0.019068 | 0.79248
1675 | PEC_1G | 1 | 75 | 0.017581 | north | N | 0.0017687 | 0.041067 | -0.011439 | 0.024522 | 0.0017687 | North | N | 0.0017687 | 0
1676 | PEC_2G | 2 | 79.6 | 0.017581 | north | N | 0.0017687 | 0.041067 | -0.011439 | 0.024522 | 0.0017687 | North | N | 0.0017687 | 0
1677 | PEC_3G | 3 | 88.4 | 0.017581 | north | N | 0.0017687 | 0.041067 | -0.011439 | 0.024522 | 0.0017687 | North | N | 0.0017687 | 0
1678 | LAMARPWR | 1 | 160 | 0.017616 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1679 | LAMARPWR | 2 | 156 | 0.017616 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1680 | LAMARPWR | 3 | 196 | 0.017616 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1681 | LAMARPWR | 4 | 156 | 0.017616 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1682 | LAMARPWR | 5 | 157 | 0.017616 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1683 | LAMARPWR | 6 | 198 | 0.017616 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1687 | VALLEY_1 | 1 | 170 | 0.017833 | north | Y | 0.0020207 | 0.041319 | -0.011187 | 0.024774 | 0.0020207 | North | N | 0.0020207 | 0
1688 | VALLEY_2 | 2 | 520 | 0.017833 | north | Y | 0.0020207 | 0.041319 | -0.011187 | 0.024774 | 0.0020207 | North | N | 0.0020207 | 0
1689 | VALLEY_3 | 3 | 370 | 0.017673 | north | Y | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
1701 | MOSES_1G | 1 | 558 | 0.017512 | north | Y | 0.0016997 | 0.040998 | -0.011508 | 0.024453 | 0.0016997 | North | N | 0.0016997 | 0
1702 | MOSES_2G | 2 | 579 | 0.017512 | north | Y | 0.0016997 | 0.040998 | -0.011508 | 0.024453 | 0.0016997 | North | N | 0.0016997 | 0
1703 | MOSES_3G | 3 | 808 | 0.017512 | north | Y | 0.0016997 | 0.040998 | -0.011508 | 0.024453 | 0.0016997 | North | N | 0.0016997 | 0
1861 | EAGLEMNT | MB | 112 | 0.020739 | north | Y | 0.0049267 | 0.044225 | -0.0082813 | 0.02768 | 0.0049267 | North | N | 0.0049267 | 0
1862 | EAGLEMNT | MB | 100 | 0.020739 | north | Y | 0.0049267 | 0.044225 | -0.0082813 | 0.02768 | 0.0049267 | North | N | 0.0049267 | 0
1863 | EAGLEMNT | MB | 378 | 0.020739 | north | Y | 0.0049267 | 0.044225 | -0.0082813 | 0.02768 | 0.0049267 | North | N | 0.0049267 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.023975 | north | Y | 0.0081627 | 0.047461 | -0.0050453 | 0.030916 | 0.0050453 | west | Y | 0.0081627 | 0.67741
1878 | WLFHOLW_ | 2 | 205 | 0.023975 | north | Y | 0.0081627 | 0.047461 | -0.0050453 | 0.030916 | 0.0050453 | west | Y | 0.0081627 | 0.63906
1879 | WLFHOLW_ | 3 | 272.4 | 0.023975 | north | Y | 0.0081627 | 0.047461 | -0.0050453 | 0.030916 | 0.0050453 | west | Y | 0.0081627 | 0.84917
1889 | DECRDOVA | MB | 770 | 0.02291 | north | Y | 0.0070977 | 0.046396 | -0.0061103 | 0.029851 | 0.0061103 | west | Y | 0.0070977 | 0
1892 | DECRDOVA | A | 70 | 0.023821 | north | Y | 0.0080087 | 0.047307 | -0.0051993 | 0.030762 | 0.0051993 | west | Y | 0.0080087 | 0.19666
1893 | DECRDOVA | B | 69 | 0.023821 | north | Y | 0.0080087 | 0.047307 | -0.0051993 | 0.030762 | 0.0051993 | west | Y | 0.0080087 | 0.19385
1894 | DECRDOVA | C | 69 | 0.023821 | north | Y | 0.0080087 | 0.047307 | -0.0051993 | 0.030762 | 0.0051993 | west | Y | 0.0080087 | 0.19385
1895 | DECRDOVA | D | 68 | 0.023821 | north | Y | 0.0080087 | 0.047307 | -0.0051993 | 0.030762 | 0.0051993 | west | Y | 0.0080087 | 0.19104
1898 | COMCHEPK | 1 | 1157 | 0.024697 | north | N | 0.0088847 | 0.048183 | -0.0043233 | 0.031638 | 0.0043233 | west | Y | 0.0088847 | 0
1899 | COMCHEPK | 2 | 1158 | 0.024697 | north | N | 0.0088847 | 0.048183 | -0.0043233 | 0.031638 | 0.0043233 | west | Y | 0.0088847 | 0
1937 | MDLTHELP | 5 | 224 | 0.01836 | north | Y | 0.0025477 | 0.041846 | -0.01066 | 0.025301 | 0.0025477 | North | N | 0.0025477 | 0
1938 | MDLTHELP | 6 | 226 | 0.01836 | north | Y | 0.0025477 | 0.041846 | -0.01066 | 0.025301 | 0.0025477 | North | N | 0.0025477 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.01714 | north | Y | 0.0013277 | 0.040626 | -0.01188 | 0.024081 | 0.0013277 | North | N | 0.0013277 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.01714 | north | Y | 0.0013277 | 0.040626 | -0.01188 | 0.024081 | 0.0013277 | North | N | 0.0013277 | 0
1943 | MDLTHELP | 3 | 212 | 0.01836 | north | Y | 0.0025477 | 0.041846 | -0.01066 | 0.025301 | 0.0025477 | North | N | 0.0025477 | 0
1944 | MDLTHELP | 4 | 211 | 0.01836 | north | Y | 0.0025477 | 0.041846 | -0.01066 | 0.025301 | 0.0025477 | North | N | 0.0025477 | 0
1947 | HANDLEY_ | 3 | 395 | 0.019533 | north | Y | 0.0037207 | 0.043019 | -0.0094873 | 0.026474 | 0.0037207 | North | N | 0.0037207 | 0
1948 | HANDLEY_ | 4 | 435 | 0.019357 | north | Y | 0.0035447 | 0.042843 | -0.0096633 | 0.026298 | 0.0035447 | North | N | 0.0035447 | 0
1949 | HANDLEY_ | 5 | 435 | 0.019533 | north | Y | 0.0037207 | 0.043019 | -0.0094873 | 0.026474 | 0.0037207 | North | N | 0.0037207 | 0
2371 | COLLIN_1 | MB | 138 | 0.018216 | north | Y | 0.0024037 | 0.041702 | -0.010804 | 0.025157 | 0.0024037 | North | N | 0.0024037 | 0
2413 | MTCK6_G | 6 | 118 | 0.017473 | north | Y | 0.0016607 | 0.040959 | -0.011547 | 0.024414 | 0.0016607 | North | N | 0.0016607 | 0
2414 | MTCK7_G | 7 | 115 | 0.017473 | north | Y | 0.0016607 | 0.040959 | -0.011547 | 0.024414 | 0.0016607 | North | N | 0.0016607 | 0
2417 | MTCK8_G | 8 | 556 | 0.017473 | north | Y | 0.0016607 | 0.040959 | -0.011547 | 0.024414 | 0.0016607 | North | N | 0.0016607 | 0
2451 | LKHB1_G | 1 | 388 | 0.017128 | north | Y | 0.0013157 | 0.040614 | -0.011892 | 0.024069 | 0.0013157 | North | N | 0.0013157 | 0
2452 | LKHB2_G | 2 | 515 | 0.017128 | north | Y | 0.0013157 | 0.040614 | -0.011892 | 0.024069 | 0.0013157 | North | N | 0.0013157 | 0
3097 | MARTLAKE | 1 | 785 | 0.015365 | north | Y | -0.00044731 | 0.038851 | -0.013655 | 0.022306 | 0.00044731 | North | N | 0.00044731 | 0
3098 | MARTLAKE | 2 | 795 | 0.015365 | north | Y | -0.00044731 | 0.038851 | -0.013655 | 0.022306 | 0.00044731 | North | N | 0.00044731 | 0
3099 | MARTLAKE | 3 | 780 | 0.015365 | north | Y | -0.00044731 | 0.038851 | -0.013655 | 0.022306 | 0.00044731 | North | N | 0.00044731 | 0
3107 | STRYKER_ | 1 | 182 | 0.014842 | north | Y | -0.00097031 | 0.038328 | -0.014178 | 0.021783 | 0.00097031 | North | N | 0.00097031 | 0
3108 | STRYKER_ | 2 | 484 | 0.014842 | north | Y | -0.00097031 | 0.038328 | -0.014178 | 0.021783 | 0.00097031 | North | N | 0.00097031 | 0
3126 | TRINIDAD | 1 | 224 | 0.014965 | north | Y | -0.00084731 | 0.038451 | -0.014055 | 0.021906 | 0.00084731 | North | N | 0.00084731 | 0
3309 | ASPN_G | 1 | 50 | 0.014946 | north | Y | -0.00086631 | 0.038432 | -0.014074 | 0.021887 | 0.00086631 | North | N | 0.00086631 | 0
3348 | CHAMPION | MB | 42 | 0.014963 | north | N | -0.00084931 | 0.038449 | -0.014057 | 0.021904 | 0.00084931 | North | N | 0.00084931 | 0
3381 | BBRN_1G | 1 | 615 | 0.01257 | north | Y | -0.0032423 | 0.036056 | -0.01645 | 0.019511 | 0.0032423 | North | N | 0.0032423 | 0
3382 | BBRN_2G | 2 | 587 | 0.01257 | north | Y | -0.0032423 | 0.036056 | -0.01645 | 0.019511 | 0.0032423 | North | N | 0.0032423 | 0
3403 | THOUSE_1 | MB | 537 | 0.011162 | north | Y | -0.0046503 | 0.034648 | -0.017858 | 0.018103 | 0.0046503 | North | N | 0.0046503 | 0
3404 | THOUSE_2 | 2 | 787 | 0.011162 | north | Y | -0.0046503 | 0.034648 | -0.017858 | 0.018103 | 0.0046503 | North | N | 0.0046503 | 0
3416 | LAKE_CRK | MB | 75 | 0.006143 | north | Y | -0.0096693 | 0.029629 | -0.022877 | 0.013084 | 0.0096693 | North | N | 0.0096693 | 0
3417 | LAKE_CRK | MB | 222 | 0.006143 | north | Y | -0.0096693 | 0.029629 | -0.022877 | 0.013084 | 0.0096693 | North | N | 0.0096693 | 0
3432 | SANDOW_4 | 4 | 569 | -0.023936 | south | Y | -0.039748 | -0.00045001 | -0.052956 | -0.016995 | 0.00045001 | south | N | 0.00045001 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.022893 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.022893 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.022953 | south | Y | -0.038765 | 0.00053299 | -0.051973 | -0.016012 | 0.00053299 | south | N | 0.00053299 | 0
5031 | BRA_VHBC | 1 | 46 | -0.022893 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5032 | BRA_VHBC | 2 | 47 | -0.022893 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5033 | BRA_VHBC | 3 | 46 | -0.022893 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5034 | BRA_VHBC | 4 | 46 | -0.022893 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5111 | CALAVER_ | 1 | 424 | -0.02297 | south | Y | -0.038782 | 0.00051599 | -0.05199 | -0.016029 | 0.00051599 | south | N | 0.00051599 | 0
5112 | CALAVER_ | 2 | 425 | -0.02297 | south | Y | -0.038782 | 0.00051599 | -0.05199 | -0.016029 | 0.00051599 | south | N | 0.00051599 | 0
5264 | LEON_LCP | 3 | 58 | -0.022843 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5265 | LEON_LCP | 4 | 89 | -0.022843 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5266 | LEON_LCP | 1 | 44 | -0.022843 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5267 | LEON_LCP | 2 | 44 | -0.022843 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5268 | LEON_LCP | 3 | 43 | -0.022843 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5269 | LEON_LCP | 4 | 45 | -0.022843 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5396 | CALAVER_ | 1 | 412 | -0.022934 | south | Y | -0.038746 | 0.00055199 | -0.051954 | -0.015993 | 0.00055199 | south | N | 0.00055199 | 0
5397 | CALAVER_ | 2 | 400 | -0.022934 | south | Y | -0.038746 | 0.00055199 | -0.051954 | -0.015993 | 0.00055199 | south | N | 0.00055199 | 0
5401 | CALAVER_ | 1 | 546 | -0.022662 | south | Y | -0.038474 | 0.00082399 | -0.051682 | -0.015721 | 0.00082399 | south | N | 0.00082399 | 0
5402 | CALAVER_ | 2 | 750 | -0.022662 | south | Y | -0.038474 | 0.00082399 | -0.051682 | -0.015721 | 0.00082399 | south | N | 0.00082399 | 0
5436 | TUTTL_WB | MB | 61 | -0.022942 | south | Y | -0.038754 | 0.00054399 | -0.051962 | -0.016001 | 0.00054399 | south | N | 0.00054399 | 0
5438 | TUTTL_WB | MB | 95 | -0.022942 | south | Y | -0.038754 | 0.00054399 | -0.051962 | -0.016001 | 0.00054399 | south | N | 0.00054399 | 0
5439 | TUTTL_WB | MB | 151 | -0.022942 | south | Y | -0.038754 | 0.00054399 | -0.051962 | -0.016001 | 0.00054399 | south | N | 0.00054399 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.022902 | south | Y | -0.038714 | 0.00058399 | -0.051922 | -0.015961 | 0.00058399 | south | N | 0.00058399 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.022902 | south | Y | -0.038714 | 0.00058399 | -0.051922 | -0.015961 | 0.00058399 | south | N | 0.00058399 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.022902 | south | Y | -0.038714 | 0.00058399 | -0.051922 | -0.015961 | 0.00058399 | south | N | 0.00058399 | 0
5503 | RAYBURNG | 1 | 22 | -0.018323 | south | Y | -0.034135 | 0.005163 | -0.047343 | -0.011382 | 0.005163 | south | N | 0.005163 | 0
5505 | RAYBURNG | 1 | 11 | -0.018323 | south | Y | -0.034135 | 0.005163 | -0.047343 | -0.011382 | 0.005163 | south | N | 0.005163 | 0
5506 | RAYBURNG | 1 | 11 | -0.018323 | south | Y | -0.034135 | 0.005163 | -0.047343 | -0.011382 | 0.005163 | south | N | 0.005163 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.018486 | south | Y | -0.034298 | 0.005 | -0.047506 | -0.011545 | 0.005 | south | N | 0.005 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.018486 | south | Y | -0.034298 | 0.005 | -0.047506 | -0.011545 | 0.005 | south | N | 0.005 | 0
5511 | RAYBURNC | 1 | 46 | -0.018486 | south | Y | -0.034298 | 0.005 | -0.047506 | -0.011545 | 0.005 | south | N | 0.005 | 0
5512 | RAYBURNC | 1 | 48 | -0.018486 | south | Y | -0.034298 | 0.005 | -0.047506 | -0.011545 | 0.005 | south | N | 0.005 | 0
5728 | FALCONHY | 2 | 12 | -0.019144 | south | N | -0.034956 | 0.004342 | -0.048164 | -0.012203 | 0.004342 | south | N | 0.004342 | 0
5729 | FALCONHY | 3 | 11 | -0.019144 | south | N | -0.034956 | 0.004342 | -0.048164 | -0.012203 | 0.004342 | south | N | 0.004342 | 0
5890 | PEARSALL | 1 | 24 | -0.01961 | south | Y | -0.035422 | 0.003876 | -0.04863 | -0.012669 | 0.003876 | south | N | 0.003876 | 0
5891 | PEARSALL | 1 | 24 | -0.01961 | south | Y | -0.035422 | 0.003876 | -0.04863 | -0.012669 | 0.003876 | south | N | 0.003876 | 0
5892 | PEARSALL | 1 | 23 | -0.01961 | south | Y | -0.035422 | 0.003876 | -0.04863 | -0.012669 | 0.003876 | south | N | 0.003876 | 0
5903 | SANMIGUE | 1 | 396 | -0.021178 | south | Y | -0.03699 | 0.002308 | -0.050198 | -0.014237 | 0.002308 | south | N | 0.002308 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.012467 | houston | N | -0.028279 | 0.011019 | -0.041487 | -0.0055263 | 0.0055263 | houston | N | 0.0055263 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.012467 | houston | N | -0.028279 | 0.011019 | -0.041487 | -0.0055263 | 0.0055263 | houston | N | 0.0055263 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.015812 | 0
5932 | SI_RAY9 | 9 | 38 | -0.019013 | south | Y | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.019013 | south | Y | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
5934 | SI_RAY5 | 5 | 15 | -0.019013 | south | Y | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
5935 | SI_RAY10 | 10 | 47 | -0.019013 | south | Y | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
6016 | SWMESA | 1 | 75 | 0.02765 | west | Y | 0.011838 | 0.051136 | -0.0013703 | 0.034591 | 0.0013703 | west | N | 0.0013703 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.02902 | 0
6144 | MCADOO1A | 1 | 150 | 0.02967 | west | Y | 0.013858 | 0.053156 | 0.00064969 | 0.036611 | 0.00064969 | west | N | 0.00064969 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.031834 | west | Y | 0.016022 | 0.05532 | 0.0028137 | 0.038775 | 0.0028137 | west | N | 0.0028137 | 0
6476 | LANGFORD | 1 | 150 | 0.02002 | west | Y | 0.0042077 | 0.043506 | -0.0090003 | 0.026961 | 0.0042077 | North | Y | 0.0090003 | 0.71889
6637 | SNYDERW1 | 1 | 63 | 0.029669 | west | Y | 0.013857 | 0.053155 | 0.00064869 | 0.03661 | 0.00064869 | west | N | 0.00064869 | 0
6752 | OKLA0A | 1 | 649.7 | 0.026547 | west | Y | 0.010735 | 0.050033 | -0.0024733 | 0.033488 | 0.0024733 | west | N | 0.0024733 | 0
6948 | DENISNDM | 1 | 40 | 0.017956 | north | N | 0.0021437 | 0.041442 | -0.011064 | 0.024897 | 0.0021437 | North | N | 0.0021437 | 0
6948 | DENISNDM | 2 | 40 | 0.017956 | north | N | 0.0021437 | 0.041442 | -0.011064 | 0.024897 | 0.0021437 | North | N | 0.0021437 | 0
7000 | L_FERGUS | 1 | 422 | -0.064639 | south | Y | -0.080451 | -0.041153 | -0.093659 | -0.057698 | 0.041153 | south | N | 0.041153 | 0
7004 | L_SIMGID | 1 | 132 | -0.026207 | south | Y | -0.042019 | -0.002721 | -0.055227 | -0.019266 | 0.002721 | south | N | 0.002721 | 0
7005 | L_SIMGID | 2 | 134 | -0.026207 | south | Y | -0.042019 | -0.002721 | -0.055227 | -0.019266 | 0.002721 | south | N | 0.002721 | 0
7006 | L_SIMGID | 3 | 323 | -0.026207 | south | Y | -0.042019 | -0.002721 | -0.055227 | -0.019266 | 0.002721 | south | N | 0.002721 | 0
7007 | L_LOSTPI | 1 | 158 | -0.024201 | south | Y | -0.040013 | -0.00071501 | -0.053221 | -0.01726 | 0.00071501 | south | N | 0.00071501 | 0
7008 | L_LOSTPI | 2 | 160 | -0.024201 | south | Y | -0.040013 | -0.00071501 | -0.053221 | -0.01726 | 0.00071501 | south | N | 0.00071501 | 0
7009 | L_LOSTPI | 3 | 175 | -0.024201 | south | Y | -0.040013 | -0.00071501 | -0.053221 | -0.01726 | 0.00071501 | south | N | 0.00071501 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.022626 | south | Y | -0.038438 | 0.00085999 | -0.051646 | -0.015685 | 0.00085999 | south | N | 0.00085999 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.022626 | south | Y | -0.038438 | 0.00085999 | -0.051646 | -0.015685 | 0.00085999 | south | N | 0.00085999 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.022615 | south | Y | -0.038427 | 0.00087099 | -0.051635 | -0.015674 | 0.00087099 | south | N | 0.00087099 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.024103 | south | Y | -0.039915 | -0.00061701 | -0.053123 | -0.017162 | 0.00061701 | south | N | 0.00061701 | 0
7015 | L_HAYSEN | 2 | 225 | -0.024103 | south | Y | -0.039915 | -0.00061701 | -0.053123 | -0.017162 | 0.00061701 | south | N | 0.00061701 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.024103 | south | Y | -0.039915 | -0.00061701 | -0.053123 | -0.017162 | 0.00061701 | south | N | 0.00061701 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.024103 | south | Y | -0.039915 | -0.00061701 | -0.053123 | -0.017162 | 0.00061701 | south | N | 0.00061701 | 0
7020 | L_AUSTPL | 1 | 8 | -0.030228 | south | N | -0.04604 | -0.006742 | -0.059248 | -0.023287 | 0.006742 | south | N | 0.006742 | 0
7020 | L_AUSTPL | 2 | 8 | -0.030228 | south | N | -0.04604 | -0.006742 | -0.059248 | -0.023287 | 0.006742 | south | N | 0.006742 | 0
7022 | L_BUCHAN | 1 | 18 | -0.09006 | south | N | -0.10587 | -0.066574 | -0.11908 | -0.083119 | 0.066574 | south | N | 0.066574 | 0
7023 | L_BUCHAN | 2 | 18 | -0.09006 | south | N | -0.10587 | -0.066574 | -0.11908 | -0.083119 | 0.066574 | south | N | 0.066574 | 0
7024 | L_BUCHAN | 3 | 15 | -0.09006 | south | N | -0.10587 | -0.066574 | -0.11908 | -0.083119 | 0.066574 | south | N | 0.066574 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.077284 | south | N | -0.093096 | -0.053798 | -0.1063 | -0.070343 | 0.053798 | south | N | 0.053798 | 0
7028 | L_MARBFA | 1 | 18 | -0.056999 | south | N | -0.072811 | -0.033513 | -0.086019 | -0.050058 | 0.033513 | south | N | 0.033513 | 0
7029 | L_MARBFA | 2 | 18 | -0.056999 | south | N | -0.072811 | -0.033513 | -0.086019 | -0.050058 | 0.033513 | south | N | 0.033513 | 0
7031 | L_MARSFO | 1 | 35 | -0.039674 | south | N | -0.055486 | -0.016188 | -0.068694 | -0.032733 | 0.016188 | south | N | 0.016188 | 0
7032 | L_MARSFO | 2 | 34 | -0.039674 | south | N | -0.055486 | -0.016188 | -0.068694 | -0.032733 | 0.016188 | south | N | 0.016188 | 0
7033 | L_MARSFO | 3 | 35 | -0.039674 | south | N | -0.055486 | -0.016188 | -0.068694 | -0.032733 | 0.016188 | south | N | 0.016188 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.065572 | south | N | -0.081384 | -0.042086 | -0.094592 | -0.058631 | 0.042086 | south | N | 0.042086 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.065572 | south | N | -0.081384 | -0.042086 | -0.094592 | -0.058631 | 0.042086 | south | N | 0.042086 | 0
7038 | L_DELAWA | 1 | 35 | 0.029061 | west | Y | 0.013249 | 0.052547 | 4.0691e-05 | 0.036002 | 4.0691e-05 | west | N | 4.0691e-05 | 0
7038 | L_DELAWA | 2 | 30 | 0.029061 | west | Y | 0.013249 | 0.052547 | 4.0691e-05 | 0.036002 | 4.0691e-05 | west | N | 4.0691e-05 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.023675 | south | Y | -0.039487 | -0.00018901 | -0.052695 | -0.016734 | 0.00018901 | south | N | 0.00018901 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.023675 | south | Y | -0.039487 | -0.00018901 | -0.052695 | -0.016734 | 0.00018901 | south | N | 0.00018901 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.023675 | south | Y | -0.039487 | -0.00018901 | -0.052695 | -0.016734 | 0.00018901 | south | N | 0.00018901 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.023675 | south | Y | -0.039487 | -0.00018901 | -0.052695 | -0.016734 | 0.00018901 | south | N | 0.00018901 | 0
7487 | L_CANYHY | 1 | 6 | -0.026853 | south | N | -0.042665 | -0.003367 | -0.055873 | -0.019912 | 0.003367 | south | N | 0.003367 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.024006 | south | N | -0.039818 | -0.00052001 | -0.053026 | -0.017065 | 0.00052001 | south | N | 0.00052001 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.024006 | south | N | -0.039818 | -0.00052001 | -0.053026 | -0.017065 | 0.00052001 | south | N | 0.00052001 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.024006 | south | N | -0.039818 | -0.00052001 | -0.053026 | -0.017065 | 0.00052001 | south | N | 0.00052001 | 0
7609 | L_SCHUMA | 1 | 4 | -0.023804 | south | N | -0.039616 | -0.00031801 | -0.052824 | -0.016863 | 0.00031801 | south | N | 0.00031801 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.023418 | south | N | -0.03923 | 6.7991e-05 | -0.052438 | -0.016477 | 6.7991e-05 | south | N | 6.7991e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.023418 | south | N | -0.03923 | 6.7991e-05 | -0.052438 | -0.016477 | 6.7991e-05 | south | N | 6.7991e-05 | 0
7800 | L_GUADGE | 1 | 147 | -0.022941 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7801 | L_GUADGE | 2 | 138 | -0.022941 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7802 | L_GUADGE | 3 | 140 | -0.022941 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7803 | L_GUADGE | 4 | 147 | -0.022941 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7804 | L_GUADGE | 5 | 182 | -0.022941 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7805 | L_GUADGE | 6 | 198 | -0.022941 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.025181 | south | Y | -0.040993 | -0.001695 | -0.054201 | -0.01824 | 0.001695 | south | N | 0.001695 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.025181 | south | Y | -0.040993 | -0.001695 | -0.054201 | -0.01824 | 0.001695 | south | N | 0.001695 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.025181 | south | Y | -0.040993 | -0.001695 | -0.054201 | -0.01824 | 0.001695 | south | N | 0.001695 | 0
7810 | L_RIONOG | 1 | 142 | -0.023509 | south | Y | -0.039321 | -2.3009e-05 | -0.052529 | -0.016568 | 2.3009e-05 | south | N | 2.3009e-05 | 0
7811 | L_RIONOG | 2 | 145 | -0.023509 | south | Y | -0.039321 | -2.3009e-05 | -0.052529 | -0.016568 | 2.3009e-05 | south | N | 2.3009e-05 | 0
7812 | L_RIONOG | 3 | 151 | -0.023509 | south | Y | -0.039321 | -2.3009e-05 | -0.052529 | -0.016568 | 2.3009e-05 | south | N | 2.3009e-05 | 0
7813 | L_RIONOG | 4 | 290 | -0.023509 | south | Y | -0.039321 | -2.3009e-05 | -0.052529 | -0.016568 | 2.3009e-05 | south | N | 2.3009e-05 | 0
8032 | AMISTADH | 1 | 33 | -0.006303 | south | N | -0.022115 | 0.017183 | -0.035323 | 0.00063768 | 0.00063768 | houston | Y | 0.017183 | 0
8033 | AMISTADH | 2 | 25 | -0.006303 | south | N | -0.022115 | 0.017183 | -0.035323 | 0.00063768 | 0.00063768 | houston | Y | 0.017183 | 0
8048 | FALCONHY | 1 | 12 | -0.019144 | south | N | -0.034956 | 0.004342 | -0.048164 | -0.012203 | 0.004342 | south | N | 0.004342 | 0
8066 | DUP1V#1 | 1 | 73 | -0.018514 | south | N | -0.034326 | 0.004972 | -0.047534 | -0.011573 | 0.004972 | south | N | 0.004972 | 0
8134 | FOR69CG0 | 1 | 79 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8138 | FOR69CG0 | 2 | 81 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.023486 | 0
8147 | UCAR #2 | 10 | 28 | -0.017999 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
8148 | UCAR #1 | 2 | 7 | -0.017999 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
8153 | FOR69CG0 | 3 | 79 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8154 | FOR69CG0 | 4 | 80 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8156 | FOR69CG0 | 6 | 25 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8157 | FOR69CG0 | 7 | 46 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8161 | COLETOU1 | 1 | 629 | -0.019587 | south | Y | -0.035399 | 0.003899 | -0.048607 | -0.012646 | 0.003899 | south | N | 0.003899 | 0
8173 | VICEC51A | 5 | 144 | -0.018702 | south | Y | -0.034514 | 0.004784 | -0.047722 | -0.011761 | 0.004784 | south | N | 0.004784 | 0
8174 | VICEC61A | 6 | 188 | -0.018702 | south | Y | -0.034514 | 0.004784 | -0.047722 | -0.011761 | 0.004784 | south | N | 0.004784 | 0
8189 | CUERO 2 | 1 | 12 | -0.021991 | south | N | -0.037803 | 0.001495 | -0.051011 | -0.01505 | 0.001495 | south | N | 0.001495 | 0
8262 | ELPS | 1 | 6 | -0.010464 | south | N | -0.026276 | 0.013022 | -0.039484 | -0.0035233 | 0.0035233 | houston | Y | 0.013022 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.023486 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.023486 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.023486 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.023486 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.023486 | 0
8442 | NBEC71A | 1 | 336 | -0.018834 | south | Y | -0.034646 | 0.004652 | -0.047854 | -0.011893 | 0.004652 | south | N | 0.004652 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.023486 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.015812 | 0.023486 | -0.02902 | 0.0069407 | 0.0069407 | houston | Y | 0.023486 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.018874 | south | Y | -0.034686 | 0.004612 | -0.047894 | -0.011933 | 0.004612 | south | N | 0.004612 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.018874 | south | Y | -0.034686 | 0.004612 | -0.047894 | -0.011933 | 0.004612 | south | N | 0.004612 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.018895 | south | N | -0.034707 | 0.004591 | -0.047915 | -0.011954 | 0.004591 | south | N | 0.004591 | 0
8506 | VAL #1 | 1 | 25 | -0.018877 | south | N | -0.034689 | 0.004609 | -0.047897 | -0.011936 | 0.004609 | south | N | 0.004609 | 0
8507 | VAL #2 | 2 | 25 | -0.018877 | south | N | -0.034689 | 0.004609 | -0.047897 | -0.011936 | 0.004609 | south | N | 0.004609 | 0
8511 | OXY_CC0A | 1 | 38 | -0.018897 | south | N | -0.034709 | 0.004589 | -0.047917 | -0.011956 | 0.004589 | south | N | 0.004589 | 0
8517 | CELANEBI | 1 | 29 | -0.01898 | south | N | -0.034792 | 0.004506 | -0.048 | -0.012039 | 0.004506 | south | N | 0.004506 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.018836 | south | N | -0.034648 | 0.00465 | -0.047856 | -0.011895 | 0.00465 | south | N | 0.00465 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.018836 | south | N | -0.034648 | 0.00465 | -0.047856 | -0.011895 | 0.00465 | south | N | 0.00465 | 0
8562 | CNOPST1 | 3 | 153 | -0.018836 | south | N | -0.034648 | 0.00465 | -0.047856 | -0.011895 | 0.00465 | south | N | 0.00465 | 0
8926 | LGE_GT10 | 1 | 158 | -0.018656 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8927 | LGE_GT20 | 2 | 153 | -0.018656 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8928 | LGE_STG0 | 3 | 100 | -0.018656 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8930 | ICPGN10A | 1 | 145 | -0.018656 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8931 | ICPGN20A | 2 | 147 | -0.018656 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8932 | ICPGN30A | 3 | 127 | -0.018656 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.019049 | south | Y | -0.034861 | 0.004437 | -0.048069 | -0.012108 | 0.004437 | south | N | 0.004437 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.019049 | south | Y | -0.034861 | 0.004437 | -0.048069 | -0.012108 | 0.004437 | south | N | 0.004437 | 0
8935 | FGNTS201 | 3 | 173 | -0.019049 | south | Y | -0.034861 | 0.004437 | -0.048069 | -0.012108 | 0.004437 | south | N | 0.004437 | 0
8936 | MVGN#1 | 1 | 207 | -0.019035 | south | Y | -0.034847 | 0.004451 | -0.048055 | -0.012094 | 0.004451 | south | N | 0.004451 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.019035 | south | Y | -0.034847 | 0.004451 | -0.048055 | -0.012094 | 0.004451 | south | N | 0.004451 | 0
8938 | MVGN#3 | 3 | 242 | -0.019035 | south | Y | -0.034847 | 0.004451 | -0.048055 | -0.012094 | 0.004451 | south | N | 0.004451 | 0
8981 | HECN1 | 1 | 144 | -0.019034 | south | Y | -0.034846 | 0.004452 | -0.048054 | -0.012093 | 0.004452 | south | N | 0.004452 | 0
8982 | HECN2 | 2 | 144 | -0.019034 | south | Y | -0.034846 | 0.004452 | -0.048054 | -0.012093 | 0.004452 | south | N | 0.004452 | 0
8983 | HECN3 | 3 | 171 | -0.019034 | south | Y | -0.034846 | 0.004452 | -0.048054 | -0.012093 | 0.004452 | south | N | 0.004452 | 0
9000 | DECKR_G1 | 1 | 310 | -0.029461 | south | Y | -0.045273 | -0.005975 | -0.058481 | -0.02252 | 0.005975 | south | N | 0.005975 | 0
9001 | DECKR_G2 | 2 | 413 | -0.029461 | south | Y | -0.045273 | -0.005975 | -0.058481 | -0.02252 | 0.005975 | south | N | 0.005975 | 0
9002 | DECKR_G3 | 3 | 42 | -0.029193 | south | Y | -0.045005 | -0.005707 | -0.058213 | -0.022252 | 0.005707 | south | N | 0.005707 | 0
9003 | DECKR_G4 | 4 | 44 | -0.029193 | south | Y | -0.045005 | -0.005707 | -0.058213 | -0.022252 | 0.005707 | south | N | 0.005707 | 0
9004 | DECKR_G5 | 5 | 44 | -0.029193 | south | Y | -0.045005 | -0.005707 | -0.058213 | -0.022252 | 0.005707 | south | N | 0.005707 | 0
9005 | DECKR_G6 | 6 | 47 | -0.029193 | south | Y | -0.045005 | -0.005707 | -0.058213 | -0.022252 | 0.005707 | south | N | 0.005707 | 0
9016 | SANDH_G1 | 1 | 49 | -0.029155 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9017 | SANDH_G2 | 2 | 46 | -0.029155 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9018 | SANDH_G3 | 3 | 46 | -0.029155 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9019 | SANDH_G4 | 4 | 47 | -0.029155 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9020 | SANDHG5A | 5A | 154 | -0.029155 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9021 | SANDHG5C | 5C | 148 | -0.029155 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9022 | SANDH_G6 | 6 | 48 | -0.029155 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9023 | SANDH_G7 | 7 | 48 | -0.029155 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
11001 | NAV1CT | 1 | 70 | 0.029258 | west | Y | 0.013446 | 0.052744 | 0.00023769 | 0.036199 | 0.00023769 | west | N | 0.00023769 | 0
11009 | NAV2CT | 1 | 70 | 0.029258 | west | Y | 0.013446 | 0.052744 | 0.00023769 | 0.036199 | 0.00023769 | west | N | 0.00023769 | 0
11011 | NAV3ST | 1 | 92.8 | 0.029258 | west | Y | 0.013446 | 0.052744 | 0.00023769 | 0.036199 | 0.00023769 | west | N | 0.00023769 | 0
11012 | NAV4CT | 1 | 80 | 0.029258 | west | Y | 0.013446 | 0.052744 | 0.00023769 | 0.036199 | 0.00023769 | west | N | 0.00023769 | 0
11013 | NAV5CT | 1 | 80 | 0.029258 | west | Y | 0.013446 | 0.052744 | 0.00023769 | 0.036199 | 0.00023769 | west | N | 0.00023769 | 0
11014 | NAV6ST | 1 | 115 | 0.029258 | west | Y | 0.013446 | 0.052744 | 0.00023769 | 0.036199 | 0.00023769 | west | N | 0.00023769 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.029256 | west | Y | 0.013444 | 0.052742 | 0.00023569 | 0.036197 | 0.00023569 | west | N | 0.00023569 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.029256 | west | Y | 0.013444 | 0.052742 | 0.00023569 | 0.036197 | 0.00023569 | west | N | 0.00023569 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.029256 | west | Y | 0.013444 | 0.052742 | 0.00023569 | 0.036197 | 0.00023569 | west | N | 0.00023569 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.029256 | west | Y | 0.013444 | 0.052742 | 0.00023569 | 0.036197 | 0.00023569 | west | N | 0.00023569 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.029256 | west | Y | 0.013444 | 0.052742 | 0.00023569 | 0.036197 | 0.00023569 | west | N | 0.00023569 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.029256 | west | Y | 0.013444 | 0.052742 | 0.00023569 | 0.036197 | 0.00023569 | west | N | 0.00023569 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.028853 | west | Y | 0.013041 | 0.052339 | -0.00016731 | 0.035794 | 0.00016731 | west | N | 0.00016731 | 0
11057 | CHAMPION | 1 | 126.5 | 0.028853 | west | Y | 0.013041 | 0.052339 | -0.00016731 | 0.035794 | 0.00016731 | west | N | 0.00016731 | 0
11058 | PYRON_1G | 1 | 249 | 0.028853 | west | Y | 0.013041 | 0.052339 | -0.00016731 | 0.035794 | 0.00016731 | west | N | 0.00016731 | 0
11059 | INADALE_ | 1 | 197 | 0.028853 | west | Y | 0.013041 | 0.052339 | -0.00016731 | 0.035794 | 0.00016731 | west | N | 0.00016731 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.029421 | west | Y | 0.013609 | 0.052907 | 0.00040069 | 0.036362 | 0.00040069 | west | N | 0.00040069 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.029421 | west | Y | 0.013609 | 0.052907 | 0.00040069 | 0.036362 | 0.00040069 | west | N | 0.00040069 | 0
11147 | NOTREES_ | 1 | 149 | 0.029117 | west | Y | 0.013305 | 0.052603 | 9.6691e-05 | 0.036058 | 9.6691e-05 | west | N | 9.6691e-05 | 0
11309 | BULLCREK | 1 | 180 | 0.029573 | west | Y | 0.013761 | 0.053059 | 0.00055269 | 0.036514 | 0.00055269 | west | N | 0.00055269 | 0
11310 | BULLCREK | 1 | 180 | 0.029573 | west | Y | 0.013761 | 0.053059 | 0.00055269 | 0.036514 | 0.00055269 | west | N | 0.00055269 | 0
11320 | COYOTE_1 | 1 | 225 | 0.029563 | west | Y | 0.013751 | 0.053049 | 0.00054269 | 0.036504 | 0.00054269 | west | N | 0.00054269 | 0
11415 | LORAINE_ | 1 | 125 | 0.029249 | west | Y | 0.013437 | 0.052735 | 0.00022869 | 0.03619 | 0.00022869 | west | N | 0.00022869 | 0
11416 | LORAINE_ | 1 | 125 | 0.029249 | west | Y | 0.013437 | 0.052735 | 0.00022869 | 0.03619 | 0.00022869 | west | N | 0.00022869 | 0
11691 | KMICHICT | 1 | 140 | 0.017673 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11692 | KMICHICT | 2 | 141 | 0.017673 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11693 | KMICHIST | 3 | 309 | 0.017673 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11694 | KMICHICT | 4 | 143 | 0.017673 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11695 | KMICHICT | 5 | 144 | 0.017673 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11696 | KMICHIST | 6 | 310 | 0.017673 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
12322 | ENNSTRAC | 1 | 196 | 0.016612 | north | Y | 0.00079969 | 0.040098 | -0.012408 | 0.023553 | 0.00079969 | North | N | 0.00079969 | 0
12323 | ENNSTRAC | 2 | 111 | 0.016612 | north | Y | 0.00079969 | 0.040098 | -0.012408 | 0.023553 | 0.00079969 | North | N | 0.00079969 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.017963 | north | N | 0.0021507 | 0.041449 | -0.011057 | 0.024904 | 0.0021507 | North | N | 0.0021507 | 0
12411 | FPLEFR1A | 1 | 161 | 0.016861 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12412 | FPLEFR1B | 2 | 164 | 0.016861 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12413 | FPLEFR1C | 3 | 164 | 0.016861 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12414 | FPLEFR1S | 4 | 414 | 0.016861 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12421 | FPLEFR2A | 1 | 162 | 0.016861 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12422 | FPLEFR2B | 2 | 161 | 0.016861 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12423 | FPLEFR2C | 3 | 163 | 0.016861 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12424 | FPLEFR2S | 4 | 409 | 0.016861 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12440 | PARKD_1S | 1 | 0 | 0.017175 | north | N | 0.0013627 | 0.040661 | -0.011845 | 0.024116 | 0.0013627 | North | N | 0.0013627 | 0
12449 | PARKD_2S | 1 | 0 | 0.017175 | north | N | 0.0013627 | 0.040661 | -0.011845 | 0.024116 | 0.0013627 | North | N | 0.0013627 | 0
13116 | TGATEWAY | 1 | 148 | 0.015163 | north | N | -0.00064931 | 0.038649 | -0.013857 | 0.022104 | 0.00064931 | North | N | 0.00064931 | 0
13117 | TGATEWAY | 2 | 130 | 0.015163 | north | N | -0.00064931 | 0.038649 | -0.013857 | 0.022104 | 0.00064931 | North | N | 0.00064931 | 0
13118 | TGATEWAY | 3 | 145 | 0.015163 | north | N | -0.00064931 | 0.038649 | -0.013857 | 0.022104 | 0.00064931 | North | N | 0.00064931 | 0
13119 | TGATEWAY | 4 | 399 | 0.015163 | north | N | -0.00064931 | 0.038649 | -0.013857 | 0.022104 | 0.00064931 | North | N | 0.00064931 | 0
13131 | CALFREST | 1 | 150.7 | 0.01301 | north | Y | -0.0028023 | 0.036496 | -0.01601 | 0.019951 | 0.0028023 | North | N | 0.0028023 | 0
13132 | CALFREST | 2 | 151 | 0.01301 | north | Y | -0.0028023 | 0.036496 | -0.01601 | 0.019951 | 0.0028023 | North | N | 0.0028023 | 0
13133 | CALFREST | 3 | 177.4 | 0.01301 | north | Y | -0.0028023 | 0.036496 | -0.01601 | 0.019951 | 0.0028023 | North | N | 0.0028023 | 0
13134 | CALFREST | 4 | 151.5 | 0.013072 | north | Y | -0.0027403 | 0.036558 | -0.015948 | 0.020013 | 0.0027403 | North | N | 0.0027403 | 0
13135 | CALFREST | 5 | 152.3 | 0.013072 | north | Y | -0.0027403 | 0.036558 | -0.015948 | 0.020013 | 0.0027403 | North | N | 0.0027403 | 0
13136 | CALFREST | 6 | 177.5 | 0.013072 | north | Y | -0.0027403 | 0.036558 | -0.015948 | 0.020013 | 0.0027403 | North | N | 0.0027403 | 0
13432 | SANDOW_5 | 5 | 581 | -0.023936 | south | Y | -0.039748 | -0.00045001 | -0.052956 | -0.016995 | 0.00045001 | south | N | 0.00045001 | 0
13691 | OAKGROVE | 1 | 855 | 0.00689 | north | Y | -0.0089223 | 0.030376 | -0.02213 | 0.013831 | 0.0089223 | North | N | 0.0089223 | 0
13692 | OAKGROVE | 2 | 855 | 0.00689 | north | Y | -0.0089223 | 0.030376 | -0.02213 | 0.013831 | 0.0089223 | North | N | 0.0089223 | 0
32798 | BRYN_TAM | 1 | 32 | 0.002178 | north | N | -0.013634 | 0.025664 | -0.026842 | 0.0091187 | 0.0091187 | houston | Y | 0.013634 | 0
32883 | BRYN_DNS | 1 | 48 | 0.00189 | north | Y | -0.013922 | 0.025376 | -0.02713 | 0.0088307 | 0.0088307 | houston | Y | 0.013922 | 0.2444
32884 | BRYN_DNS | 1 | 46 | 0.00189 | north | Y | -0.013922 | 0.025376 | -0.02713 | 0.0088307 | 0.0088307 | houston | Y | 0.013922 | 0.23422
32886 | BRYN_ATK | MB | 12 | 0.002194 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0
32887 | BRYN_ATK | MB | 51 | 0.002194 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0
32888 | BRYN_ATK | 1 | 17 | 0.002194 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0.076222
32890 | BRYN_ATK | MB | 22 | 0.002194 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0
32891 | BRYN_ATK | MB | 25 | 0.002194 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0
32892 | BRYN_DNS | 1 | 105 | 0.00189 | north | Y | -0.013922 | 0.025376 | -0.02713 | 0.0088307 | 0.0088307 | houston | Y | 0.013922 | 0.53462
36998 | RDCNYNG1 | 1 | 84 | 0.02964 | west | Y | 0.013828 | 0.053126 | 0.00061969 | 0.036581 | 0.00061969 | west | N | 0.00061969 | 0
38332 | WDWRDU2 | 1 | 80 | 0.027617 | west | Y | 0.011805 | 0.051103 | -0.0014033 | 0.034558 | 0.0014033 | west | N | 0.0014033 | 0
38437 | TNSRBNMS | 1 | 150 | 0.027604 | west | Y | 0.011792 | 0.05109 | -0.0014163 | 0.034545 | 0.0014163 | west | N | 0.0014163 | 0
38438 | TNSRBNMS | 1 | 150 | 0.027604 | west | Y | 0.011792 | 0.05109 | -0.0014163 | 0.034545 | 0.0014163 | west | N | 0.0014163 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.007172 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.007172 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38600 | TNBP_CGN | 5 | 53 | -0.007172 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.007172 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.007172 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.007172 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38614 | TNBPAMCG | 4 | 96 | -0.007172 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38615 | TNBPAMCG | 1 | 244 | -0.007172 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38690 | TNBP_CGN | 3 | 40 | -0.007172 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.007175 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.007175 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.007175 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.007175 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
39470 | TNDOWCGN | 1 | 32 | -0.007175 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
39480 | TNDOWCGN | 1 | 30 | -0.007175 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.009269 | houston | N | -0.025081 | 0.014217 | -0.038289 | -0.0023283 | 0.0023283 | houston | N | 0.0023283 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.009269 | houston | N | -0.025081 | 0.014217 | -0.038289 | -0.0023283 | 0.0023283 | houston | N | 0.0023283 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.009269 | houston | N | -0.025081 | 0.014217 | -0.038289 | -0.0023283 | 0.0023283 | houston | N | 0.0023283 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.009269 | houston | N | -0.025081 | 0.014217 | -0.038289 | -0.0023283 | 0.0023283 | houston | N | 0.0023283 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.00689 | north | Y | -0.0089223 | 0.030376 | -0.02213 | 0.013831 | 0.0089223 | North | N | 0.0089223 | 0
39970 | TNTNPONE | 1 | 153 | 0.00689 | north | Y | -0.0089223 | 0.030376 | -0.02213 | 0.013831 | 0.0089223 | North | N | 0.0089223 | 0
48500 | APD_GT1_ | 1 | 136 | -0.005895 | houston | N | -0.021707 | 0.017591 | -0.034915 | 0.0010457 | 0.0010457 | houston | N | 0.0010457 | 0
48510 | AK_GT1__ | 1 | 33 | -0.007871 | houston | N | -0.023683 | 0.015615 | -0.036891 | -0.00093032 | 0.00093032 | houston | N | 0.00093032 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.005889 | houston | Y | -0.021701 | 0.017597 | -0.034909 | 0.0010517 | 0.0010517 | houston | N | 0.0010517 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.005889 | houston | Y | -0.021701 | 0.017597 | -0.034909 | 0.0010517 | 0.0010517 | houston | N | 0.0010517 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.005889 | houston | Y | -0.021701 | 0.017597 | -0.034909 | 0.0010517 | 0.0010517 | houston | N | 0.0010517 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.005889 | houston | Y | -0.021701 | 0.017597 | -0.034909 | 0.0010517 | 0.0010517 | houston | N | 0.0010517 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.009619 | houston | N | -0.025431 | 0.013867 | -0.038639 | -0.0026783 | 0.0026783 | houston | N | 0.0026783 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.009619 | houston | N | -0.025431 | 0.013867 | -0.038639 | -0.0026783 | 0.0026783 | houston | N | 0.0026783 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.007987 | houston | N | -0.023799 | 0.015499 | -0.037007 | -0.0010463 | 0.0010463 | houston | N | 0.0010463 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.007987 | houston | N | -0.023799 | 0.015499 | -0.037007 | -0.0010463 | 0.0010463 | houston | N | 0.0010463 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.007987 | houston | N | -0.023799 | 0.015499 | -0.037007 | -0.0010463 | 0.0010463 | houston | N | 0.0010463 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.006372 | houston | N | -0.022184 | 0.017114 | -0.035392 | 0.00056868 | 0.00056868 | houston | N | 0.00056868 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.006372 | houston | N | -0.022184 | 0.017114 | -0.035392 | 0.00056868 | 0.00056868 | houston | N | 0.00056868 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.006372 | houston | N | -0.022184 | 0.017114 | -0.035392 | 0.00056868 | 0.00056868 | houston | N | 0.00056868 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.006372 | houston | N | -0.022184 | 0.017114 | -0.035392 | 0.00056868 | 0.00056868 | houston | N | 0.00056868 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.006062 | houston | N | -0.021874 | 0.017424 | -0.035082 | 0.00087868 | 0.00087868 | houston | N | 0.00087868 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.006062 | houston | N | -0.021874 | 0.017424 | -0.035082 | 0.00087868 | 0.00087868 | houston | N | 0.00087868 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.006466 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.006466 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.006466 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.006466 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.006466 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.005501 | houston | Y | -0.021313 | 0.017985 | -0.034521 | 0.0014397 | 0.0014397 | houston | N | 0.0014397 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.005659 | houston | Y | -0.021471 | 0.017827 | -0.034679 | 0.0012817 | 0.0012817 | houston | N | 0.0012817 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.005454 | houston | Y | -0.021266 | 0.018032 | -0.034474 | 0.0014867 | 0.0014867 | houston | N | 0.0014867 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.005454 | houston | Y | -0.021266 | 0.018032 | -0.034474 | 0.0014867 | 0.0014867 | houston | N | 0.0014867 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.005454 | houston | Y | -0.021266 | 0.018032 | -0.034474 | 0.0014867 | 0.0014867 | houston | N | 0.0014867 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.004578 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.005863 | houston | N | -0.021675 | 0.017623 | -0.034883 | 0.0010777 | 0.0010777 | houston | N | 0.0010777 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.005863 | houston | N | -0.021675 | 0.017623 | -0.034883 | 0.0010777 | 0.0010777 | houston | N | 0.0010777 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.005342 | houston | N | -0.021154 | 0.018144 | -0.034362 | 0.0015987 | 0.0015987 | houston | N | 0.0015987 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.005342 | houston | N | -0.021154 | 0.018144 | -0.034362 | 0.0015987 | 0.0015987 | houston | N | 0.0015987 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.005342 | houston | N | -0.021154 | 0.018144 | -0.034362 | 0.0015987 | 0.0015987 | houston | N | 0.0015987 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.005342 | houston | N | -0.021154 | 0.018144 | -0.034362 | 0.0015987 | 0.0015987 | houston | N | 0.0015987 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.006051 | houston | N | -0.021863 | 0.017435 | -0.035071 | 0.00088968 | 0.00088968 | houston | N | 0.00088968 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.006051 | houston | N | -0.021863 | 0.017435 | -0.035071 | 0.00088968 | 0.00088968 | houston | N | 0.00088968 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.006051 | houston | N | -0.021863 | 0.017435 | -0.035071 | 0.00088968 | 0.00088968 | houston | N | 0.00088968 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.006051 | houston | N | -0.021863 | 0.017435 | -0.035071 | 0.00088968 | 0.00088968 | houston | N | 0.00088968 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.006153 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.006153 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.006153 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.006153 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.006153 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48651 | EP_1_2 | 1 | 5 | -0.005509 | houston | N | -0.021321 | 0.017977 | -0.034529 | 0.0014317 | 0.0014317 | houston | N | 0.0014317 | 0
48651 | EP_1_2 | 2 | 21 | -0.005509 | houston | N | -0.021321 | 0.017977 | -0.034529 | 0.0014317 | 0.0014317 | houston | N | 0.0014317 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.001559 | north | N | -0.014253 | 0.025045 | -0.027461 | 0.0084997 | 0.0084997 | houston | Y | 0.014253 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.001559 | north | N | -0.014253 | 0.025045 | -0.027461 | 0.0084997 | 0.0084997 | houston | Y | 0.014253 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.001559 | north | N | -0.014253 | 0.025045 | -0.027461 | 0.0084997 | 0.0084997 | houston | Y | 0.014253 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.001559 | north | N | -0.014253 | 0.025045 | -0.027461 | 0.0084997 | 0.0084997 | houston | Y | 0.014253 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.005302 | houston | Y | -0.021114 | 0.018184 | -0.034322 | 0.0016387 | 0.0016387 | houston | N | 0.0016387 | 0
48691 | GBY_7374 | A | 46 | -0.006229 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48691 | GBY_7374 | B | 46 | -0.006229 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48692 | GBY_8182 | C | 46 | -0.006229 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48692 | GBY_8182 | D | 55 | -0.006229 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48693 | GBY_8384 | E | 55 | -0.006229 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48693 | GBY_8384 | F | 54 | -0.006229 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48721 | LEG_1___ | 1 | 827 | 0.008588 | north | Y | -0.0072243 | 0.032074 | -0.020432 | 0.015529 | 0.0072243 | North | N | 0.0072243 | 0
48722 | LEG_2___ | 2 | 819 | 0.008588 | north | Y | -0.0072243 | 0.032074 | -0.020432 | 0.015529 | 0.0072243 | North | N | 0.0072243 | 0
48730 | MNS_GT | 1 | 46.1 | -0.008053 | houston | N | -0.023865 | 0.015433 | -0.037073 | -0.0011123 | 0.0011123 | houston | N | 0.0011123 | 0
48731 | CBE_GT1 | 1 | 76 | -0.012312 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48732 | CBE_GT2 | 1 | 76 | -0.012312 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48733 | CBE_ST12 | 1 | 105 | -0.012312 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48734 | CBE_GT3 | 1 | 74 | -0.012312 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48735 | CBE_GT4 | 1 | 74 | -0.012312 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48736 | CBE_ST34 | 1 | 102 | -0.012312 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.006048 | houston | N | -0.02186 | 0.017438 | -0.035068 | 0.00089268 | 0.00089268 | houston | N | 0.00089268 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.006048 | houston | N | -0.02186 | 0.017438 | -0.035068 | 0.00089268 | 0.00089268 | houston | N | 0.00089268 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.006048 | houston | N | -0.02186 | 0.017438 | -0.035068 | 0.00089268 | 0.00089268 | houston | N | 0.00089268 | 0
48761 | PR_GT1__ | 1 | 35 | -0.006111 | houston | N | -0.021923 | 0.017375 | -0.035131 | 0.00082968 | 0.00082968 | houston | N | 0.00082968 | 0
48772 | PHR_GN2_ | MB | 459 | -0.006705 | houston | Y | -0.022517 | 0.016781 | -0.035725 | 0.00023568 | 0.00023568 | houston | N | 0.00023568 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.005507 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.005507 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.005507 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.005507 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.005507 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.005507 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.005507 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.004578 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.004578 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.004578 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.004578 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.005471 | houston | N | -0.021283 | 0.018015 | -0.034491 | 0.0014697 | 0.0014697 | houston | N | 0.0014697 | 0
48820 | SHELLG1_ | 1 | 71 | -0.00599 | houston | N | -0.021802 | 0.017496 | -0.03501 | 0.00095068 | 0.00095068 | houston | N | 0.00095068 | 0
48821 | SHELLG2 | 2 | 72 | -0.00599 | houston | N | -0.021802 | 0.017496 | -0.03501 | 0.00095068 | 0.00095068 | houston | N | 0.00095068 | 0
48822 | SHELLG3_ | 1 | 39 | -0.00599 | houston | N | -0.021802 | 0.017496 | -0.03501 | 0.00095068 | 0.00095068 | houston | N | 0.00095068 | 0
48822 | SHELLG3_ | 2 | 30 | -0.00599 | houston | N | -0.021802 | 0.017496 | -0.03501 | 0.00095068 | 0.00095068 | houston | N | 0.00095068 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.006199 | houston | N | -0.022011 | 0.017287 | -0.035219 | 0.00074168 | 0.00074168 | houston | N | 0.00074168 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.006199 | houston | N | -0.022011 | 0.017287 | -0.035219 | 0.00074168 | 0.00074168 | houston | N | 0.00074168 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.006052 | houston | N | -0.021864 | 0.017434 | -0.035072 | 0.00088868 | 0.00088868 | houston | N | 0.00088868 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.006064 | houston | Y | -0.021876 | 0.017422 | -0.035084 | 0.00087668 | 0.00087668 | houston | N | 0.00087668 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.006068 | houston | Y | -0.02188 | 0.017418 | -0.035088 | 0.00087268 | 0.00087268 | houston | N | 0.00087268 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.006053 | houston | Y | -0.021865 | 0.017433 | -0.035073 | 0.00088768 | 0.00088768 | houston | N | 0.00088768 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.00605 | houston | Y | -0.021862 | 0.017436 | -0.03507 | 0.00089068 | 0.00089068 | houston | N | 0.00089068 | 0
48855 | SRB_GT21 | B2 | 12 | -0.00607 | houston | Y | -0.021882 | 0.017416 | -0.03509 | 0.00087068 | 0.00087068 | houston | N | 0.00087068 | 0
48855 | SRB_GT21 | MB | 18 | -0.00607 | houston | Y | -0.021882 | 0.017416 | -0.03509 | 0.00087068 | 0.00087068 | houston | N | 0.00087068 | 0
48865 | TECO_GT1 | 1 | 50 | -0.006902 | houston | Y | -0.022714 | 0.016584 | -0.035922 | 3.8679e-05 | 3.8679e-05 | houston | N | 3.8679e-05 | 0
48873 | THW_ST3_ | 3 | 104 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48874 | THW_ST4_ | 4 | 104 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48875 | THW_3132 | A | 54 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48875 | THW_3132 | B | 53 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48877 | THW_3334 | C | 54 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48877 | THW_3334 | D | 57 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48879 | THW_4142 | E | 54 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48879 | THW_4142 | F | 54 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48881 | THW_4344 | G | 58 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48881 | THW_4344 | H | 58 | -0.005711 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48883 | THW_GT1_ | B2 | 12 | -0.005567 | houston | Y | -0.021379 | 0.017919 | -0.034587 | 0.0013737 | 0.0013737 | houston | N | 0.0013737 | 0
48885 | THW_5152 | A | 56 | -0.005233 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48885 | THW_5152 | B | 59 | -0.005233 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48886 | THW_5354 | C | 56 | -0.005233 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48886 | THW_5354 | D | 56 | -0.005233 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48887 | THW_5556 | E | 59 | -0.005233 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48887 | THW_5556 | F | 56 | -0.005233 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.011803 | houston | Y | -0.027615 | 0.011683 | -0.040823 | -0.0048623 | 0.0048623 | houston | N | 0.0048623 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.007793 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.007793 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.007793 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.007793 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.007793 | houston | N | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.007997 | houston | Y | -0.023809 | 0.015489 | -0.037017 | -0.0010563 | 0.0010563 | houston | N | 0.0010563 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.007997 | houston | Y | -0.023809 | 0.015489 | -0.037017 | -0.0010563 | 0.0010563 | houston | N | 0.0010563 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.007997 | houston | Y | -0.023809 | 0.015489 | -0.037017 | -0.0010563 | 0.0010563 | houston | N | 0.0010563 | 0
48929 | WAPGT21_ | B1 | 13 | -0.007793 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48940 | WARVUE_G | G1 | 12 | -0.005505 | houston | Y | -0.021317 | 0.017981 | -0.034525 | 0.0014357 | 0.0014357 | houston | N | 0.0014357 | 0
49803 | EXN_15GT | 1 | 34 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49826 | EXN938GT | 5 | 45.9 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49828 | EXN941GT | 10 | 17.7 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49829 | EXN942GT | 11 | 20.4 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49830 | EXN943GT | 12 | 19.9 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49831 | EXN944GT | 13 | 35 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49832 | EXN945GT | 9 | 18 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49837 | EXN_GT | 4 | 85.4 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49838 | EXN_14GT | 14 | 148 | -0.00562 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49851 | DOW17000 | 37 | 62 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49858 | DOW38100 | 31 | 71.4 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49859 | DOW38200 | 33 | 45 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49860 | DOW38300 | 32 | 101 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49862 | DOW39100 | 36 | 86 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49863 | DOW39200 | 35 | 88 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49865 | DOW41000 | 41 | 50 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49866 | DOW42000 | 42 | 18 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49869 | DOW49000 | 45 | 94 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49870 | DOW61000 | 61 | 70 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49871 | DOW62000 | 62 | 63 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49872 | DOW63000 | 63 | 72 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49873 | DOW64000 | 64 | 64.8 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49876 | DOW65000 | 65 | 101 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49877 | DOW66000 | 66 | 97 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49878 | DOW67000 | 67 | 103 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49882 | DOW81000 | 81 | 76 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49884 | DOW82000 | 82 | 80 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49885 | DOW83000 | 83 | 80 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49886 | DOW84000 | 84 | 171 | -0.010055 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
58909 | PEARSALL | 1 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 2 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 3 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 4 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 5 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 6 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 1 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 2 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 3 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 4 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 5 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 6 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 1 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 2 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 3 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 4 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 5 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 6 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 1 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 2 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 3 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 4 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 5 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 6 | 8.4 | -0.019263 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
60000 | DSKY2 | 1 | 76.5 | 0.027025 | west | Y | 0.011213 | 0.050511 | -0.0019953 | 0.033966 | 0.0019953 | west | N | 0.0019953 | 0
60003 | KING_NE1 | 1 | 80 | 0.02765 | west | Y | 0.011838 | 0.051136 | -0.0013703 | 0.034591 | 0.0013703 | west | N | 0.0013703 | 0
60005 | KING_SE1 | 1 | 40 | 0.02765 | west | Y | 0.011838 | 0.051136 | -0.0013703 | 0.034591 | 0.0013703 | west | N | 0.0013703 | 0
60007 | KING_SW1 | 1 | 80 | 0.027774 | west | Y | 0.011962 | 0.05126 | -0.0012463 | 0.034715 | 0.0012463 | west | N | 0.0012463 | 0
60016 | WOODWRD1 | 1 | 80 | 0.027619 | west | Y | 0.011807 | 0.051105 | -0.0014013 | 0.03456 | 0.0014013 | west | N | 0.0014013 | 0
60017 | ORNNWP1 | 1 | 80 | 0.02702 | west | Y | 0.011208 | 0.050506 | -0.0020003 | 0.033961 | 0.0020003 | west | N | 0.0020003 | 0
60018 | DSKY1 | 1 | 84 | 0.026823 | west | Y | 0.011011 | 0.050309 | -0.0021973 | 0.033764 | 0.0021973 | west | N | 0.0021973 | 0
60019 | KING_NW1 | 1 | 80 | 0.027774 | west | Y | 0.011962 | 0.05126 | -0.0012463 | 0.034715 | 0.0012463 | west | N | 0.0012463 | 0
60057 | CALLAHAN | 1 | 114 | -0.026074 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60058 | BUFF_GAP | 1 | 120 | 0.031232 | west | Y | 0.01542 | 0.054718 | 0.0022117 | 0.038173 | 0.0022117 | west | N | 0.0022117 | 0
60060 | CIRELLO | 1 | 233 | 0.031232 | west | Y | 0.01542 | 0.054718 | 0.0022117 | 0.038173 | 0.0022117 | west | N | 0.0022117 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.031232 | west | Y | 0.01542 | 0.054718 | 0.0022117 | 0.038173 | 0.0022117 | west | N | 0.0022117 | 0
60066 | H_HOLLOW | 1 | 222 | -0.026074 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.026074 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.026074 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.026074 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60074 | HORSH5 | 1 | 100 | -0.026074 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60081 | WHRLWIND | 1 | 60 | 0.029294 | west | Y | 0.013482 | 0.05278 | 0.00027369 | 0.036235 | 0.00027369 | west | N | 0.00027369 | 0
60201 | RIO DRCS | F | 0 | -0.024024 | south | N | -0.039836 | -0.00053801 | -0.053044 | -0.017083 | 0.00053801 | south | N | 0.00053801 | 0
60202 | FRIEND_R | F | 0 | 0.023642 | west | N | 0.0078297 | 0.047128 | -0.0053783 | 0.030583 | 0.0053783 | west | N | 0.0053783 | 0
60203 | PRES0A | BT | 4.8 | 0.028124 | west | N | 0.012312 | 0.05161 | -0.00089631 | 0.035065 | 0.00089631 | west | N | 0.00089631 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.029393 | west | Y | 0.013581 | 0.052879 | 0.00037269 | 0.036334 | 0.00037269 | west | N | 0.00037269 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.029393 | west | Y | 0.013581 | 0.052879 | 0.00037269 | 0.036334 | 0.00037269 | west | N | 0.00037269 | 0
71057 | L_SWEETW | W1 | 135 | 0.029393 | west | Y | 0.013581 | 0.052879 | 0.00037269 | 0.036334 | 0.00037269 | west | N | 0.00037269 | 0
71059 | L_SWEETW | W1 | 119 | 0.029393 | west | Y | 0.013581 | 0.052879 | 0.00037269 | 0.036334 | 0.00037269 | west | N | 0.00037269 | 0
71060 | L_SWEETW | W1 | 105 | 0.029393 | west | Y | 0.013581 | 0.052879 | 0.00037269 | 0.036334 | 0.00037269 | west | N | 0.00037269 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.029393 | west | Y | 0.013581 | 0.052879 | 0.00037269 | 0.036334 | 0.00037269 | west | N | 0.00037269 | 0
76031 | L_GASCCR | W1 | 150 | 0.03101 | west | Y | 0.015198 | 0.054496 | 0.0019897 | 0.037951 | 0.0019897 | west | N | 0.0019897 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.031312 | west | Y | 0.0155 | 0.054798 | 0.0022917 | 0.038253 | 0.0022917 | west | N | 0.0022917 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.031312 | west | Y | 0.0155 | 0.054798 | 0.0022917 | 0.038253 | 0.0022917 | west | N | 0.0022917 | 0
76096 | L_CAPRSI | W1 | 186 | 0.031312 | west | Y | 0.0155 | 0.054798 | 0.0022917 | 0.038253 | 0.0022917 | west | N | 0.0022917 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.031312 | west | Y | 0.0155 | 0.054798 | 0.0022917 | 0.038253 | 0.0022917 | west | N | 0.0022917 | 0
80003 | MILHWYS | F | 0 | -0.019013 | south | N | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
80010 | EPLVT1 | F | 0 | -0.011432 | south | N | -0.027244 | 0.012054 | -0.040452 | -0.0044913 | 0.0044913 | houston | Y | 0.012054 | 0
80012 | LAR | F | 0 | -0.019569 | south | N | -0.035381 | 0.003917 | -0.048589 | -0.012628 | 0.003917 | south | N | 0.003917 | 0
80051 | FORPVCM0 | 8 | 28 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
80053 | FOR69CG0 | 10 | 74 | -0.017413 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
80080 | GWINDT11 | 1 | 94 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80080 | GWINDT11 | 2 | 41 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80080 | GWINDT11 | 3 | 38 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80080 | GWINDT11 | 4 | 19 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80081 | GWINDT21 | 1 | 94 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80081 | GWINDT21 | 2 | 36 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80081 | GWINDT21 | 3 | 43 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80081 | GWINDT21 | 4 | 22 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80137 | CSDR89 | 8 | 39 | -0.017999 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80137 | CSDR89 | 9 | 15 | -0.017999 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80138 | CSDR7 | 7 | 7 | -0.017999 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80139 | CSDR56 | 5 | 15 | -0.017999 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80139 | CSDR56 | 6 | 39 | -0.017999 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80140 | CSDR11 | 11 | 39 | -0.017999 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80180 | PNSCALT1 | 1 | 148 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80180 | PNSCALT1 | 2 | 50 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80181 | PNSCALT2 | 1 | 55 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80181 | PNSCALT2 | 2 | 50 | -0.019006 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80223 | REYSHR G | 1 | 12 | -0.018656 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
80224 | VISTRONG | 1 | 15 | -0.018189 | south | N | -0.034001 | 0.005297 | -0.047209 | -0.011248 | 0.005297 | south | N | 0.005297 | 0
80225 | VISTRONG | 2 | 23 | -0.018189 | south | N | -0.034001 | 0.005297 | -0.047209 | -0.011248 | 0.005297 | south | N | 0.005297 | 0
80226 | ALCOA G | 1 | 48 | -0.017551 | south | N | -0.033363 | 0.005935 | -0.046571 | -0.01061 | 0.005935 | south | N | 0.005935 | 0
80227 | AIRCO G | 1 | 8 | -0.018071 | south | N | -0.033883 | 0.005415 | -0.047091 | -0.01113 | 0.005415 | south | N | 0.005415 | 0
80261 | NBEC81A | 1 | 180 | -0.018839 | south | Y | -0.034651 | 0.004647 | -0.047859 | -0.011898 | 0.004647 | south | N | 0.004647 | 0
80262 | NBEC91A | 1 | 180 | -0.018834 | south | Y | -0.034646 | 0.004652 | -0.047854 | -0.011893 | 0.004652 | south | N | 0.004652 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.018874 | south | Y | -0.034686 | 0.004612 | -0.047894 | -0.011933 | 0.004612 | south | N | 0.004612 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.018874 | south | Y | -0.034686 | 0.004612 | -0.047894 | -0.011933 | 0.004612 | south | N | 0.004612 | 0
80265 | LARECU40 | 4 | 100 | -0.019571 | south | Y | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
80266 | LARECU50 | 5 | 100 | -0.019571 | south | Y | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
80291 | PAPALOTE | 1 | 25 | -0.018727 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80291 | PAPALOTE | 2 | 25 | -0.018727 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80291 | PAPALOTE | 3 | 25 | -0.018727 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80291 | PAPALOTE | 4 | 16 | -0.018727 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80294 | PAPALOTE | 5 | 25 | -0.018727 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80294 | PAPALOTE | 6 | 25 | -0.018727 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80294 | PAPALOTE | 7 | 25 | -0.018727 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80294 | PAPALOTE | 8 | 15 | -0.018727 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
86104 | CID-138 | EQ | 0 | -0.019571 | south | N | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
86105 | CID-230 | EQ | 500 | -0.019571 | south | N | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
86106 | CUF-230 | EQ | 500 | -0.019571 | south | N | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
86107 | CUF-138 | EQ | 0 | -0.019571 | south | N | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
88198 | BEEVILLE | F | 0 | -0.019781 | south | N | -0.035593 | 0.003705 | -0.048801 | -0.01284 | 0.003705 | south | N | 0.003705 | 0
88253 | HAMILTON | F | 0 | -0.006303 | south | N | -0.022115 | 0.017183 | -0.035323 | 0.00063768 | 0.00063768 | houston | Y | 0.017183 | 0
88299 | ZAPATA | F | 0 | -0.019234 | south | N | -0.035046 | 0.004252 | -0.048254 | -0.012293 | 0.004252 | south | N | 0.004252 | 0
88508 | FALFURRI | F | 0 | -0.019241 | south | N | -0.035053 | 0.004245 | -0.048261 | -0.0123 | 0.004245 | south | N | 0.004245 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Evant - Adamsvill [7068 - 7066] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0 | 0 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0 | 0 | 0 | Weighted Shift Factors
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0 | 0 | 0 | South | -0.023486
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0 | 0 | 0 | North | 0.017918
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023486 | 0 | 0 | 0 |  | -0.041404
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023486 | 0 | 0 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79199 | 0 | 0.018908 | 0 | 0 | 0 | Line Rating | 260
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.71417 | 0 | 0.018908 | 0 | 0 | 0 | Conc Gen | 342
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.70501 | 0 | 0.018908 | 0 | 0 | 0 | Weighted Imp. | 6.2425
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.70501 | 0 | 0.018908 | 0 | 0 | 0 | PTDF | 0.018253
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.004578 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74164 | 0 | 0.018908 | 0 | 0 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29305 | 56 | 0.018253 | 1.0222 | 56 | 1.0222 | Concentration | -0.44085
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30875 | 59 | 0.018253 | 1.0769 | 115 | 2.0991
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29305 | 56 | 0.018253 | 1.0222 | 171 | 3.1213
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29305 | 56 | 0.018253 | 1.0222 | 227 | 4.1434
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30875 | 59 | 0.018253 | 1.0769 | 286 | 5.2204
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29305 | 56 | 0.018253 | 1.0222 | 342 | 6.2425
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.005302 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.1102 | 398 | 0.018184 | 7.2372
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86968 | 0 | 0.018144 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8622 | 0 | 0.018144 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84884 | 0 | 0.018144 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4381 | 0 | 0.018144 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.005454 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93809 | 172 | 0.018032 | 3.1015
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.005454 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93809 | 172 | 0.018032 | 3.1015
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.005454 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93809 | 172 | 0.018032 | 3.1015
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.005471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85895 | 0 | 0.018015 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.005501 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.0872 | 743 | 0.017985 | 13.3628
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.005505 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.06606 | 12 | 0.017981 | 0.21577
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35796 | 0 | 0.017979 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36346 | 0 | 0.017979 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38549 | 0 | 0.017979 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34694 | 0 | 0.017979 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34143 | 0 | 0.017979 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57273 | 0 | 0.017979 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32491 | 0 | 0.017979 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.005509 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027545 | 0 | 0.017977 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.005509 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11569 | 0 | 0.017977 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.005567 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.066804 | 12 | 0.017919 | 0.21503
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19108 | 0 | 0.017866 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19501 | 0 | 0.017866 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18377 | 0 | 0.017866 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25796 | 0 | 0.017866 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.099474 | 0 | 0.017866 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11465 | 0 | 0.017866 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11184 | 0 | 0.017866 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1967 | 0 | 0.017866 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10116 | 0 | 0.017866 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47995 | 0 | 0.017866 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.83176 | 0 | 0.017866 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.005659 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.1594 | 735 | 0.017827 | 13.1028
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.59394 | 104 | 0.017775 | 1.8486
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.59394 | 104 | 0.017775 | 1.8486
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30839 | 54 | 0.017775 | 0.95985
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30268 | 53 | 0.017775 | 0.94207
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30839 | 54 | 0.017775 | 0.95985
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32553 | 57 | 0.017775 | 1.0132
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30839 | 54 | 0.017775 | 0.95985
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30839 | 54 | 0.017775 | 0.95985
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.33124 | 58 | 0.017775 | 1.0309
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.33124 | 58 | 0.017775 | 1.0309
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.005863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0143 | 0 | 0.017623 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.005863 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79151 | 0 | 0.017623 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24734 | 42 | 0.017597 | 0.73907
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24734 | 42 | 0.017597 | 0.73907
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.22378 | 38 | 0.017597 | 0.66869
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.22378 | 38 | 0.017597 | 0.66869
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.005895 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.80172 | 0 | 0.017591 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42529 | 0 | 0.017496 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43128 | 0 | 0.017496 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23361 | 0 | 0.017496 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1797 | 0 | 0.017496 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.006048 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0886 | 0 | 0.017438 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.006048 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95921 | 0 | 0.017438 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.006048 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.94954 | 0 | 0.017438 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.00605 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.3794 | 228 | 0.017436 | 3.9754
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38726 | 0 | 0.017435 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38242 | 0 | 0.017435 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49981 | 0 | 0.017435 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44535 | 0 | 0.017435 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.006052 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.098042 | 0 | 0.017434 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.006053 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2893 | 213 | 0.017433 | 3.7132
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.006062 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90324 | 0 | 0.017424 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.006062 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39464 | 0 | 0.017424 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.006064 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0006 | 165 | 0.017422 | 2.8746
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.006068 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0255 | 169 | 0.017418 | 2.9436
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.07284 | 12 | 0.017416 | 0.20899
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.00607 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.017416 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.006111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21388 | 0 | 0.017375 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0042 | 0 | 0.017333 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.96664 | 0 | 0.017333 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.9691 | 0 | 0.017333 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.96602 | 0 | 0.017333 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6552 | 0 | 0.017333 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.006199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.48352 | 0 | 0.017287 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.006199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49592 | 0 | 0.017287 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28653 | 46 | 0.017257 | 0.79382
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28653 | 46 | 0.017257 | 0.79382
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28653 | 46 | 0.017257 | 0.79382
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.34259 | 55 | 0.017257 | 0.94913
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.34259 | 55 | 0.017257 | 0.94913
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33637 | 54 | 0.017257 | 0.93188
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.006303 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.208 | 0 | 0.017183 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.006303 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15757 | 0 | 0.017183 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.006303 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.017183 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.41418 | 0 | 0.017114 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.38232 | 0 | 0.017114 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.41418 | 0 | 0.017114 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.41418 | 0 | 0.017114 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.58841 | 0 | 0.01702 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56642 | 0 | 0.01702 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56254 | 0 | 0.01702 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3524 | 0 | 0.01702 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078885 | 0 | 0.01702 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.03488 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.0928 | 60 | 0.016962 | 1.0177
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.006705 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016781 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.006902 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3451 | 50 | 0.016584 | 0.8292
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50778 | 0 | 0.016314 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47837 | 0 | 0.016314 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38012 | 0 | 0.016314 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0988 | 0 | 0.016314 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1009 | 0 | 0.016314 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0923 | 0 | 0.016314 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.68851 | 0 | 0.016314 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.75 | 0 | 0.016314 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28688 | 0 | 0.016314 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.007175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2296 | 0 | 0.016311 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.007175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21525 | 0 | 0.016311 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.71965 | 0 | 0.016311 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.66656 | 0 | 0.016311 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.73687 | 0 | 0.016311 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.73185 | 0 | 0.016311 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.007793 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2547 | 161 | 0.015693 | 2.5266
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.007793 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2936 | 166 | 0.015693 | 2.605
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.007793 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.9327 | 248 | 0.015693 | 3.8919
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.007793 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.255 | 546 | 0.015693 | 8.5684
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.007793 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -5.0109 | 0 | 0.015693 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.007793 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10131 | 13 | 0.015693 | 0.20401
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.007871 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25974 | 0 | 0.015615 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.007987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3019 | 0 | 0.015499 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.007987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3019 | 0 | 0.015499 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.007987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9568 | 0 | 0.015499 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.007997 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.206 | 651 | 0.015489 | 10.0833
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.007997 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.5103 | 564 | 0.015489 | 8.7358
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.007997 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.7982 | 600 | 0.015489 | 9.2934
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.008053 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37124 | 0 | 0.015433 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0289 | 0 | 0.014217 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0289 | 0 | 0.014217 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.103 | 0 | 0.014217 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.015 | 0 | 0.014217 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.031834 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3959 | 169.5 | 0.013916 | 2.3588
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.009619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68295 | 0 | 0.013867 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.009619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09619 | 0 | 0.013867 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.62341 | 0 | 0.013431 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71793 | 0 | 0.013431 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45248 | 0 | 0.013431 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0156 | 0 | 0.013431 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86473 | 0 | 0.013431 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88484 | 0 | 0.013431 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50275 | 0 | 0.013431 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18099 | 0 | 0.013431 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.94517 | 0 | 0.013431 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70385 | 0 | 0.013431 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63346 | 0 | 0.013431 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72396 | 0 | 0.013431 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65156 | 0 | 0.013431 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0156 | 0 | 0.013431 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.97533 | 0 | 0.013431 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0357 | 0 | 0.013431 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76418 | 0 | 0.013431 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8044 | 0 | 0.013431 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8044 | 0 | 0.013431 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7194 | 0 | 0.013431 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5226 | 112.5 | 0.013394 | 1.5068
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6811 | 149.5 | 0.013394 | 2.0024
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.824 | 186 | 0.013394 | 2.4913
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7164 | 214.5 | 0.013394 | 2.8731
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.031232 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7478 | 120 | 0.013314 | 1.5977
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.031232 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2771 | 233 | 0.013314 | 3.1022
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.031232 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3157 | 170.2 | 0.013314 | 2.2661
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.031059 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20499 | 6.6 | 0.013141 | 0.086732
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.031059 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0653 | 34.3 | 0.013141 | 0.45074
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.03101 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6515 | 150 | 0.013092 | 1.9638
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.010464 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.062784 | 0 | 0.013022 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.030837 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6255 | 150 | 0.012919 | 1.9379
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.030837 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1145 | 101 | 0.012919 | 1.3048
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.030053 | west | 8 | N | N | Nwest | Nwest | 1 | 0.77537 | 0 | 0.012135 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.011432 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012054 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.029717 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.566 | 120 | 0.011799 | 1.4159
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.02971 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5652 | 120 | 0.011792 | 1.4151
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.02967 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4505 | 150 | 0.011752 | 1.7628
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.029669 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8691 | 63 | 0.011751 | 0.74032
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.02964 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4898 | 84 | 0.011722 | 0.98466
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.029633 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9337 | 99 | 0.011715 | 1.1598
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.029633 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8076 | 61 | 0.011715 | 0.71463
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.029633 | west | 7 | N | N | Nwest | Nwest | 1 | 0.74082 | 0 | 0.011715 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.029633 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3542 | 0 | 0.011715 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.029633 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3542 | 0 | 0.011715 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.029632 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1781 | 141 | 0.011714 | 1.6517
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.029632 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5558 | 120 | 0.011714 | 1.4057
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.011803 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.779 | 66 | 0.011683 | 0.77108
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9535 | 66 | 0.01168 | 0.77089
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0423 | 69 | 0.01168 | 0.80593
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0423 | 69 | 0.01168 | 0.80593
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9831 | 67 | 0.01168 | 0.78257
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9831 | 67 | 0.01168 | 0.78257
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9239 | 65 | 0.01168 | 0.75921
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.029573 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3231 | 180 | 0.011655 | 2.0979
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.029573 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3231 | 180 | 0.011655 | 2.0979
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.029563 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6517 | 225 | 0.011645 | 2.6202
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.029459 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9606 | 100.5 | 0.011541 | 1.1599
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4131 | 150 | 0.011503 | 1.7255
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4726 | 220 | 0.011503 | 2.5307
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8842 | 200 | 0.011503 | 2.3006
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5864 | 121.9 | 0.011503 | 1.4022
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.02942 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3018 | 214.2 | 0.011502 | 2.4638
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.029398 | west | 8 | N | N | Nwest | Nwest | 1 | 2.0579 | 0 | 0.01148 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.029398 | west | 8 | N | N | Nwest | Nwest | 1 | 2.1578 | 0 | 0.01148 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.029398 | west | 8 | N | N | Nwest | Nwest | 1 | 2.0696 | 0 | 0.01148 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1022 | 37.5 | 0.011475 | 0.43032
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1597 | 107.5 | 0.011475 | 1.2336
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9681 | 135 | 0.011475 | 1.5491
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4978 | 119 | 0.011475 | 1.3655
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0863 | 105 | 0.011475 | 1.2049
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3661 | 80.5 | 0.011475 | 0.92375
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.029391 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7047 | 58 | 0.011473 | 0.66544
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.029294 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7576 | 60 | 0.011376 | 0.68257
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0481 | 70 | 0.01134 | 0.79381
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0481 | 70 | 0.01134 | 0.79381
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7151 | 92.8 | 0.01134 | 1.0524
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3406 | 80 | 0.01134 | 0.90721
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3406 | 80 | 0.01134 | 0.90721
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.3647 | 115 | 0.01134 | 1.3041
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.0911 | 208.2 | 0.011338 | 2.3606
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.1573 | 142.1 | 0.011338 | 1.6112
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.8735 | 132.4 | 0.011338 | 1.5012
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.9788 | 136 | 0.011338 | 1.542
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3006 | 147 | 0.011338 | 1.6667
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.1438 | 210 | 0.011338 | 2.381
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.029249 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6561 | 125 | 0.011331 | 1.4164
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.029249 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6561 | 125 | 0.011331 | 1.4164
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.029117 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3384 | 149 | 0.011199 | 1.6687
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93571 | 76 | 0.011174 | 0.84922
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93571 | 76 | 0.011174 | 0.84922
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2928 | 105 | 0.011174 | 1.1733
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.91109 | 74 | 0.011174 | 0.82688
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.91109 | 74 | 0.011174 | 0.82688
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2558 | 102 | 0.011174 | 1.1397
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.029061 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0171 | 35 | 0.011143 | 0.39001
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.029061 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.87183 | 30 | 0.011143 | 0.3343
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9167 | 66 | 0.011123 | 0.73413
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.8877 | 65 | 0.011123 | 0.72301
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9457 | 67 | 0.011123 | 0.74525
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9457 | 67 | 0.011123 | 0.74525
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9457 | 67 | 0.011123 | 0.74525
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.029041 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.011123 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.029041 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.011123 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.012467 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -16.6185 | 0 | 0.011019 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.012467 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -16.5562 | 0 | 0.011019 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0303 | 209 | 0.010935 | 2.2855
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6499 | 126.5 | 0.010935 | 1.3833
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1844 | 249 | 0.010935 | 2.7229
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.684 | 197 | 0.010935 | 2.1542
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.028124 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.135 | 0 | 0.010206 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027774 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2219 | 80 | 0.0098562 | 0.78849
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027774 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2219 | 80 | 0.0098562 | 0.78849
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.02765 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0737 | 75 | 0.0097322 | 0.72991
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.02765 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.212 | 80 | 0.0097322 | 0.77857
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.02765 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.106 | 40 | 0.0097322 | 0.38929
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.027629 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.0516 | 400 | 0.0097112 | 3.8845
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.027623 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.519 | 236 | 0.0097052 | 2.2904
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027619 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2095 | 80 | 0.0097012 | 0.77609
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.027617 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2094 | 80 | 0.0096992 | 0.77593
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.027604 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1406 | 150 | 0.0096862 | 1.4529
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.027604 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1406 | 150 | 0.0096862 | 1.4529
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.027587 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0139 | 73 | 0.0096692 | 0.70585
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.027587 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.2829 | 119 | 0.0096692 | 1.1506
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.027587 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.6553 | 205 | 0.0096692 | 1.9822
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.027587 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.8139 | 102 | 0.0096692 | 0.98626
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.027587 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.6484 | 96 | 0.0096692 | 0.92824
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.027025 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0674 | 76.5 | 0.0091072 | 0.6967
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.02702 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1616 | 80 | 0.0091022 | 0.72817
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.026936 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4444 | 165 | 0.0090182 | 1.488
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.026823 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2531 | 84 | 0.0089052 | 0.74804
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.026547 | west | 4 | Y | N | Ywest | Nwest | 1 | 17.2476 | 649.7 | 0.0086292 | 5.6064
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.026138 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.3254 | 242 | 0.0082202 | 1.9893
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.025634 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.0761 | 120 | 0.0077162 | 0.92594
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.0254 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.3048 | 0 | 0.0074822 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.0254 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.3048 | 0 | 0.0074822 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4968 | 20 | 0.0069222 | 0.13844
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4968 | 20 | 0.0069222 | 0.13844
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4968 | 20 | 0.0069222 | 0.13844
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.42228 | 17 | 0.0069222 | 0.11768
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.02476 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.0622 | 366 | 0.0068422 | 2.5042
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.024697 | north | 3 | N | N | Nnorth | Nnorth | 1 | 28.5744 | 0 | 0.0067792 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.024697 | north | 3 | N | N | Nnorth | Nnorth | 1 | 28.5991 | 0 | 0.0067792 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.024125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.43425 | 18 | 0.0062072 | 0.11173
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.024125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.43425 | 18 | 0.0062072 | 0.11173
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.024125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.91675 | 38 | 0.0062072 | 0.23587
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3756 | 0 | 0.006073 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4105 | 0 | 0.006073 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3756 | 0 | 0.006073 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.393 | 0 | 0.006073 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3652 | 0 | 0.006073 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.43533 | 0 | 0.006073 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.801 | 0 | 0.006073 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48756 | 0 | 0.006073 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.75921 | 0 | 0.006073 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2886 | 0 | 0.006073 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.023975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.2098 | 217.3 | 0.0060572 | 1.3162
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.023975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9149 | 205 | 0.0060572 | 1.2417
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.023975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5308 | 272.4 | 0.0060572 | 1.65
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.017551 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.84245 | 0 | 0.005935 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6675 | 70 | 0.0059032 | 0.41322
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6436 | 69 | 0.0059032 | 0.40732
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6436 | 69 | 0.0059032 | 0.40732
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6198 | 68 | 0.0059032 | 0.40142
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.023642 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0057242 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.50397 | 0 | 0.005487 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12599 | 0 | 0.005487 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.70196 | 0 | 0.005487 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26998 | 0 | 0.005487 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12599 | 0 | 0.005487 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26998 | 0 | 0.005487 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.70196 | 0 | 0.005487 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.70196 | 0 | 0.005487 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.018071 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14457 | 0 | 0.005415 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.018189 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27283 | 0 | 0.005297 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.018189 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.41835 | 0 | 0.005297 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.018323 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.40311 | 22 | 0.005163 | 0.11359
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.018323 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20155 | 11 | 0.005163 | 0.056793
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.018323 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20155 | 11 | 0.005163 | 0.056793
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.022935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6787 | 204 | 0.0050172 | 1.0235
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.022935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6099 | 201 | 0.0050172 | 1.0085
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.022935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.5503 | 242 | 0.0050172 | 1.2142
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.88178 | 47.7 | 0.005 | 0.2385
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.68953 | 37.3 | 0.005 | 0.1865
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.85036 | 46 | 0.005 | 0.23
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.88733 | 48 | 0.005 | 0.24
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.02291 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0049922 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.018514 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3515 | 0 | 0.004972 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.9476 | 0 | 0.00483 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.8544 | 0 | 0.00483 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8656 | 0 | 0.00483 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7051 | 0 | 0.00483 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7424 | 0 | 0.00483 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.3693 | 0 | 0.00483 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018656 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.22387 | 0 | 0.00483 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.018702 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6931 | 144 | 0.004784 | 0.68889
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.018702 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.516 | 188 | 0.004784 | 0.89939
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 25 | 0.004759 | 0.11897
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 25 | 0.004759 | 0.11897
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 25 | 0.004759 | 0.11897
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.29963 | 16 | 0.004759 | 0.076144
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 25 | 0.004759 | 0.11897
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 25 | 0.004759 | 0.11897
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 25 | 0.004759 | 0.11897
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.28091 | 15 | 0.004759 | 0.071385
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3282 | 336 | 0.004652 | 1.5631
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3901 | 180 | 0.004652 | 0.83736
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018836 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7934 | 0 | 0.00465 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018836 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.799 | 0 | 0.00465 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018836 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.8819 | 0 | 0.00465 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.391 | 180 | 0.004647 | 0.83646
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.022533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4895 | 288 | 0.0046152 | 1.3292
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.022533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3124 | 147 | 0.0046152 | 0.67843
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.022533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3124 | 147 | 0.0046152 | 0.67843
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018874 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3039 | 334 | 0.004612 | 1.5404
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018874 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.4172 | 340 | 0.004612 | 1.5681
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018874 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3973 | 180 | 0.004612 | 0.83016
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018874 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3973 | 180 | 0.004612 | 0.83016
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.018877 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47192 | 0 | 0.004609 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.018877 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47192 | 0 | 0.004609 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.018895 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71801 | 0 | 0.004591 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.018897 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71809 | 0 | 0.004589 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.55042 | 0 | 0.004506 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7866 | 94 | 0.00448 | 0.42112
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77925 | 41 | 0.00448 | 0.18368
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.72223 | 38 | 0.00448 | 0.17024
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.36111 | 19 | 0.00448 | 0.08512
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7866 | 94 | 0.00448 | 0.42112
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.68422 | 36 | 0.00448 | 0.16128
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.81726 | 43 | 0.00448 | 0.19264
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.41813 | 22 | 0.00448 | 0.09856
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8129 | 148 | 0.00448 | 0.66304
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.9503 | 50 | 0.00448 | 0.224
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0453 | 55 | 0.00448 | 0.2464
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.9503 | 50 | 0.00448 | 0.224
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.019013 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004473 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.019013 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.72249 | 38 | 0.004473 | 0.16997
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.019013 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.36695 | 19.3 | 0.004473 | 0.086329
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.019013 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.28519 | 15 | 0.004473 | 0.067095
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.019013 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.89361 | 47 | 0.004473 | 0.21023
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.019034 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7409 | 144 | 0.004452 | 0.64109
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.019034 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7409 | 144 | 0.004452 | 0.64109
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.019034 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2548 | 171 | 0.004452 | 0.76129
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.019035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9402 | 207 | 0.004451 | 0.92136
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.019035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1249 | 216.7 | 0.004451 | 0.96453
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.019035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6065 | 242 | 0.004451 | 1.0771
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.019049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7907 | 146.5 | 0.004437 | 0.65002
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.019049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8173 | 147.9 | 0.004437 | 0.65623
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.019049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2955 | 173 | 0.004437 | 0.7676
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.019144 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22973 | 0 | 0.004342 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.019144 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21058 | 0 | 0.004342 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.019144 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22973 | 0 | 0.004342 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.019234 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004252 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.019241 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004245 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.019569 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003917 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.019571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9571 | 100 | 0.003915 | 0.3915
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.019571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9571 | 100 | 0.003915 | 0.3915
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.019571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.019571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.019571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.019571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.019587 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.3202 | 629 | 0.003899 | 2.4525
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.01961 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.47064 | 24 | 0.003876 | 0.093024
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.01961 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.47064 | 24 | 0.003876 | 0.093024
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.01961 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.45103 | 23 | 0.003876 | 0.089148
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.019781 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003705 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.021294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5774 | 168 | 0.0033762 | 0.5672
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.021294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9165 | 90 | 0.0033762 | 0.30386
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.020961 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.3581 | 112.5 | 0.0030432 | 0.34236
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.020739 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.020739 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.020739 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.021178 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.3865 | 396 | 0.002308 | 0.91396
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.02002 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.003 | 150 | 0.0021022 | 0.31533
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.019674 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1804 | 60 | 0.0017562 | 0.10537
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.019674 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2395 | 63 | 0.0017562 | 0.11064
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.019533 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.7155 | 395 | 0.0016152 | 0.638
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.019533 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.4969 | 435 | 0.0016152 | 0.7026
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.021991 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.26389 | 0 | 0.001495 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.019357 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.4203 | 435 | 0.0014392 | 0.62604
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.022615 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7923 | 433 | 0.00087099 | 0.37714
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.022626 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.2136 | 584 | 0.00085999 | 0.50223
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.022626 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.4625 | 595 | 0.00085999 | 0.51169
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.022662 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.3735 | 546 | 0.00082399 | 0.4499
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.022662 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.9965 | 750 | 0.00082399 | 0.61799
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.022843 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3249 | 58 | 0.00064299 | 0.037293
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.022843 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.033 | 89 | 0.00064299 | 0.057226
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0051 | 44 | 0.00064299 | 0.028292
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0051 | 44 | 0.00064299 | 0.028292
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.98225 | 43 | 0.00064299 | 0.027649
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0279 | 45 | 0.00064299 | 0.028935
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.022893 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.7846 | 209 | 0.00059299 | 0.12394
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.022893 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.9449 | 216 | 0.00059299 | 0.12809
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0531 | 46 | 0.00059299 | 0.027278
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.076 | 47 | 0.00059299 | 0.027871
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0531 | 46 | 0.00059299 | 0.027278
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0531 | 46 | 0.00059299 | 0.027278
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.022902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5498 | 155 | 0.00058399 | 0.090519
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.022902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8933 | 170 | 0.00058399 | 0.099279
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.022902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5498 | 155 | 0.00058399 | 0.090519
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.022934 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.4488 | 412 | 0.00055199 | 0.22742
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.022934 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1736 | 400 | 0.00055199 | 0.2208
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3723 | 147 | 0.00054499 | 0.080114
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1659 | 138 | 0.00054499 | 0.075209
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2117 | 140 | 0.00054499 | 0.076299
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3723 | 147 | 0.00054499 | 0.080114
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1753 | 182 | 0.00054499 | 0.099188
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5423 | 198 | 0.00054499 | 0.10791
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.022942 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.022942 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.022942 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.022953 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.3419 | 407 | 0.00053299 | 0.21693
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.02297 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7393 | 424 | 0.00051599 | 0.21878
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.02297 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7622 | 425 | 0.00051599 | 0.2193
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1126 | 224 | 0.00044218 | 0.099048
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1494 | 226 | 0.00044218 | 0.099933
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8923 | 212 | 0.00044218 | 0.093742
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.874 | 211 | 0.00044218 | 0.0933
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.018216 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00029818 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.023418 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.056203 | 0 | 6.7991e-05 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.023418 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.056203 | 0 | 6.7991e-05 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.017963 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 4.518e-05 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.017956 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71824 | 0 | 3.818e-05 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.017956 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71824 | 0 | 3.818e-05 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3383 | 142 | -2.3009e-05 | -0.0032672
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4088 | 145 | -2.3009e-05 | -0.0033363
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5499 | 151 | -2.3009e-05 | -0.0034743
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8176 | 290 | -2.3009e-05 | -0.0066725
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.017833 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0316 | 170 | -8.482e-05 | -0.014419
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.017833 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.2732 | 520 | -8.482e-05 | -0.044106
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1838 | 50 | -0.00018901 | -0.0094504
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1838 | 50 | -0.00018901 | -0.0094504
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1838 | 50 | -0.00018901 | -0.0094504
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1838 | 50 | -0.00018901 | -0.0094504
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.017673 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.539 | 370 | -0.00024482 | -0.090583
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4742 | 0 | -0.00024482 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4919 | 0 | -0.00024482 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.461 | 0 | -0.00024482 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5272 | 0 | -0.00024482 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5449 | 0 | -0.00024482 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.4786 | 0 | -0.00024482 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8186 | 160 | -0.00030182 | -0.048291
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7481 | 156 | -0.00030182 | -0.047084
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4527 | 196 | -0.00030182 | -0.059157
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7481 | 156 | -0.00030182 | -0.047084
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7657 | 157 | -0.00030182 | -0.047386
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.488 | 198 | -0.00030182 | -0.05976
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.023804 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.095216 | 0 | -0.00031801 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.017581 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.3186 | 0 | -0.00033682 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.017581 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.3994 | 0 | -0.00033682 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.017581 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5542 | 0 | -0.00033682 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.017512 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.7717 | 558 | -0.00040582 | -0.22645
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.017512 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.1394 | 579 | -0.00040582 | -0.23497
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.017512 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.1497 | 808 | -0.00040582 | -0.3279
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.017473 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0618 | 118 | -0.00044482 | -0.052489
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.017473 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0094 | 115 | -0.00044482 | -0.051154
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.017473 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.715 | 556 | -0.00044482 | -0.24732
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.023936 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.6196 | 569 | -0.00045001 | -0.25605
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.023936 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.9068 | 581 | -0.00045001 | -0.26146
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.024006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.057614 | 0 | -0.00052001 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.024006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.057614 | 0 | -0.00052001 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.024006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.067217 | 0 | -0.00052001 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.017346 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3703 | 79 | -0.00057182 | -0.045174
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.017346 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8387 | 106 | -0.00057182 | -0.060613
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.017346 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5325 | 146 | -0.00057182 | -0.083486
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.017346 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.3183 | 76 | -0.00057182 | -0.043458
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.017303 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.69212 | 40 | -0.00061482 | -0.024593
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3967 | 223.9 | -0.00061701 | -0.13815
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4232 | 225 | -0.00061701 | -0.13883
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4135 | 224.6 | -0.00061701 | -0.13858
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4642 | 226.7 | -0.00061701 | -0.13988
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.01727 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.3454 | 20 | -0.00064782 | -0.012956
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.01727 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.43175 | 25 | -0.00064782 | -0.016196
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.01727 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.70807 | 41 | -0.00064782 | -0.026561
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.024201 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8238 | 158 | -0.00071501 | -0.11297
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.024201 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8722 | 160 | -0.00071501 | -0.1144
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.024201 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.2352 | 175 | -0.00071501 | -0.12513
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017175 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00074282 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017175 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00074282 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.01714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7091 | 216.4 | -0.00077782 | -0.16832
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.01714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.704 | 216.1 | -0.00077782 | -0.16809
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.017128 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.6457 | 388 | -0.00078982 | -0.30645
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.017128 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.8209 | 515 | -0.00078982 | -0.40676
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7146 | 161 | -0.0010568 | -0.17015
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7652 | 164 | -0.0010568 | -0.17332
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7652 | 164 | -0.0010568 | -0.17332
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9805 | 414 | -0.0010568 | -0.43752
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7315 | 162 | -0.0010568 | -0.1712
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7146 | 161 | -0.0010568 | -0.17015
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7483 | 163 | -0.0010568 | -0.17226
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.8961 | 409 | -0.0010568 | -0.43224
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.016612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.256 | 196 | -0.0013058 | -0.25594
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.016612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8439 | 111 | -0.0013058 | -0.14495
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.025181 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8401 | 152.5 | -0.001695 | -0.25849
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.025181 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7646 | 149.5 | -0.001695 | -0.2534
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.025181 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8571 | 232.6 | -0.001695 | -0.39426
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.015365 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.0615 | 785 | -0.0025528 | -2.004
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.015365 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.2152 | 795 | -0.0025528 | -2.0295
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.015365 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.9847 | 780 | -0.0025528 | -1.9912
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9724 | 114 | -0.002588 | -0.29503
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7884 | 222 | -0.002588 | -0.57454
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7976 | 184 | -0.002588 | -0.47619
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8406 | 224 | -0.002588 | -0.57971
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9985 | 115 | -0.002588 | -0.29762
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026207 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.4593 | 132 | -0.002721 | -0.35917
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026207 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.5117 | 134 | -0.002721 | -0.36462
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026207 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.4649 | 323 | -0.002721 | -0.87889
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2441 | 0 | -0.0027548 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9712 | 0 | -0.0027548 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.1986 | 0 | -0.0027548 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.05 | 0 | -0.0027548 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.014965 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.3522 | 224 | -0.0029528 | -0.66143
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.014963 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0029548 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.014946 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.7473 | 50 | -0.0029718 | -0.14859
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.014842 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7012 | 182 | -0.0030758 | -0.5598
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.014842 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.1835 | 484 | -0.0030758 | -1.4887
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.026853 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16112 | 0 | -0.003367 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.013267 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.199 | 0 | -0.0046508 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.013267 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.199 | 0 | -0.0046508 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.013072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9804 | 151.5 | -0.0048458 | -0.73414
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.013072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9909 | 152.3 | -0.0048458 | -0.73802
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.013072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3203 | 177.5 | -0.0048458 | -0.86013
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9606 | 150.7 | -0.0049078 | -0.73961
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9645 | 151 | -0.0049078 | -0.74108
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.308 | 177.4 | -0.0049078 | -0.87065
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.01257 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.7306 | 615 | -0.0053478 | -3.2889
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.01257 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.3786 | 587 | -0.0053478 | -3.1392
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4286 | 49 | -0.005669 | -0.27778
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3411 | 46 | -0.005669 | -0.26077
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3411 | 46 | -0.005669 | -0.26077
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3703 | 47 | -0.005669 | -0.26644
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.029155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.4899 | 154 | -0.005669 | -0.87303
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.029155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3149 | 148 | -0.005669 | -0.83901
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3994 | 48 | -0.005669 | -0.27211
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3994 | 48 | -0.005669 | -0.27211
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2261 | 42 | -0.005707 | -0.23969
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2845 | 44 | -0.005707 | -0.25111
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2845 | 44 | -0.005707 | -0.25111
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3721 | 47 | -0.005707 | -0.26823
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.029461 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1329 | 310 | -0.005975 | -1.8523
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.029461 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.1674 | 413 | -0.005975 | -2.4677
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.011495 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7243 | 150 | -0.0064228 | -0.96342
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.011495 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9196 | 80 | -0.0064228 | -0.51383
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.030228 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24182 | 0 | -0.006742 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.030228 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24182 | 0 | -0.006742 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.011162 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0067558 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.011162 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.7845 | 787 | -0.0067558 | -5.3168
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.011099 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8302 | 255 | -0.0068188 | -1.7388
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.011099 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6538 | 149 | -0.0068188 | -1.016
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.011099 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6981 | 153 | -0.0068188 | -1.0433
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.008588 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.1023 | 827 | -0.0093298 | -7.7158
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.008588 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0336 | 819 | -0.0093298 | -7.6411
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.891 | 855 | -0.011028 | -9.4288
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.891 | 855 | -0.011028 | -9.4288
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.0493 | 152.3 | -0.011028 | -1.6795
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.0542 | 153 | -0.011028 | -1.6873
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006143 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.011775 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006143 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.011775 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.002764 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.2797 | 463 | -0.015154 | -7.0162
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.002194 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.037298 | 17 | -0.015724 | -0.2673
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.002178 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.069696 | 0 | -0.01574 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.00189 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.09072 | 48 | -0.016028 | -0.76934
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.00189 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.08694 | 46 | -0.016028 | -0.73728
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.00189 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.19845 | 105 | -0.016028 | -1.6829
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.039674 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3886 | 0 | -0.016188 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.039674 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3489 | 0 | -0.016188 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.039674 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3886 | 0 | -0.016188 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2404 | 0 | -0.016359 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2432 | 0 | -0.016359 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2432 | 0 | -0.016359 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.59242 | 0 | -0.016359 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.017918 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.017918 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.056999 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.026 | 0 | -0.033513 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.056999 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.026 | 0 | -0.033513 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.064639 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -27.2777 | 422 | -0.041153 | -17.3666
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.024024 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.041942 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.065572 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.836 | 0 | -0.042086 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.065572 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9016 | 0 | -0.042086 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -2.6074 | 100 | -0.043992 | -4.3992
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.077284 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0588 | 0 | -0.053798 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.09006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6211 | 0 | -0.066574 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.09006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6211 | 0 | -0.066574 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.09006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3509 | 0 | -0.066574 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Evant - Adamsvill [7068 - 7066] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.09006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6211 | 0 | -0.066574 | 0 | 0 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.09006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6211 | 0 | -0.066574 | 0 | 0 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.09006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3509 | 0 | -0.066574 | 0 | 0 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.077284 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0588 | 0 | -0.053798 | 0 | 0 | 0 | Weighted Shift Factors
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -2.6074 | 0 | -0.043992 | 0 | 0 | 0 | South | -0.023486
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.065572 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.836 | 0 | -0.042086 | 0 | 0 | 0 | North | 0.017918
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.065572 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9016 | 0 | -0.042086 | 0 | 0 | 0 |  | -0.041404
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.024024 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.041942 | 0 | 0 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.064639 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -27.2777 | 422 | -0.041153 | -17.3666 | 422 | 17.3666 | Line Rating | 260
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.056999 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.026 | 0 | -0.033513 | 0 | 422 | 17.3666 | Conc Gen | 516
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.056999 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.026 | 0 | -0.033513 | 0 | 422 | 17.3666 | Weighted Imp. | 18.8732
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.017918 | 0 | 422 | 17.3666 | PTDF | 0.036576
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.017918 | 0 | 422 | 17.3666
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2404 | 0 | -0.016359 | 0 | 422 | 17.3666 | Concentration | -0.8834
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2432 | 0 | -0.016359 | 0 | 422 | 17.3666
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2432 | 0 | -0.016359 | 0 | 422 | 17.3666
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.001559 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.59242 | 0 | -0.016359 | 0 | 422 | 17.3666
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.039674 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3886 | 0 | -0.016188 | 0 | 422 | 17.3666
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.039674 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3489 | 0 | -0.016188 | 0 | 422 | 17.3666
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.039674 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3886 | 0 | -0.016188 | 0 | 422 | 17.3666
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.00189 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.09072 | 48 | -0.016028 | -0.76934 | 470 | 18.1359
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.00189 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.08694 | 46 | -0.016028 | -0.73728 | 516 | 18.8732
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.00189 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.19845 | 105 | -0.016028 | -1.6829
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.002178 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.069696 | 0 | -0.01574 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.002194 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.037298 | 17 | -0.015724 | -0.2673
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.002194 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.002764 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.2797 | 0 | -0.015154 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006143 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.011775 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006143 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.011775 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.891 | 0 | -0.011028 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.891 | 0 | -0.011028 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.0493 | 0 | -0.011028 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.00689 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.0542 | 0 | -0.011028 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.008588 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.1023 | 0 | -0.0093298 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.008588 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0336 | 0 | -0.0093298 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.011099 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8302 | 255 | -0.0068188 | -1.7388
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.011099 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6538 | 149 | -0.0068188 | -1.016
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.011099 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6981 | 153 | -0.0068188 | -1.0433
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.011162 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0067558 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.011162 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.7845 | 787 | -0.0067558 | -5.3168
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.030228 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24182 | 0 | -0.006742 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.030228 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24182 | 0 | -0.006742 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.011495 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7243 | 150 | -0.0064228 | -0.96342
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.011495 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.9196 | 80 | -0.0064228 | -0.51383
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.029461 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1329 | 310 | -0.005975 | -1.8523
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.029461 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.1674 | 413 | -0.005975 | -2.4677
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2261 | 42 | -0.005707 | -0.23969
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2845 | 44 | -0.005707 | -0.25111
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2845 | 44 | -0.005707 | -0.25111
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.029193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3721 | 47 | -0.005707 | -0.26823
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4286 | 49 | -0.005669 | -0.27778
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3411 | 46 | -0.005669 | -0.26077
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3411 | 46 | -0.005669 | -0.26077
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3703 | 47 | -0.005669 | -0.26644
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.029155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.4899 | 154 | -0.005669 | -0.87303
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.029155 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3149 | 148 | -0.005669 | -0.83901
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3994 | 48 | -0.005669 | -0.27211
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.029155 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3994 | 48 | -0.005669 | -0.27211
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.01257 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.7306 | 0 | -0.0053478 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.01257 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.3786 | 0 | -0.0053478 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9606 | 150.7 | -0.0049078 | -0.73961
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9645 | 151 | -0.0049078 | -0.74108
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.01301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.308 | 177.4 | -0.0049078 | -0.87065
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.013072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9804 | 151.5 | -0.0048458 | -0.73414
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.013072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9909 | 152.3 | -0.0048458 | -0.73802
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.013072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3203 | 177.5 | -0.0048458 | -0.86013
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.013267 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.199 | 0 | -0.0046508 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.013267 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.199 | 0 | -0.0046508 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.026853 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16112 | 0 | -0.003367 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.014842 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7012 | 182 | -0.0030758 | -0.5598
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.014842 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.1835 | 484 | -0.0030758 | -1.4887
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.014946 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.7473 | 0 | -0.0029718 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.014963 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0029548 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.014965 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.3522 | 224 | -0.0029528 | -0.66143
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2441 | 0 | -0.0027548 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9712 | 0 | -0.0027548 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.1986 | 0 | -0.0027548 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.015163 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.05 | 0 | -0.0027548 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026207 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.4593 | 132 | -0.002721 | -0.35917
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026207 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.5117 | 134 | -0.002721 | -0.36462
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026207 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.4649 | 323 | -0.002721 | -0.87889
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9724 | 0 | -0.002588 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7884 | 0 | -0.002588 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7976 | 0 | -0.002588 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8406 | 0 | -0.002588 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.026074 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9985 | 0 | -0.002588 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.015365 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.0615 | 0 | -0.0025528 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.015365 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.2152 | 0 | -0.0025528 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.015365 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.9847 | 0 | -0.0025528 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.025181 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8401 | 152.5 | -0.001695 | -0.25849
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.025181 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7646 | 149.5 | -0.001695 | -0.2534
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.025181 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8571 | 232.6 | -0.001695 | -0.39426
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.016612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.256 | 196 | -0.0013058 | -0.25594
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.016612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8439 | 111 | -0.0013058 | -0.14495
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7146 | 161 | -0.0010568 | -0.17015
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7652 | 164 | -0.0010568 | -0.17332
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7652 | 164 | -0.0010568 | -0.17332
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9805 | 414 | -0.0010568 | -0.43752
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7315 | 162 | -0.0010568 | -0.1712
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7146 | 161 | -0.0010568 | -0.17015
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7483 | 163 | -0.0010568 | -0.17226
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.016861 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.8961 | 409 | -0.0010568 | -0.43224
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.017128 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.6457 | 388 | -0.00078982 | -0.30645
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.017128 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.8209 | 515 | -0.00078982 | -0.40676
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.01714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7091 | 216.4 | -0.00077782 | -0.16832
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.01714 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.704 | 216.1 | -0.00077782 | -0.16809
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017175 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00074282 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017175 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00074282 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.024201 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8238 | 158 | -0.00071501 | -0.11297
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.024201 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8722 | 160 | -0.00071501 | -0.1144
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.024201 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.2352 | 175 | -0.00071501 | -0.12513
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.01727 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.3454 | 20 | -0.00064782 | -0.012956
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.01727 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.43175 | 25 | -0.00064782 | -0.016196
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.01727 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.70807 | 41 | -0.00064782 | -0.026561
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3967 | 223.9 | -0.00061701 | -0.13815
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4232 | 225 | -0.00061701 | -0.13883
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4135 | 224.6 | -0.00061701 | -0.13858
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.024103 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4642 | 226.7 | -0.00061701 | -0.13988
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.017303 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.69212 | 40 | -0.00061482 | -0.024593
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.017346 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3703 | 79 | -0.00057182 | -0.045174
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.017346 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8387 | 106 | -0.00057182 | -0.060613
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.017346 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5325 | 146 | -0.00057182 | -0.083486
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.017346 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.3183 | 76 | -0.00057182 | -0.043458
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.024006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.057614 | 0 | -0.00052001 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.024006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.057614 | 0 | -0.00052001 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.024006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.067217 | 0 | -0.00052001 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.023936 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.6196 | 0 | -0.00045001 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.023936 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.9068 | 0 | -0.00045001 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.017473 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0618 | 118 | -0.00044482 | -0.052489
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.017473 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0094 | 115 | -0.00044482 | -0.051154
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.017473 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.715 | 556 | -0.00044482 | -0.24732
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.017512 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.7717 | 0 | -0.00040582 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.017512 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.1394 | 0 | -0.00040582 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.017512 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.1497 | 0 | -0.00040582 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.017581 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.3186 | 0 | -0.00033682 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.017581 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.3994 | 0 | -0.00033682 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.017581 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5542 | 0 | -0.00033682 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.023804 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.095216 | 0 | -0.00031801 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8186 | 160 | -0.00030182 | -0.048291
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7481 | 156 | -0.00030182 | -0.047084
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4527 | 196 | -0.00030182 | -0.059157
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7481 | 156 | -0.00030182 | -0.047084
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7657 | 157 | -0.00030182 | -0.047386
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.017616 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.488 | 198 | -0.00030182 | -0.05976
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.017673 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.539 | 370 | -0.00024482 | -0.090583
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4742 | 0 | -0.00024482 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4919 | 0 | -0.00024482 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.461 | 0 | -0.00024482 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5272 | 0 | -0.00024482 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5449 | 0 | -0.00024482 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.017673 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.4786 | 0 | -0.00024482 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1838 | 50 | -0.00018901 | -0.0094504
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1838 | 50 | -0.00018901 | -0.0094504
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1838 | 50 | -0.00018901 | -0.0094504
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.023675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1838 | 50 | -0.00018901 | -0.0094504
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.017833 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0316 | 170 | -8.482e-05 | -0.014419
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.017833 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.2732 | 520 | -8.482e-05 | -0.044106
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3383 | 142 | -2.3009e-05 | -0.0032672
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4088 | 145 | -2.3009e-05 | -0.0033363
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5499 | 151 | -2.3009e-05 | -0.0034743
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.023509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8176 | 290 | -2.3009e-05 | -0.0066725
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.017956 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71824 | 0 | 3.818e-05 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.017956 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71824 | 0 | 3.818e-05 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.017963 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 4.518e-05 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.023418 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.056203 | 0 | 6.7991e-05 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.023418 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.056203 | 0 | 6.7991e-05 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.018216 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00029818 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1126 | 224 | 0.00044218 | 0.099048
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1494 | 226 | 0.00044218 | 0.099933
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8923 | 212 | 0.00044218 | 0.093742
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.01836 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.874 | 211 | 0.00044218 | 0.0933
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.02297 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7393 | 0 | 0.00051599 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.02297 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7622 | 0 | 0.00051599 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.022953 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.3419 | 407 | 0.00053299 | 0.21693
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.022942 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.022942 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.022942 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3723 | 147 | 0.00054499 | 0.080114
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1659 | 138 | 0.00054499 | 0.075209
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2117 | 140 | 0.00054499 | 0.076299
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3723 | 147 | 0.00054499 | 0.080114
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1753 | 182 | 0.00054499 | 0.099188
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.022941 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5423 | 198 | 0.00054499 | 0.10791
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.022934 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.4488 | 412 | 0.00055199 | 0.22742
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.022934 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1736 | 400 | 0.00055199 | 0.2208
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.022902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5498 | 155 | 0.00058399 | 0.090519
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.022902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8933 | 170 | 0.00058399 | 0.099279
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.022902 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5498 | 155 | 0.00058399 | 0.090519
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.022893 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.7846 | 209 | 0.00059299 | 0.12394
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.022893 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.9449 | 216 | 0.00059299 | 0.12809
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0531 | 46 | 0.00059299 | 0.027278
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.076 | 47 | 0.00059299 | 0.027871
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0531 | 46 | 0.00059299 | 0.027278
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.022893 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0531 | 46 | 0.00059299 | 0.027278
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.022843 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3249 | 58 | 0.00064299 | 0.037293
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.022843 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.033 | 89 | 0.00064299 | 0.057226
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0051 | 44 | 0.00064299 | 0.028292
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0051 | 44 | 0.00064299 | 0.028292
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.98225 | 43 | 0.00064299 | 0.027649
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.022843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0279 | 45 | 0.00064299 | 0.028935
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.022662 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.3735 | 0 | 0.00082399 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.022662 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.9965 | 0 | 0.00082399 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.022626 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.2136 | 0 | 0.00085999 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.022626 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.4625 | 0 | 0.00085999 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.022615 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7923 | 0 | 0.00087099 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.019357 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.4203 | 435 | 0.0014392 | 0.62604
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.021991 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.26389 | 0 | 0.001495 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.019533 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.7155 | 395 | 0.0016152 | 0.638
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.019533 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.4969 | 435 | 0.0016152 | 0.7026
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.019674 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1804 | 60 | 0.0017562 | 0.10537
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.019674 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2395 | 63 | 0.0017562 | 0.11064
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.02002 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.003 | 0 | 0.0021022 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.021178 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.3865 | 0 | 0.002308 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.020739 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.020739 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.020739 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.020961 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.3581 | 0 | 0.0030432 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.021294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5774 | 168 | 0.0033762 | 0.5672
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.021294 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9165 | 90 | 0.0033762 | 0.30386
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.019781 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003705 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.01961 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.47064 | 24 | 0.003876 | 0.093024
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.01961 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.47064 | 24 | 0.003876 | 0.093024
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.01961 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.45103 | 23 | 0.003876 | 0.089148
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.019587 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.3202 | 0 | 0.003899 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.019571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9571 | 100 | 0.003915 | 0.3915
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.019571 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9571 | 100 | 0.003915 | 0.3915
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.019571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.019571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.019571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.019571 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.019569 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003917 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019263 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.16181 | 8.4 | 0.004223 | 0.035473
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.019241 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004245 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.019234 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004252 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.019144 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22973 | 0 | 0.004342 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.019144 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21058 | 0 | 0.004342 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.019144 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22973 | 0 | 0.004342 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.019049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7907 | 146.5 | 0.004437 | 0.65002
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.019049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8173 | 147.9 | 0.004437 | 0.65623
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.019049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2955 | 173 | 0.004437 | 0.7676
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.019035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9402 | 207 | 0.004451 | 0.92136
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.019035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1249 | 216.7 | 0.004451 | 0.96453
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.019035 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6065 | 242 | 0.004451 | 1.0771
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.019034 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7409 | 144 | 0.004452 | 0.64109
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.019034 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7409 | 144 | 0.004452 | 0.64109
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.019034 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2548 | 171 | 0.004452 | 0.76129
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.019013 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.72249 | 38 | 0.004473 | 0.16997
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.019013 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.36695 | 19.3 | 0.004473 | 0.086329
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.019013 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.28519 | 15 | 0.004473 | 0.067095
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.019013 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.89361 | 47 | 0.004473 | 0.21023
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.019013 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004473 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7866 | 0 | 0.00448 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77925 | 0 | 0.00448 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.72223 | 0 | 0.00448 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.36111 | 0 | 0.00448 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7866 | 0 | 0.00448 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.68422 | 0 | 0.00448 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.81726 | 0 | 0.00448 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.41813 | 0 | 0.00448 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8129 | 0 | 0.00448 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.9503 | 0 | 0.00448 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0453 | 0 | 0.00448 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.019006 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.9503 | 0 | 0.00448 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.55042 | 0 | 0.004506 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.018897 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71809 | 0 | 0.004589 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.018895 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71801 | 0 | 0.004591 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.018877 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47192 | 0 | 0.004609 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.018877 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47192 | 0 | 0.004609 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018874 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3039 | 334 | 0.004612 | 1.5404
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018874 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.4172 | 340 | 0.004612 | 1.5681
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018874 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3973 | 180 | 0.004612 | 0.83016
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018874 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3973 | 180 | 0.004612 | 0.83016
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.022533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4895 | 288 | 0.0046152 | 1.3292
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.022533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3124 | 147 | 0.0046152 | 0.67843
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.022533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3124 | 147 | 0.0046152 | 0.67843
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018839 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.391 | 180 | 0.004647 | 0.83646
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018836 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7934 | 0 | 0.00465 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018836 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.799 | 0 | 0.00465 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018836 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.8819 | 0 | 0.00465 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3282 | 336 | 0.004652 | 1.5631
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3901 | 180 | 0.004652 | 0.83736
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 0 | 0.004759 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 0 | 0.004759 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 0 | 0.004759 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.29963 | 0 | 0.004759 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 0 | 0.004759 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 0 | 0.004759 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46818 | 0 | 0.004759 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018727 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.28091 | 0 | 0.004759 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.018702 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6931 | 144 | 0.004784 | 0.68889
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.018702 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.516 | 188 | 0.004784 | 0.89939
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.9476 | 0 | 0.00483 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.8544 | 0 | 0.00483 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8656 | 0 | 0.00483 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7051 | 0 | 0.00483 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7424 | 0 | 0.00483 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018656 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.3693 | 0 | 0.00483 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018656 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.22387 | 0 | 0.00483 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.018514 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3515 | 0 | 0.004972 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.02291 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0049922 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.88178 | 47.7 | 0.005 | 0.2385
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.68953 | 37.3 | 0.005 | 0.1865
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.85036 | 46 | 0.005 | 0.23
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.018486 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.88733 | 48 | 0.005 | 0.24
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.022935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6787 | 204 | 0.0050172 | 1.0235
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.022935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6099 | 201 | 0.0050172 | 1.0085
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.022935 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.5503 | 242 | 0.0050172 | 1.2142
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.018323 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.40311 | 22 | 0.005163 | 0.11359
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.018323 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20155 | 11 | 0.005163 | 0.056793
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.018323 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20155 | 11 | 0.005163 | 0.056793
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.018189 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27283 | 0 | 0.005297 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.018189 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.41835 | 0 | 0.005297 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.018071 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14457 | 0 | 0.005415 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.50397 | 0 | 0.005487 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12599 | 0 | 0.005487 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.70196 | 0 | 0.005487 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26998 | 0 | 0.005487 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12599 | 0 | 0.005487 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26998 | 0 | 0.005487 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.70196 | 0 | 0.005487 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.70196 | 0 | 0.005487 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.023642 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0057242 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6675 | 70 | 0.0059032 | 0.41322
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6436 | 69 | 0.0059032 | 0.40732
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6436 | 69 | 0.0059032 | 0.40732
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.023821 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6198 | 68 | 0.0059032 | 0.40142
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.017551 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.84245 | 0 | 0.005935 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.023975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.2098 | 217.3 | 0.0060572 | 1.3162
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.023975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9149 | 205 | 0.0060572 | 1.2417
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.023975 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5308 | 272.4 | 0.0060572 | 1.65
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3756 | 0 | 0.006073 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4105 | 0 | 0.006073 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3756 | 0 | 0.006073 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.393 | 0 | 0.006073 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3652 | 0 | 0.006073 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.43533 | 0 | 0.006073 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.801 | 0 | 0.006073 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48756 | 0 | 0.006073 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.75921 | 0 | 0.006073 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.017413 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2886 | 0 | 0.006073 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.024125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.43425 | 18 | 0.0062072 | 0.11173
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.024125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.43425 | 18 | 0.0062072 | 0.11173
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.024125 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.91675 | 38 | 0.0062072 | 0.23587
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.024697 | north | 3 | N | N | Nnorth | Nnorth | 1 | 28.5744 | 0 | 0.0067792 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.024697 | north | 3 | N | N | Nnorth | Nnorth | 1 | 28.5991 | 0 | 0.0067792 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.02476 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.0622 | 366 | 0.0068422 | 2.5042
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4968 | 20 | 0.0069222 | 0.13844
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4968 | 20 | 0.0069222 | 0.13844
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4968 | 20 | 0.0069222 | 0.13844
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.02484 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.42228 | 17 | 0.0069222 | 0.11768
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.0254 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.3048 | 0 | 0.0074822 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.0254 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.3048 | 0 | 0.0074822 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.025634 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.0761 | 0 | 0.0077162 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.026138 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.3254 | 242 | 0.0082202 | 1.9893
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.026547 | west | 4 | Y | N | Ywest | Nwest | 1 | 17.2476 | 0 | 0.0086292 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.026823 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2531 | 0 | 0.0089052 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.026936 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4444 | 0 | 0.0090182 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.02702 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1616 | 0 | 0.0091022 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.027025 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0674 | 0 | 0.0091072 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.027587 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0139 | 73 | 0.0096692 | 0.70585
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.027587 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.2829 | 119 | 0.0096692 | 1.1506
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.027587 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.6553 | 205 | 0.0096692 | 1.9822
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.027587 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.8139 | 102 | 0.0096692 | 0.98626
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.027587 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.6484 | 96 | 0.0096692 | 0.92824
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.027604 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1406 | 0 | 0.0096862 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.027604 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1406 | 0 | 0.0096862 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.027617 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2094 | 0 | 0.0096992 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027619 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2095 | 0 | 0.0097012 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.027623 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.519 | 0 | 0.0097052 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.027629 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.0516 | 0 | 0.0097112 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.02765 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0737 | 0 | 0.0097322 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.02765 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.212 | 0 | 0.0097322 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.02765 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.106 | 0 | 0.0097322 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027774 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2219 | 0 | 0.0098562 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027774 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2219 | 0 | 0.0098562 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.028124 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.135 | 0 | 0.010206 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0303 | 0 | 0.010935 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6499 | 0 | 0.010935 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1844 | 0 | 0.010935 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.028853 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.684 | 0 | 0.010935 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.012467 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -16.6185 | 0 | 0.011019 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.012467 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -16.5562 | 0 | 0.011019 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9167 | 66 | 0.011123 | 0.73413
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.8877 | 65 | 0.011123 | 0.72301
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9457 | 67 | 0.011123 | 0.74525
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9457 | 67 | 0.011123 | 0.74525
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.029041 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9457 | 67 | 0.011123 | 0.74525
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.029041 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.011123 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.029041 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.011123 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.029061 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0171 | 0 | 0.011143 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.029061 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.87183 | 0 | 0.011143 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93571 | 76 | 0.011174 | 0.84922
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93571 | 76 | 0.011174 | 0.84922
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2928 | 105 | 0.011174 | 1.1733
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.91109 | 74 | 0.011174 | 0.82688
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.91109 | 74 | 0.011174 | 0.82688
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.012312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2558 | 102 | 0.011174 | 1.1397
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.029117 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3384 | 0 | 0.011199 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.029249 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6561 | 0 | 0.011331 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.029249 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6561 | 0 | 0.011331 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.0911 | 208.2 | 0.011338 | 2.3606
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.1573 | 142.1 | 0.011338 | 1.6112
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.8735 | 132.4 | 0.011338 | 1.5012
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.9788 | 136 | 0.011338 | 1.542
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3006 | 147 | 0.011338 | 1.6667
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.029256 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.1438 | 210 | 0.011338 | 2.381
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0481 | 70 | 0.01134 | 0.79381
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0481 | 70 | 0.01134 | 0.79381
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7151 | 92.8 | 0.01134 | 1.0524
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3406 | 80 | 0.01134 | 0.90721
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3406 | 80 | 0.01134 | 0.90721
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.029258 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.3647 | 115 | 0.01134 | 1.3041
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.029294 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7576 | 0 | 0.011376 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.029391 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7047 | 0 | 0.011473 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1022 | 0 | 0.011475 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1597 | 0 | 0.011475 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9681 | 0 | 0.011475 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4978 | 0 | 0.011475 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0863 | 0 | 0.011475 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.029393 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3661 | 0 | 0.011475 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.029398 | west | 8 | N | N | Nwest | Nwest | 1 | 2.0579 | 0 | 0.01148 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.029398 | west | 8 | N | N | Nwest | Nwest | 1 | 2.1578 | 0 | 0.01148 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.029398 | west | 8 | N | N | Nwest | Nwest | 1 | 2.0696 | 0 | 0.01148 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.02942 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3018 | 0 | 0.011502 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4131 | 0 | 0.011503 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4726 | 0 | 0.011503 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8842 | 0 | 0.011503 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.029421 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5864 | 0 | 0.011503 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.029459 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9606 | 0 | 0.011541 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.029563 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6517 | 0 | 0.011645 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.029573 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3231 | 0 | 0.011655 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.029573 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3231 | 0 | 0.011655 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9535 | 66 | 0.01168 | 0.77089
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0423 | 69 | 0.01168 | 0.80593
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0423 | 69 | 0.01168 | 0.80593
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9831 | 67 | 0.01168 | 0.78257
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9831 | 67 | 0.01168 | 0.78257
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.029598 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9239 | 65 | 0.01168 | 0.75921
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.011803 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.779 | 66 | 0.011683 | 0.77108
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.029632 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1781 | 0 | 0.011714 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.029632 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5558 | 0 | 0.011714 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.029633 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9337 | 0 | 0.011715 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.029633 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8076 | 0 | 0.011715 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.029633 | west | 7 | N | N | Nwest | Nwest | 1 | 0.74082 | 0 | 0.011715 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.029633 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3542 | 0 | 0.011715 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.029633 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3542 | 0 | 0.011715 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.02964 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4898 | 0 | 0.011722 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.029669 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8691 | 0 | 0.011751 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.02967 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4505 | 0 | 0.011752 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.02971 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5652 | 0 | 0.011792 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.029717 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.566 | 0 | 0.011799 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.011432 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012054 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.030053 | west | 8 | N | N | Nwest | Nwest | 1 | 0.77537 | 0 | 0.012135 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.030837 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6255 | 0 | 0.012919 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.030837 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1145 | 0 | 0.012919 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.010464 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.062784 | 0 | 0.013022 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.03101 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6515 | 0 | 0.013092 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.031059 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20499 | 0 | 0.013141 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.031059 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0653 | 0 | 0.013141 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.031232 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7478 | 0 | 0.013314 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.031232 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2771 | 0 | 0.013314 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.031232 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3157 | 0 | 0.013314 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5226 | 0 | 0.013394 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6811 | 0 | 0.013394 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.824 | 0 | 0.013394 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.031312 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7164 | 0 | 0.013394 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.62341 | 0 | 0.013431 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71793 | 0 | 0.013431 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45248 | 0 | 0.013431 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0156 | 0 | 0.013431 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86473 | 0 | 0.013431 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88484 | 0 | 0.013431 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50275 | 0 | 0.013431 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18099 | 0 | 0.013431 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.94517 | 0 | 0.013431 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70385 | 0 | 0.013431 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63346 | 0 | 0.013431 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72396 | 0 | 0.013431 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65156 | 0 | 0.013431 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0156 | 0 | 0.013431 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.97533 | 0 | 0.013431 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0357 | 0 | 0.013431 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76418 | 0 | 0.013431 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8044 | 0 | 0.013431 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8044 | 0 | 0.013431 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.010055 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7194 | 0 | 0.013431 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.009619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68295 | 0 | 0.013867 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.009619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09619 | 0 | 0.013867 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.031834 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3959 | 0 | 0.013916 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0289 | 0 | 0.014217 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0289 | 0 | 0.014217 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.103 | 0 | 0.014217 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.009269 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.015 | 0 | 0.014217 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.008053 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37124 | 0 | 0.015433 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.007997 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.206 | 0 | 0.015489 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.007997 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.5103 | 0 | 0.015489 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.007997 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.7982 | 0 | 0.015489 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.007987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3019 | 0 | 0.015499 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.007987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3019 | 0 | 0.015499 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.007987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9568 | 0 | 0.015499 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.007871 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25974 | 0 | 0.015615 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.007793 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2547 | 161 | 0.015693 | 2.5266
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.007793 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2936 | 166 | 0.015693 | 2.605
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.007793 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.9327 | 248 | 0.015693 | 3.8919
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.007793 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.255 | 546 | 0.015693 | 8.5684
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.007793 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -5.0109 | 0 | 0.015693 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.007793 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10131 | 13 | 0.015693 | 0.20401
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.71965 | 0 | 0.016311 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.66656 | 0 | 0.016311 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.73687 | 0 | 0.016311 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.007175 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.73185 | 0 | 0.016311 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.007175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2296 | 0 | 0.016311 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.007175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21525 | 0 | 0.016311 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50778 | 0 | 0.016314 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47837 | 0 | 0.016314 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38012 | 0 | 0.016314 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0988 | 0 | 0.016314 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1009 | 0 | 0.016314 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0923 | 0 | 0.016314 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.68851 | 0 | 0.016314 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.007172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.75 | 0 | 0.016314 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.007172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28688 | 0 | 0.016314 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.006902 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3451 | 50 | 0.016584 | 0.8292
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.006705 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016781 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.03488 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.0928 | 0 | 0.016962 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.58841 | 0 | 0.01702 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56642 | 0 | 0.01702 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56254 | 0 | 0.01702 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3524 | 0 | 0.01702 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.006466 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078885 | 0 | 0.01702 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.41418 | 0 | 0.017114 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.38232 | 0 | 0.017114 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.41418 | 0 | 0.017114 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.006372 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.41418 | 0 | 0.017114 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.006303 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.208 | 0 | 0.017183 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.006303 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15757 | 0 | 0.017183 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.006303 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.017183 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28653 | 46 | 0.017257 | 0.79382
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28653 | 46 | 0.017257 | 0.79382
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28653 | 46 | 0.017257 | 0.79382
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.34259 | 55 | 0.017257 | 0.94913
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.34259 | 55 | 0.017257 | 0.94913
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.006229 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33637 | 54 | 0.017257 | 0.93188
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.006199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.48352 | 0 | 0.017287 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.006199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49592 | 0 | 0.017287 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0042 | 0 | 0.017333 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.96664 | 0 | 0.017333 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.9691 | 0 | 0.017333 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.96602 | 0 | 0.017333 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.006153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6552 | 0 | 0.017333 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.006111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21388 | 0 | 0.017375 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.07284 | 12 | 0.017416 | 0.20899
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.00607 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.017416 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.006068 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0255 | 169 | 0.017418 | 2.9436
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.006064 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0006 | 165 | 0.017422 | 2.8746
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.006062 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90324 | 0 | 0.017424 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.006062 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39464 | 0 | 0.017424 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.006053 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2893 | 213 | 0.017433 | 3.7132
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.006052 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.098042 | 0 | 0.017434 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38726 | 0 | 0.017435 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38242 | 0 | 0.017435 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49981 | 0 | 0.017435 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.006051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44535 | 0 | 0.017435 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.00605 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.3794 | 228 | 0.017436 | 3.9754
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.006048 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0886 | 0 | 0.017438 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.006048 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95921 | 0 | 0.017438 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.006048 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.94954 | 0 | 0.017438 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42529 | 0 | 0.017496 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43128 | 0 | 0.017496 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23361 | 0 | 0.017496 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1797 | 0 | 0.017496 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.005895 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.80172 | 0 | 0.017591 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24734 | 42 | 0.017597 | 0.73907
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24734 | 42 | 0.017597 | 0.73907
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.22378 | 38 | 0.017597 | 0.66869
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.005889 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.22378 | 38 | 0.017597 | 0.66869
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.005863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0143 | 0 | 0.017623 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.005863 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79151 | 0 | 0.017623 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.59394 | 104 | 0.017775 | 1.8486
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.59394 | 104 | 0.017775 | 1.8486
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30839 | 54 | 0.017775 | 0.95985
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30268 | 53 | 0.017775 | 0.94207
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30839 | 54 | 0.017775 | 0.95985
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32553 | 57 | 0.017775 | 1.0132
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30839 | 54 | 0.017775 | 0.95985
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30839 | 54 | 0.017775 | 0.95985
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.33124 | 58 | 0.017775 | 1.0309
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.005711 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.33124 | 58 | 0.017775 | 1.0309
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.005659 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.1594 | 735 | 0.017827 | 13.1028
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19108 | 0 | 0.017866 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19501 | 0 | 0.017866 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18377 | 0 | 0.017866 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25796 | 0 | 0.017866 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.099474 | 0 | 0.017866 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11465 | 0 | 0.017866 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11184 | 0 | 0.017866 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1967 | 0 | 0.017866 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10116 | 0 | 0.017866 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47995 | 0 | 0.017866 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.00562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.83176 | 0 | 0.017866 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.005567 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.066804 | 12 | 0.017919 | 0.21503
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.005509 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027545 | 0 | 0.017977 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.005509 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11569 | 0 | 0.017977 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35796 | 0 | 0.017979 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36346 | 0 | 0.017979 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38549 | 0 | 0.017979 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34694 | 0 | 0.017979 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34143 | 0 | 0.017979 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57273 | 0 | 0.017979 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.005507 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32491 | 0 | 0.017979 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.005505 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.06606 | 0 | 0.017981 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.005501 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.0872 | 743 | 0.017985 | 13.3628
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.005471 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85895 | 0 | 0.018015 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.005454 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93809 | 172 | 0.018032 | 3.1015
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.005454 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93809 | 172 | 0.018032 | 3.1015
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.005454 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93809 | 172 | 0.018032 | 3.1015
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86968 | 0 | 0.018144 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8622 | 0 | 0.018144 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84884 | 0 | 0.018144 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.005342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4381 | 0 | 0.018144 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.005302 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.1102 | 398 | 0.018184 | 7.2372
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29305 | 56 | 0.018253 | 1.0222
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30875 | 59 | 0.018253 | 1.0769
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29305 | 56 | 0.018253 | 1.0222
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29305 | 56 | 0.018253 | 1.0222
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30875 | 59 | 0.018253 | 1.0769
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.005233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29305 | 56 | 0.018253 | 1.0222
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79199 | 0 | 0.018908 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.71417 | 0 | 0.018908 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.70501 | 0 | 0.018908 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004578 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.70501 | 0 | 0.018908 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.004578 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74164 | 0 | 0.018908 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023486 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023486 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023486 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown