## test results
CRE test for: |  | 3592 WACOATCO 13591 COTTONB_ | [5 empty] | PASS
Line Rating: |  | 247.95
Direction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3592 WACOATCO 13591 COTTONB_
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.02895
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.039908
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.025626
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.0085273
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3592 WACOATCO 13591 COTTONB_
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.031358
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.039231
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.025753
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0079312
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3592 WACOATCO 13591 COTTONB_
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.068181
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.0031975
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.036881
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.065661
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.031381
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.033557
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | -0.071266 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.071266 | 0.068181
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.034816
[6 empty] | Concentration |  | -0.48853 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.017605
[6 empty] | Concentration |  | -0.24703 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 17.3572
| Percent of line rating => | [6 empty] | 7% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -5.9034
[7 empty] | B1(N-S) | 0.00057374 | -0.40193 | -0.4025 | 0.00057374
[7 empty] | B2 (N-W) | 0.0022623 | -0.016614 | -0.018876 | 0.0022623
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.0014264 | -0.21915 | -0.21773 | -0.0014264
[7 empty] | B4 (S-W) | 0.0019637 | 0.38958 | 0.38762 | 0.0019637
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.001794 | 0.18705 | 0.18525 | 0.001794
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0036938 | -0.20179 | -0.1981 | -0.0036938
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | 0.1364%
Deployment Error Percent | [6 empty] | B2 | 0.5377%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -0.339%
[7 empty] | B4 | 0.4668%
[7 empty] | B5 | 0.4264%
[7 empty] | B6 | -0.878%
[7 empty] | Max Abs Error | 0.878% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | S-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3592 WACOATCO 13591 COTTONB_ C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 3405 - 3412 and 3409 - 3414 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3592 WACOATCO 13591 COTTONB_ C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 3405 - 3412 and 3409 - 3414
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.04599 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 11.7274
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.04599 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 6.8525
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.038591 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.57886
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.038591 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.57886
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.04599 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 7.0365
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.040679 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 6.1018
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.040679 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 3.2543
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.030092 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 2.1967
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.030092 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 3.5809
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.030092 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 6.1689
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.030092 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 3.0694
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.030092 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 2.8888
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.02954 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.35448
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.02954 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.35448
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.032063 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 5.3866
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.032063 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 2.8857
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.030257 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.54463
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.030257 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.54463
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.030257 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 1.1498
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.03018 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 8.6918
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.03018 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 4.4365
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.03018 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 4.4365
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.03007 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 3.3829
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.030015 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 1.2006
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.03 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 2.37
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.03 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 3.18
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.03 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 4.38
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.03 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 2.28
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.030209 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.8125
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.030209 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.9032
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.02997 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.5994
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.02997 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.74925
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.02997 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 1.2288
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.01096 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 5.0745
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 1.6598
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 1.6347
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.685
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.685
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.685
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.025149 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 2.867
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.025149 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 12.9517
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 1.723
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 1.8013
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 1.8013
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 1.7491
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 1.7491
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 1.6969
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.025969 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 1.8178
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.025969 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 1.9061
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.025969 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 1.8282
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 3.9069
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 5.7301
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.026162 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 2.59
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.026162 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 1.5959
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.026155 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 3.6879
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.026162 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.65405
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.026162 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.1956
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.026162 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.1956
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.026155 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 3.1386
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.025701 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.66309
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.025644 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 2.5772
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.025875 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 3.105
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.02564 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 1.4871
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.025706 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 5.5062
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.026253 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 3.9379
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.025291 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.16692
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.025291 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 0.86748
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.026253 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 2.6516
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.025887 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 3.1064
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.02891 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 10.5811
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.028818 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 6.974
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.027489 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 10.9956
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.027491 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 6.4879
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.027832 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 4.5923
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.029713 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 6.0615
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.029713 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 5.9723
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.029713 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 7.1905
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.57904
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.57904
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.57904
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.49218
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.029508 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 3.541
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.028928 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 1.7357
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.029982 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 2.2487
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.029982 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 2.3866
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.029982 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 2.6504
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 4.7997
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 4.6797
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 5.8796
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 4.6797
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 4.7097
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 5.9396
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.030033 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 5.1056
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.030033 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 15.6172
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.030013 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 11.1048
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.029973 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 16.7249
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.029973 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 17.3544
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.029973 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 24.2182
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.030522 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 3.4185
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.030522 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 3.0522
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.030522 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 11.5373
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.03061 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 6.6516
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.03061 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 6.2751
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.03061 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 8.3382
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.03076 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 23.6852
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 2.1759
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 2.1448
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 2.1448
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 2.1137
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.030486 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 35.2723
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.030486 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 35.3028
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 7.2549
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 7.3197
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.032355 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 7.0016
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.032355 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 6.9919
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 6.8663
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 6.8339
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.031121 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 12.2928
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.031084 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 13.5215
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.031121 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 13.5376
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.030165 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 4.1628
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.030484 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 3.5971
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.030484 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 3.5057
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.030484 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 16.9491
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.029995 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 11.6381
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.029995 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 15.4474
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.028873 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 22.6653
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.028873 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 22.954
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.028873 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 22.5209
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.028548 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 5.1957
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.028548 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 13.8172
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.030564 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 6.8463
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.0286 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 1.43
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.028613 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 1.2017
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.026863 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 16.5207
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.026863 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 15.7686
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.047385 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 25.4457
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.047385 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 37.292
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.069442 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 5.2081
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.069442 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 15.4161
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.059577 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -33.8993
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.038005 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -7.943
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.038005 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -8.2091
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.037992 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -15.4627
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.7482
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -1.7862
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.7482
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.7482
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.038075 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -16.1438
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.038075 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -16.1819
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.037784 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -2.1915
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.037784 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -3.3628
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.6625
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.6625
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -1.6247
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.7003
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.038049 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -15.6762
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.038049 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -15.2196
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.037705 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -20.5869
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.037705 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -28.2787
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.038176 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -2.3287
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.038176 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -3.6267
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.038176 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -5.7646
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.037909 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -5.8759
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.037909 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -6.4445
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.037909 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -5.8759
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.030449 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.66988
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.030449 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.33494
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.030449 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.33494
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -1.4659
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -1.1463
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -1.4136
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -1.4751
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.032143 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.38572
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.032143 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.35357
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.033642 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.80741
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.033642 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.80741
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.033642 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.77377
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.035634 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -14.1111
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.019463 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -25.9442
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.019463 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -25.8469
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.03162 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -1.2016
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.03162 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.61027
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.03162 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.4743
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.03162 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -1.4861
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.02249 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 1.6867
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.026549 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 3.9823
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.024985 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 4.235
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.011007 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 1.651
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.026131 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 1.6463
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.028095 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 18.2533
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.030051 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 1.202
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.030051 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 1.202
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.045366 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -19.1445
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.048044 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -6.3418
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.048044 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -6.4379
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.048044 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -15.5182
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.047735 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -7.5421
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.047735 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -7.6376
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.047735 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -8.3536
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.042637 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -24.9
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.042637 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -25.369
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.042595 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -18.4436
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -9.3774
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -9.4235
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -9.4067
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -9.4946
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.050557 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.40446
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.050557 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.40446
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.046352 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.83434
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.046352 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.83434
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.046352 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.69528
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.045262 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.62009
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.046648 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.83966
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.046648 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.83966
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.049556 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -1.7345
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.049556 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -1.6849
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.049556 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -1.7345
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.045734 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -1.2806
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.045734 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -1.3263
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.025173 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 0.88106
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.025173 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 0.75519
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -2.1726
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -2.1726
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -2.1726
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -2.1726
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.043249 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.25949
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.040653 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.097567
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.040653 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.097567
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.040653 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.11383
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.040044 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.16018
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.040114 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.096274
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.040114 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.096274
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -5.7301
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -5.3792
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -5.4572
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -5.7301
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -7.0944
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -7.718
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.048236 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -7.356
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.048236 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -7.2113
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.048236 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -11.2197
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -5.7362
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -5.8574
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -6.0998
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -11.7148
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.018408 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.60746
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.018408 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.4602
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.032143 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.38572
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.030799 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -2.2483
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -2.2707
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -2.3282
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.83532
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.20883
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -2.2707
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -2.2994
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -2.2535
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.71857
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -1.3222
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.032652 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -20.5381
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.031151 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -4.4857
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.031151 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -5.8564
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.037643 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.45172
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.023143 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.13886
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.031278 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -10.5094
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.031351 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -10.4712
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.031351 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -10.6593
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.031396 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -1.193
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.031362 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.78405
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.031362 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.78405
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.031394 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -1.193
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.031547 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.91486
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.031282 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -4.6391
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.031282 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -4.6485
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.031282 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -4.7861
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -4.8901
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -4.7354
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -3.095
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -4.4878
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -4.5496
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -3.9306
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.031746 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -4.6508
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.031746 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -4.6952
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.031746 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -5.4921
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.031683 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -6.5584
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.031683 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -6.8657
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.031683 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -7.6673
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.031682 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -4.5622
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.031682 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -4.5622
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.031682 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -5.4176
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.050625 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -15.6937
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.050625 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -20.9081
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -2.1466
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -2.2488
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -2.2488
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -2.4021
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -2.4477
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -2.2979
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -2.2979
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -2.3478
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.049954 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -7.6929
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.049954 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -7.3932
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -2.3978
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -2.3978
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 1.794
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 1.794
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 2.3784
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.0503
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.0503
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 2.9473
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 5.3349
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 3.6412
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 3.3926
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 3.4849
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 3.7667
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 5.381
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 5.5421
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 3.3544
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 6.6027
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 5.2238
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 5.2092
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 3.175
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.025254 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 3.7628
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.025971 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 4.6748
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.025971 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 4.6748
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.025946 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 5.8379
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.026315 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 3.2894
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.026315 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 3.2894
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 4.2018
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 4.2318
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 9.274
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 4.2919
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 4.3219
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 9.304
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.031339 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 6.1424
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.031339 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 3.4786
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.030187 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 4.7926
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 4.882
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 4.882
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 12.324
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 4.8224
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 4.7926
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 4.8522
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 12.1751
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.030091 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.030091 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 4.2547
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 3.7372
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 4.1685
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 11.4705
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.027189 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 4.0974
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.027189 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 4.1055
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.027189 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 4.8233
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.027259 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 4.1297
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.027259 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 4.1515
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.027259 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 4.8385
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.059577 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -34.6142
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 16.2544
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 16.2544
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.009251 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.29603
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.008441 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.40517
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.008441 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.38829
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.11124
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.47277
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00927 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.15759
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.20394
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.23175
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.008441 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.88631
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.026234 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 2.2037
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.022443 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 1.7954
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.022418 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 3.3627
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.022418 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 3.3627
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.6355
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.5987
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.47573
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -1.3751
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -1.3778
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -1.367
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.8617
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -2.1901
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.35904
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.90089
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.83443
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.92245
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.91616
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.008982 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.28742
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.008982 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.26946
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.4625
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.4625
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -1.5679
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -1.4428
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 2.8954
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 2.9087
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.006421 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.87326
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.010375 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.34237
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.26905
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.26905
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.24343
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.24343
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.013849 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.98328
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.013849 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.13849
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.010628 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.7324
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.010628 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.7324
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.010628 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -2.6039
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.47937
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.4425
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.47937
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.47937
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.006753 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -1.0062
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.006753 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.43962
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.68823
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.66252
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.65798
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.41218
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.092269
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.005626 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -4.1801
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.005943 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -4.3681
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.00553 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.95116
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.00553 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.95116
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.00553 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.95116
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.65273
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.006358 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -1.0999
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.006358 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.85833
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.86382
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.85639
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.84312
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -1.4284
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.43085
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.42546
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.55606
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.49548
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -1.1311
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -1.0889
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -1.0916
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -1.0882
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -1.8644
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.005642 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.02821
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.005642 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.11848
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 1.3287
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.3443
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.3443
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 3.2745
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.005229 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -2.0811
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.32642
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.32642
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.32642
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.39028
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.39028
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.38318
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.022389 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 18.5157
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.022389 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 18.3366
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.010739 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.49507
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -1.4695
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -1.4695
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -2.0303
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -1.4309
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -1.4309
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -1.9723
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.006726 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -1.2107
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.006726 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -1.0667
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.006726 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -1.056
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.006853 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.23986
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.008041 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -3.6908
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.3666
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.37224
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.3948
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.35532
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.34968
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.58656
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.33276
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.58859
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.58104
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.58104
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.003773 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.61123
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.005568 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.87418
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.46917
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.47578
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.25771
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.19824
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.007027 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.54811
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.007027 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.56216
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.006734 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.10909
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.006758 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -1.1151
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.006765 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -1.1433
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.006736 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -1.4348
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.006729 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -1.5342
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.006769 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.081228
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.006769 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.12184
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.00845 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.4225
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.63003
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.63003
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.32713
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.32107
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.32713
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.34531
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.32713
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.32713
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.35136
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.35136
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.005767 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.069204
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.28515
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.30043
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.28515
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.28515
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.30043
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.28515
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.018223 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -1.2027
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010264 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -1.6525
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010264 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -1.7038
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010264 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -2.5455
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010264 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -5.6041
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010264 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -6.5998
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.010649 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -6.9325
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.010649 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -6.006
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.010649 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -6.3894
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010264 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.13343
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.005635 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.06762
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.19944
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.20355
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.19182
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.26925
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.10383
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.11967
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.11673
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.20531
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.10559
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.50096
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.86817
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.9114
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -1.0496
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.6615
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -1.4847
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -1.2642
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -1.2936
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.735
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.2646
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -1.3818
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -1.029
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.9261
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -1.0584
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.95256
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -1.4847
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -1.4259
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -1.5141
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -1.1172
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -1.176
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -1.176
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -2.5137
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.27942
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.021281 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 1.628
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.02249 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 1.7992
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.02249 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 0.8996
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.022684 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 1.8147
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.022448 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 1.7958
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.021451 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 1.7161
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.021125 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 1.7745
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.022684 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 1.8147
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -4.5583
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.025833 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 3.1
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.025833 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 6.0191
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.025833 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 4.3968
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -8.8767
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -7.3572
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -8.9566
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -4.5983
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -3.9985
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.026948 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 1.6169
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.022437 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.015925 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.023406 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.11235
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 0.99199
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 2.8437
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 3.5712
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 3.1479
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 2.7776
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 2.1295
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.025531 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 3.8296
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 2.8584
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 3.7985
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 4.7259
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 5.45
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.03162 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.024244 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.033375 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.8048
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -1.2532
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -2.127
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -2.9702
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -1.2955
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -1.2007
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.60036
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -2.9702
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -1.1375
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -1.3587
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.69516
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.1635
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.44749
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.20883
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.44749
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.1635
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.1635
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -4.6765
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -1.5799
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -1.7379
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -1.5799
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.03095 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.3714
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.030183 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.45275
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.030183 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.69421
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.029 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -1.392
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.029957 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.23966
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.031288 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -5.6318
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.031278 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -5.63
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.031351 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -5.6432
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.031351 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -5.6432
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.033378 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -3.3378
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.033378 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -3.3378
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.77697
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.77697
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.77697
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.49726
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.77697
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.77697
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.77697
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.46619
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.033378 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.033378 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -16.689
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.033378 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -16.689
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.033378 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.033097 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.018408 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.032522 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.032145 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:3592 WACOATCO 13591 COTTONB_ C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 3405 - 3412 and 3409 - 3414 | [7 empty] | 17.3572
Number of Bus | Name of Bus | ID | Max MW | L:3592 WACOATCO 13591 COTTONB_ C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 3405 - 3412 and 3409 - 3414 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.04599 | north | Y | 0.01704 | 0.085898 | 0.020364 | 0.054517 | 0.01704 | North | N | 0.01704 | 0
239 | BOSQUESW | 1 | 149 | 0.04599 | north | Y | 0.01704 | 0.085898 | 0.020364 | 0.054517 | 0.01704 | North | N | 0.01704 | 0
244 | WHITNYDM | 1 | 15 | 0.038591 | north | N | 0.0096408 | 0.078499 | 0.012965 | 0.047118 | 0.0096408 | North | N | 0.0096408 | 0
245 | WHITNYDM | 2 | 15 | 0.038591 | north | N | 0.0096408 | 0.078499 | 0.012965 | 0.047118 | 0.0096408 | North | N | 0.0096408 | 0
247 | BOSQUESW | 2 | 153 | 0.04599 | north | Y | 0.01704 | 0.085898 | 0.020364 | 0.054517 | 0.01704 | North | N | 0.01704 | 0
251 | BOSQUESW | 2 | 150 | 0.040679 | north | Y | 0.011729 | 0.080587 | 0.015053 | 0.049206 | 0.011729 | North | N | 0.011729 | 0
253 | BOSQUESW | 2 | 80 | 0.040679 | north | Y | 0.011729 | 0.080587 | 0.015053 | 0.049206 | 0.011729 | North | N | 0.011729 | 0
332 | RWMILLER | 1 | 73 | 0.030092 | north | Y | 0.0011418 | 0.07 | 0.0044662 | 0.038619 | 0.0011418 | North | N | 0.0011418 | 0
333 | RWMILLER | 2 | 119 | 0.030092 | north | Y | 0.0011418 | 0.07 | 0.0044662 | 0.038619 | 0.0011418 | North | N | 0.0011418 | 0
334 | RWMILLER | 3 | 205 | 0.030092 | north | Y | 0.0011418 | 0.07 | 0.0044662 | 0.038619 | 0.0011418 | North | N | 0.0011418 | 0
335 | RWMILLER | 4 | 102 | 0.030092 | north | Y | 0.0011418 | 0.07 | 0.0044662 | 0.038619 | 0.0011418 | North | N | 0.0011418 | 0
336 | RWMILLER | 5 | 96 | 0.030092 | north | Y | 0.0011418 | 0.07 | 0.0044662 | 0.038619 | 0.0011418 | North | N | 0.0011418 | 0
344 | MRSSHPRD | 1 | 12 | 0.02954 | north | N | 0.00058983 | 0.069448 | 0.0039142 | 0.038067 | 0.00058983 | North | N | 0.00058983 | 0
345 | MRSSHPRD | 2 | 12 | 0.02954 | north | N | 0.00058983 | 0.069448 | 0.0039142 | 0.038067 | 0.00058983 | North | N | 0.00058983 | 0
366 | JNSNCNTY | 1 | 168 | 0.032063 | north | Y | 0.0031128 | 0.071971 | 0.0064372 | 0.04059 | 0.0031128 | North | N | 0.0031128 | 0
367 | JNSNCNTY | 2 | 90 | 0.032063 | north | Y | 0.0031128 | 0.071971 | 0.0064372 | 0.04059 | 0.0031128 | North | N | 0.0031128 | 0
503 | NTHTEXAS | 1 | 18 | 0.030257 | north | Y | 0.0013068 | 0.070165 | 0.0046312 | 0.038784 | 0.0013068 | North | N | 0.0013068 | 0
504 | NTHTEXAS | 2 | 18 | 0.030257 | north | Y | 0.0013068 | 0.070165 | 0.0046312 | 0.038784 | 0.0013068 | North | N | 0.0013068 | 0
505 | NTHTEXAS | 3 | 38 | 0.030257 | north | Y | 0.0013068 | 0.070165 | 0.0046312 | 0.038784 | 0.0013068 | North | N | 0.0013068 | 0
580 | JCKCNTY8 | 1 | 288 | 0.03018 | north | Y | 0.0012298 | 0.070088 | 0.0045542 | 0.038707 | 0.0012298 | North | N | 0.0012298 | 0
581 | JCKCNTY8 | 2 | 147 | 0.03018 | north | Y | 0.0012298 | 0.070088 | 0.0045542 | 0.038707 | 0.0012298 | North | N | 0.0012298 | 0
582 | JCKCNTY8 | 3 | 147 | 0.03018 | north | Y | 0.0012298 | 0.070088 | 0.0045542 | 0.038707 | 0.0012298 | North | N | 0.0012298 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.03007 | north | Y | 0.0011198 | 0.069978 | 0.0044442 | 0.038597 | 0.0011198 | North | N | 0.0011198 | 0
837 | NEWMAN_G | 1 | 40 | 0.030015 | north | Y | 0.0010648 | 0.069923 | 0.0043892 | 0.038542 | 0.0010648 | North | N | 0.0010648 | 0
842 | OLINGER_ | 1 | 79 | 0.03 | north | Y | 0.0010498 | 0.069908 | 0.0043742 | 0.038527 | 0.0010498 | North | N | 0.0010498 | 0
843 | OLINGER_ | 1 | 106 | 0.03 | north | Y | 0.0010498 | 0.069908 | 0.0043742 | 0.038527 | 0.0010498 | North | N | 0.0010498 | 0
844 | OLINGER_ | 1 | 146 | 0.03 | north | Y | 0.0010498 | 0.069908 | 0.0043742 | 0.038527 | 0.0010498 | North | N | 0.0010498 | 0
845 | OLINGER_ | 1 | 76 | 0.03 | north | Y | 0.0010498 | 0.069908 | 0.0043742 | 0.038527 | 0.0010498 | North | N | 0.0010498 | 0
923 | SPENCER_ | 1 | 60 | 0.030209 | north | Y | 0.0012588 | 0.070117 | 0.0045832 | 0.038736 | 0.0012588 | North | N | 0.0012588 | 0
924 | SPENCER_ | 1 | 63 | 0.030209 | north | Y | 0.0012588 | 0.070117 | 0.0045832 | 0.038736 | 0.0012588 | North | N | 0.0012588 | 0
948 | STEAM1 | 1 | 20 | 0.02997 | north | Y | 0.0010198 | 0.069878 | 0.0043442 | 0.038497 | 0.0010198 | North | N | 0.0010198 | 0
949 | STEAM2 | 1 | 25 | 0.02997 | north | Y | 0.0010198 | 0.069878 | 0.0043442 | 0.038497 | 0.0010198 | North | N | 0.0010198 | 0
950 | STEAM3 | 1 | 41 | 0.02997 | north | Y | 0.0010198 | 0.069878 | 0.0043442 | 0.038497 | 0.0010198 | North | N | 0.0010198 | 0
990 | GIBN_CRE | 1 | 463 | 0.01096 | north | Y | -0.01799 | 0.050868 | -0.014666 | 0.019487 | 0.014666 | west | Y | 0.01799 | 1.5392
1002 | PBCTAGE_ | A | 66 | 0.025149 | west | Y | -0.0038012 | 0.065057 | -0.00047676 | 0.033676 | 0.00047676 | west | N | 0.00047676 | 0
1003 | PBCTBGE_ | B | 65 | 0.025149 | west | Y | -0.0038012 | 0.065057 | -0.00047676 | 0.033676 | 0.00047676 | west | N | 0.00047676 | 0
1004 | PBCTCGE_ | C | 67 | 0.025149 | west | Y | -0.0038012 | 0.065057 | -0.00047676 | 0.033676 | 0.00047676 | west | N | 0.00047676 | 0
1005 | PBCTDGE_ | D | 67 | 0.025149 | west | Y | -0.0038012 | 0.065057 | -0.00047676 | 0.033676 | 0.00047676 | west | N | 0.00047676 | 0
1006 | PBCTEGE_ | E | 67 | 0.025149 | west | Y | -0.0038012 | 0.065057 | -0.00047676 | 0.033676 | 0.00047676 | west | N | 0.00047676 | 0
1007 | PB5GEN_6 | MB | 114 | 0.025149 | west | Y | -0.0038012 | 0.065057 | -0.00047676 | 0.033676 | 0.00047676 | west | N | 0.00047676 | 0
1008 | PB6GEN_7 | MB | 515 | 0.025149 | west | Y | -0.0038012 | 0.065057 | -0.00047676 | 0.033676 | 0.00047676 | west | N | 0.00047676 | 0
1039 | MRGNAG_1 | A | 66 | 0.026106 | west | Y | -0.0028442 | 0.066014 | 0.00048024 | 0.034633 | 0.00048024 | west | N | 0.00048024 | 0
1040 | MRGNBG_2 | B | 69 | 0.026106 | west | Y | -0.0028442 | 0.066014 | 0.00048024 | 0.034633 | 0.00048024 | west | N | 0.00048024 | 0
1041 | MRGNCG_3 | C | 69 | 0.026106 | west | Y | -0.0028442 | 0.066014 | 0.00048024 | 0.034633 | 0.00048024 | west | N | 0.00048024 | 0
1042 | MRGNDG_4 | D | 67 | 0.026106 | west | Y | -0.0028442 | 0.066014 | 0.00048024 | 0.034633 | 0.00048024 | west | N | 0.00048024 | 0
1043 | MRGNEG_5 | E | 67 | 0.026106 | west | Y | -0.0028442 | 0.066014 | 0.00048024 | 0.034633 | 0.00048024 | west | N | 0.00048024 | 0
1044 | MRGNFG_6 | F | 65 | 0.026106 | west | Y | -0.0028442 | 0.066014 | 0.00048024 | 0.034633 | 0.00048024 | west | N | 0.00048024 | 0
1045 | CALENG1G | 1 | 70 | 0.025969 | west | N | -0.0029812 | 0.065877 | 0.00034324 | 0.034496 | 0.00034324 | west | N | 0.00034324 | 0
1046 | CALENG2G | 2 | 73.4 | 0.025969 | west | N | -0.0029812 | 0.065877 | 0.00034324 | 0.034496 | 0.00034324 | west | N | 0.00034324 | 0
1047 | CALENG3G | 3 | 70.4 | 0.025969 | west | N | -0.0029812 | 0.065877 | 0.00034324 | 0.034496 | 0.00034324 | west | N | 0.00034324 | 0
1058 | LONGSHOR | 1 | 150 | 0.026046 | west | Y | -0.0029042 | 0.065954 | 0.00042024 | 0.034573 | 0.00042024 | west | N | 0.00042024 | 0
1058 | LONGSHOR | 2 | 220 | 0.026046 | west | Y | -0.0029042 | 0.065954 | 0.00042024 | 0.034573 | 0.00042024 | west | N | 0.00042024 | 0
1061 | CIELOGEN | 1 | 99 | 0.026162 | west | Y | -0.0027882 | 0.06607 | 0.00053624 | 0.034689 | 0.00053624 | west | N | 0.00053624 | 0
1062 | CIELOGEN | 1 | 61 | 0.026162 | west | Y | -0.0027882 | 0.06607 | 0.00053624 | 0.034689 | 0.00053624 | west | N | 0.00053624 | 0
1068 | SCURRYCW | 1 | 141 | 0.026155 | west | Y | -0.0027952 | 0.066063 | 0.00052924 | 0.034682 | 0.00052924 | west | N | 0.00052924 | 0
1069 | KINDERMG | 1 | 25 | 0.026162 | west | N | -0.0027882 | 0.06607 | 0.00053624 | 0.034689 | 0.00053624 | west | N | 0.00053624 | 0
1070 | KINDERMG | 1 | 45.7 | 0.026162 | west | N | -0.0027882 | 0.06607 | 0.00053624 | 0.034689 | 0.00053624 | west | N | 0.00053624 | 0
1071 | KINDERMG | 1 | 45.7 | 0.026162 | west | N | -0.0027882 | 0.06607 | 0.00053624 | 0.034689 | 0.00053624 | west | N | 0.00053624 | 0
1073 | SCURRYCW | 2 | 120 | 0.026155 | west | Y | -0.0027952 | 0.066063 | 0.00052924 | 0.034682 | 0.00052924 | west | N | 0.00052924 | 0
1320 | BSP 1 | 1 | 25.8 | 0.025701 | west | N | -0.0032492 | 0.065609 | 7.5239e-05 | 0.034228 | 7.5239e-05 | west | N | 7.5239e-05 | 0
1326 | STANTONW | 1 | 100.5 | 0.025644 | west | Y | -0.0033062 | 0.065552 | 1.8239e-05 | 0.034171 | 1.8239e-05 | west | N | 1.8239e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.025875 | west | Y | -0.0030752 | 0.065783 | 0.00024924 | 0.034402 | 0.00024924 | west | N | 0.00024924 | 0
1328 | OCOTILLO | 1 | 58 | 0.02564 | west | Y | -0.0033102 | 0.065548 | 1.4239e-05 | 0.034167 | 1.4239e-05 | west | N | 1.4239e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.025706 | west | Y | -0.0032442 | 0.065614 | 8.0239e-05 | 0.034233 | 8.0239e-05 | west | N | 8.0239e-05 | 0
1343 | TRENTIPP | 1 | 150 | 0.026253 | west | Y | -0.0026972 | 0.066161 | 0.00062724 | 0.03478 | 0.00062724 | west | N | 0.00062724 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.025291 | west | Y | -0.0036592 | 0.065199 | -0.00033476 | 0.033818 | 0.00033476 | west | N | 0.00033476 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.025291 | west | Y | -0.0036592 | 0.065199 | -0.00033476 | 0.033818 | 0.00033476 | west | N | 0.00033476 | 0
1354 | AEPWIND_ | 1 | 101 | 0.026253 | west | Y | -0.0026972 | 0.066161 | 0.00062724 | 0.03478 | 0.00062724 | west | N | 0.00062724 | 0
1360 | GUNSIGHT | 1 | 120 | 0.025887 | west | Y | -0.0030632 | 0.065795 | 0.00026124 | 0.034414 | 0.00026124 | west | N | 0.00026124 | 0
1432 | GRHAMSES | 2 | 366 | 0.02891 | north | Y | -4.0171e-05 | 0.068818 | 0.0032842 | 0.037437 | 4.0171e-05 | North | N | 4.0171e-05 | 0
1433 | GRHAMSES | 1 | 242 | 0.028818 | north | Y | -0.00013217 | 0.068726 | 0.0031922 | 0.037345 | 0.00013217 | North | N | 0.00013217 | 0
1437 | MESQUITW | 1 | 400 | 0.027489 | west | Y | -0.0014612 | 0.067397 | 0.0018632 | 0.036016 | 0.0014612 | North | Y | 0.0018632 | 0.16083
1438 | MESQUITW | 1 | 236 | 0.027491 | west | Y | -0.0014592 | 0.067399 | 0.0018652 | 0.036018 | 0.0014592 | North | Y | 0.0018652 | 0.095832
1442 | COKFIELD | 1 | 165 | 0.027832 | west | Y | -0.0011182 | 0.06774 | 0.0022062 | 0.036359 | 0.0011182 | North | Y | 0.0022062 | 0.17953
1453 | WCPWRCO_ | 1 | 204 | 0.029713 | north | Y | 0.00076283 | 0.069621 | 0.0040872 | 0.03824 | 0.00076283 | North | N | 0.00076283 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.029713 | north | Y | 0.00076283 | 0.069621 | 0.0040872 | 0.03824 | 0.00076283 | North | N | 0.00076283 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.029713 | north | Y | 0.00076283 | 0.069621 | 0.0040872 | 0.03824 | 0.00076283 | North | N | 0.00076283 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.028952 | west | Y | 1.8294e-06 | 0.06886 | 0.0033262 | 0.037479 | 1.8294e-06 | North | Y | 0.0033262 | 0.066488
1479 | WFCOGEN_ | 2 | 20 | 0.028952 | west | Y | 1.8294e-06 | 0.06886 | 0.0033262 | 0.037479 | 1.8294e-06 | North | Y | 0.0033262 | 0.066488
1482 | WFCOGEN_ | 1 | 20 | 0.028952 | west | Y | 1.8294e-06 | 0.06886 | 0.0033262 | 0.037479 | 1.8294e-06 | North | Y | 0.0033262 | 0.066488
1482 | WFCOGEN_ | 2 | 17 | 0.028952 | west | Y | 1.8294e-06 | 0.06886 | 0.0033262 | 0.037479 | 1.8294e-06 | North | Y | 0.0033262 | 0.056515
1600 | BARTNWND | 1 | 120 | 0.029508 | north | Y | 0.00055783 | 0.069416 | 0.0038822 | 0.038035 | 0.00055783 | North | N | 0.00055783 | 0
1643 | SLSTR1PP | 1 | 60 | 0.028928 | north | Y | -2.2171e-05 | 0.068836 | 0.0033022 | 0.037455 | 2.2171e-05 | North | N | 2.2171e-05 | 0
1675 | PEC_1G | 1 | 75 | 0.029982 | north | N | 0.0010318 | 0.06989 | 0.0043562 | 0.038509 | 0.0010318 | North | N | 0.0010318 | 0
1676 | PEC_2G | 2 | 79.6 | 0.029982 | north | N | 0.0010318 | 0.06989 | 0.0043562 | 0.038509 | 0.0010318 | North | N | 0.0010318 | 0
1677 | PEC_3G | 3 | 88.4 | 0.029982 | north | N | 0.0010318 | 0.06989 | 0.0043562 | 0.038509 | 0.0010318 | North | N | 0.0010318 | 0
1678 | LAMARPWR | 1 | 160 | 0.029998 | north | Y | 0.0010478 | 0.069906 | 0.0043722 | 0.038525 | 0.0010478 | North | N | 0.0010478 | 0
1679 | LAMARPWR | 2 | 156 | 0.029998 | north | Y | 0.0010478 | 0.069906 | 0.0043722 | 0.038525 | 0.0010478 | North | N | 0.0010478 | 0
1680 | LAMARPWR | 3 | 196 | 0.029998 | north | Y | 0.0010478 | 0.069906 | 0.0043722 | 0.038525 | 0.0010478 | North | N | 0.0010478 | 0
1681 | LAMARPWR | 4 | 156 | 0.029998 | north | Y | 0.0010478 | 0.069906 | 0.0043722 | 0.038525 | 0.0010478 | North | N | 0.0010478 | 0
1682 | LAMARPWR | 5 | 157 | 0.029998 | north | Y | 0.0010478 | 0.069906 | 0.0043722 | 0.038525 | 0.0010478 | North | N | 0.0010478 | 0
1683 | LAMARPWR | 6 | 198 | 0.029998 | north | Y | 0.0010478 | 0.069906 | 0.0043722 | 0.038525 | 0.0010478 | North | N | 0.0010478 | 0
1687 | VALLEY_1 | 1 | 170 | 0.030033 | north | Y | 0.0010828 | 0.069941 | 0.0044072 | 0.03856 | 0.0010828 | North | N | 0.0010828 | 0
1688 | VALLEY_2 | 2 | 520 | 0.030033 | north | Y | 0.0010828 | 0.069941 | 0.0044072 | 0.03856 | 0.0010828 | North | N | 0.0010828 | 0
1689 | VALLEY_3 | 3 | 370 | 0.030013 | north | Y | 0.0010628 | 0.069921 | 0.0043872 | 0.03854 | 0.0010628 | North | N | 0.0010628 | 0
1701 | MOSES_1G | 1 | 558 | 0.029973 | north | Y | 0.0010228 | 0.069881 | 0.0043472 | 0.0385 | 0.0010228 | North | N | 0.0010228 | 0
1702 | MOSES_2G | 2 | 579 | 0.029973 | north | Y | 0.0010228 | 0.069881 | 0.0043472 | 0.0385 | 0.0010228 | North | N | 0.0010228 | 0
1703 | MOSES_3G | 3 | 808 | 0.029973 | north | Y | 0.0010228 | 0.069881 | 0.0043472 | 0.0385 | 0.0010228 | North | N | 0.0010228 | 0
1861 | EAGLEMNT | MB | 112 | 0.030522 | north | Y | 0.0015718 | 0.07043 | 0.0048962 | 0.039049 | 0.0015718 | North | N | 0.0015718 | 0
1862 | EAGLEMNT | MB | 100 | 0.030522 | north | Y | 0.0015718 | 0.07043 | 0.0048962 | 0.039049 | 0.0015718 | North | N | 0.0015718 | 0
1863 | EAGLEMNT | MB | 378 | 0.030522 | north | Y | 0.0015718 | 0.07043 | 0.0048962 | 0.039049 | 0.0015718 | North | N | 0.0015718 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.03061 | north | Y | 0.0016598 | 0.070518 | 0.0049842 | 0.039137 | 0.0016598 | North | N | 0.0016598 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.03061 | north | Y | 0.0016598 | 0.070518 | 0.0049842 | 0.039137 | 0.0016598 | North | N | 0.0016598 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.03061 | north | Y | 0.0016598 | 0.070518 | 0.0049842 | 0.039137 | 0.0016598 | North | N | 0.0016598 | 0
1889 | DECRDOVA | MB | 770 | 0.03076 | north | Y | 0.0018098 | 0.070668 | 0.0051342 | 0.039287 | 0.0018098 | North | N | 0.0018098 | 0
1892 | DECRDOVA | A | 70 | 0.031084 | north | Y | 0.0021338 | 0.070992 | 0.0054582 | 0.039611 | 0.0021338 | North | N | 0.0021338 | 0
1893 | DECRDOVA | B | 69 | 0.031084 | north | Y | 0.0021338 | 0.070992 | 0.0054582 | 0.039611 | 0.0021338 | North | N | 0.0021338 | 0
1894 | DECRDOVA | C | 69 | 0.031084 | north | Y | 0.0021338 | 0.070992 | 0.0054582 | 0.039611 | 0.0021338 | North | N | 0.0021338 | 0
1895 | DECRDOVA | D | 68 | 0.031084 | north | Y | 0.0021338 | 0.070992 | 0.0054582 | 0.039611 | 0.0021338 | North | N | 0.0021338 | 0
1898 | COMCHEPK | 1 | 1157 | 0.030486 | north | N | 0.0015358 | 0.070394 | 0.0048602 | 0.039013 | 0.0015358 | North | N | 0.0015358 | 0
1899 | COMCHEPK | 2 | 1158 | 0.030486 | north | N | 0.0015358 | 0.070394 | 0.0048602 | 0.039013 | 0.0015358 | North | N | 0.0015358 | 0
1937 | MDLTHELP | 5 | 224 | 0.032388 | north | Y | 0.0034378 | 0.072296 | 0.0067622 | 0.040915 | 0.0034378 | North | N | 0.0034378 | 0
1938 | MDLTHELP | 6 | 226 | 0.032388 | north | Y | 0.0034378 | 0.072296 | 0.0067622 | 0.040915 | 0.0034378 | North | N | 0.0034378 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.032355 | north | Y | 0.0034048 | 0.072263 | 0.0067292 | 0.040882 | 0.0034048 | North | N | 0.0034048 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.032355 | north | Y | 0.0034048 | 0.072263 | 0.0067292 | 0.040882 | 0.0034048 | North | N | 0.0034048 | 0
1943 | MDLTHELP | 3 | 212 | 0.032388 | north | Y | 0.0034378 | 0.072296 | 0.0067622 | 0.040915 | 0.0034378 | North | N | 0.0034378 | 0
1944 | MDLTHELP | 4 | 211 | 0.032388 | north | Y | 0.0034378 | 0.072296 | 0.0067622 | 0.040915 | 0.0034378 | North | N | 0.0034378 | 0
1947 | HANDLEY_ | 3 | 395 | 0.031121 | north | Y | 0.0021708 | 0.071029 | 0.0054952 | 0.039648 | 0.0021708 | North | N | 0.0021708 | 0
1948 | HANDLEY_ | 4 | 435 | 0.031084 | north | Y | 0.0021338 | 0.070992 | 0.0054582 | 0.039611 | 0.0021338 | North | N | 0.0021338 | 0
1949 | HANDLEY_ | 5 | 435 | 0.031121 | north | Y | 0.0021708 | 0.071029 | 0.0054952 | 0.039648 | 0.0021708 | North | N | 0.0021708 | 0
2371 | COLLIN_1 | MB | 138 | 0.030165 | north | Y | 0.0012148 | 0.070073 | 0.0045392 | 0.038692 | 0.0012148 | North | N | 0.0012148 | 0
2413 | MTCK6_G | 6 | 118 | 0.030484 | north | Y | 0.0015338 | 0.070392 | 0.0048582 | 0.039011 | 0.0015338 | North | N | 0.0015338 | 0
2414 | MTCK7_G | 7 | 115 | 0.030484 | north | Y | 0.0015338 | 0.070392 | 0.0048582 | 0.039011 | 0.0015338 | North | N | 0.0015338 | 0
2417 | MTCK8_G | 8 | 556 | 0.030484 | north | Y | 0.0015338 | 0.070392 | 0.0048582 | 0.039011 | 0.0015338 | North | N | 0.0015338 | 0
2451 | LKHB1_G | 1 | 388 | 0.029995 | north | Y | 0.0010448 | 0.069903 | 0.0043692 | 0.038522 | 0.0010448 | North | N | 0.0010448 | 0
2452 | LKHB2_G | 2 | 515 | 0.029995 | north | Y | 0.0010448 | 0.069903 | 0.0043692 | 0.038522 | 0.0010448 | North | N | 0.0010448 | 0
3097 | MARTLAKE | 1 | 785 | 0.028873 | north | Y | -7.7171e-05 | 0.068781 | 0.0032472 | 0.0374 | 7.7171e-05 | North | N | 7.7171e-05 | 0
3098 | MARTLAKE | 2 | 795 | 0.028873 | north | Y | -7.7171e-05 | 0.068781 | 0.0032472 | 0.0374 | 7.7171e-05 | North | N | 7.7171e-05 | 0
3099 | MARTLAKE | 3 | 780 | 0.028873 | north | Y | -7.7171e-05 | 0.068781 | 0.0032472 | 0.0374 | 7.7171e-05 | North | N | 7.7171e-05 | 0
3107 | STRYKER_ | 1 | 182 | 0.028548 | north | Y | -0.00040217 | 0.068456 | 0.0029222 | 0.037075 | 0.00040217 | North | N | 0.00040217 | 0
3108 | STRYKER_ | 2 | 484 | 0.028548 | north | Y | -0.00040217 | 0.068456 | 0.0029222 | 0.037075 | 0.00040217 | North | N | 0.00040217 | 0
3126 | TRINIDAD | 1 | 224 | 0.030564 | north | Y | 0.0016138 | 0.070472 | 0.0049382 | 0.039091 | 0.0016138 | North | N | 0.0016138 | 0
3309 | ASPN_G | 1 | 50 | 0.0286 | north | Y | -0.00035017 | 0.068508 | 0.0029742 | 0.037127 | 0.00035017 | North | N | 0.00035017 | 0
3348 | CHAMPION | MB | 42 | 0.028613 | north | N | -0.00033717 | 0.068521 | 0.0029872 | 0.03714 | 0.00033717 | North | N | 0.00033717 | 0
3381 | BBRN_1G | 1 | 615 | 0.026863 | north | Y | -0.0020872 | 0.066771 | 0.0012372 | 0.03539 | 0.0012372 | west | Y | 0.0020872 | 0.52271
3382 | BBRN_2G | 2 | 587 | 0.026863 | north | Y | -0.0020872 | 0.066771 | 0.0012372 | 0.03539 | 0.0012372 | west | Y | 0.0020872 | 0.49891
3403 | THOUSE_1 | MB | 537 | 0.047385 | north | Y | 0.018435 | 0.087293 | 0.021759 | 0.055912 | 0.018435 | North | N | 0.018435 | 0
3404 | THOUSE_2 | 2 | 787 | 0.047385 | north | Y | 0.018435 | 0.087293 | 0.021759 | 0.055912 | 0.018435 | North | N | 0.018435 | 0
3416 | LAKE_CRK | MB | 75 | 0.069442 | north | Y | 0.040492 | 0.10935 | 0.043816 | 0.077969 | 0.040492 | North | N | 0.040492 | 0
3417 | LAKE_CRK | MB | 222 | 0.069442 | north | Y | 0.040492 | 0.10935 | 0.043816 | 0.077969 | 0.040492 | North | N | 0.040492 | 0
3432 | SANDOW_4 | 4 | 569 | -0.059577 | south | Y | -0.088527 | -0.019669 | -0.085203 | -0.05105 | 0.019669 | south | N | 0.019669 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.038005 | south | Y | -0.066955 | 0.0019028 | -0.063631 | -0.029478 | 0.0019028 | south | N | 0.0019028 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.038005 | south | Y | -0.066955 | 0.0019028 | -0.063631 | -0.029478 | 0.0019028 | south | N | 0.0019028 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.037992 | south | Y | -0.066942 | 0.0019158 | -0.063618 | -0.029465 | 0.0019158 | south | N | 0.0019158 | 0
5031 | BRA_VHBC | 1 | 46 | -0.038005 | south | Y | -0.066955 | 0.0019028 | -0.063631 | -0.029478 | 0.0019028 | south | N | 0.0019028 | 0
5032 | BRA_VHBC | 2 | 47 | -0.038005 | south | Y | -0.066955 | 0.0019028 | -0.063631 | -0.029478 | 0.0019028 | south | N | 0.0019028 | 0
5033 | BRA_VHBC | 3 | 46 | -0.038005 | south | Y | -0.066955 | 0.0019028 | -0.063631 | -0.029478 | 0.0019028 | south | N | 0.0019028 | 0
5034 | BRA_VHBC | 4 | 46 | -0.038005 | south | Y | -0.066955 | 0.0019028 | -0.063631 | -0.029478 | 0.0019028 | south | N | 0.0019028 | 0
5111 | CALAVER_ | 1 | 424 | -0.038075 | south | Y | -0.067025 | 0.0018328 | -0.063701 | -0.029548 | 0.0018328 | south | N | 0.0018328 | 0
5112 | CALAVER_ | 2 | 425 | -0.038075 | south | Y | -0.067025 | 0.0018328 | -0.063701 | -0.029548 | 0.0018328 | south | N | 0.0018328 | 0
5264 | LEON_LCP | 3 | 58 | -0.037784 | south | Y | -0.066734 | 0.0021238 | -0.06341 | -0.029257 | 0.0021238 | south | N | 0.0021238 | 0
5265 | LEON_LCP | 4 | 89 | -0.037784 | south | Y | -0.066734 | 0.0021238 | -0.06341 | -0.029257 | 0.0021238 | south | N | 0.0021238 | 0
5266 | LEON_LCP | 1 | 44 | -0.037784 | south | Y | -0.066734 | 0.0021238 | -0.06341 | -0.029257 | 0.0021238 | south | N | 0.0021238 | 0
5267 | LEON_LCP | 2 | 44 | -0.037784 | south | Y | -0.066734 | 0.0021238 | -0.06341 | -0.029257 | 0.0021238 | south | N | 0.0021238 | 0
5268 | LEON_LCP | 3 | 43 | -0.037784 | south | Y | -0.066734 | 0.0021238 | -0.06341 | -0.029257 | 0.0021238 | south | N | 0.0021238 | 0
5269 | LEON_LCP | 4 | 45 | -0.037784 | south | Y | -0.066734 | 0.0021238 | -0.06341 | -0.029257 | 0.0021238 | south | N | 0.0021238 | 0
5396 | CALAVER_ | 1 | 412 | -0.038049 | south | Y | -0.066999 | 0.0018588 | -0.063675 | -0.029522 | 0.0018588 | south | N | 0.0018588 | 0
5397 | CALAVER_ | 2 | 400 | -0.038049 | south | Y | -0.066999 | 0.0018588 | -0.063675 | -0.029522 | 0.0018588 | south | N | 0.0018588 | 0
5401 | CALAVER_ | 1 | 546 | -0.037705 | south | Y | -0.066655 | 0.0022028 | -0.063331 | -0.029178 | 0.0022028 | south | N | 0.0022028 | 0
5402 | CALAVER_ | 2 | 750 | -0.037705 | south | Y | -0.066655 | 0.0022028 | -0.063331 | -0.029178 | 0.0022028 | south | N | 0.0022028 | 0
5436 | TUTTL_WB | MB | 61 | -0.038176 | south | Y | -0.067126 | 0.0017318 | -0.063802 | -0.029649 | 0.0017318 | south | N | 0.0017318 | 0
5438 | TUTTL_WB | MB | 95 | -0.038176 | south | Y | -0.067126 | 0.0017318 | -0.063802 | -0.029649 | 0.0017318 | south | N | 0.0017318 | 0
5439 | TUTTL_WB | MB | 151 | -0.038176 | south | Y | -0.067126 | 0.0017318 | -0.063802 | -0.029649 | 0.0017318 | south | N | 0.0017318 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.037909 | south | Y | -0.066859 | 0.0019988 | -0.063535 | -0.029382 | 0.0019988 | south | N | 0.0019988 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.037909 | south | Y | -0.066859 | 0.0019988 | -0.063535 | -0.029382 | 0.0019988 | south | N | 0.0019988 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.037909 | south | Y | -0.066859 | 0.0019988 | -0.063535 | -0.029382 | 0.0019988 | south | N | 0.0019988 | 0
5503 | RAYBURNG | 1 | 22 | -0.030449 | south | Y | -0.059399 | 0.0094588 | -0.056075 | -0.021922 | 0.0094588 | south | N | 0.0094588 | 0
5505 | RAYBURNG | 1 | 11 | -0.030449 | south | Y | -0.059399 | 0.0094588 | -0.056075 | -0.021922 | 0.0094588 | south | N | 0.0094588 | 0
5506 | RAYBURNG | 1 | 11 | -0.030449 | south | Y | -0.059399 | 0.0094588 | -0.056075 | -0.021922 | 0.0094588 | south | N | 0.0094588 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.030731 | south | Y | -0.059681 | 0.0091768 | -0.056357 | -0.022204 | 0.0091768 | south | N | 0.0091768 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.030731 | south | Y | -0.059681 | 0.0091768 | -0.056357 | -0.022204 | 0.0091768 | south | N | 0.0091768 | 0
5511 | RAYBURNC | 1 | 46 | -0.030731 | south | Y | -0.059681 | 0.0091768 | -0.056357 | -0.022204 | 0.0091768 | south | N | 0.0091768 | 0
5512 | RAYBURNC | 1 | 48 | -0.030731 | south | Y | -0.059681 | 0.0091768 | -0.056357 | -0.022204 | 0.0091768 | south | N | 0.0091768 | 0
5728 | FALCONHY | 2 | 12 | -0.032143 | south | N | -0.061093 | 0.0077648 | -0.057769 | -0.023616 | 0.0077648 | south | N | 0.0077648 | 0
5729 | FALCONHY | 3 | 11 | -0.032143 | south | N | -0.061093 | 0.0077648 | -0.057769 | -0.023616 | 0.0077648 | south | N | 0.0077648 | 0
5890 | PEARSALL | 1 | 24 | -0.033642 | south | Y | -0.062592 | 0.0062658 | -0.059268 | -0.025115 | 0.0062658 | south | N | 0.0062658 | 0
5891 | PEARSALL | 1 | 24 | -0.033642 | south | Y | -0.062592 | 0.0062658 | -0.059268 | -0.025115 | 0.0062658 | south | N | 0.0062658 | 0
5892 | PEARSALL | 1 | 23 | -0.033642 | south | Y | -0.062592 | 0.0062658 | -0.059268 | -0.025115 | 0.0062658 | south | N | 0.0062658 | 0
5903 | SANMIGUE | 1 | 396 | -0.035634 | south | Y | -0.064584 | 0.0042738 | -0.06126 | -0.027107 | 0.0042738 | south | N | 0.0042738 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.019463 | houston | N | -0.048413 | 0.020445 | -0.045089 | -0.010936 | 0.010936 | houston | N | 0.010936 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.019463 | houston | N | -0.048413 | 0.020445 | -0.045089 | -0.010936 | 0.010936 | houston | N | 0.010936 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.02895 | 0
5932 | SI_RAY9 | 9 | 38 | -0.03162 | south | Y | -0.06057 | 0.0082878 | -0.057246 | -0.023093 | 0.0082878 | south | N | 0.0082878 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.03162 | south | Y | -0.06057 | 0.0082878 | -0.057246 | -0.023093 | 0.0082878 | south | N | 0.0082878 | 0
5934 | SI_RAY5 | 5 | 15 | -0.03162 | south | Y | -0.06057 | 0.0082878 | -0.057246 | -0.023093 | 0.0082878 | south | N | 0.0082878 | 0
5935 | SI_RAY10 | 10 | 47 | -0.03162 | south | Y | -0.06057 | 0.0082878 | -0.057246 | -0.023093 | 0.0082878 | south | N | 0.0082878 | 0
6016 | SWMESA | 1 | 75 | 0.02249 | west | Y | -0.0064602 | 0.062398 | -0.0031358 | 0.031017 | 0.0031358 | west | N | 0.0031358 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.025626 | 0
6144 | MCADOO1A | 1 | 150 | 0.026549 | west | Y | -0.0024012 | 0.066457 | 0.00092324 | 0.035076 | 0.00092324 | west | N | 0.00092324 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.024985 | west | Y | -0.0039652 | 0.064893 | -0.00064076 | 0.033512 | 0.00064076 | west | N | 0.00064076 | 0
6476 | LANGFORD | 1 | 150 | 0.011007 | west | Y | -0.017943 | 0.050915 | -0.014619 | 0.019534 | 0.014619 | west | N | 0.014619 | 0
6637 | SNYDERW1 | 1 | 63 | 0.026131 | west | Y | -0.0028192 | 0.066039 | 0.00050524 | 0.034658 | 0.00050524 | west | N | 0.00050524 | 0
6752 | OKLA0A | 1 | 649.7 | 0.028095 | west | Y | -0.00085517 | 0.068003 | 0.0024692 | 0.036622 | 0.00085517 | North | Y | 0.0024692 | 1.0487
6948 | DENISNDM | 1 | 40 | 0.030051 | north | N | 0.0011008 | 0.069959 | 0.0044252 | 0.038578 | 0.0011008 | North | N | 0.0011008 | 0
6948 | DENISNDM | 2 | 40 | 0.030051 | north | N | 0.0011008 | 0.069959 | 0.0044252 | 0.038578 | 0.0011008 | North | N | 0.0011008 | 0
7000 | L_FERGUS | 1 | 422 | -0.045366 | south | Y | -0.074316 | -0.0054582 | -0.070992 | -0.036839 | 0.0054582 | south | N | 0.0054582 | 0
7004 | L_SIMGID | 1 | 132 | -0.048044 | south | Y | -0.076994 | -0.0081362 | -0.07367 | -0.039517 | 0.0081362 | south | N | 0.0081362 | 0
7005 | L_SIMGID | 2 | 134 | -0.048044 | south | Y | -0.076994 | -0.0081362 | -0.07367 | -0.039517 | 0.0081362 | south | N | 0.0081362 | 0
7006 | L_SIMGID | 3 | 323 | -0.048044 | south | Y | -0.076994 | -0.0081362 | -0.07367 | -0.039517 | 0.0081362 | south | N | 0.0081362 | 0
7007 | L_LOSTPI | 1 | 158 | -0.047735 | south | Y | -0.076685 | -0.0078272 | -0.073361 | -0.039208 | 0.0078272 | south | N | 0.0078272 | 0
7008 | L_LOSTPI | 2 | 160 | -0.047735 | south | Y | -0.076685 | -0.0078272 | -0.073361 | -0.039208 | 0.0078272 | south | N | 0.0078272 | 0
7009 | L_LOSTPI | 3 | 175 | -0.047735 | south | Y | -0.076685 | -0.0078272 | -0.073361 | -0.039208 | 0.0078272 | south | N | 0.0078272 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.042637 | south | Y | -0.071587 | -0.0027292 | -0.068263 | -0.03411 | 0.0027292 | south | N | 0.0027292 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.042637 | south | Y | -0.071587 | -0.0027292 | -0.068263 | -0.03411 | 0.0027292 | south | N | 0.0027292 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.042595 | south | Y | -0.071545 | -0.0026872 | -0.068221 | -0.034068 | 0.0026872 | south | N | 0.0026872 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.041882 | south | Y | -0.070832 | -0.0019742 | -0.067508 | -0.033355 | 0.0019742 | south | N | 0.0019742 | 0
7015 | L_HAYSEN | 2 | 225 | -0.041882 | south | Y | -0.070832 | -0.0019742 | -0.067508 | -0.033355 | 0.0019742 | south | N | 0.0019742 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.041882 | south | Y | -0.070832 | -0.0019742 | -0.067508 | -0.033355 | 0.0019742 | south | N | 0.0019742 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.041882 | south | Y | -0.070832 | -0.0019742 | -0.067508 | -0.033355 | 0.0019742 | south | N | 0.0019742 | 0
7020 | L_AUSTPL | 1 | 8 | -0.050557 | south | N | -0.079507 | -0.010649 | -0.076183 | -0.04203 | 0.010649 | south | N | 0.010649 | 0
7020 | L_AUSTPL | 2 | 8 | -0.050557 | south | N | -0.079507 | -0.010649 | -0.076183 | -0.04203 | 0.010649 | south | N | 0.010649 | 0
7022 | L_BUCHAN | 1 | 18 | -0.046352 | south | N | -0.075302 | -0.0064442 | -0.071978 | -0.037825 | 0.0064442 | south | N | 0.0064442 | 0
7023 | L_BUCHAN | 2 | 18 | -0.046352 | south | N | -0.075302 | -0.0064442 | -0.071978 | -0.037825 | 0.0064442 | south | N | 0.0064442 | 0
7024 | L_BUCHAN | 3 | 15 | -0.046352 | south | N | -0.075302 | -0.0064442 | -0.071978 | -0.037825 | 0.0064442 | south | N | 0.0064442 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.045262 | south | N | -0.074212 | -0.0053542 | -0.070888 | -0.036735 | 0.0053542 | south | N | 0.0053542 | 0
7028 | L_MARBFA | 1 | 18 | -0.046648 | south | N | -0.075598 | -0.0067402 | -0.072274 | -0.038121 | 0.0067402 | south | N | 0.0067402 | 0
7029 | L_MARBFA | 2 | 18 | -0.046648 | south | N | -0.075598 | -0.0067402 | -0.072274 | -0.038121 | 0.0067402 | south | N | 0.0067402 | 0
7031 | L_MARSFO | 1 | 35 | -0.049556 | south | N | -0.078506 | -0.0096482 | -0.075182 | -0.041029 | 0.0096482 | south | N | 0.0096482 | 0
7032 | L_MARSFO | 2 | 34 | -0.049556 | south | N | -0.078506 | -0.0096482 | -0.075182 | -0.041029 | 0.0096482 | south | N | 0.0096482 | 0
7033 | L_MARSFO | 3 | 35 | -0.049556 | south | N | -0.078506 | -0.0096482 | -0.075182 | -0.041029 | 0.0096482 | south | N | 0.0096482 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.045734 | south | N | -0.074684 | -0.0058262 | -0.07136 | -0.037207 | 0.0058262 | south | N | 0.0058262 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.045734 | south | N | -0.074684 | -0.0058262 | -0.07136 | -0.037207 | 0.0058262 | south | N | 0.0058262 | 0
7038 | L_DELAWA | 1 | 35 | 0.025173 | west | Y | -0.0037772 | 0.065081 | -0.00045276 | 0.0337 | 0.00045276 | west | N | 0.00045276 | 0
7038 | L_DELAWA | 2 | 30 | 0.025173 | west | Y | -0.0037772 | 0.065081 | -0.00045276 | 0.0337 | 0.00045276 | west | N | 0.00045276 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.043453 | south | Y | -0.072403 | -0.0035452 | -0.069079 | -0.034926 | 0.0035452 | south | N | 0.0035452 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.043453 | south | Y | -0.072403 | -0.0035452 | -0.069079 | -0.034926 | 0.0035452 | south | N | 0.0035452 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.043453 | south | Y | -0.072403 | -0.0035452 | -0.069079 | -0.034926 | 0.0035452 | south | N | 0.0035452 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.043453 | south | Y | -0.072403 | -0.0035452 | -0.069079 | -0.034926 | 0.0035452 | south | N | 0.0035452 | 0
7487 | L_CANYHY | 1 | 6 | -0.043249 | south | N | -0.072199 | -0.0033412 | -0.068875 | -0.034722 | 0.0033412 | south | N | 0.0033412 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.040653 | south | N | -0.069603 | -0.00074516 | -0.066279 | -0.032126 | 0.00074516 | south | N | 0.00074516 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.040653 | south | N | -0.069603 | -0.00074516 | -0.066279 | -0.032126 | 0.00074516 | south | N | 0.00074516 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.040653 | south | N | -0.069603 | -0.00074516 | -0.066279 | -0.032126 | 0.00074516 | south | N | 0.00074516 | 0
7609 | L_SCHUMA | 1 | 4 | -0.040044 | south | N | -0.068994 | -0.00013616 | -0.06567 | -0.031517 | 0.00013616 | south | N | 0.00013616 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.040114 | south | N | -0.069064 | -0.00020616 | -0.06574 | -0.031587 | 0.00020616 | south | N | 0.00020616 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.040114 | south | N | -0.069064 | -0.00020616 | -0.06574 | -0.031587 | 0.00020616 | south | N | 0.00020616 | 0
7800 | L_GUADGE | 1 | 147 | -0.03898 | south | Y | -0.06793 | 0.00092784 | -0.064606 | -0.030453 | 0.00092784 | south | N | 0.00092784 | 0
7801 | L_GUADGE | 2 | 138 | -0.03898 | south | Y | -0.06793 | 0.00092784 | -0.064606 | -0.030453 | 0.00092784 | south | N | 0.00092784 | 0
7802 | L_GUADGE | 3 | 140 | -0.03898 | south | Y | -0.06793 | 0.00092784 | -0.064606 | -0.030453 | 0.00092784 | south | N | 0.00092784 | 0
7803 | L_GUADGE | 4 | 147 | -0.03898 | south | Y | -0.06793 | 0.00092784 | -0.064606 | -0.030453 | 0.00092784 | south | N | 0.00092784 | 0
7804 | L_GUADGE | 5 | 182 | -0.03898 | south | Y | -0.06793 | 0.00092784 | -0.064606 | -0.030453 | 0.00092784 | south | N | 0.00092784 | 0
7805 | L_GUADGE | 6 | 198 | -0.03898 | south | Y | -0.06793 | 0.00092784 | -0.064606 | -0.030453 | 0.00092784 | south | N | 0.00092784 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.048236 | south | Y | -0.077186 | -0.0083282 | -0.073862 | -0.039709 | 0.0083282 | south | N | 0.0083282 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.048236 | south | Y | -0.077186 | -0.0083282 | -0.073862 | -0.039709 | 0.0083282 | south | N | 0.0083282 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.048236 | south | Y | -0.077186 | -0.0083282 | -0.073862 | -0.039709 | 0.0083282 | south | N | 0.0083282 | 0
7810 | L_RIONOG | 1 | 142 | -0.040396 | south | Y | -0.069346 | -0.00048816 | -0.066022 | -0.031869 | 0.00048816 | south | N | 0.00048816 | 0
7811 | L_RIONOG | 2 | 145 | -0.040396 | south | Y | -0.069346 | -0.00048816 | -0.066022 | -0.031869 | 0.00048816 | south | N | 0.00048816 | 0
7812 | L_RIONOG | 3 | 151 | -0.040396 | south | Y | -0.069346 | -0.00048816 | -0.066022 | -0.031869 | 0.00048816 | south | N | 0.00048816 | 0
7813 | L_RIONOG | 4 | 290 | -0.040396 | south | Y | -0.069346 | -0.00048816 | -0.066022 | -0.031869 | 0.00048816 | south | N | 0.00048816 | 0
8032 | AMISTADH | 1 | 33 | -0.018408 | south | N | -0.047358 | 0.0215 | -0.044034 | -0.0098807 | 0.0098807 | houston | Y | 0.0215 | 0
8033 | AMISTADH | 2 | 25 | -0.018408 | south | N | -0.047358 | 0.0215 | -0.044034 | -0.0098807 | 0.0098807 | houston | Y | 0.0215 | 0
8048 | FALCONHY | 1 | 12 | -0.032143 | south | N | -0.061093 | 0.0077648 | -0.057769 | -0.023616 | 0.0077648 | south | N | 0.0077648 | 0
8066 | DUP1V#1 | 1 | 73 | -0.030799 | south | N | -0.059749 | 0.0091088 | -0.056425 | -0.022272 | 0.0091088 | south | N | 0.0091088 | 0
8134 | FOR69CG0 | 1 | 79 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
8138 | FOR69CG0 | 2 | 81 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.039908 | 0
8147 | UCAR #2 | 10 | 28 | -0.029833 | south | N | -0.058783 | 0.010075 | -0.055459 | -0.021306 | 0.010075 | south | N | 0.010075 | 0
8148 | UCAR #1 | 2 | 7 | -0.029833 | south | N | -0.058783 | 0.010075 | -0.055459 | -0.021306 | 0.010075 | south | N | 0.010075 | 0
8153 | FOR69CG0 | 3 | 79 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
8154 | FOR69CG0 | 4 | 80 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
8156 | FOR69CG0 | 6 | 25 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
8157 | FOR69CG0 | 7 | 46 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
8161 | COLETOU1 | 1 | 629 | -0.032652 | south | Y | -0.061602 | 0.0072558 | -0.058278 | -0.024125 | 0.0072558 | south | N | 0.0072558 | 0
8173 | VICEC51A | 5 | 144 | -0.031151 | south | Y | -0.060101 | 0.0087568 | -0.056777 | -0.022624 | 0.0087568 | south | N | 0.0087568 | 0
8174 | VICEC61A | 6 | 188 | -0.031151 | south | Y | -0.060101 | 0.0087568 | -0.056777 | -0.022624 | 0.0087568 | south | N | 0.0087568 | 0
8189 | CUERO 2 | 1 | 12 | -0.037643 | south | N | -0.066593 | 0.0022648 | -0.063269 | -0.029116 | 0.0022648 | south | N | 0.0022648 | 0
8262 | ELPS | 1 | 6 | -0.023143 | south | N | -0.052093 | 0.016765 | -0.048769 | -0.014616 | 0.014616 | houston | Y | 0.016765 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.039908 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.039908 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.039908 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.039908 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.039908 | 0
8442 | NBEC71A | 1 | 336 | -0.031278 | south | Y | -0.060228 | 0.0086298 | -0.056904 | -0.022751 | 0.0086298 | south | N | 0.0086298 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.039908 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.02895 | 0.039908 | -0.025626 | 0.0085273 | 0.0085273 | houston | Y | 0.039908 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.031351 | south | Y | -0.060301 | 0.0085568 | -0.056977 | -0.022824 | 0.0085568 | south | N | 0.0085568 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.031351 | south | Y | -0.060301 | 0.0085568 | -0.056977 | -0.022824 | 0.0085568 | south | N | 0.0085568 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.031396 | south | N | -0.060346 | 0.0085118 | -0.057022 | -0.022869 | 0.0085118 | south | N | 0.0085118 | 0
8506 | VAL #1 | 1 | 25 | -0.031362 | south | N | -0.060312 | 0.0085458 | -0.056988 | -0.022835 | 0.0085458 | south | N | 0.0085458 | 0
8507 | VAL #2 | 2 | 25 | -0.031362 | south | N | -0.060312 | 0.0085458 | -0.056988 | -0.022835 | 0.0085458 | south | N | 0.0085458 | 0
8511 | OXY_CC0A | 1 | 38 | -0.031394 | south | N | -0.060344 | 0.0085138 | -0.05702 | -0.022867 | 0.0085138 | south | N | 0.0085138 | 0
8517 | CELANEBI | 1 | 29 | -0.031547 | south | N | -0.060497 | 0.0083608 | -0.057173 | -0.02302 | 0.0083608 | south | N | 0.0083608 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.031282 | south | N | -0.060232 | 0.0086258 | -0.056908 | -0.022755 | 0.0086258 | south | N | 0.0086258 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.031282 | south | N | -0.060232 | 0.0086258 | -0.056908 | -0.022755 | 0.0086258 | south | N | 0.0086258 | 0
8562 | CNOPST1 | 3 | 153 | -0.031282 | south | N | -0.060232 | 0.0086258 | -0.056908 | -0.022755 | 0.0086258 | south | N | 0.0086258 | 0
8926 | LGE_GT10 | 1 | 158 | -0.03095 | south | N | -0.0599 | 0.0089578 | -0.056576 | -0.022423 | 0.0089578 | south | N | 0.0089578 | 0
8927 | LGE_GT20 | 2 | 153 | -0.03095 | south | N | -0.0599 | 0.0089578 | -0.056576 | -0.022423 | 0.0089578 | south | N | 0.0089578 | 0
8928 | LGE_STG0 | 3 | 100 | -0.03095 | south | N | -0.0599 | 0.0089578 | -0.056576 | -0.022423 | 0.0089578 | south | N | 0.0089578 | 0
8930 | ICPGN10A | 1 | 145 | -0.03095 | south | N | -0.0599 | 0.0089578 | -0.056576 | -0.022423 | 0.0089578 | south | N | 0.0089578 | 0
8931 | ICPGN20A | 2 | 147 | -0.03095 | south | N | -0.0599 | 0.0089578 | -0.056576 | -0.022423 | 0.0089578 | south | N | 0.0089578 | 0
8932 | ICPGN30A | 3 | 127 | -0.03095 | south | N | -0.0599 | 0.0089578 | -0.056576 | -0.022423 | 0.0089578 | south | N | 0.0089578 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.031746 | south | Y | -0.060696 | 0.0081618 | -0.057372 | -0.023219 | 0.0081618 | south | N | 0.0081618 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.031746 | south | Y | -0.060696 | 0.0081618 | -0.057372 | -0.023219 | 0.0081618 | south | N | 0.0081618 | 0
8935 | FGNTS201 | 3 | 173 | -0.031746 | south | Y | -0.060696 | 0.0081618 | -0.057372 | -0.023219 | 0.0081618 | south | N | 0.0081618 | 0
8936 | MVGN#1 | 1 | 207 | -0.031683 | south | Y | -0.060633 | 0.0082248 | -0.057309 | -0.023156 | 0.0082248 | south | N | 0.0082248 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.031683 | south | Y | -0.060633 | 0.0082248 | -0.057309 | -0.023156 | 0.0082248 | south | N | 0.0082248 | 0
8938 | MVGN#3 | 3 | 242 | -0.031683 | south | Y | -0.060633 | 0.0082248 | -0.057309 | -0.023156 | 0.0082248 | south | N | 0.0082248 | 0
8981 | HECN1 | 1 | 144 | -0.031682 | south | Y | -0.060632 | 0.0082258 | -0.057308 | -0.023155 | 0.0082258 | south | N | 0.0082258 | 0
8982 | HECN2 | 2 | 144 | -0.031682 | south | Y | -0.060632 | 0.0082258 | -0.057308 | -0.023155 | 0.0082258 | south | N | 0.0082258 | 0
8983 | HECN3 | 3 | 171 | -0.031682 | south | Y | -0.060632 | 0.0082258 | -0.057308 | -0.023155 | 0.0082258 | south | N | 0.0082258 | 0
9000 | DECKR_G1 | 1 | 310 | -0.050625 | south | Y | -0.079575 | -0.010717 | -0.076251 | -0.042098 | 0.010717 | south | N | 0.010717 | 0
9001 | DECKR_G2 | 2 | 413 | -0.050625 | south | Y | -0.079575 | -0.010717 | -0.076251 | -0.042098 | 0.010717 | south | N | 0.010717 | 0
9002 | DECKR_G3 | 3 | 42 | -0.051109 | south | Y | -0.080059 | -0.011201 | -0.076735 | -0.042582 | 0.011201 | south | N | 0.011201 | 0
9003 | DECKR_G4 | 4 | 44 | -0.051109 | south | Y | -0.080059 | -0.011201 | -0.076735 | -0.042582 | 0.011201 | south | N | 0.011201 | 0
9004 | DECKR_G5 | 5 | 44 | -0.051109 | south | Y | -0.080059 | -0.011201 | -0.076735 | -0.042582 | 0.011201 | south | N | 0.011201 | 0
9005 | DECKR_G6 | 6 | 47 | -0.051109 | south | Y | -0.080059 | -0.011201 | -0.076735 | -0.042582 | 0.011201 | south | N | 0.011201 | 0
9016 | SANDH_G1 | 1 | 49 | -0.049954 | south | Y | -0.078904 | -0.010046 | -0.07558 | -0.041427 | 0.010046 | south | N | 0.010046 | 0
9017 | SANDH_G2 | 2 | 46 | -0.049954 | south | Y | -0.078904 | -0.010046 | -0.07558 | -0.041427 | 0.010046 | south | N | 0.010046 | 0
9018 | SANDH_G3 | 3 | 46 | -0.049954 | south | Y | -0.078904 | -0.010046 | -0.07558 | -0.041427 | 0.010046 | south | N | 0.010046 | 0
9019 | SANDH_G4 | 4 | 47 | -0.049954 | south | Y | -0.078904 | -0.010046 | -0.07558 | -0.041427 | 0.010046 | south | N | 0.010046 | 0
9020 | SANDHG5A | 5A | 154 | -0.049954 | south | Y | -0.078904 | -0.010046 | -0.07558 | -0.041427 | 0.010046 | south | N | 0.010046 | 0
9021 | SANDHG5C | 5C | 148 | -0.049954 | south | Y | -0.078904 | -0.010046 | -0.07558 | -0.041427 | 0.010046 | south | N | 0.010046 | 0
9022 | SANDH_G6 | 6 | 48 | -0.049954 | south | Y | -0.078904 | -0.010046 | -0.07558 | -0.041427 | 0.010046 | south | N | 0.010046 | 0
9023 | SANDH_G7 | 7 | 48 | -0.049954 | south | Y | -0.078904 | -0.010046 | -0.07558 | -0.041427 | 0.010046 | south | N | 0.010046 | 0
11001 | NAV1CT | 1 | 70 | 0.025629 | west | Y | -0.0033212 | 0.065537 | 3.239e-06 | 0.034156 | 3.239e-06 | west | N | 3.239e-06 | 0
11009 | NAV2CT | 1 | 70 | 0.025629 | west | Y | -0.0033212 | 0.065537 | 3.239e-06 | 0.034156 | 3.239e-06 | west | N | 3.239e-06 | 0
11011 | NAV3ST | 1 | 92.8 | 0.025629 | west | Y | -0.0033212 | 0.065537 | 3.239e-06 | 0.034156 | 3.239e-06 | west | N | 3.239e-06 | 0
11012 | NAV4CT | 1 | 80 | 0.025629 | west | Y | -0.0033212 | 0.065537 | 3.239e-06 | 0.034156 | 3.239e-06 | west | N | 3.239e-06 | 0
11013 | NAV5CT | 1 | 80 | 0.025629 | west | Y | -0.0033212 | 0.065537 | 3.239e-06 | 0.034156 | 3.239e-06 | west | N | 3.239e-06 | 0
11014 | NAV6ST | 1 | 115 | 0.025629 | west | Y | -0.0033212 | 0.065537 | 3.239e-06 | 0.034156 | 3.239e-06 | west | N | 3.239e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.025624 | west | Y | -0.0033262 | 0.065532 | -1.761e-06 | 0.034151 | 1.761e-06 | west | N | 1.761e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.025624 | west | Y | -0.0033262 | 0.065532 | -1.761e-06 | 0.034151 | 1.761e-06 | west | N | 1.761e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.025624 | west | Y | -0.0033262 | 0.065532 | -1.761e-06 | 0.034151 | 1.761e-06 | west | N | 1.761e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.025624 | west | Y | -0.0033262 | 0.065532 | -1.761e-06 | 0.034151 | 1.761e-06 | west | N | 1.761e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.025624 | west | Y | -0.0033262 | 0.065532 | -1.761e-06 | 0.034151 | 1.761e-06 | west | N | 1.761e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.025624 | west | Y | -0.0033262 | 0.065532 | -1.761e-06 | 0.034151 | 1.761e-06 | west | N | 1.761e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.026517 | west | Y | -0.0024332 | 0.066425 | 0.00089124 | 0.035044 | 0.00089124 | west | N | 0.00089124 | 0
11057 | CHAMPION | 1 | 126.5 | 0.026517 | west | Y | -0.0024332 | 0.066425 | 0.00089124 | 0.035044 | 0.00089124 | west | N | 0.00089124 | 0
11058 | PYRON_1G | 1 | 249 | 0.026517 | west | Y | -0.0024332 | 0.066425 | 0.00089124 | 0.035044 | 0.00089124 | west | N | 0.00089124 | 0
11059 | INADALE_ | 1 | 197 | 0.026517 | west | Y | -0.0024332 | 0.066425 | 0.00089124 | 0.035044 | 0.00089124 | west | N | 0.00089124 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.026046 | west | Y | -0.0029042 | 0.065954 | 0.00042024 | 0.034573 | 0.00042024 | west | N | 0.00042024 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.026046 | west | Y | -0.0029042 | 0.065954 | 0.00042024 | 0.034573 | 0.00042024 | west | N | 0.00042024 | 0
11147 | NOTREES_ | 1 | 149 | 0.025254 | west | Y | -0.0036962 | 0.065162 | -0.00037176 | 0.033781 | 0.00037176 | west | N | 0.00037176 | 0
11309 | BULLCREK | 1 | 180 | 0.025971 | west | Y | -0.0029792 | 0.065879 | 0.00034524 | 0.034498 | 0.00034524 | west | N | 0.00034524 | 0
11310 | BULLCREK | 1 | 180 | 0.025971 | west | Y | -0.0029792 | 0.065879 | 0.00034524 | 0.034498 | 0.00034524 | west | N | 0.00034524 | 0
11320 | COYOTE_1 | 1 | 225 | 0.025946 | west | Y | -0.0030042 | 0.065854 | 0.00032024 | 0.034473 | 0.00032024 | west | N | 0.00032024 | 0
11415 | LORAINE_ | 1 | 125 | 0.026315 | west | Y | -0.0026352 | 0.066223 | 0.00068924 | 0.034842 | 0.00068924 | west | N | 0.00068924 | 0
11416 | LORAINE_ | 1 | 125 | 0.026315 | west | Y | -0.0026352 | 0.066223 | 0.00068924 | 0.034842 | 0.00068924 | west | N | 0.00068924 | 0
11691 | KMICHICT | 1 | 140 | 0.030013 | north | N | 0.0010628 | 0.069921 | 0.0043872 | 0.03854 | 0.0010628 | North | N | 0.0010628 | 0
11692 | KMICHICT | 2 | 141 | 0.030013 | north | N | 0.0010628 | 0.069921 | 0.0043872 | 0.03854 | 0.0010628 | North | N | 0.0010628 | 0
11693 | KMICHIST | 3 | 309 | 0.030013 | north | N | 0.0010628 | 0.069921 | 0.0043872 | 0.03854 | 0.0010628 | North | N | 0.0010628 | 0
11694 | KMICHICT | 4 | 143 | 0.030013 | north | N | 0.0010628 | 0.069921 | 0.0043872 | 0.03854 | 0.0010628 | North | N | 0.0010628 | 0
11695 | KMICHICT | 5 | 144 | 0.030013 | north | N | 0.0010628 | 0.069921 | 0.0043872 | 0.03854 | 0.0010628 | North | N | 0.0010628 | 0
11696 | KMICHIST | 6 | 310 | 0.030013 | north | N | 0.0010628 | 0.069921 | 0.0043872 | 0.03854 | 0.0010628 | North | N | 0.0010628 | 0
12322 | ENNSTRAC | 1 | 196 | 0.031339 | north | Y | 0.0023888 | 0.071247 | 0.0057132 | 0.039866 | 0.0023888 | North | N | 0.0023888 | 0
12323 | ENNSTRAC | 2 | 111 | 0.031339 | north | Y | 0.0023888 | 0.071247 | 0.0057132 | 0.039866 | 0.0023888 | North | N | 0.0023888 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.030187 | north | N | 0.0012368 | 0.070095 | 0.0045612 | 0.038714 | 0.0012368 | North | N | 0.0012368 | 0
12411 | FPLEFR1A | 1 | 161 | 0.029768 | north | Y | 0.00081783 | 0.069676 | 0.0041422 | 0.038295 | 0.00081783 | North | N | 0.00081783 | 0
12412 | FPLEFR1B | 2 | 164 | 0.029768 | north | Y | 0.00081783 | 0.069676 | 0.0041422 | 0.038295 | 0.00081783 | North | N | 0.00081783 | 0
12413 | FPLEFR1C | 3 | 164 | 0.029768 | north | Y | 0.00081783 | 0.069676 | 0.0041422 | 0.038295 | 0.00081783 | North | N | 0.00081783 | 0
12414 | FPLEFR1S | 4 | 414 | 0.029768 | north | Y | 0.00081783 | 0.069676 | 0.0041422 | 0.038295 | 0.00081783 | North | N | 0.00081783 | 0
12421 | FPLEFR2A | 1 | 162 | 0.029768 | north | Y | 0.00081783 | 0.069676 | 0.0041422 | 0.038295 | 0.00081783 | North | N | 0.00081783 | 0
12422 | FPLEFR2B | 2 | 161 | 0.029768 | north | Y | 0.00081783 | 0.069676 | 0.0041422 | 0.038295 | 0.00081783 | North | N | 0.00081783 | 0
12423 | FPLEFR2C | 3 | 163 | 0.029768 | north | Y | 0.00081783 | 0.069676 | 0.0041422 | 0.038295 | 0.00081783 | North | N | 0.00081783 | 0
12424 | FPLEFR2S | 4 | 409 | 0.029768 | north | Y | 0.00081783 | 0.069676 | 0.0041422 | 0.038295 | 0.00081783 | North | N | 0.00081783 | 0
12440 | PARKD_1S | 1 | 0 | 0.030091 | north | N | 0.0011408 | 0.069999 | 0.0044652 | 0.038618 | 0.0011408 | North | N | 0.0011408 | 0
12449 | PARKD_2S | 1 | 0 | 0.030091 | north | N | 0.0011408 | 0.069999 | 0.0044652 | 0.038618 | 0.0011408 | North | N | 0.0011408 | 0
13116 | TGATEWAY | 1 | 148 | 0.028748 | north | N | -0.00020217 | 0.068656 | 0.0031222 | 0.037275 | 0.00020217 | North | N | 0.00020217 | 0
13117 | TGATEWAY | 2 | 130 | 0.028748 | north | N | -0.00020217 | 0.068656 | 0.0031222 | 0.037275 | 0.00020217 | North | N | 0.00020217 | 0
13118 | TGATEWAY | 3 | 145 | 0.028748 | north | N | -0.00020217 | 0.068656 | 0.0031222 | 0.037275 | 0.00020217 | North | N | 0.00020217 | 0
13119 | TGATEWAY | 4 | 399 | 0.028748 | north | N | -0.00020217 | 0.068656 | 0.0031222 | 0.037275 | 0.00020217 | North | N | 0.00020217 | 0
13131 | CALFREST | 1 | 150.7 | 0.027189 | north | Y | -0.0017612 | 0.067097 | 0.0015632 | 0.035716 | 0.0015632 | west | Y | 0.0017612 | 0.029828
13132 | CALFREST | 2 | 151 | 0.027189 | north | Y | -0.0017612 | 0.067097 | 0.0015632 | 0.035716 | 0.0015632 | west | Y | 0.0017612 | 0.029888
13133 | CALFREST | 3 | 177.4 | 0.027189 | north | Y | -0.0017612 | 0.067097 | 0.0015632 | 0.035716 | 0.0015632 | west | Y | 0.0017612 | 0.035113
13134 | CALFREST | 4 | 151.5 | 0.027259 | north | Y | -0.0016912 | 0.067167 | 0.0016332 | 0.035786 | 0.0016332 | west | Y | 0.0016912 | 0.0087766
13135 | CALFREST | 5 | 152.3 | 0.027259 | north | Y | -0.0016912 | 0.067167 | 0.0016332 | 0.035786 | 0.0016332 | west | Y | 0.0016912 | 0.008823
13136 | CALFREST | 6 | 177.5 | 0.027259 | north | Y | -0.0016912 | 0.067167 | 0.0016332 | 0.035786 | 0.0016332 | west | Y | 0.0016912 | 0.010283
13432 | SANDOW_5 | 5 | 581 | -0.059577 | south | Y | -0.088527 | -0.019669 | -0.085203 | -0.05105 | 0.019669 | south | N | 0.019669 | 0
13691 | OAKGROVE | 1 | 855 | 0.019011 | north | Y | -0.0099392 | 0.058919 | -0.0066148 | 0.027538 | 0.0066148 | west | Y | 0.0099392 | 2.8424
13692 | OAKGROVE | 2 | 855 | 0.019011 | north | Y | -0.0099392 | 0.058919 | -0.0066148 | 0.027538 | 0.0066148 | west | Y | 0.0099392 | 2.8424
32798 | BRYN_TAM | 1 | 32 | 0.009251 | north | N | -0.019699 | 0.049159 | -0.016375 | 0.017778 | 0.016375 | west | Y | 0.019699 | 0
32883 | BRYN_DNS | 1 | 48 | 0.008441 | north | Y | -0.020509 | 0.048349 | -0.017185 | 0.016968 | 0.016968 | houston | Y | 0.020509 | 0.16996
32884 | BRYN_DNS | 1 | 46 | 0.008441 | north | Y | -0.020509 | 0.048349 | -0.017185 | 0.016968 | 0.016968 | houston | Y | 0.020509 | 0.16288
32886 | BRYN_ATK | MB | 12 | 0.00927 | north | Y | -0.01968 | 0.049178 | -0.016356 | 0.017797 | 0.016356 | west | Y | 0.01968 | 0
32887 | BRYN_ATK | MB | 51 | 0.00927 | north | Y | -0.01968 | 0.049178 | -0.016356 | 0.017797 | 0.016356 | west | Y | 0.01968 | 0
32888 | BRYN_ATK | 1 | 17 | 0.00927 | north | Y | -0.01968 | 0.049178 | -0.016356 | 0.017797 | 0.016356 | west | Y | 0.01968 | 0.056515
32890 | BRYN_ATK | MB | 22 | 0.00927 | north | Y | -0.01968 | 0.049178 | -0.016356 | 0.017797 | 0.016356 | west | Y | 0.01968 | 0
32891 | BRYN_ATK | MB | 25 | 0.00927 | north | Y | -0.01968 | 0.049178 | -0.016356 | 0.017797 | 0.016356 | west | Y | 0.01968 | 0
32892 | BRYN_DNS | 1 | 105 | 0.008441 | north | Y | -0.020509 | 0.048349 | -0.017185 | 0.016968 | 0.016968 | houston | Y | 0.020509 | 0.37179
36998 | RDCNYNG1 | 1 | 84 | 0.026234 | west | Y | -0.0027162 | 0.066142 | 0.00060824 | 0.034761 | 0.00060824 | west | N | 0.00060824 | 0
38332 | WDWRDU2 | 1 | 80 | 0.022443 | west | Y | -0.0065072 | 0.062351 | -0.0031828 | 0.03097 | 0.0031828 | west | N | 0.0031828 | 0
38437 | TNSRBNMS | 1 | 150 | 0.022418 | west | Y | -0.0065322 | 0.062326 | -0.0032078 | 0.030945 | 0.0032078 | west | N | 0.0032078 | 0
38438 | TNSRBNMS | 1 | 150 | 0.022418 | west | Y | -0.0065322 | 0.062326 | -0.0032078 | 0.030945 | 0.0032078 | west | N | 0.0032078 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.008976 | houston | N | -0.037926 | 0.030932 | -0.034602 | -0.00044869 | 0.00044869 | houston | N | 0.00044869 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.008976 | houston | N | -0.037926 | 0.030932 | -0.034602 | -0.00044869 | 0.00044869 | houston | N | 0.00044869 | 0
38600 | TNBP_CGN | 5 | 53 | -0.008976 | houston | N | -0.037926 | 0.030932 | -0.034602 | -0.00044869 | 0.00044869 | houston | N | 0.00044869 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.008976 | houston | N | -0.037926 | 0.030932 | -0.034602 | -0.00044869 | 0.00044869 | houston | N | 0.00044869 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.008976 | houston | N | -0.037926 | 0.030932 | -0.034602 | -0.00044869 | 0.00044869 | houston | N | 0.00044869 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.008976 | houston | N | -0.037926 | 0.030932 | -0.034602 | -0.00044869 | 0.00044869 | houston | N | 0.00044869 | 0
38614 | TNBPAMCG | 4 | 96 | -0.008976 | houston | N | -0.037926 | 0.030932 | -0.034602 | -0.00044869 | 0.00044869 | houston | N | 0.00044869 | 0
38615 | TNBPAMCG | 1 | 244 | -0.008976 | houston | N | -0.037926 | 0.030932 | -0.034602 | -0.00044869 | 0.00044869 | houston | N | 0.00044869 | 0
38690 | TNBP_CGN | 3 | 40 | -0.008976 | houston | N | -0.037926 | 0.030932 | -0.034602 | -0.00044869 | 0.00044869 | houston | N | 0.00044869 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.008982 | houston | N | -0.037932 | 0.030926 | -0.034608 | -0.00045469 | 0.00045469 | houston | N | 0.00045469 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.008982 | houston | N | -0.037932 | 0.030926 | -0.034608 | -0.00045469 | 0.00045469 | houston | N | 0.00045469 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.008982 | houston | N | -0.037932 | 0.030926 | -0.034608 | -0.00045469 | 0.00045469 | houston | N | 0.00045469 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.008982 | houston | N | -0.037932 | 0.030926 | -0.034608 | -0.00045469 | 0.00045469 | houston | N | 0.00045469 | 0
39470 | TNDOWCGN | 1 | 32 | -0.008982 | houston | N | -0.037932 | 0.030926 | -0.034608 | -0.00045469 | 0.00045469 | houston | N | 0.00045469 | 0
39480 | TNDOWCGN | 1 | 30 | -0.008982 | houston | N | -0.037932 | 0.030926 | -0.034608 | -0.00045469 | 0.00045469 | houston | N | 0.00045469 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.013176 | houston | N | -0.042126 | 0.026732 | -0.038802 | -0.0046487 | 0.0046487 | houston | N | 0.0046487 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.013176 | houston | N | -0.042126 | 0.026732 | -0.038802 | -0.0046487 | 0.0046487 | houston | N | 0.0046487 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.013176 | houston | N | -0.042126 | 0.026732 | -0.038802 | -0.0046487 | 0.0046487 | houston | N | 0.0046487 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.013176 | houston | N | -0.042126 | 0.026732 | -0.038802 | -0.0046487 | 0.0046487 | houston | N | 0.0046487 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.019011 | north | Y | -0.0099392 | 0.058919 | -0.0066148 | 0.027538 | 0.0066148 | west | Y | 0.0099392 | 0.50631
39970 | TNTNPONE | 1 | 153 | 0.019011 | north | Y | -0.0099392 | 0.058919 | -0.0066148 | 0.027538 | 0.0066148 | west | Y | 0.0099392 | 0.50863
48500 | APD_GT1_ | 1 | 136 | -0.006421 | houston | N | -0.035371 | 0.033487 | -0.032047 | 0.0021063 | 0.0021063 | houston | N | 0.0021063 | 0
48510 | AK_GT1__ | 1 | 33 | -0.010375 | houston | N | -0.039325 | 0.029533 | -0.036001 | -0.0018477 | 0.0018477 | houston | N | 0.0018477 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.006406 | houston | Y | -0.035356 | 0.033502 | -0.032032 | 0.0021213 | 0.0021213 | houston | N | 0.0021213 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.006406 | houston | Y | -0.035356 | 0.033502 | -0.032032 | 0.0021213 | 0.0021213 | houston | N | 0.0021213 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.006406 | houston | Y | -0.035356 | 0.033502 | -0.032032 | 0.0021213 | 0.0021213 | houston | N | 0.0021213 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.006406 | houston | Y | -0.035356 | 0.033502 | -0.032032 | 0.0021213 | 0.0021213 | houston | N | 0.0021213 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.013849 | houston | N | -0.042799 | 0.026059 | -0.039475 | -0.0053217 | 0.0053217 | houston | N | 0.0053217 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.013849 | houston | N | -0.042799 | 0.026059 | -0.039475 | -0.0053217 | 0.0053217 | houston | N | 0.0053217 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.010628 | houston | N | -0.039578 | 0.02928 | -0.036254 | -0.0021007 | 0.0021007 | houston | N | 0.0021007 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.010628 | houston | N | -0.039578 | 0.02928 | -0.036254 | -0.0021007 | 0.0021007 | houston | N | 0.0021007 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.010628 | houston | N | -0.039578 | 0.02928 | -0.036254 | -0.0021007 | 0.0021007 | houston | N | 0.0021007 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.007375 | houston | N | -0.036325 | 0.032533 | -0.033001 | 0.0011523 | 0.0011523 | houston | N | 0.0011523 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.007375 | houston | N | -0.036325 | 0.032533 | -0.033001 | 0.0011523 | 0.0011523 | houston | N | 0.0011523 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.007375 | houston | N | -0.036325 | 0.032533 | -0.033001 | 0.0011523 | 0.0011523 | houston | N | 0.0011523 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.007375 | houston | N | -0.036325 | 0.032533 | -0.033001 | 0.0011523 | 0.0011523 | houston | N | 0.0011523 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.006753 | houston | N | -0.035703 | 0.033155 | -0.032379 | 0.0017743 | 0.0017743 | houston | N | 0.0017743 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.006753 | houston | N | -0.035703 | 0.033155 | -0.032379 | 0.0017743 | 0.0017743 | houston | N | 0.0017743 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.007563 | houston | N | -0.036513 | 0.032345 | -0.033189 | 0.00096431 | 0.00096431 | houston | N | 0.00096431 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.007563 | houston | N | -0.036513 | 0.032345 | -0.033189 | 0.00096431 | 0.00096431 | houston | N | 0.00096431 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.007563 | houston | N | -0.036513 | 0.032345 | -0.033189 | 0.00096431 | 0.00096431 | houston | N | 0.00096431 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.007563 | houston | N | -0.036513 | 0.032345 | -0.033189 | 0.00096431 | 0.00096431 | houston | N | 0.00096431 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.007563 | houston | N | -0.036513 | 0.032345 | -0.033189 | 0.00096431 | 0.00096431 | houston | N | 0.00096431 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.005626 | houston | Y | -0.034576 | 0.034282 | -0.031252 | 0.0029013 | 0.0029013 | houston | N | 0.0029013 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.005943 | houston | Y | -0.034893 | 0.033965 | -0.031569 | 0.0025843 | 0.0025843 | houston | N | 0.0025843 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.00553 | houston | Y | -0.03448 | 0.034378 | -0.031156 | 0.0029973 | 0.0029973 | houston | N | 0.0029973 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.00553 | houston | Y | -0.03448 | 0.034378 | -0.031156 | 0.0029973 | 0.0029973 | houston | N | 0.0029973 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.00553 | houston | Y | -0.03448 | 0.034378 | -0.031156 | 0.0029973 | 0.0029973 | houston | N | 0.0029973 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.003773 | houston | N | -0.032723 | 0.036135 | -0.029399 | 0.0047543 | 0.0047543 | houston | N | 0.0047543 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.006358 | houston | N | -0.035308 | 0.03355 | -0.031984 | 0.0021693 | 0.0021693 | houston | N | 0.0021693 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.006358 | houston | N | -0.035308 | 0.03355 | -0.031984 | 0.0021693 | 0.0021693 | houston | N | 0.0021693 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.005306 | houston | N | -0.034256 | 0.034602 | -0.030932 | 0.0032213 | 0.0032213 | houston | N | 0.0032213 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.005306 | houston | N | -0.034256 | 0.034602 | -0.030932 | 0.0032213 | 0.0032213 | houston | N | 0.0032213 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.005306 | houston | N | -0.034256 | 0.034602 | -0.030932 | 0.0032213 | 0.0032213 | houston | N | 0.0032213 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.005306 | houston | N | -0.034256 | 0.034602 | -0.030932 | 0.0032213 | 0.0032213 | houston | N | 0.0032213 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.006732 | houston | N | -0.035682 | 0.033176 | -0.032358 | 0.0017953 | 0.0017953 | houston | N | 0.0017953 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.006732 | houston | N | -0.035682 | 0.033176 | -0.032358 | 0.0017953 | 0.0017953 | houston | N | 0.0017953 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.006732 | houston | N | -0.035682 | 0.033176 | -0.032358 | 0.0017953 | 0.0017953 | houston | N | 0.0017953 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.006732 | houston | N | -0.035682 | 0.033176 | -0.032358 | 0.0017953 | 0.0017953 | houston | N | 0.0017953 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.006931 | houston | N | -0.035881 | 0.032977 | -0.032557 | 0.0015963 | 0.0015963 | houston | N | 0.0015963 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.006931 | houston | N | -0.035881 | 0.032977 | -0.032557 | 0.0015963 | 0.0015963 | houston | N | 0.0015963 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.006931 | houston | N | -0.035881 | 0.032977 | -0.032557 | 0.0015963 | 0.0015963 | houston | N | 0.0015963 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.006931 | houston | N | -0.035881 | 0.032977 | -0.032557 | 0.0015963 | 0.0015963 | houston | N | 0.0015963 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.006931 | houston | N | -0.035881 | 0.032977 | -0.032557 | 0.0015963 | 0.0015963 | houston | N | 0.0015963 | 0
48651 | EP_1_2 | 1 | 5 | -0.005642 | houston | N | -0.034592 | 0.034266 | -0.031268 | 0.0028853 | 0.0028853 | houston | N | 0.0028853 | 0
48651 | EP_1_2 | 2 | 21 | -0.005642 | houston | N | -0.034592 | 0.034266 | -0.031268 | 0.0028853 | 0.0028853 | houston | N | 0.0028853 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.008617 | north | N | -0.020333 | 0.048525 | -0.017009 | 0.017144 | 0.017009 | west | Y | 0.020333 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.008617 | north | N | -0.020333 | 0.048525 | -0.017009 | 0.017144 | 0.017009 | west | Y | 0.020333 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.008617 | north | N | -0.020333 | 0.048525 | -0.017009 | 0.017144 | 0.017009 | west | Y | 0.020333 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.008617 | north | N | -0.020333 | 0.048525 | -0.017009 | 0.017144 | 0.017009 | west | Y | 0.020333 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.005229 | houston | Y | -0.034179 | 0.034679 | -0.030855 | 0.0032983 | 0.0032983 | houston | N | 0.0032983 | 0
48691 | GBY_7374 | A | 46 | -0.007096 | houston | Y | -0.036046 | 0.032812 | -0.032722 | 0.0014313 | 0.0014313 | houston | N | 0.0014313 | 0
48691 | GBY_7374 | B | 46 | -0.007096 | houston | Y | -0.036046 | 0.032812 | -0.032722 | 0.0014313 | 0.0014313 | houston | N | 0.0014313 | 0
48692 | GBY_8182 | C | 46 | -0.007096 | houston | Y | -0.036046 | 0.032812 | -0.032722 | 0.0014313 | 0.0014313 | houston | N | 0.0014313 | 0
48692 | GBY_8182 | D | 55 | -0.007096 | houston | Y | -0.036046 | 0.032812 | -0.032722 | 0.0014313 | 0.0014313 | houston | N | 0.0014313 | 0
48693 | GBY_8384 | E | 55 | -0.007096 | houston | Y | -0.036046 | 0.032812 | -0.032722 | 0.0014313 | 0.0014313 | houston | N | 0.0014313 | 0
48693 | GBY_8384 | F | 54 | -0.007096 | houston | Y | -0.036046 | 0.032812 | -0.032722 | 0.0014313 | 0.0014313 | houston | N | 0.0014313 | 0
48721 | LEG_1___ | 1 | 827 | 0.022389 | north | Y | -0.0065612 | 0.062297 | -0.0032368 | 0.030916 | 0.0032368 | west | Y | 0.0065612 | 2.7493
48722 | LEG_2___ | 2 | 819 | 0.022389 | north | Y | -0.0065612 | 0.062297 | -0.0032368 | 0.030916 | 0.0032368 | west | Y | 0.0065612 | 2.7227
48730 | MNS_GT | 1 | 46.1 | -0.010739 | houston | N | -0.039689 | 0.029169 | -0.036365 | -0.0022117 | 0.0022117 | houston | N | 0.0022117 | 0
48731 | CBE_GT1 | 1 | 76 | -0.019336 | houston | Y | -0.048286 | 0.020572 | -0.044962 | -0.010809 | 0.010809 | houston | N | 0.010809 | 0
48732 | CBE_GT2 | 1 | 76 | -0.019336 | houston | Y | -0.048286 | 0.020572 | -0.044962 | -0.010809 | 0.010809 | houston | N | 0.010809 | 0
48733 | CBE_ST12 | 1 | 105 | -0.019336 | houston | Y | -0.048286 | 0.020572 | -0.044962 | -0.010809 | 0.010809 | houston | N | 0.010809 | 0
48734 | CBE_GT3 | 1 | 74 | -0.019336 | houston | Y | -0.048286 | 0.020572 | -0.044962 | -0.010809 | 0.010809 | houston | N | 0.010809 | 0
48735 | CBE_GT4 | 1 | 74 | -0.019336 | houston | Y | -0.048286 | 0.020572 | -0.044962 | -0.010809 | 0.010809 | houston | N | 0.010809 | 0
48736 | CBE_ST34 | 1 | 102 | -0.019336 | houston | Y | -0.048286 | 0.020572 | -0.044962 | -0.010809 | 0.010809 | houston | N | 0.010809 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.006726 | houston | N | -0.035676 | 0.033182 | -0.032352 | 0.0018013 | 0.0018013 | houston | N | 0.0018013 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.006726 | houston | N | -0.035676 | 0.033182 | -0.032352 | 0.0018013 | 0.0018013 | houston | N | 0.0018013 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.006726 | houston | N | -0.035676 | 0.033182 | -0.032352 | 0.0018013 | 0.0018013 | houston | N | 0.0018013 | 0
48761 | PR_GT1__ | 1 | 35 | -0.006853 | houston | N | -0.035803 | 0.033055 | -0.032479 | 0.0016743 | 0.0016743 | houston | N | 0.0016743 | 0
48772 | PHR_GN2_ | MB | 459 | -0.008041 | houston | Y | -0.036991 | 0.031867 | -0.033667 | 0.00048631 | 0.00048631 | houston | N | 0.00048631 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.00564 | houston | N | -0.03459 | 0.034268 | -0.031266 | 0.0028873 | 0.0028873 | houston | N | 0.0028873 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.00564 | houston | N | -0.03459 | 0.034268 | -0.031266 | 0.0028873 | 0.0028873 | houston | N | 0.0028873 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.00564 | houston | N | -0.03459 | 0.034268 | -0.031266 | 0.0028873 | 0.0028873 | houston | N | 0.0028873 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.00564 | houston | N | -0.03459 | 0.034268 | -0.031266 | 0.0028873 | 0.0028873 | houston | N | 0.0028873 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.00564 | houston | N | -0.03459 | 0.034268 | -0.031266 | 0.0028873 | 0.0028873 | houston | N | 0.0028873 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.00564 | houston | N | -0.03459 | 0.034268 | -0.031266 | 0.0028873 | 0.0028873 | houston | N | 0.0028873 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.00564 | houston | N | -0.03459 | 0.034268 | -0.031266 | 0.0028873 | 0.0028873 | houston | N | 0.0028873 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.003773 | houston | N | -0.032723 | 0.036135 | -0.029399 | 0.0047543 | 0.0047543 | houston | N | 0.0047543 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.003773 | houston | N | -0.032723 | 0.036135 | -0.029399 | 0.0047543 | 0.0047543 | houston | N | 0.0047543 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.003773 | houston | N | -0.032723 | 0.036135 | -0.029399 | 0.0047543 | 0.0047543 | houston | N | 0.0047543 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.003773 | houston | N | -0.032723 | 0.036135 | -0.029399 | 0.0047543 | 0.0047543 | houston | N | 0.0047543 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.005568 | houston | N | -0.034518 | 0.03434 | -0.031194 | 0.0029593 | 0.0029593 | houston | N | 0.0029593 | 0
48820 | SHELLG1_ | 1 | 71 | -0.006608 | houston | N | -0.035558 | 0.0333 | -0.032234 | 0.0019193 | 0.0019193 | houston | N | 0.0019193 | 0
48821 | SHELLG2 | 2 | 72 | -0.006608 | houston | N | -0.035558 | 0.0333 | -0.032234 | 0.0019193 | 0.0019193 | houston | N | 0.0019193 | 0
48822 | SHELLG3_ | 1 | 39 | -0.006608 | houston | N | -0.035558 | 0.0333 | -0.032234 | 0.0019193 | 0.0019193 | houston | N | 0.0019193 | 0
48822 | SHELLG3_ | 2 | 30 | -0.006608 | houston | N | -0.035558 | 0.0333 | -0.032234 | 0.0019193 | 0.0019193 | houston | N | 0.0019193 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.007027 | houston | N | -0.035977 | 0.032881 | -0.032653 | 0.0015003 | 0.0015003 | houston | N | 0.0015003 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.007027 | houston | N | -0.035977 | 0.032881 | -0.032653 | 0.0015003 | 0.0015003 | houston | N | 0.0015003 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.006734 | houston | N | -0.035684 | 0.033174 | -0.03236 | 0.0017933 | 0.0017933 | houston | N | 0.0017933 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.006758 | houston | Y | -0.035708 | 0.03315 | -0.032384 | 0.0017693 | 0.0017693 | houston | N | 0.0017693 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.006765 | houston | Y | -0.035715 | 0.033143 | -0.032391 | 0.0017623 | 0.0017623 | houston | N | 0.0017623 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.006736 | houston | Y | -0.035686 | 0.033172 | -0.032362 | 0.0017913 | 0.0017913 | houston | N | 0.0017913 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.006729 | houston | Y | -0.035679 | 0.033179 | -0.032355 | 0.0017983 | 0.0017983 | houston | N | 0.0017983 | 0
48855 | SRB_GT21 | B2 | 12 | -0.006769 | houston | Y | -0.035719 | 0.033139 | -0.032395 | 0.0017583 | 0.0017583 | houston | N | 0.0017583 | 0
48855 | SRB_GT21 | MB | 18 | -0.006769 | houston | Y | -0.035719 | 0.033139 | -0.032395 | 0.0017583 | 0.0017583 | houston | N | 0.0017583 | 0
48865 | TECO_GT1 | 1 | 50 | -0.00845 | houston | Y | -0.0374 | 0.031458 | -0.034076 | 7.7309e-05 | 7.7309e-05 | houston | N | 7.7309e-05 | 0
48873 | THW_ST3_ | 3 | 104 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48874 | THW_ST4_ | 4 | 104 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48875 | THW_3132 | A | 54 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48875 | THW_3132 | B | 53 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48877 | THW_3334 | C | 54 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48877 | THW_3334 | D | 57 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48879 | THW_4142 | E | 54 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48879 | THW_4142 | F | 54 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48881 | THW_4344 | G | 58 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48881 | THW_4344 | H | 58 | -0.006058 | houston | Y | -0.035008 | 0.03385 | -0.031684 | 0.0024693 | 0.0024693 | houston | N | 0.0024693 | 0
48883 | THW_GT1_ | B2 | 12 | -0.005767 | houston | Y | -0.034717 | 0.034141 | -0.031393 | 0.0027603 | 0.0027603 | houston | N | 0.0027603 | 0
48885 | THW_5152 | A | 56 | -0.005092 | houston | Y | -0.034042 | 0.034816 | -0.030718 | 0.0034353 | 0.0034353 | houston | N | 0.0034353 | 0
48885 | THW_5152 | B | 59 | -0.005092 | houston | Y | -0.034042 | 0.034816 | -0.030718 | 0.0034353 | 0.0034353 | houston | N | 0.0034353 | 0
48886 | THW_5354 | C | 56 | -0.005092 | houston | Y | -0.034042 | 0.034816 | -0.030718 | 0.0034353 | 0.0034353 | houston | N | 0.0034353 | 0
48886 | THW_5354 | D | 56 | -0.005092 | houston | Y | -0.034042 | 0.034816 | -0.030718 | 0.0034353 | 0.0034353 | houston | N | 0.0034353 | 0
48887 | THW_5556 | E | 59 | -0.005092 | houston | Y | -0.034042 | 0.034816 | -0.030718 | 0.0034353 | 0.0034353 | houston | N | 0.0034353 | 0
48887 | THW_5556 | F | 56 | -0.005092 | houston | Y | -0.034042 | 0.034816 | -0.030718 | 0.0034353 | 0.0034353 | houston | N | 0.0034353 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.018223 | houston | Y | -0.047173 | 0.021685 | -0.043849 | -0.0096957 | 0.0096957 | houston | N | 0.0096957 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.010264 | houston | Y | -0.039214 | 0.029644 | -0.03589 | -0.0017367 | 0.0017367 | houston | N | 0.0017367 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.010264 | houston | Y | -0.039214 | 0.029644 | -0.03589 | -0.0017367 | 0.0017367 | houston | N | 0.0017367 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.010264 | houston | Y | -0.039214 | 0.029644 | -0.03589 | -0.0017367 | 0.0017367 | houston | N | 0.0017367 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.010264 | houston | Y | -0.039214 | 0.029644 | -0.03589 | -0.0017367 | 0.0017367 | houston | N | 0.0017367 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.010264 | houston | N | -0.039214 | 0.029644 | -0.03589 | -0.0017367 | 0.0017367 | houston | N | 0.0017367 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.010649 | houston | Y | -0.039599 | 0.029259 | -0.036275 | -0.0021217 | 0.0021217 | houston | N | 0.0021217 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.010649 | houston | Y | -0.039599 | 0.029259 | -0.036275 | -0.0021217 | 0.0021217 | houston | N | 0.0021217 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.010649 | houston | Y | -0.039599 | 0.029259 | -0.036275 | -0.0021217 | 0.0021217 | houston | N | 0.0021217 | 0
48929 | WAPGT21_ | B1 | 13 | -0.010264 | houston | Y | -0.039214 | 0.029644 | -0.03589 | -0.0017367 | 0.0017367 | houston | N | 0.0017367 | 0
48940 | WARVUE_G | G1 | 12 | -0.005635 | houston | Y | -0.034585 | 0.034273 | -0.031261 | 0.0028923 | 0.0028923 | houston | N | 0.0028923 | 0
49803 | EXN_15GT | 1 | 34 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49826 | EXN938GT | 5 | 45.9 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49828 | EXN941GT | 10 | 17.7 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49829 | EXN942GT | 11 | 20.4 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49830 | EXN943GT | 12 | 19.9 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49831 | EXN944GT | 13 | 35 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49832 | EXN945GT | 9 | 18 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49837 | EXN_GT | 4 | 85.4 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49838 | EXN_14GT | 14 | 148 | -0.005866 | houston | N | -0.034816 | 0.034042 | -0.031492 | 0.0026613 | 0.0026613 | houston | N | 0.0026613 | 0
49851 | DOW17000 | 37 | 62 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49858 | DOW38100 | 31 | 71.4 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49859 | DOW38200 | 33 | 45 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49860 | DOW38300 | 32 | 101 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49862 | DOW39100 | 36 | 86 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49863 | DOW39200 | 35 | 88 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49865 | DOW41000 | 41 | 50 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49866 | DOW42000 | 42 | 18 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49869 | DOW49000 | 45 | 94 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49870 | DOW61000 | 61 | 70 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49871 | DOW62000 | 62 | 63 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49872 | DOW63000 | 63 | 72 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49873 | DOW64000 | 64 | 64.8 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49876 | DOW65000 | 65 | 101 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49877 | DOW66000 | 66 | 97 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49878 | DOW67000 | 67 | 103 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49882 | DOW81000 | 81 | 76 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49884 | DOW82000 | 82 | 80 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49885 | DOW83000 | 83 | 80 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
49886 | DOW84000 | 84 | 171 | -0.0147 | houston | N | -0.04365 | 0.025208 | -0.040326 | -0.0061727 | 0.0061727 | houston | N | 0.0061727 | 0
58909 | PEARSALL | 1 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58909 | PEARSALL | 2 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58909 | PEARSALL | 3 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58909 | PEARSALL | 4 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58909 | PEARSALL | 5 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58909 | PEARSALL | 6 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58919 | PEARSALL | 1 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58919 | PEARSALL | 2 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58919 | PEARSALL | 3 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58919 | PEARSALL | 4 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58919 | PEARSALL | 5 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58919 | PEARSALL | 6 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58929 | PEARSALL | 1 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58929 | PEARSALL | 2 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58929 | PEARSALL | 3 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58929 | PEARSALL | 4 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58929 | PEARSALL | 5 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58929 | PEARSALL | 6 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58949 | PEARSALL | 1 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58949 | PEARSALL | 2 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58949 | PEARSALL | 3 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58949 | PEARSALL | 4 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58949 | PEARSALL | 5 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
58949 | PEARSALL | 6 | 8.4 | -0.033264 | south | Y | -0.062214 | 0.0066438 | -0.05889 | -0.024737 | 0.0066438 | south | N | 0.0066438 | 0
60000 | DSKY2 | 1 | 76.5 | 0.021281 | west | Y | -0.0076692 | 0.061189 | -0.0043448 | 0.029808 | 0.0043448 | west | N | 0.0043448 | 0
60003 | KING_NE1 | 1 | 80 | 0.02249 | west | Y | -0.0064602 | 0.062398 | -0.0031358 | 0.031017 | 0.0031358 | west | N | 0.0031358 | 0
60005 | KING_SE1 | 1 | 40 | 0.02249 | west | Y | -0.0064602 | 0.062398 | -0.0031358 | 0.031017 | 0.0031358 | west | N | 0.0031358 | 0
60007 | KING_SW1 | 1 | 80 | 0.022684 | west | Y | -0.0062662 | 0.062592 | -0.0029418 | 0.031211 | 0.0029418 | west | N | 0.0029418 | 0
60016 | WOODWRD1 | 1 | 80 | 0.022448 | west | Y | -0.0065022 | 0.062356 | -0.0031778 | 0.030975 | 0.0031778 | west | N | 0.0031778 | 0
60017 | ORNNWP1 | 1 | 80 | 0.021451 | west | Y | -0.0074992 | 0.061359 | -0.0041748 | 0.029978 | 0.0041748 | west | N | 0.0041748 | 0
60018 | DSKY1 | 1 | 84 | 0.021125 | west | Y | -0.0078252 | 0.061033 | -0.0045008 | 0.029652 | 0.0045008 | west | N | 0.0045008 | 0
60019 | KING_NW1 | 1 | 80 | 0.022684 | west | Y | -0.0062662 | 0.062592 | -0.0029418 | 0.031211 | 0.0029418 | west | N | 0.0029418 | 0
60057 | CALLAHAN | 1 | 114 | -0.039985 | south | Y | -0.068935 | -7.7157e-05 | -0.065611 | -0.031458 | 7.7157e-05 | south | N | 7.7157e-05 | 0
60058 | BUFF_GAP | 1 | 120 | 0.025833 | west | Y | -0.0031172 | 0.065741 | 0.00020724 | 0.03436 | 0.00020724 | west | N | 0.00020724 | 0
60060 | CIRELLO | 1 | 233 | 0.025833 | west | Y | -0.0031172 | 0.065741 | 0.00020724 | 0.03436 | 0.00020724 | west | N | 0.00020724 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.025833 | west | Y | -0.0031172 | 0.065741 | 0.00020724 | 0.03436 | 0.00020724 | west | N | 0.00020724 | 0
60066 | H_HOLLOW | 1 | 222 | -0.039985 | south | Y | -0.068935 | -7.7157e-05 | -0.065611 | -0.031458 | 7.7157e-05 | south | N | 7.7157e-05 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.039985 | south | Y | -0.068935 | -7.7157e-05 | -0.065611 | -0.031458 | 7.7157e-05 | south | N | 7.7157e-05 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.039985 | south | Y | -0.068935 | -7.7157e-05 | -0.065611 | -0.031458 | 7.7157e-05 | south | N | 7.7157e-05 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.039985 | south | Y | -0.068935 | -7.7157e-05 | -0.065611 | -0.031458 | 7.7157e-05 | south | N | 7.7157e-05 | 0
60074 | HORSH5 | 1 | 100 | -0.039985 | south | Y | -0.068935 | -7.7157e-05 | -0.065611 | -0.031458 | 7.7157e-05 | south | N | 7.7157e-05 | 0
60081 | WHRLWIND | 1 | 60 | 0.026948 | west | Y | -0.0020022 | 0.066856 | 0.0013222 | 0.035475 | 0.0013222 | west | N | 0.0013222 | 0
60201 | RIO DRCS | F | 0 | -0.022437 | south | N | -0.051387 | 0.017471 | -0.048063 | -0.01391 | 0.01391 | houston | Y | 0.017471 | 0
60202 | FRIEND_R | F | 0 | 0.015925 | west | N | -0.013025 | 0.055833 | -0.0097008 | 0.024452 | 0.0097008 | west | N | 0.0097008 | 0
60203 | PRES0A | BT | 4.8 | 0.023406 | west | N | -0.0055442 | 0.063314 | -0.0022198 | 0.031933 | 0.0022198 | west | N | 0.0022198 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.026453 | west | Y | -0.0024972 | 0.066361 | 0.00082724 | 0.03498 | 0.00082724 | west | N | 0.00082724 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.026453 | west | Y | -0.0024972 | 0.066361 | 0.00082724 | 0.03498 | 0.00082724 | west | N | 0.00082724 | 0
71057 | L_SWEETW | W1 | 135 | 0.026453 | west | Y | -0.0024972 | 0.066361 | 0.00082724 | 0.03498 | 0.00082724 | west | N | 0.00082724 | 0
71059 | L_SWEETW | W1 | 119 | 0.026453 | west | Y | -0.0024972 | 0.066361 | 0.00082724 | 0.03498 | 0.00082724 | west | N | 0.00082724 | 0
71060 | L_SWEETW | W1 | 105 | 0.026453 | west | Y | -0.0024972 | 0.066361 | 0.00082724 | 0.03498 | 0.00082724 | west | N | 0.00082724 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.026453 | west | Y | -0.0024972 | 0.066361 | 0.00082724 | 0.03498 | 0.00082724 | west | N | 0.00082724 | 0
76031 | L_GASCCR | W1 | 150 | 0.025531 | west | Y | -0.0034192 | 0.065439 | -9.4761e-05 | 0.034058 | 9.4761e-05 | west | N | 9.4761e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.025408 | west | Y | -0.0035422 | 0.065316 | -0.00021776 | 0.033935 | 0.00021776 | west | N | 0.00021776 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.025408 | west | Y | -0.0035422 | 0.065316 | -0.00021776 | 0.033935 | 0.00021776 | west | N | 0.00021776 | 0
76096 | L_CAPRSI | W1 | 186 | 0.025408 | west | Y | -0.0035422 | 0.065316 | -0.00021776 | 0.033935 | 0.00021776 | west | N | 0.00021776 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.025408 | west | Y | -0.0035422 | 0.065316 | -0.00021776 | 0.033935 | 0.00021776 | west | N | 0.00021776 | 0
80003 | MILHWYS | F | 0 | -0.03162 | south | N | -0.06057 | 0.0082878 | -0.057246 | -0.023093 | 0.0082878 | south | N | 0.0082878 | 0
80010 | EPLVT1 | F | 0 | -0.024244 | south | N | -0.053194 | 0.015664 | -0.04987 | -0.015717 | 0.015664 | south | N | 0.015664 | 0
80012 | LAR | F | 0 | -0.033375 | south | N | -0.062325 | 0.0065328 | -0.059001 | -0.024848 | 0.0065328 | south | N | 0.0065328 | 0
80051 | FORPVCM0 | 8 | 28 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
80053 | FOR69CG0 | 10 | 74 | -0.028743 | south | N | -0.057693 | 0.011165 | -0.054369 | -0.020216 | 0.011165 | south | N | 0.011165 | 0
80080 | GWINDT11 | 1 | 94 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80080 | GWINDT11 | 2 | 41 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80080 | GWINDT11 | 3 | 38 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80080 | GWINDT11 | 4 | 19 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80081 | GWINDT21 | 1 | 94 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80081 | GWINDT21 | 2 | 36 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80081 | GWINDT21 | 3 | 43 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80081 | GWINDT21 | 4 | 22 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80137 | CSDR89 | 8 | 39 | -0.029833 | south | N | -0.058783 | 0.010075 | -0.055459 | -0.021306 | 0.010075 | south | N | 0.010075 | 0
80137 | CSDR89 | 9 | 15 | -0.029833 | south | N | -0.058783 | 0.010075 | -0.055459 | -0.021306 | 0.010075 | south | N | 0.010075 | 0
80138 | CSDR7 | 7 | 7 | -0.029833 | south | N | -0.058783 | 0.010075 | -0.055459 | -0.021306 | 0.010075 | south | N | 0.010075 | 0
80139 | CSDR56 | 5 | 15 | -0.029833 | south | N | -0.058783 | 0.010075 | -0.055459 | -0.021306 | 0.010075 | south | N | 0.010075 | 0
80139 | CSDR56 | 6 | 39 | -0.029833 | south | N | -0.058783 | 0.010075 | -0.055459 | -0.021306 | 0.010075 | south | N | 0.010075 | 0
80140 | CSDR11 | 11 | 39 | -0.029833 | south | N | -0.058783 | 0.010075 | -0.055459 | -0.021306 | 0.010075 | south | N | 0.010075 | 0
80180 | PNSCALT1 | 1 | 148 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80180 | PNSCALT1 | 2 | 50 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80181 | PNSCALT2 | 1 | 55 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80181 | PNSCALT2 | 2 | 50 | -0.031598 | south | Y | -0.060548 | 0.0083098 | -0.057224 | -0.023071 | 0.0083098 | south | N | 0.0083098 | 0
80223 | REYSHR G | 1 | 12 | -0.03095 | south | N | -0.0599 | 0.0089578 | -0.056576 | -0.022423 | 0.0089578 | south | N | 0.0089578 | 0
80224 | VISTRONG | 1 | 15 | -0.030183 | south | N | -0.059133 | 0.0097248 | -0.055809 | -0.021656 | 0.0097248 | south | N | 0.0097248 | 0
80225 | VISTRONG | 2 | 23 | -0.030183 | south | N | -0.059133 | 0.0097248 | -0.055809 | -0.021656 | 0.0097248 | south | N | 0.0097248 | 0
80226 | ALCOA G | 1 | 48 | -0.029 | south | N | -0.05795 | 0.010908 | -0.054626 | -0.020473 | 0.010908 | south | N | 0.010908 | 0
80227 | AIRCO G | 1 | 8 | -0.029957 | south | N | -0.058907 | 0.0099508 | -0.055583 | -0.02143 | 0.0099508 | south | N | 0.0099508 | 0
80261 | NBEC81A | 1 | 180 | -0.031288 | south | Y | -0.060238 | 0.0086198 | -0.056914 | -0.022761 | 0.0086198 | south | N | 0.0086198 | 0
80262 | NBEC91A | 1 | 180 | -0.031278 | south | Y | -0.060228 | 0.0086298 | -0.056904 | -0.022751 | 0.0086298 | south | N | 0.0086298 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.031351 | south | Y | -0.060301 | 0.0085568 | -0.056977 | -0.022824 | 0.0085568 | south | N | 0.0085568 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.031351 | south | Y | -0.060301 | 0.0085568 | -0.056977 | -0.022824 | 0.0085568 | south | N | 0.0085568 | 0
80265 | LARECU40 | 4 | 100 | -0.033378 | south | Y | -0.062328 | 0.0065298 | -0.059004 | -0.024851 | 0.0065298 | south | N | 0.0065298 | 0
80266 | LARECU50 | 5 | 100 | -0.033378 | south | Y | -0.062328 | 0.0065298 | -0.059004 | -0.024851 | 0.0065298 | south | N | 0.0065298 | 0
80291 | PAPALOTE | 1 | 25 | -0.031079 | south | Y | -0.060029 | 0.0088288 | -0.056705 | -0.022552 | 0.0088288 | south | N | 0.0088288 | 0
80291 | PAPALOTE | 2 | 25 | -0.031079 | south | Y | -0.060029 | 0.0088288 | -0.056705 | -0.022552 | 0.0088288 | south | N | 0.0088288 | 0
80291 | PAPALOTE | 3 | 25 | -0.031079 | south | Y | -0.060029 | 0.0088288 | -0.056705 | -0.022552 | 0.0088288 | south | N | 0.0088288 | 0
80291 | PAPALOTE | 4 | 16 | -0.031079 | south | Y | -0.060029 | 0.0088288 | -0.056705 | -0.022552 | 0.0088288 | south | N | 0.0088288 | 0
80294 | PAPALOTE | 5 | 25 | -0.031079 | south | Y | -0.060029 | 0.0088288 | -0.056705 | -0.022552 | 0.0088288 | south | N | 0.0088288 | 0
80294 | PAPALOTE | 6 | 25 | -0.031079 | south | Y | -0.060029 | 0.0088288 | -0.056705 | -0.022552 | 0.0088288 | south | N | 0.0088288 | 0
80294 | PAPALOTE | 7 | 25 | -0.031079 | south | Y | -0.060029 | 0.0088288 | -0.056705 | -0.022552 | 0.0088288 | south | N | 0.0088288 | 0
80294 | PAPALOTE | 8 | 15 | -0.031079 | south | Y | -0.060029 | 0.0088288 | -0.056705 | -0.022552 | 0.0088288 | south | N | 0.0088288 | 0
86104 | CID-138 | EQ | 0 | -0.033378 | south | N | -0.062328 | 0.0065298 | -0.059004 | -0.024851 | 0.0065298 | south | N | 0.0065298 | 0
86105 | CID-230 | EQ | 500 | -0.033378 | south | N | -0.062328 | 0.0065298 | -0.059004 | -0.024851 | 0.0065298 | south | N | 0.0065298 | 0
86106 | CUF-230 | EQ | 500 | -0.033378 | south | N | -0.062328 | 0.0065298 | -0.059004 | -0.024851 | 0.0065298 | south | N | 0.0065298 | 0
86107 | CUF-138 | EQ | 0 | -0.033378 | south | N | -0.062328 | 0.0065298 | -0.059004 | -0.024851 | 0.0065298 | south | N | 0.0065298 | 0
88198 | BEEVILLE | F | 0 | -0.033097 | south | N | -0.062047 | 0.0068108 | -0.058723 | -0.02457 | 0.0068108 | south | N | 0.0068108 | 0
88253 | HAMILTON | F | 0 | -0.018408 | south | N | -0.047358 | 0.0215 | -0.044034 | -0.0098807 | 0.0098807 | houston | Y | 0.0215 | 0
88299 | ZAPATA | F | 0 | -0.032522 | south | N | -0.061472 | 0.0073858 | -0.058148 | -0.023995 | 0.0073858 | south | N | 0.0073858 | 0
88508 | FALFURRI | F | 0 | -0.032145 | south | N | -0.061095 | 0.0077628 | -0.057771 | -0.023618 | 0.0077628 | south | N | 0.0077628 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3592 WACOATCO 13591 COTTONB_ C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 3405 - 3412 and 3409 - 3414 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0 | 0 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0 | 0 | 0 | Weighted Shift Factors
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0 | 0 | 0 | South | -0.039908
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0 | 0 | 0 | North | 0.031358
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039908 | 0 | 0 | 0 |  | -0.071266
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039908 | 0 | 0 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.069442 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.038084 | 0 | 0 | 0 | Line Rating | 247.95
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.069442 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.038084 | 0 | 0 | 0 | Conc Gen | 342
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.65273 | 0 | 0.036135 | 0 | 0 | 0 | Weighted Imp. | 11.907
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.58859 | 0 | 0.036135 | 0 | 0 | 0 | PTDF | 0.034816
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.58104 | 0 | 0.036135 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.58104 | 0 | 0.036135 | 0 | 0 | 0 | Concentration | -0.48853
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.003773 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61123 | 0 | 0.036135 | 0 | 0 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28515 | 56 | 0.034816 | 1.9497 | 56 | 1.9497
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30043 | 59 | 0.034816 | 2.0541 | 115 | 4.0038
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28515 | 56 | 0.034816 | 1.9497 | 171 | 5.9535
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28515 | 56 | 0.034816 | 1.9497 | 227 | 7.9032
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30043 | 59 | 0.034816 | 2.0541 | 286 | 9.9573
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28515 | 56 | 0.034816 | 1.9497 | 342 | 11.907
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.005229 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.0811 | 398 | 0.034679 | 13.8022
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86382 | 0 | 0.034602 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85639 | 0 | 0.034602 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84312 | 0 | 0.034602 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4284 | 0 | 0.034602 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.00553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.95116 | 172 | 0.034378 | 5.913
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.00553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.95116 | 172 | 0.034378 | 5.913
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.00553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.95116 | 172 | 0.034378 | 5.913
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.005568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.87418 | 0 | 0.03434 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.005626 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.1801 | 743 | 0.034282 | 25.4714
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.005635 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.06762 | 12 | 0.034273 | 0.41127
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3666 | 0 | 0.034268 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37224 | 0 | 0.034268 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3948 | 0 | 0.034268 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35532 | 0 | 0.034268 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34968 | 0 | 0.034268 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.58656 | 0 | 0.034268 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33276 | 0 | 0.034268 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.005642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02821 | 0 | 0.034266 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.005642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11848 | 0 | 0.034266 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.005767 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.069204 | 12 | 0.034141 | 0.40969
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19944 | 0 | 0.034042 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20355 | 0 | 0.034042 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19182 | 0 | 0.034042 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26925 | 0 | 0.034042 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10383 | 0 | 0.034042 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11967 | 0 | 0.034042 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11673 | 0 | 0.034042 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20531 | 0 | 0.034042 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10559 | 0 | 0.034042 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50096 | 0 | 0.034042 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86817 | 0 | 0.034042 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.005943 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.3681 | 735 | 0.033965 | 24.9642
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.63003 | 104 | 0.03385 | 3.5204
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.63003 | 104 | 0.03385 | 3.5204
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32713 | 54 | 0.03385 | 1.8279
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32107 | 53 | 0.03385 | 1.794
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32713 | 54 | 0.03385 | 1.8279
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.34531 | 57 | 0.03385 | 1.9294
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32713 | 54 | 0.03385 | 1.8279
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32713 | 54 | 0.03385 | 1.8279
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35136 | 58 | 0.03385 | 1.9633
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35136 | 58 | 0.03385 | 1.9633
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.006358 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0999 | 0 | 0.03355 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.006358 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85833 | 0 | 0.03355 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.26905 | 42 | 0.033502 | 1.4071
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.26905 | 42 | 0.033502 | 1.4071
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24343 | 38 | 0.033502 | 1.2731
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24343 | 38 | 0.033502 | 1.2731
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.006421 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.87326 | 0 | 0.033487 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.46917 | 0 | 0.0333 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47578 | 0 | 0.0333 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25771 | 0 | 0.0333 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19824 | 0 | 0.0333 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.006726 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2107 | 0 | 0.033182 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.006726 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0667 | 0 | 0.033182 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.006726 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.056 | 0 | 0.033182 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.006729 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.5342 | 228 | 0.033179 | 7.5648
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43085 | 0 | 0.033176 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42546 | 0 | 0.033176 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55606 | 0 | 0.033176 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49548 | 0 | 0.033176 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.006734 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10909 | 0 | 0.033174 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.006736 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.4348 | 213 | 0.033172 | 7.0656
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.006753 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0062 | 0 | 0.033155 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.006753 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43962 | 0 | 0.033155 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.006758 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.1151 | 165 | 0.03315 | 5.4697
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.006765 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.1433 | 169 | 0.033143 | 5.6011
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.006769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.081228 | 12 | 0.033139 | 0.39767
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.006769 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.033139 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.006853 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23986 | 0 | 0.033055 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1311 | 0 | 0.032977 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0889 | 0 | 0.032977 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0916 | 0 | 0.032977 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0882 | 0 | 0.032977 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8644 | 0 | 0.032977 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.007027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.54811 | 0 | 0.032881 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.007027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.56216 | 0 | 0.032881 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.32642 | 46 | 0.032812 | 1.5093
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.32642 | 46 | 0.032812 | 1.5093
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.32642 | 46 | 0.032812 | 1.5093
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39028 | 55 | 0.032812 | 1.8047
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39028 | 55 | 0.032812 | 1.8047
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.38318 | 54 | 0.032812 | 1.7718
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.47937 | 0 | 0.032533 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4425 | 0 | 0.032533 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.47937 | 0 | 0.032533 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.47937 | 0 | 0.032533 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68823 | 0 | 0.032345 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66252 | 0 | 0.032345 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65798 | 0 | 0.032345 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41218 | 0 | 0.032345 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.092269 | 0 | 0.032345 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.008041 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.031867 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.00845 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.4225 | 50 | 0.031458 | 1.5729
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6355 | 0 | 0.030932 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5987 | 0 | 0.030932 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47573 | 0 | 0.030932 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3751 | 0 | 0.030932 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3778 | 0 | 0.030932 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.367 | 0 | 0.030932 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.8617 | 0 | 0.030932 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1901 | 0 | 0.030932 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35904 | 0 | 0.030932 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.008982 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28742 | 0 | 0.030926 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.008982 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26946 | 0 | 0.030926 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.90089 | 0 | 0.030926 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.83443 | 0 | 0.030926 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.92245 | 0 | 0.030926 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.91616 | 0 | 0.030926 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.010264 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.6525 | 161 | 0.029644 | 4.7727
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.010264 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7038 | 166 | 0.029644 | 4.9209
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.010264 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.5455 | 248 | 0.029644 | 7.3517
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.010264 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -5.6041 | 546 | 0.029644 | 16.1855
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.010264 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -6.5998 | 0 | 0.029644 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.010264 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13343 | 13 | 0.029644 | 0.38537
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.010375 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34237 | 0 | 0.029533 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.010628 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7324 | 0 | 0.02928 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.010628 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7324 | 0 | 0.02928 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.010628 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6039 | 0 | 0.02928 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.010649 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.9325 | 651 | 0.029259 | 19.0475
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.010649 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.006 | 564 | 0.029259 | 16.502
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.010649 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.3894 | 600 | 0.029259 | 17.5553
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.010739 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49507 | 0 | 0.029169 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4625 | 0 | 0.026732 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4625 | 0 | 0.026732 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5679 | 0 | 0.026732 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4428 | 0 | 0.026732 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.013849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.98328 | 0 | 0.026059 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.013849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13849 | 0 | 0.026059 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9114 | 0 | 0.025208 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0496 | 0 | 0.025208 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6615 | 0 | 0.025208 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4847 | 0 | 0.025208 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2642 | 0 | 0.025208 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2936 | 0 | 0.025208 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.735 | 0 | 0.025208 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2646 | 0 | 0.025208 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3818 | 0 | 0.025208 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.029 | 0 | 0.025208 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9261 | 0 | 0.025208 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0584 | 0 | 0.025208 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.95256 | 0 | 0.025208 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4847 | 0 | 0.025208 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4259 | 0 | 0.025208 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5141 | 0 | 0.025208 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1172 | 0 | 0.025208 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.176 | 0 | 0.025208 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.176 | 0 | 0.025208 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5137 | 0 | 0.025208 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.018223 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2027 | 66 | 0.021685 | 1.4312
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.018408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.60746 | 0 | 0.0215 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.018408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.4602 | 0 | 0.0215 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.018408 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0215 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4695 | 76 | 0.020572 | 1.5635
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4695 | 76 | 0.020572 | 1.5635
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0303 | 105 | 0.020572 | 2.16
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4309 | 74 | 0.020572 | 1.5223
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4309 | 74 | 0.020572 | 1.5223
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9723 | 102 | 0.020572 | 2.0983
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.019463 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -25.9442 | 0 | 0.020445 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.019463 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -25.8469 | 0 | 0.020445 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.023143 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13886 | 0 | 0.016765 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.047385 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.016027 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.047385 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 37.292 | 787 | 0.016027 | 12.6131
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.024244 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015664 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.04599 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7274 | 255 | 0.014632 | 3.7311
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.04599 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.8525 | 149 | 0.014632 | 2.1801
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.04599 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.0365 | 153 | 0.014632 | 2.2387
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2707 | 0 | 0.011165 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.3282 | 0 | 0.011165 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2707 | 0 | 0.011165 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2994 | 0 | 0.011165 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2535 | 0 | 0.011165 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71857 | 0 | 0.011165 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3222 | 0 | 0.011165 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.8048 | 0 | 0.011165 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2532 | 0 | 0.011165 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.127 | 0 | 0.011165 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.029 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.392 | 0 | 0.010908 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.83532 | 0 | 0.010075 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.20883 | 0 | 0.010075 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1635 | 0 | 0.010075 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.44749 | 0 | 0.010075 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.20883 | 0 | 0.010075 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.44749 | 0 | 0.010075 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1635 | 0 | 0.010075 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1635 | 0 | 0.010075 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.029957 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.23966 | 0 | 0.0099508 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.030183 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.45275 | 0 | 0.0097248 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.030183 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.69421 | 0 | 0.0097248 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.030449 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.66988 | 22 | 0.0094588 | 0.20809
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.030449 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.33494 | 11 | 0.0094588 | 0.10405
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.030449 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.33494 | 11 | 0.0094588 | 0.10405
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.040679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.1018 | 150 | 0.0093209 | 1.3981
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.040679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2543 | 80 | 0.0093209 | 0.74567
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4659 | 47.7 | 0.0091768 | 0.43774
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1463 | 37.3 | 0.0091768 | 0.3423
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4136 | 46 | 0.0091768 | 0.42213
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4751 | 48 | 0.0091768 | 0.44049
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.030799 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2483 | 0 | 0.0091088 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.8901 | 0 | 0.0089578 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.7354 | 0 | 0.0089578 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.095 | 0 | 0.0089578 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.4878 | 0 | 0.0089578 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.5496 | 0 | 0.0089578 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.9306 | 0 | 0.0089578 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.03095 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.3714 | 0 | 0.0089578 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 25 | 0.0088288 | 0.22072
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 25 | 0.0088288 | 0.22072
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 25 | 0.0088288 | 0.22072
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.49726 | 16 | 0.0088288 | 0.14126
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 25 | 0.0088288 | 0.22072
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 25 | 0.0088288 | 0.22072
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 25 | 0.0088288 | 0.22072
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46619 | 15 | 0.0088288 | 0.13243
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.031151 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.4857 | 144 | 0.0087568 | 1.261
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.031151 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8564 | 188 | 0.0087568 | 1.6463
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.031278 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5094 | 336 | 0.0086298 | 2.8996
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.031278 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.63 | 180 | 0.0086298 | 1.5534
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.031282 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.6391 | 0 | 0.0086258 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.031282 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.6485 | 0 | 0.0086258 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.031282 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.7861 | 0 | 0.0086258 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.031288 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6318 | 180 | 0.0086198 | 1.5516
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.031351 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.4712 | 334 | 0.0085568 | 2.858
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.031351 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.6593 | 340 | 0.0085568 | 2.9093
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.031351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6432 | 180 | 0.0085568 | 1.5402
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.031351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6432 | 180 | 0.0085568 | 1.5402
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.031362 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78405 | 0 | 0.0085458 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.031362 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78405 | 0 | 0.0085458 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.031394 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.193 | 0 | 0.0085138 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.031396 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.193 | 0 | 0.0085118 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.031547 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.91486 | 0 | 0.0083608 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9702 | 94 | 0.0083098 | 0.78113
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2955 | 41 | 0.0083098 | 0.3407
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2007 | 38 | 0.0083098 | 0.31577
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.60036 | 19 | 0.0083098 | 0.15789
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9702 | 94 | 0.0083098 | 0.78113
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1375 | 36 | 0.0083098 | 0.29915
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.3587 | 43 | 0.0083098 | 0.35732
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.69516 | 22 | 0.0083098 | 0.18282
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.6765 | 148 | 0.0083098 | 1.2299
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5799 | 50 | 0.0083098 | 0.41549
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7379 | 55 | 0.0083098 | 0.45704
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5799 | 50 | 0.0083098 | 0.41549
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.03162 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0082878 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.03162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2016 | 38 | 0.0082878 | 0.31494
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.03162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.61027 | 19.3 | 0.0082878 | 0.15996
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.03162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.4743 | 15 | 0.0082878 | 0.12432
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.03162 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4861 | 47 | 0.0082878 | 0.38953
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.031682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5622 | 144 | 0.0082258 | 1.1845
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.031682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5622 | 144 | 0.0082258 | 1.1845
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.031682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4176 | 171 | 0.0082258 | 1.4066
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.031683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.5584 | 207 | 0.0082248 | 1.7025
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.031683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8657 | 216.7 | 0.0082248 | 1.7823
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.031683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6673 | 242 | 0.0082248 | 1.9904
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.031746 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6508 | 146.5 | 0.0081618 | 1.1957
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.031746 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6952 | 147.9 | 0.0081618 | 1.2071
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.031746 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4921 | 173 | 0.0081618 | 1.412
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.032143 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38572 | 0 | 0.0077648 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.032143 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.35357 | 0 | 0.0077648 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.032143 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38572 | 0 | 0.0077648 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.032145 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0077628 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.032522 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0073858 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.032652 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -20.5381 | 629 | 0.0072558 | 4.5639
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.038591 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.57886 | 0 | 0.0072329 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.038591 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.57886 | 0 | 0.0072329 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.033097 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0068108 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.033375 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065328 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.033378 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.3378 | 100 | 0.0065298 | 0.65298
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.033378 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.3378 | 100 | 0.0065298 | 0.65298
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.033378 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065298 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.033378 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065298 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.033378 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065298 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.033378 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065298 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.033642 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.80741 | 24 | 0.0062658 | 0.15038
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.033642 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.80741 | 24 | 0.0062658 | 0.15038
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.033642 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.77377 | 23 | 0.0062658 | 0.14411
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.035634 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.1111 | 396 | 0.0042738 | 1.6924
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.037643 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45172 | 0 | 0.0022648 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.037705 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -20.5869 | 546 | 0.0022028 | 1.2028
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.037705 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -28.2787 | 750 | 0.0022028 | 1.6521
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.037784 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.1915 | 58 | 0.0021238 | 0.12318
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.037784 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3628 | 89 | 0.0021238 | 0.18902
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6625 | 44 | 0.0021238 | 0.093449
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6625 | 44 | 0.0021238 | 0.093449
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6247 | 43 | 0.0021238 | 0.091325
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7003 | 45 | 0.0021238 | 0.095573
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.037909 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8759 | 155 | 0.0019988 | 0.30982
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.037909 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4445 | 170 | 0.0019988 | 0.3398
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.037909 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8759 | 155 | 0.0019988 | 0.30982
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.037992 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.4627 | 407 | 0.0019158 | 0.77975
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.038005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.943 | 209 | 0.0019028 | 0.39769
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.038005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.2091 | 216 | 0.0019028 | 0.41101
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7482 | 46 | 0.0019028 | 0.087531
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7862 | 47 | 0.0019028 | 0.089434
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7482 | 46 | 0.0019028 | 0.087531
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7482 | 46 | 0.0019028 | 0.087531
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.038049 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.6762 | 412 | 0.0018588 | 0.76584
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.038049 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.2196 | 400 | 0.0018588 | 0.74354
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.038075 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.1438 | 424 | 0.0018328 | 0.77713
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.038075 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.1819 | 425 | 0.0018328 | 0.77896
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.038176 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0017318 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.038176 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0017318 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.038176 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0017318 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.2549 | 224 | 0.0010299 | 0.23069
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.3197 | 226 | 0.0010299 | 0.23275
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.8663 | 212 | 0.0010299 | 0.21833
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.8339 | 211 | 0.0010299 | 0.2173
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.032355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0016 | 216.4 | 0.00099687 | 0.21572
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.032355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9919 | 216.1 | 0.00099687 | 0.21542
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7301 | 147 | 0.00092784 | 0.13639
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3792 | 138 | 0.00092784 | 0.12804
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4572 | 140 | 0.00092784 | 0.1299
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7301 | 147 | 0.00092784 | 0.13639
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0944 | 182 | 0.00092784 | 0.16887
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.718 | 198 | 0.00092784 | 0.18371
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.032063 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.3866 | 168 | 0.00070487 | 0.11842
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.032063 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8857 | 90 | 0.00070487 | 0.063439
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.031339 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.1424 | 196 | -1.9126e-05 | -0.0037488
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.031339 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4786 | 111 | -1.9126e-05 | -0.002123
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.5583 | 114 | -7.7157e-05 | -0.0087958
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.8767 | 222 | -7.7157e-05 | -0.017129
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.3572 | 184 | -7.7157e-05 | -0.014197
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.9566 | 224 | -7.7157e-05 | -0.017283
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.5983 | 115 | -7.7157e-05 | -0.008873
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.040044 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16018 | 0 | -0.00013616 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.040114 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.096274 | 0 | -0.00020616 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.040114 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.096274 | 0 | -0.00020616 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.031121 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.2928 | 395 | -0.00023713 | -0.093665
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.031121 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 13.5376 | 435 | -0.00023713 | -0.10315
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.1759 | 70 | -0.00027413 | -0.019189
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.1448 | 69 | -0.00027413 | -0.018915
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.1448 | 69 | -0.00027413 | -0.018915
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.1137 | 68 | -0.00027413 | -0.018641
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.031084 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 13.5215 | 435 | -0.00027413 | -0.11924
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7362 | 142 | -0.00048816 | -0.069318
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8574 | 145 | -0.00048816 | -0.070783
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.0998 | 151 | -0.00048816 | -0.073712
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7148 | 290 | -0.00048816 | -0.14157
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.03076 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00059813 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.040653 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.097567 | 0 | -0.00074516 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.040653 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.097567 | 0 | -0.00074516 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.040653 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11383 | 0 | -0.00074516 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.03061 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.6516 | 217.3 | -0.00074813 | -0.16257
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.03061 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.2751 | 205 | -0.00074813 | -0.15337
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.03061 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.3382 | 272.4 | -0.00074813 | -0.20379
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.030564 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.8463 | 224 | -0.00079413 | -0.17788
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.030522 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00083613 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.030522 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00083613 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.030522 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00083613 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.030486 | north | 3 | N | N | Nnorth | Nnorth | 1 | 35.2723 | 0 | -0.00087213 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.030486 | north | 3 | N | N | Nnorth | Nnorth | 1 | 35.3028 | 0 | -0.00087213 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.030484 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.5971 | 118 | -0.00087413 | -0.10315
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.030484 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5057 | 115 | -0.00087413 | -0.10052
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.030484 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.9491 | 556 | -0.00087413 | -0.48601
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.030257 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.54463 | 18 | -0.0011011 | -0.01982
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.030257 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.54463 | 18 | -0.0011011 | -0.01982
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.030257 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.1498 | 38 | -0.0011011 | -0.041843
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.030209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8125 | 60 | -0.0011491 | -0.068948
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.030209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9032 | 63 | -0.0011491 | -0.072395
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.030187 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0011711 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.03018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.6918 | 288 | -0.0011781 | -0.3393
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.03018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4365 | 147 | -0.0011781 | -0.17318
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.03018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4365 | 147 | -0.0011781 | -0.17318
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.030165 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0011931 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.030092 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1967 | 73 | -0.0012661 | -0.092427
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.030092 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.5809 | 119 | -0.0012661 | -0.15067
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.030092 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.1689 | 205 | -0.0012661 | -0.25956
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.030092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.0694 | 102 | -0.0012661 | -0.12914
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.030092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.8888 | 96 | -0.0012661 | -0.12155
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.030091 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0012671 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.030091 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0012671 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.03007 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.3829 | 112.5 | -0.0012881 | -0.14491
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.030051 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.202 | 0 | -0.0013071 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.030051 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.202 | 0 | -0.0013071 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.030033 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.1056 | 170 | -0.0013251 | -0.22527
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.030033 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.6172 | 520 | -0.0013251 | -0.68907
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.030015 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2006 | 40 | -0.0013431 | -0.053725
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.030013 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 11.1048 | 370 | -0.0013451 | -0.4977
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.2018 | 0 | -0.0013451 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.2318 | 0 | -0.0013451 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.274 | 0 | -0.0013451 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.2919 | 0 | -0.0013451 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.3219 | 0 | -0.0013451 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.304 | 0 | -0.0013451 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.03 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.37 | 79 | -0.0013581 | -0.10729
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.03 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.18 | 106 | -0.0013581 | -0.14396
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.03 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.38 | 146 | -0.0013581 | -0.19829
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.03 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.28 | 76 | -0.0013581 | -0.10322
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7997 | 160 | -0.0013601 | -0.21762
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6797 | 156 | -0.0013601 | -0.21218
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.8796 | 196 | -0.0013601 | -0.26658
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6797 | 156 | -0.0013601 | -0.21218
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7097 | 157 | -0.0013601 | -0.21354
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.9396 | 198 | -0.0013601 | -0.26931
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.029995 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 11.6381 | 388 | -0.0013631 | -0.52889
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.029995 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.4474 | 515 | -0.0013631 | -0.70201
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.029982 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.2487 | 0 | -0.0013761 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.029982 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.3866 | 0 | -0.0013761 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.029982 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.6504 | 0 | -0.0013761 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.029973 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.7249 | 558 | -0.0013851 | -0.7729
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.029973 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.3544 | 579 | -0.0013851 | -0.80199
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.029973 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 24.2182 | 808 | -0.0013851 | -1.1192
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.02997 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.5994 | 20 | -0.0013881 | -0.027763
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.02997 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.74925 | 25 | -0.0013881 | -0.034703
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.02997 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2288 | 41 | -0.0013881 | -0.056913
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7926 | 161 | -0.0015901 | -0.25601
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.882 | 164 | -0.0015901 | -0.26078
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.882 | 164 | -0.0015901 | -0.26078
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.324 | 414 | -0.0015901 | -0.65831
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8224 | 162 | -0.0015901 | -0.2576
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7926 | 161 | -0.0015901 | -0.25601
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8522 | 163 | -0.0015901 | -0.25919
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.1751 | 409 | -0.0015901 | -0.65036
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.029713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0615 | 204 | -0.0016451 | -0.33561
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.029713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.9723 | 201 | -0.0016451 | -0.33067
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.029713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.1905 | 242 | -0.0016451 | -0.39812
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.02954 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.35448 | 0 | -0.0018181 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.02954 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.35448 | 0 | -0.0018181 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.029508 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.541 | 120 | -0.0018501 | -0.22202
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.3774 | 223.9 | -0.0019742 | -0.44201
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4235 | 225 | -0.0019742 | -0.44419
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4067 | 224.6 | -0.0019742 | -0.4434
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4946 | 226.7 | -0.0019742 | -0.44754
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57904 | 20 | -0.0024061 | -0.048123
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57904 | 20 | -0.0024061 | -0.048123
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57904 | 20 | -0.0024061 | -0.048123
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.49218 | 17 | -0.0024061 | -0.040904
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.028928 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.7357 | 60 | -0.0024301 | -0.14581
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.02891 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.5811 | 366 | -0.0024481 | -0.89601
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.028873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.6653 | 785 | -0.0024851 | -1.9508
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.028873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.954 | 795 | -0.0024851 | -1.9757
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.028873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.5209 | 780 | -0.0024851 | -1.9384
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.028818 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.974 | 242 | -0.0025401 | -0.61471
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.2547 | 0 | -0.0026101 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.7372 | 0 | -0.0026101 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.1685 | 0 | -0.0026101 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.4705 | 0 | -0.0026101 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.042595 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.4436 | 433 | -0.0026872 | -1.1635
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.042637 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.9 | 584 | -0.0027292 | -1.5938
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.042637 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -25.369 | 595 | -0.0027292 | -1.6238
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.028613 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0027451 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.0286 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.43 | 50 | -0.0027581 | -0.13791
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.028548 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.1957 | 182 | -0.0028101 | -0.51144
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.028548 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.8172 | 484 | -0.0028101 | -1.3601
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.028095 | west | 4 | Y | N | Ywest | Nwest | 1 | 18.2533 | 649.7 | -0.0032631 | -2.1201
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.043249 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25949 | 0 | -0.0033412 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.027832 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5923 | 165 | -0.0035261 | -0.58181
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1726 | 50 | -0.0035452 | -0.17726
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1726 | 50 | -0.0035452 | -0.17726
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1726 | 50 | -0.0035452 | -0.17726
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1726 | 50 | -0.0035452 | -0.17726
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.027491 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4879 | 236 | -0.0038671 | -0.91264
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.027489 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.9956 | 400 | -0.0038691 | -1.5477
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.027259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1297 | 151.5 | -0.0040991 | -0.62102
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.027259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1515 | 152.3 | -0.0040991 | -0.6243
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.027259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8385 | 177.5 | -0.0040991 | -0.72759
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.027189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0974 | 150.7 | -0.0041691 | -0.62829
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.027189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1055 | 151 | -0.0041691 | -0.62954
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.027189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8233 | 177.4 | -0.0041691 | -0.7396
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.026948 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.6169 | 60 | -0.0044101 | -0.26461
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.026863 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.5207 | 615 | -0.0044951 | -2.7645
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.026863 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 15.7686 | 587 | -0.0044951 | -2.6386
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.026549 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9823 | 150 | -0.0048091 | -0.72137
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5421 | 209 | -0.0048411 | -1.0118
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3544 | 126.5 | -0.0048411 | -0.6124
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6027 | 249 | -0.0048411 | -1.2054
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2238 | 197 | -0.0048411 | -0.9537
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.99199 | 37.5 | -0.0049051 | -0.18394
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8437 | 107.5 | -0.0049051 | -0.5273
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5712 | 135 | -0.0049051 | -0.66219
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1479 | 119 | -0.0049051 | -0.58371
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7776 | 105 | -0.0049051 | -0.51504
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1295 | 80.5 | -0.0049051 | -0.39486
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.026315 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2894 | 125 | -0.0050431 | -0.63039
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.026315 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2894 | 125 | -0.0050431 | -0.63039
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.026253 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9379 | 150 | -0.0051051 | -0.76577
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.026253 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6516 | 101 | -0.0051051 | -0.51562
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.026234 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2037 | 84 | -0.0051241 | -0.43043
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.026162 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.59 | 99 | -0.0051961 | -0.51442
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.026162 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5959 | 61 | -0.0051961 | -0.31696
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.026162 | west | 7 | N | N | Nwest | Nwest | 1 | 0.65405 | 0 | -0.0051961 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.026162 | west | 7 | N | N | Nwest | Nwest | 1 | 1.1956 | 0 | -0.0051961 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.026162 | west | 7 | N | N | Nwest | Nwest | 1 | 1.1956 | 0 | -0.0051961 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.026155 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6879 | 141 | -0.0052031 | -0.73364
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.026155 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1386 | 120 | -0.0052031 | -0.62438
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.026131 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.6463 | 63 | -0.0052271 | -0.32931
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.723 | 66 | -0.0052521 | -0.34664
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.8013 | 69 | -0.0052521 | -0.3624
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.8013 | 69 | -0.0052521 | -0.3624
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.7491 | 67 | -0.0052521 | -0.35189
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.7491 | 67 | -0.0052521 | -0.35189
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.6969 | 65 | -0.0052521 | -0.34139
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9069 | 150 | -0.0053121 | -0.79682
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.7301 | 220 | -0.0053121 | -1.1687
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2092 | 200 | -0.0053121 | -1.0624
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.175 | 121.9 | -0.0053121 | -0.64755
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.045262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62009 | 0 | -0.0053542 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.025971 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6748 | 180 | -0.0053871 | -0.96968
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.025971 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6748 | 180 | -0.0053871 | -0.96968
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.025969 | west | 8 | N | N | Nwest | Nwest | 1 | 1.8178 | 0 | -0.0053891 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.025969 | west | 8 | N | N | Nwest | Nwest | 1 | 1.9061 | 0 | -0.0053891 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.025969 | west | 8 | N | N | Nwest | Nwest | 1 | 1.8282 | 0 | -0.0053891 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.025946 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8379 | 225 | -0.0054121 | -1.2177
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.045366 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.1445 | 422 | -0.0054582 | -2.3033
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.025887 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1064 | 120 | -0.0054711 | -0.65654
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.025875 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.105 | 120 | -0.0054831 | -0.65798
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.025833 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1 | 120 | -0.0055251 | -0.66302
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.025833 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0191 | 233 | -0.0055251 | -1.2874
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.025833 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3968 | 170.2 | -0.0055251 | -0.94038
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.025706 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5062 | 214.2 | -0.0056521 | -1.2107
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.025701 | west | 8 | N | N | Nwest | Nwest | 1 | 0.66309 | 0 | -0.0056571 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.025644 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5772 | 100.5 | -0.0057141 | -0.57427
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.02564 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.4871 | 58 | -0.0057181 | -0.33165
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.794 | 70 | -0.0057291 | -0.40104
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.794 | 70 | -0.0057291 | -0.40104
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3784 | 92.8 | -0.0057291 | -0.53166
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0503 | 80 | -0.0057291 | -0.45833
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0503 | 80 | -0.0057291 | -0.45833
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.9473 | 115 | -0.0057291 | -0.65885
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.3349 | 208.2 | -0.0057341 | -1.1938
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6412 | 142.1 | -0.0057341 | -0.81482
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.3926 | 132.4 | -0.0057341 | -0.7592
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.4849 | 136 | -0.0057341 | -0.77984
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7667 | 147 | -0.0057341 | -0.84292
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.381 | 210 | -0.0057341 | -1.2042
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.045734 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2806 | 0 | -0.0058262 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.045734 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3263 | 0 | -0.0058262 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.025531 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8296 | 150 | -0.0058271 | -0.87407
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8584 | 112.5 | -0.0059501 | -0.66939
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7985 | 149.5 | -0.0059501 | -0.88954
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7259 | 186 | -0.0059501 | -1.1067
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.45 | 214.5 | -0.0059501 | -1.2763
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.025291 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.16692 | 6.6 | -0.0060671 | -0.040043
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.025291 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.86748 | 34.3 | -0.0060671 | -0.2081
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.025254 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7628 | 149 | -0.0061041 | -0.90951
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.025173 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.88106 | 35 | -0.0061851 | -0.21648
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.025173 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.75519 | 30 | -0.0061851 | -0.18555
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.6598 | 66 | -0.0062091 | -0.4098
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.6347 | 65 | -0.0062091 | -0.40359
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.685 | 67 | -0.0062091 | -0.41601
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.685 | 67 | -0.0062091 | -0.41601
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.685 | 67 | -0.0062091 | -0.41601
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.025149 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062091 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.025149 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062091 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.024985 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.235 | 169.5 | -0.0063731 | -1.0802
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.046352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83434 | 0 | -0.0064442 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.046352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83434 | 0 | -0.0064442 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.046352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69528 | 0 | -0.0064442 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.046648 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83966 | 0 | -0.0067402 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.046648 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83966 | 0 | -0.0067402 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.047735 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.5421 | 158 | -0.0078272 | -1.2367
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.047735 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6376 | 160 | -0.0078272 | -1.2523
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.047735 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3536 | 175 | -0.0078272 | -1.3698
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.023406 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.11235 | 0 | -0.0079521 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.048044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3418 | 132 | -0.0081362 | -1.074
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.048044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.4379 | 134 | -0.0081362 | -1.0902
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.048044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.5182 | 323 | -0.0081362 | -2.628
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.048236 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.356 | 152.5 | -0.0083282 | -1.27
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.048236 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2113 | 149.5 | -0.0083282 | -1.2451
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.048236 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.2197 | 232.6 | -0.0083282 | -1.9371
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.022684 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8147 | 80 | -0.0086741 | -0.69393
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.022684 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8147 | 80 | -0.0086741 | -0.69393
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.02249 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.6867 | 75 | -0.0088681 | -0.66511
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.02249 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7992 | 80 | -0.0088681 | -0.70945
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.02249 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8996 | 40 | -0.0088681 | -0.35473
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.022448 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7958 | 80 | -0.0089101 | -0.71281
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.022443 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7954 | 80 | -0.0089151 | -0.71321
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.022418 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3627 | 150 | -0.0089401 | -1.341
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.022418 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3627 | 150 | -0.0089401 | -1.341
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.022389 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 18.5157 | 827 | -0.0089691 | -7.4175
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.022389 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 18.3366 | 819 | -0.0089691 | -7.3457
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.049556 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7345 | 0 | -0.0096482 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.049556 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6849 | 0 | -0.0096482 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.049556 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7345 | 0 | -0.0096482 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.021451 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7161 | 80 | -0.0099071 | -0.79257
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.4477 | 49 | -0.010046 | -0.49226
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2979 | 46 | -0.010046 | -0.46212
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2979 | 46 | -0.010046 | -0.46212
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.3478 | 47 | -0.010046 | -0.47217
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.049954 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6929 | 154 | -0.010046 | -1.5471
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.049954 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.3932 | 148 | -0.010046 | -1.4868
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.3978 | 48 | -0.010046 | -0.48222
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.3978 | 48 | -0.010046 | -0.48222
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.021281 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.628 | 76.5 | -0.010077 | -0.7709
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.021125 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7745 | 84 | -0.010233 | -0.85958
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.050557 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.40446 | 0 | -0.010649 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.050557 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.40446 | 0 | -0.010649 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.050625 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.6937 | 310 | -0.010717 | -3.3223
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.050625 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -20.9081 | 413 | -0.010717 | -4.4262
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1466 | 42 | -0.011201 | -0.47045
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2488 | 44 | -0.011201 | -0.49285
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2488 | 44 | -0.011201 | -0.49285
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.4021 | 47 | -0.011201 | -0.52645
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.2544 | 855 | -0.012347 | -10.5568
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.2544 | 855 | -0.012347 | -10.5568
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.8954 | 152.3 | -0.012347 | -1.8805
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9087 | 153 | -0.012347 | -1.8891
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.015925 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.015433 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.059577 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -33.8993 | 569 | -0.019669 | -11.1918
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.059577 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -34.6142 | 581 | -0.019669 | -11.4278
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.011007 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.651 | 150 | -0.020351 | -3.0527
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.01096 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.0745 | 463 | -0.020398 | -9.4443
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.022088 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.022088 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.00927 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.15759 | 17 | -0.022088 | -0.3755
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.022088 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.022088 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.009251 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.29603 | 0 | -0.022107 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.3287 | 0 | -0.022741 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.3443 | 0 | -0.022741 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.3443 | 0 | -0.022741 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.2745 | 0 | -0.022741 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.008441 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.40517 | 48 | -0.022917 | -1.1
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.008441 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38829 | 46 | -0.022917 | -1.0542
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.008441 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.88631 | 105 | -0.022917 | -2.4063
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.031358 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.031358 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.022437 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.053795 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.9985 | 100 | -0.071343 | -7.1343

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3592 WACOATCO 13591 COTTONB_ C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 3405 - 3412 and 3409 - 3414 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.9985 | 0 | -0.071343 | 0 | 0 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.022437 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.053795 | 0 | 0 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.031358 | 0 | 0 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.031358 | 0 | 0 | 0 | Weighted Shift Factors
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.008441 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.40517 | 48 | -0.022917 | -1.1 | 48 | 1.1 | South | -0.039908
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.008441 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38829 | 46 | -0.022917 | -1.0542 | 94 | 2.1542 | North | 0.031358
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.008441 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.88631 | 105 | -0.022917 | -2.4063 | 199 | 4.5605 |  | -0.071266
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.3287 | 0 | -0.022741 | 0 | 199 | 4.5605
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.3443 | 0 | -0.022741 | 0 | 199 | 4.5605 | Line Rating | 247.95
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.3443 | 0 | -0.022741 | 0 | 199 | 4.5605 | Conc Gen | 393
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.008617 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.2745 | 0 | -0.022741 | 0 | 199 | 4.5605 | Weighted Imp. | 6.9186
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.009251 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.29603 | 0 | -0.022107 | 0 | 199 | 4.5605 | PTDF | 0.017605
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.022088 | 0 | 199 | 4.5605
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.022088 | 0 | 199 | 4.5605 | Concentration | -0.24703
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.00927 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.15759 | 17 | -0.022088 | -0.3755 | 216 | 4.936
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.022088 | 0 | 216 | 4.936
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.00927 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.022088 | 0 | 216 | 4.936
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.01096 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.0745 | 0 | -0.020398 | 0 | 216 | 4.936
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.011007 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.651 | 0 | -0.020351 | 0 | 216 | 4.936
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.059577 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -33.8993 | 0 | -0.019669 | 0 | 216 | 4.936
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.059577 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -34.6142 | 0 | -0.019669 | 0 | 216 | 4.936
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.015925 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.015433 | 0 | 216 | 4.936
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.2544 | 0 | -0.012347 | 0 | 216 | 4.936
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.2544 | 0 | -0.012347 | 0 | 216 | 4.936
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.8954 | 0 | -0.012347 | 0 | 216 | 4.936
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.019011 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.9087 | 0 | -0.012347 | 0 | 216 | 4.936
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1466 | 42 | -0.011201 | -0.47045 | 258 | 5.4065
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2488 | 44 | -0.011201 | -0.49285 | 302 | 5.8993
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2488 | 44 | -0.011201 | -0.49285 | 346 | 6.3922
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.051109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.4021 | 47 | -0.011201 | -0.52645 | 393 | 6.9186
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.050625 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.6937 | 310 | -0.010717 | -3.3223
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.050625 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -20.9081 | 413 | -0.010717 | -4.4262
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.050557 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.40446 | 0 | -0.010649 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.050557 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.40446 | 0 | -0.010649 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.021125 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7745 | 0 | -0.010233 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.021281 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.628 | 0 | -0.010077 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.4477 | 49 | -0.010046 | -0.49226
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2979 | 46 | -0.010046 | -0.46212
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.2979 | 46 | -0.010046 | -0.46212
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.3478 | 47 | -0.010046 | -0.47217
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.049954 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6929 | 154 | -0.010046 | -1.5471
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.049954 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.3932 | 148 | -0.010046 | -1.4868
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.3978 | 48 | -0.010046 | -0.48222
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.049954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.3978 | 48 | -0.010046 | -0.48222
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.021451 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7161 | 0 | -0.0099071 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.049556 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7345 | 0 | -0.0096482 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.049556 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6849 | 0 | -0.0096482 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.049556 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7345 | 0 | -0.0096482 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.022389 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 18.5157 | 0 | -0.0089691 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.022389 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 18.3366 | 0 | -0.0089691 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.022418 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3627 | 0 | -0.0089401 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.022418 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3627 | 0 | -0.0089401 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.022443 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7954 | 0 | -0.0089151 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.022448 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7958 | 0 | -0.0089101 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.02249 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.6867 | 0 | -0.0088681 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.02249 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7992 | 0 | -0.0088681 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.02249 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8996 | 0 | -0.0088681 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.022684 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8147 | 0 | -0.0086741 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.022684 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8147 | 0 | -0.0086741 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.048236 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.356 | 152.5 | -0.0083282 | -1.27
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.048236 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2113 | 149.5 | -0.0083282 | -1.2451
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.048236 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.2197 | 232.6 | -0.0083282 | -1.9371
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.048044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3418 | 132 | -0.0081362 | -1.074
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.048044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.4379 | 134 | -0.0081362 | -1.0902
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.048044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.5182 | 323 | -0.0081362 | -2.628
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.023406 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.11235 | 0 | -0.0079521 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.047735 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.5421 | 158 | -0.0078272 | -1.2367
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.047735 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6376 | 160 | -0.0078272 | -1.2523
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.047735 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3536 | 175 | -0.0078272 | -1.3698
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.046648 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83966 | 0 | -0.0067402 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.046648 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83966 | 0 | -0.0067402 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.046352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83434 | 0 | -0.0064442 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.046352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83434 | 0 | -0.0064442 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.046352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69528 | 0 | -0.0064442 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.024985 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.235 | 0 | -0.0063731 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.6598 | 66 | -0.0062091 | -0.4098
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.6347 | 65 | -0.0062091 | -0.40359
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.685 | 67 | -0.0062091 | -0.41601
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.685 | 67 | -0.0062091 | -0.41601
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.025149 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.685 | 67 | -0.0062091 | -0.41601
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.025149 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062091 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.025149 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062091 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.025173 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.88106 | 0 | -0.0061851 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.025173 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.75519 | 0 | -0.0061851 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.025254 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7628 | 0 | -0.0061041 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.025291 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.16692 | 0 | -0.0060671 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.025291 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.86748 | 0 | -0.0060671 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8584 | 0 | -0.0059501 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7985 | 0 | -0.0059501 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7259 | 0 | -0.0059501 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.025408 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.45 | 0 | -0.0059501 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.025531 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8296 | 0 | -0.0058271 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.045734 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2806 | 0 | -0.0058262 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.045734 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3263 | 0 | -0.0058262 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.3349 | 208.2 | -0.0057341 | -1.1938
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6412 | 142.1 | -0.0057341 | -0.81482
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.3926 | 132.4 | -0.0057341 | -0.7592
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.4849 | 136 | -0.0057341 | -0.77984
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7667 | 147 | -0.0057341 | -0.84292
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.025624 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.381 | 210 | -0.0057341 | -1.2042
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.794 | 70 | -0.0057291 | -0.40104
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.794 | 70 | -0.0057291 | -0.40104
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3784 | 92.8 | -0.0057291 | -0.53166
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0503 | 80 | -0.0057291 | -0.45833
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0503 | 80 | -0.0057291 | -0.45833
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.025629 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.9473 | 115 | -0.0057291 | -0.65885
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.02564 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.4871 | 0 | -0.0057181 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.025644 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5772 | 0 | -0.0057141 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.025701 | west | 8 | N | N | Nwest | Nwest | 1 | 0.66309 | 0 | -0.0056571 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.025706 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5062 | 0 | -0.0056521 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.025833 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1 | 0 | -0.0055251 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.025833 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0191 | 0 | -0.0055251 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.025833 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3968 | 0 | -0.0055251 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.025875 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.105 | 0 | -0.0054831 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.025887 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1064 | 0 | -0.0054711 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.045366 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.1445 | 422 | -0.0054582 | -2.3033
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.025946 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8379 | 0 | -0.0054121 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.025969 | west | 8 | N | N | Nwest | Nwest | 1 | 1.8178 | 0 | -0.0053891 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.025969 | west | 8 | N | N | Nwest | Nwest | 1 | 1.9061 | 0 | -0.0053891 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.025969 | west | 8 | N | N | Nwest | Nwest | 1 | 1.8282 | 0 | -0.0053891 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.025971 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6748 | 0 | -0.0053871 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.025971 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6748 | 0 | -0.0053871 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.045262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62009 | 0 | -0.0053542 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9069 | 0 | -0.0053121 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.7301 | 0 | -0.0053121 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2092 | 0 | -0.0053121 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.026046 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.175 | 0 | -0.0053121 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.723 | 66 | -0.0052521 | -0.34664
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.8013 | 69 | -0.0052521 | -0.3624
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.8013 | 69 | -0.0052521 | -0.3624
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.7491 | 67 | -0.0052521 | -0.35189
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.7491 | 67 | -0.0052521 | -0.35189
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.026106 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.6969 | 65 | -0.0052521 | -0.34139
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.026131 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.6463 | 0 | -0.0052271 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.026155 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6879 | 0 | -0.0052031 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.026155 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1386 | 0 | -0.0052031 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.026162 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.59 | 0 | -0.0051961 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.026162 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5959 | 0 | -0.0051961 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.026162 | west | 7 | N | N | Nwest | Nwest | 1 | 0.65405 | 0 | -0.0051961 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.026162 | west | 7 | N | N | Nwest | Nwest | 1 | 1.1956 | 0 | -0.0051961 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.026162 | west | 7 | N | N | Nwest | Nwest | 1 | 1.1956 | 0 | -0.0051961 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.026234 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2037 | 0 | -0.0051241 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.026253 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9379 | 0 | -0.0051051 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.026253 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6516 | 0 | -0.0051051 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.026315 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2894 | 0 | -0.0050431 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.026315 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2894 | 0 | -0.0050431 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.99199 | 0 | -0.0049051 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8437 | 0 | -0.0049051 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5712 | 0 | -0.0049051 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1479 | 0 | -0.0049051 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.7776 | 0 | -0.0049051 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.026453 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1295 | 0 | -0.0049051 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5421 | 0 | -0.0048411 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3544 | 0 | -0.0048411 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6027 | 0 | -0.0048411 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.026517 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2238 | 0 | -0.0048411 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.026549 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9823 | 0 | -0.0048091 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.026863 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.5207 | 0 | -0.0044951 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.026863 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 15.7686 | 0 | -0.0044951 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.026948 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.6169 | 0 | -0.0044101 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.027189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0974 | 150.7 | -0.0041691 | -0.62829
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.027189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1055 | 151 | -0.0041691 | -0.62954
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.027189 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8233 | 177.4 | -0.0041691 | -0.7396
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.027259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1297 | 151.5 | -0.0040991 | -0.62102
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.027259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1515 | 152.3 | -0.0040991 | -0.6243
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.027259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8385 | 177.5 | -0.0040991 | -0.72759
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.027489 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.9956 | 0 | -0.0038691 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.027491 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4879 | 0 | -0.0038671 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1726 | 50 | -0.0035452 | -0.17726
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1726 | 50 | -0.0035452 | -0.17726
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1726 | 50 | -0.0035452 | -0.17726
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.043453 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.1726 | 50 | -0.0035452 | -0.17726
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.027832 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5923 | 0 | -0.0035261 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.043249 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25949 | 0 | -0.0033412 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.028095 | west | 4 | Y | N | Ywest | Nwest | 1 | 18.2533 | 0 | -0.0032631 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.028548 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.1957 | 182 | -0.0028101 | -0.51144
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.028548 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.8172 | 484 | -0.0028101 | -1.3601
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.0286 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.43 | 0 | -0.0027581 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.028613 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0027451 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.042637 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.9 | 0 | -0.0027292 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.042637 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -25.369 | 0 | -0.0027292 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.042595 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.4436 | 0 | -0.0026872 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.2547 | 0 | -0.0026101 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.7372 | 0 | -0.0026101 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.1685 | 0 | -0.0026101 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.028748 | north | 1 | N | N | Nnorth | Nnorth | 1 | 11.4705 | 0 | -0.0026101 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.028818 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.974 | 242 | -0.0025401 | -0.61471
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.028873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.6653 | 0 | -0.0024851 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.028873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.954 | 0 | -0.0024851 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.028873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.5209 | 0 | -0.0024851 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.02891 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.5811 | 366 | -0.0024481 | -0.89601
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.028928 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.7357 | 0 | -0.0024301 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57904 | 20 | -0.0024061 | -0.048123
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57904 | 20 | -0.0024061 | -0.048123
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.57904 | 20 | -0.0024061 | -0.048123
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.028952 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.49218 | 17 | -0.0024061 | -0.040904
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.3774 | 223.9 | -0.0019742 | -0.44201
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4235 | 225 | -0.0019742 | -0.44419
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4067 | 224.6 | -0.0019742 | -0.4434
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.041882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.4946 | 226.7 | -0.0019742 | -0.44754
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.029508 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.541 | 0 | -0.0018501 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.02954 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.35448 | 0 | -0.0018181 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.02954 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.35448 | 0 | -0.0018181 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.029713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0615 | 204 | -0.0016451 | -0.33561
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.029713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.9723 | 201 | -0.0016451 | -0.33067
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.029713 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.1905 | 242 | -0.0016451 | -0.39812
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7926 | 161 | -0.0015901 | -0.25601
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.882 | 164 | -0.0015901 | -0.26078
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.882 | 164 | -0.0015901 | -0.26078
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.324 | 414 | -0.0015901 | -0.65831
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8224 | 162 | -0.0015901 | -0.2576
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7926 | 161 | -0.0015901 | -0.25601
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.8522 | 163 | -0.0015901 | -0.25919
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.029768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.1751 | 409 | -0.0015901 | -0.65036
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.02997 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.5994 | 20 | -0.0013881 | -0.027763
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.02997 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.74925 | 25 | -0.0013881 | -0.034703
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.02997 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2288 | 41 | -0.0013881 | -0.056913
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.029973 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.7249 | 0 | -0.0013851 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.029973 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.3544 | 0 | -0.0013851 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.029973 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 24.2182 | 0 | -0.0013851 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.029982 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.2487 | 0 | -0.0013761 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.029982 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.3866 | 0 | -0.0013761 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.029982 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.6504 | 0 | -0.0013761 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.029995 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 11.6381 | 388 | -0.0013631 | -0.52889
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.029995 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.4474 | 515 | -0.0013631 | -0.70201
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7997 | 160 | -0.0013601 | -0.21762
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6797 | 156 | -0.0013601 | -0.21218
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.8796 | 196 | -0.0013601 | -0.26658
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6797 | 156 | -0.0013601 | -0.21218
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7097 | 157 | -0.0013601 | -0.21354
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.029998 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.9396 | 198 | -0.0013601 | -0.26931
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.03 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.37 | 79 | -0.0013581 | -0.10729
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.03 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.18 | 106 | -0.0013581 | -0.14396
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.03 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.38 | 146 | -0.0013581 | -0.19829
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.03 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.28 | 76 | -0.0013581 | -0.10322
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.030013 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 11.1048 | 370 | -0.0013451 | -0.4977
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.2018 | 0 | -0.0013451 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.2318 | 0 | -0.0013451 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.274 | 0 | -0.0013451 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.2919 | 0 | -0.0013451 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.3219 | 0 | -0.0013451 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.030013 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.304 | 0 | -0.0013451 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.030015 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2006 | 40 | -0.0013431 | -0.053725
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.030033 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.1056 | 170 | -0.0013251 | -0.22527
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.030033 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.6172 | 520 | -0.0013251 | -0.68907
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.030051 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.202 | 0 | -0.0013071 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.030051 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.202 | 0 | -0.0013071 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.03007 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.3829 | 0 | -0.0012881 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.030091 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0012671 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.030091 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0012671 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.030092 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1967 | 73 | -0.0012661 | -0.092427
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.030092 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.5809 | 119 | -0.0012661 | -0.15067
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.030092 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.1689 | 205 | -0.0012661 | -0.25956
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.030092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.0694 | 102 | -0.0012661 | -0.12914
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.030092 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.8888 | 96 | -0.0012661 | -0.12155
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.030165 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0011931 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.03018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.6918 | 288 | -0.0011781 | -0.3393
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.03018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4365 | 147 | -0.0011781 | -0.17318
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.03018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4365 | 147 | -0.0011781 | -0.17318
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.030187 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0011711 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.030209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8125 | 60 | -0.0011491 | -0.068948
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.030209 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9032 | 63 | -0.0011491 | -0.072395
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.030257 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.54463 | 18 | -0.0011011 | -0.01982
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.030257 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.54463 | 18 | -0.0011011 | -0.01982
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.030257 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.1498 | 38 | -0.0011011 | -0.041843
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.030484 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.5971 | 118 | -0.00087413 | -0.10315
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.030484 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5057 | 115 | -0.00087413 | -0.10052
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.030484 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.9491 | 556 | -0.00087413 | -0.48601
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.030486 | north | 3 | N | N | Nnorth | Nnorth | 1 | 35.2723 | 0 | -0.00087213 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.030486 | north | 3 | N | N | Nnorth | Nnorth | 1 | 35.3028 | 0 | -0.00087213 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.030522 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00083613 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.030522 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00083613 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.030522 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00083613 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.030564 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.8463 | 224 | -0.00079413 | -0.17788
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.03061 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.6516 | 217.3 | -0.00074813 | -0.16257
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.03061 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.2751 | 205 | -0.00074813 | -0.15337
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.03061 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.3382 | 272.4 | -0.00074813 | -0.20379
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.040653 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.097567 | 0 | -0.00074516 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.040653 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.097567 | 0 | -0.00074516 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.040653 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11383 | 0 | -0.00074516 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.03076 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00059813 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7362 | 142 | -0.00048816 | -0.069318
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8574 | 145 | -0.00048816 | -0.070783
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.0998 | 151 | -0.00048816 | -0.073712
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.040396 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7148 | 290 | -0.00048816 | -0.14157
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.031084 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 13.5215 | 435 | -0.00027413 | -0.11924
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.1759 | 70 | -0.00027413 | -0.019189
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.1448 | 69 | -0.00027413 | -0.018915
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.1448 | 69 | -0.00027413 | -0.018915
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.031084 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.1137 | 68 | -0.00027413 | -0.018641
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.031121 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.2928 | 395 | -0.00023713 | -0.093665
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.031121 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 13.5376 | 435 | -0.00023713 | -0.10315
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.040114 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.096274 | 0 | -0.00020616 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.040114 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.096274 | 0 | -0.00020616 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.040044 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16018 | 0 | -0.00013616 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.5583 | 0 | -7.7157e-05 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.8767 | 0 | -7.7157e-05 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.3572 | 0 | -7.7157e-05 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.9566 | 0 | -7.7157e-05 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.039985 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.5983 | 0 | -7.7157e-05 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.031339 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.1424 | 196 | -1.9126e-05 | -0.0037488
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.031339 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4786 | 111 | -1.9126e-05 | -0.002123
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.032063 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.3866 | 168 | 0.00070487 | 0.11842
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.032063 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8857 | 90 | 0.00070487 | 0.063439
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7301 | 147 | 0.00092784 | 0.13639
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3792 | 138 | 0.00092784 | 0.12804
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4572 | 140 | 0.00092784 | 0.1299
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7301 | 147 | 0.00092784 | 0.13639
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0944 | 182 | 0.00092784 | 0.16887
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.03898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.718 | 198 | 0.00092784 | 0.18371
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.032355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0016 | 216.4 | 0.00099687 | 0.21572
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.032355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9919 | 216.1 | 0.00099687 | 0.21542
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.2549 | 224 | 0.0010299 | 0.23069
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.3197 | 226 | 0.0010299 | 0.23275
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.8663 | 212 | 0.0010299 | 0.21833
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.032388 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.8339 | 211 | 0.0010299 | 0.2173
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.038176 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0017318 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.038176 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0017318 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.038176 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0017318 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.038075 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.1438 | 0 | 0.0018328 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.038075 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.1819 | 0 | 0.0018328 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.038049 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.6762 | 412 | 0.0018588 | 0.76584
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.038049 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.2196 | 400 | 0.0018588 | 0.74354
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.038005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.943 | 209 | 0.0019028 | 0.39769
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.038005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.2091 | 216 | 0.0019028 | 0.41101
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7482 | 46 | 0.0019028 | 0.087531
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7862 | 47 | 0.0019028 | 0.089434
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7482 | 46 | 0.0019028 | 0.087531
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.038005 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7482 | 46 | 0.0019028 | 0.087531
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.037992 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.4627 | 407 | 0.0019158 | 0.77975
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.037909 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8759 | 155 | 0.0019988 | 0.30982
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.037909 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4445 | 170 | 0.0019988 | 0.3398
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.037909 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8759 | 155 | 0.0019988 | 0.30982
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.037784 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.1915 | 58 | 0.0021238 | 0.12318
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.037784 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3628 | 89 | 0.0021238 | 0.18902
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6625 | 44 | 0.0021238 | 0.093449
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6625 | 44 | 0.0021238 | 0.093449
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6247 | 43 | 0.0021238 | 0.091325
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.037784 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7003 | 45 | 0.0021238 | 0.095573
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.037705 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -20.5869 | 0 | 0.0022028 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.037705 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -28.2787 | 0 | 0.0022028 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.037643 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45172 | 0 | 0.0022648 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.035634 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.1111 | 0 | 0.0042738 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.033642 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.80741 | 24 | 0.0062658 | 0.15038
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.033642 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.80741 | 24 | 0.0062658 | 0.15038
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.033642 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.77377 | 23 | 0.0062658 | 0.14411
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.033378 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.3378 | 100 | 0.0065298 | 0.65298
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.033378 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.3378 | 100 | 0.0065298 | 0.65298
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.033378 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065298 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.033378 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065298 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.033378 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065298 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.033378 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065298 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.033375 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0065328 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.033264 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.27942 | 8.4 | 0.0066438 | 0.055808
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.033097 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0068108 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.038591 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.57886 | 0 | 0.0072329 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.038591 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.57886 | 0 | 0.0072329 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.032652 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -20.5381 | 0 | 0.0072558 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.032522 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0073858 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.032145 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0077628 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.032143 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38572 | 0 | 0.0077648 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.032143 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.35357 | 0 | 0.0077648 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.032143 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38572 | 0 | 0.0077648 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.031746 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6508 | 146.5 | 0.0081618 | 1.1957
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.031746 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6952 | 147.9 | 0.0081618 | 1.2071
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.031746 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4921 | 173 | 0.0081618 | 1.412
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.031683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.5584 | 207 | 0.0082248 | 1.7025
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.031683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8657 | 216.7 | 0.0082248 | 1.7823
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.031683 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.6673 | 242 | 0.0082248 | 1.9904
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.031682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5622 | 144 | 0.0082258 | 1.1845
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.031682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5622 | 144 | 0.0082258 | 1.1845
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.031682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4176 | 171 | 0.0082258 | 1.4066
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.03162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2016 | 38 | 0.0082878 | 0.31494
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.03162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.61027 | 19.3 | 0.0082878 | 0.15996
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.03162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.4743 | 15 | 0.0082878 | 0.12432
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.03162 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4861 | 47 | 0.0082878 | 0.38953
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.03162 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0082878 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9702 | 0 | 0.0083098 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2955 | 0 | 0.0083098 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2007 | 0 | 0.0083098 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.60036 | 0 | 0.0083098 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9702 | 0 | 0.0083098 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1375 | 0 | 0.0083098 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.3587 | 0 | 0.0083098 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.69516 | 0 | 0.0083098 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.6765 | 0 | 0.0083098 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5799 | 0 | 0.0083098 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7379 | 0 | 0.0083098 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.031598 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5799 | 0 | 0.0083098 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.031547 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.91486 | 0 | 0.0083608 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.031396 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.193 | 0 | 0.0085118 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.031394 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.193 | 0 | 0.0085138 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.031362 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78405 | 0 | 0.0085458 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.031362 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.78405 | 0 | 0.0085458 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.031351 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.4712 | 334 | 0.0085568 | 2.858
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.031351 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.6593 | 340 | 0.0085568 | 2.9093
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.031351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6432 | 180 | 0.0085568 | 1.5402
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.031351 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6432 | 180 | 0.0085568 | 1.5402
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.031288 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6318 | 180 | 0.0086198 | 1.5516
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.031282 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.6391 | 0 | 0.0086258 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.031282 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.6485 | 0 | 0.0086258 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.031282 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.7861 | 0 | 0.0086258 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.031278 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5094 | 336 | 0.0086298 | 2.8996
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.031278 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.63 | 180 | 0.0086298 | 1.5534
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.031151 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.4857 | 144 | 0.0087568 | 1.261
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.031151 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8564 | 188 | 0.0087568 | 1.6463
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 0 | 0.0088288 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 0 | 0.0088288 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 0 | 0.0088288 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.49726 | 0 | 0.0088288 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 0 | 0.0088288 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 0 | 0.0088288 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77697 | 0 | 0.0088288 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.031079 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46619 | 0 | 0.0088288 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.8901 | 0 | 0.0089578 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.7354 | 0 | 0.0089578 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.095 | 0 | 0.0089578 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.4878 | 0 | 0.0089578 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.5496 | 0 | 0.0089578 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.03095 | south | 8 | N | N | Nsouth | Nsouth | -1 | -3.9306 | 0 | 0.0089578 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.03095 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.3714 | 0 | 0.0089578 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.030799 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2483 | 0 | 0.0091088 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4659 | 47.7 | 0.0091768 | 0.43774
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1463 | 37.3 | 0.0091768 | 0.3423
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4136 | 46 | 0.0091768 | 0.42213
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.030731 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.4751 | 48 | 0.0091768 | 0.44049
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.040679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.1018 | 150 | 0.0093209 | 1.3981
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.040679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2543 | 80 | 0.0093209 | 0.74567
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.030449 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.66988 | 22 | 0.0094588 | 0.20809
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.030449 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.33494 | 11 | 0.0094588 | 0.10405
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.030449 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.33494 | 11 | 0.0094588 | 0.10405
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.030183 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.45275 | 0 | 0.0097248 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.030183 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.69421 | 0 | 0.0097248 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.029957 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.23966 | 0 | 0.0099508 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.83532 | 0 | 0.010075 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.20883 | 0 | 0.010075 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1635 | 0 | 0.010075 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.44749 | 0 | 0.010075 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.20883 | 0 | 0.010075 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.44749 | 0 | 0.010075 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1635 | 0 | 0.010075 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.029833 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1635 | 0 | 0.010075 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.029 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.392 | 0 | 0.010908 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2707 | 0 | 0.011165 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.3282 | 0 | 0.011165 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2707 | 0 | 0.011165 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2994 | 0 | 0.011165 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2535 | 0 | 0.011165 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71857 | 0 | 0.011165 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3222 | 0 | 0.011165 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.8048 | 0 | 0.011165 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2532 | 0 | 0.011165 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.028743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.127 | 0 | 0.011165 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.04599 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7274 | 255 | 0.014632 | 3.7311
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.04599 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.8525 | 149 | 0.014632 | 2.1801
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.04599 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.0365 | 153 | 0.014632 | 2.2387
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.024244 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015664 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.047385 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.016027 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.047385 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 37.292 | 787 | 0.016027 | 12.6131
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.023143 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13886 | 0 | 0.016765 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.019463 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -25.9442 | 0 | 0.020445 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.019463 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -25.8469 | 0 | 0.020445 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4695 | 76 | 0.020572 | 1.5635
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4695 | 76 | 0.020572 | 1.5635
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0303 | 105 | 0.020572 | 2.16
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4309 | 74 | 0.020572 | 1.5223
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4309 | 74 | 0.020572 | 1.5223
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.019336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9723 | 102 | 0.020572 | 2.0983
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.018408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.60746 | 0 | 0.0215 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.018408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.4602 | 0 | 0.0215 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.018408 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0215 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.018223 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2027 | 66 | 0.021685 | 1.4312
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9114 | 0 | 0.025208 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0496 | 0 | 0.025208 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6615 | 0 | 0.025208 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4847 | 0 | 0.025208 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2642 | 0 | 0.025208 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2936 | 0 | 0.025208 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.735 | 0 | 0.025208 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2646 | 0 | 0.025208 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3818 | 0 | 0.025208 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.029 | 0 | 0.025208 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9261 | 0 | 0.025208 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0584 | 0 | 0.025208 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.95256 | 0 | 0.025208 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4847 | 0 | 0.025208 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4259 | 0 | 0.025208 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5141 | 0 | 0.025208 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1172 | 0 | 0.025208 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.176 | 0 | 0.025208 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.176 | 0 | 0.025208 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.0147 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5137 | 0 | 0.025208 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.013849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.98328 | 0 | 0.026059 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.013849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13849 | 0 | 0.026059 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4625 | 0 | 0.026732 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4625 | 0 | 0.026732 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5679 | 0 | 0.026732 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.013176 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4428 | 0 | 0.026732 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.010739 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49507 | 0 | 0.029169 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.010649 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.9325 | 0 | 0.029259 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.010649 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.006 | 0 | 0.029259 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.010649 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.3894 | 0 | 0.029259 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.010628 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7324 | 0 | 0.02928 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.010628 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7324 | 0 | 0.02928 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.010628 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6039 | 0 | 0.02928 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.010375 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34237 | 0 | 0.029533 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.010264 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.6525 | 161 | 0.029644 | 4.7727
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.010264 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7038 | 166 | 0.029644 | 4.9209
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.010264 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.5455 | 248 | 0.029644 | 7.3517
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.010264 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -5.6041 | 546 | 0.029644 | 16.1855
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.010264 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -6.5998 | 0 | 0.029644 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.010264 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13343 | 13 | 0.029644 | 0.38537
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.90089 | 0 | 0.030926 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.83443 | 0 | 0.030926 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.92245 | 0 | 0.030926 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.008982 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.91616 | 0 | 0.030926 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.008982 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28742 | 0 | 0.030926 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.008982 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26946 | 0 | 0.030926 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6355 | 0 | 0.030932 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5987 | 0 | 0.030932 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47573 | 0 | 0.030932 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3751 | 0 | 0.030932 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3778 | 0 | 0.030932 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.367 | 0 | 0.030932 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.8617 | 0 | 0.030932 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.008976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1901 | 0 | 0.030932 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.008976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35904 | 0 | 0.030932 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.00845 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.4225 | 50 | 0.031458 | 1.5729
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.008041 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.031867 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68823 | 0 | 0.032345 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66252 | 0 | 0.032345 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65798 | 0 | 0.032345 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41218 | 0 | 0.032345 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.007563 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.092269 | 0 | 0.032345 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.47937 | 0 | 0.032533 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4425 | 0 | 0.032533 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.47937 | 0 | 0.032533 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.007375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.47937 | 0 | 0.032533 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.32642 | 46 | 0.032812 | 1.5093
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.32642 | 46 | 0.032812 | 1.5093
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.32642 | 46 | 0.032812 | 1.5093
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39028 | 55 | 0.032812 | 1.8047
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39028 | 55 | 0.032812 | 1.8047
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.007096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.38318 | 54 | 0.032812 | 1.7718
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.007027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.54811 | 0 | 0.032881 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.007027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.56216 | 0 | 0.032881 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1311 | 0 | 0.032977 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0889 | 0 | 0.032977 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0916 | 0 | 0.032977 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0882 | 0 | 0.032977 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.006931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8644 | 0 | 0.032977 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.006853 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23986 | 0 | 0.033055 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.006769 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.081228 | 12 | 0.033139 | 0.39767
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.006769 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.033139 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.006765 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.1433 | 169 | 0.033143 | 5.6011
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.006758 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.1151 | 165 | 0.03315 | 5.4697
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.006753 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0062 | 0 | 0.033155 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.006753 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43962 | 0 | 0.033155 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.006736 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.4348 | 213 | 0.033172 | 7.0656
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.006734 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10909 | 0 | 0.033174 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43085 | 0 | 0.033176 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42546 | 0 | 0.033176 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55606 | 0 | 0.033176 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.006732 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49548 | 0 | 0.033176 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.006729 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.5342 | 228 | 0.033179 | 7.5648
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.006726 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2107 | 0 | 0.033182 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.006726 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0667 | 0 | 0.033182 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.006726 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.056 | 0 | 0.033182 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.46917 | 0 | 0.0333 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47578 | 0 | 0.0333 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25771 | 0 | 0.0333 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.006608 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19824 | 0 | 0.0333 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.006421 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.87326 | 0 | 0.033487 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.26905 | 42 | 0.033502 | 1.4071
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.26905 | 42 | 0.033502 | 1.4071
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24343 | 38 | 0.033502 | 1.2731
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.006406 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24343 | 38 | 0.033502 | 1.2731
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.006358 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0999 | 0 | 0.03355 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.006358 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85833 | 0 | 0.03355 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.63003 | 104 | 0.03385 | 3.5204
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.63003 | 104 | 0.03385 | 3.5204
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32713 | 54 | 0.03385 | 1.8279
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32107 | 53 | 0.03385 | 1.794
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32713 | 54 | 0.03385 | 1.8279
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.34531 | 57 | 0.03385 | 1.9294
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32713 | 54 | 0.03385 | 1.8279
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32713 | 54 | 0.03385 | 1.8279
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35136 | 58 | 0.03385 | 1.9633
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.006058 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35136 | 58 | 0.03385 | 1.9633
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.005943 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.3681 | 735 | 0.033965 | 24.9642
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19944 | 0 | 0.034042 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20355 | 0 | 0.034042 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19182 | 0 | 0.034042 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26925 | 0 | 0.034042 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10383 | 0 | 0.034042 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11967 | 0 | 0.034042 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11673 | 0 | 0.034042 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20531 | 0 | 0.034042 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10559 | 0 | 0.034042 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50096 | 0 | 0.034042 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.005866 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86817 | 0 | 0.034042 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.005767 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.069204 | 12 | 0.034141 | 0.40969
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.005642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02821 | 0 | 0.034266 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.005642 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11848 | 0 | 0.034266 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3666 | 0 | 0.034268 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37224 | 0 | 0.034268 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3948 | 0 | 0.034268 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35532 | 0 | 0.034268 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34968 | 0 | 0.034268 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.58656 | 0 | 0.034268 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.00564 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33276 | 0 | 0.034268 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.005635 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.06762 | 0 | 0.034273 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.005626 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.1801 | 743 | 0.034282 | 25.4714
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.005568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.87418 | 0 | 0.03434 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.00553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.95116 | 172 | 0.034378 | 5.913
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.00553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.95116 | 172 | 0.034378 | 5.913
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.00553 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.95116 | 172 | 0.034378 | 5.913
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86382 | 0 | 0.034602 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85639 | 0 | 0.034602 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84312 | 0 | 0.034602 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.005306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4284 | 0 | 0.034602 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.005229 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.0811 | 398 | 0.034679 | 13.8022
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28515 | 56 | 0.034816 | 1.9497
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30043 | 59 | 0.034816 | 2.0541
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28515 | 56 | 0.034816 | 1.9497
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28515 | 56 | 0.034816 | 1.9497
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30043 | 59 | 0.034816 | 2.0541
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.005092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28515 | 56 | 0.034816 | 1.9497
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.65273 | 0 | 0.036135 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.58859 | 0 | 0.036135 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.58104 | 0 | 0.036135 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.003773 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.58104 | 0 | 0.036135 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.003773 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61123 | 0 | 0.036135 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.069442 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.038084 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.069442 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.038084 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039908 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039908 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039908 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 268
| 25 | 268
| 30 | 268
| 35 | 268
| 40 | 268
| 45 | 268
| 50 | 268
| 55 | 268
| 60 | 267
| 65 | 261
| 70 | 256
| 75 | 250
| 80 | 245
| 85 | 239
| 90 | 233
| 95 | 226
| 100 | 220
| 105 | 213
| 110 | 206
| 115 | 199
| Max | 268
| Min | 199
| Avg | 247.95